## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_135-13_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_135-13_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_135-13_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_135-13_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_135-13_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_135-13_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_135-13_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_135-13_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_135-13_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_135-13_0_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_135-13_0_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_135-13_0_2_node_39 | 0.4 | n |  | TRUE
12 | bus_LV_135-13_0_2_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_135-13_0_2_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_135-13_0_2_node_126 | 0.4 | n |  | TRUE
15 | bus_LV_135-13_0_2_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_135-13_0_2_node_155 | 0.4 | n |  | TRUE
17 | bus_LV_135-13_0_2_node_156 | 0.4 | n |  | TRUE
18 | bus_LV_135-13_0_2_node_137 | 0.4 | n |  | TRUE
19 | bus_LV_135-13_0_2_node_57 | 0.4 | n |  | TRUE
20 | bus_LV_135-13_0_2_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_135-13_0_2_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_135-13_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_135-13_0_2_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_135-13_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_135-13_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_135-13_0_2_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_135-13_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_135-13_0_2_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_135-13_0_2_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_135-13_0_2_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_135-13_0_2_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_135-13_0_2_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_135-13_0_2_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_135-13_0_2_node_60 | 0.4 | n |  | TRUE
35 | bus_LV_135-13_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_135-13_0_2_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_135-13_0_2_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_135-13_0_2_node_120 | 0.4 | n |  | TRUE
39 | bus_LV_135-13_0_2_node_117 | 0.4 | n |  | TRUE
40 | bus_LV_135-13_0_2_node_113 | 0.4 | n |  | TRUE
41 | bus_LV_135-13_0_2_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_135-13_0_2_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_135-13_0_2_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_135-13_0_2_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_135-13_0_2_node_118 | 0.4 | n |  | TRUE
46 | bus_LV_135-13_0_2_node_112 | 0.4 | n |  | TRUE
47 | bus_LV_135-13_0_2_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_135-13_0_2_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_135-13_0_2_node_121 | 0.4 | n |  | TRUE
50 | bus_LV_135-13_0_2_node_122 | 0.4 | n |  | TRUE
51 | bus_LV_135-13_0_2_node_127 | 0.4 | n |  | TRUE
52 | bus_LV_135-13_0_2_node_150 | 0.4 | n |  | TRUE
53 | bus_LV_135-13_0_2_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_135-13_0_2_node_109 | 0.4 | n |  | TRUE
55 | bus_LV_135-13_0_2_node_110 | 0.4 | n |  | TRUE
56 | bus_LV_135-13_0_2_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_135-13_0_2_node_114 | 0.4 | n |  | TRUE
58 | bus_LV_135-13_0_2_node_119 | 0.4 | n |  | TRUE
59 | bus_LV_135-13_0_2_node_124 | 0.4 | n |  | TRUE
60 | bus_LV_135-13_0_2_node_125 | 0.4 | n |  | TRUE
61 | bus_LV_135-13_0_2_node_129 | 0.4 | n |  | TRUE
62 | bus_LV_135-13_0_2_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_135-13_0_2_node_131 | 0.4 | n |  | TRUE
64 | bus_LV_135-13_0_2_node_133 | 0.4 | n |  | TRUE
65 | bus_LV_135-13_0_2_node_135 | 0.4 | n |  | TRUE
66 | bus_LV_135-13_0_2_node_136 | 0.4 | n |  | TRUE
67 | bus_LV_135-13_0_2_node_143 | 0.4 | n |  | TRUE
68 | bus_LV_135-13_0_2_node_139 | 0.4 | n |  | TRUE
69 | bus_LV_135-13_0_2_node_138 | 0.4 | n |  | TRUE
70 | bus_LV_135-13_0_2_node_154 | 0.4 | n |  | TRUE
71 | bus_LV_135-13_0_2_node_147 | 0.4 | n |  | TRUE
72 | bus_LV_135-13_0_2_node_162 | 0.4 | n |  | TRUE
73 | bus_LV_135-13_0_2_node_140 | 0.4 | n |  | TRUE
74 | bus_LV_135-13_0_2_node_145 | 0.4 | n |  | TRUE
75 | bus_LV_135-13_0_2_node_141 | 0.4 | n |  | TRUE
76 | bus_LV_135-13_0_2_node_142 | 0.4 | n |  | TRUE
77 | bus_LV_135-13_0_2_node_161 | 0.4 | n |  | TRUE
78 | bus_LV_135-13_0_2_node_158 | 0.4 | n |  | TRUE
79 | bus_LV_135-13_0_2_node_165 | 0.4 | n |  | TRUE
80 | bus_LV_135-13_0_2_node_159 | 0.4 | n |  | TRUE
81 | bus_LV_135-13_0_2_node_144 | 0.4 | n |  | TRUE
82 | bus_LV_135-13_0_2_node_146 | 0.4 | n |  | TRUE
83 | bus_LV_135-13_0_2_node_148 | 0.4 | n |  | TRUE
84 | bus_LV_135-13_0_2_node_149 | 0.4 | n |  | TRUE
85 | bus_LV_135-13_0_2_node_151 | 0.4 | n |  | TRUE
86 | bus_LV_135-13_0_2_node_152 | 0.4 | n |  | TRUE
87 | bus_LV_135-13_0_2_node_153 | 0.4 | n |  | TRUE
88 | bus_LV_135-13_0_2_node_163 | 0.4 | n |  | TRUE
89 | bus_LV_135-13_0_2_node_160 | 0.4 | n |  | TRUE
90 | bus_MV_360_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_135-13_0_2_load_0 | 0 | 0.0036583 | 0.00091685 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_135-13_0_2_load_1 | 1 | 0.0050853 | 0.0012745 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_135-13_0_2_load_4 | 4 | 0.0035354 | 0.00088607 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_135-13_0_2_load_5 | 5 | 0.0074409 | 0.0018649 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_135-13_0_2_load_7 | 7 | 0.0054544 | 0.001367 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_135-13_0_2_load_8 | 8 | 0.0036293 | 0.00090958 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_135-13_0_2_load_37 | 10 | 0.0025528 | 0.0006398 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_135-13_0_2_load_33 | 12 | 0.0053571 | 0.0013426 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_135-13_0_2_load_126 | 14 | 0.0018247 | 0.0004573 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_135-13_0_2_load_156 | 17 | 0.005634 | 0.001412 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_135-13_0_2_load_137 | 18 | 0.0029224 | 0.00073243 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_135-13_0_2_load_57 | 19 | 0.0088117 | 0.0022084 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_135-13_0_2_load_10 | 20 | 0.0026853 | 0.000673 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_135-13_0_2_load_11 | 21 | 0.0064222 | 0.0016096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_135-13_0_2_load_13 | 23 | 0.0060405 | 0.0015139 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_135-13_0_2_load_17 | 27 | 0.001523 | 0.0003817 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_135-13_0_2_load_18 | 28 | 0.0019358 | 0.00048516 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_135-13_0_2_load_19 | 29 | 0.0057552 | 0.0014424 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_135-13_0_2_load_27 | 31 | 0.002875 | 0.00072054 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_135-13_0_2_load_22 | 32 | 0.003992 | 0.0010005 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_135-13_0_2_load_41 | 33 | 0.0018699 | 0.00046864 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_135-13_0_2_load_60 | 34 | 0.00094 | 0.00023559 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_135-13_0_2_load_56 | 36 | 0.0085826 | 0.002151 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_135-13_0_2_load_120 | 38 | 0.0069694 | 0.0017467 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_135-13_0_2_load_113 | 40 | 0.0035584 | 0.00089183 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_135-13_0_2_load_28 | 41 | 0.004329 | 0.001085 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_135-13_0_2_load_116 | 42 | 0.0038643 | 0.00096849 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_135-13_0_2_load_36 | 43 | 0.0045786 | 0.0011475 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_135-13_0_2_load_118 | 45 | 0.0065008 | 0.0016292 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_135-13_0_2_load_112 | 46 | 0.0019906 | 0.00049889 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_135-13_0_2_load_40 | 47 | 0.01228 | 0.0030776 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_135-13_0_2_load_35 | 48 | 0.0012669 | 0.00031753 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_135-13_0_2_load_121 | 49 | 0.0027543 | 0.00069029 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_135-13_0_2_load_127 | 51 | 0.0018185 | 0.00045575 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_135-13_0_2_load_150 | 52 | 0.00099719 | 0.00024992 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_135-13_0_2_load_55 | 53 | 0.0034272 | 0.00085893 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_135-13_0_2_load_109 | 54 | 0.0035175 | 0.00088157 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_135-13_0_2_load_110 | 55 | 0.0037262 | 0.00093387 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_135-13_0_2_load_111 | 56 | 0.0028115 | 0.00070464 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_135-13_0_2_load_119 | 58 | 0.0035133 | 0.00088052 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_135-13_0_2_load_124 | 59 | 0.0011254 | 0.00028206 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_135-13_0_2_load_125 | 60 | 0.0011086 | 0.00027783 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_135-13_0_2_load_129 | 61 | 0.0010322 | 0.00025869 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_135-13_0_2_load_130 | 62 | 0.0046964 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_135-13_0_2_load_135 | 65 | 0.0015064 | 0.00037753 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_135-13_0_2_load_136 | 66 | 0.0065584 | 0.0016437 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_135-13_0_2_load_143 | 67 | 0.0015682 | 0.00039303 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_135-13_0_2_load_154 | 70 | 0.0020217 | 0.0005067 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_135-13_0_2_load_162 | 72 | 0.0013661 | 0.00034239 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_135-13_0_2_load_145 | 74 | 0.0073065 | 0.0018312 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_135-13_0_2_load_141 | 75 | 0.016621 | 0.0041656 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_135-13_0_2_load_142 | 76 | 0.0052469 | 0.001315 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_135-13_0_2_load_158 | 78 | 0.002126 | 0.00053283 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_135-13_0_2_load_165 | 79 | 0.0043717 | 0.0010956 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_135-13_0_2_load_159 | 80 | 0.002126 | 0.00053283 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_135-13_0_2_load_144 | 81 | 0.0022394 | 0.00056124 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_135-13_0_2_load_148 | 83 | 0.0021891 | 0.00054865 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_135-13_0_2_load_149 | 84 | 0.0054518 | 0.0013663 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_135-13_0_2_load_151 | 85 | 0.0043183 | 0.0010823 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_135-13_0_2_load_152 | 86 | 0.0026484 | 0.00066375 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_135-13_0_2_load_153 | 87 | 0.0016769 | 0.00042028 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_135-13_0_2_load_160 | 89 | 0.0043925 | 0.0011009 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_135-13_0_2_line_0 |  | 0 | 1 | 0.0040346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_135-13_0_2_line_1 |  | 0 | 2 | 0.019342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_135-13_0_2_line_2 |  | 1 | 3 | 0.025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_135-13_0_2_line_3 |  | 2 | 4 | 0.0092579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_135-13_0_2_line_4 |  | 2 | 5 | 0.015403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_135-13_0_2_line_5 |  | 3 | 6 | 0.013473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_135-13_0_2_line_6 |  | 3 | 7 | 0.0077325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_135-13_0_2_line_7 |  | 4 | 8 | 0.015057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_135-13_0_2_line_8 |  | 5 | 9 | 0.07235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_135-13_0_2_line_9 |  | 6 | 10 | 0.059563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_135-13_0_2_line_10 |  | 6 | 11 | 0.059024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_135-13_0_2_line_11 |  | 7 | 12 | 0.0064541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_135-13_0_2_line_12 |  | 9 | 13 | 0.026846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_135-13_0_2_line_13 |  | 10 | 14 | 0.0094656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_135-13_0_2_line_14 |  | 11 | 18 | 0.0099845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_135-13_0_2_line_15 |  | 11 | 16 | 0.025143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_135-13_0_2_line_16 |  | 13 | 19 | 0.055282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_135-13_0_2_line_17 |  | 14 | 51 | 0.012916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_135-13_0_2_line_18 |  | 15 | 16 | 0.010786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_135-13_0_2_line_19 |  | 15 | 17 | 0.019216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_135-13_0_2_line_20 |  | 16 | 52 | 0.020117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_135-13_0_2_line_21 |  | 19 | 36 | 0.066494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_135-13_0_2_line_22 |  | 20 | 21 | 0.00053248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_135-13_0_2_line_23 |  | 20 | 22 | 0.026266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_135-13_0_2_line_24 |  | 21 | 23 | 0.036324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_135-13_0_2_line_25 |  | 22 | 24 | 0.060946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_135-13_0_2_line_26 |  | 22 | 25 | 0.029157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_135-13_0_2_line_27 |  | 23 | 26 | 0.018586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_135-13_0_2_line_28 |  | 24 | 27 | 0.02712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_135-13_0_2_line_29 |  | 24 | 28 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_135-13_0_2_line_30 |  | 25 | 29 | 0.0067566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_135-13_0_2_line_31 |  | 25 | 30 | 0.026335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_135-13_0_2_line_32 |  | 26 | 31 | 0.010373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_135-13_0_2_line_33 |  | 27 | 32 | 0.018341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_135-13_0_2_line_34 |  | 28 | 33 | 0.033977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_135-13_0_2_line_35 |  | 29 | 34 | 0.02574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_135-13_0_2_line_36 |  | 30 | 35 | 0.003802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_135-13_0_2_line_37 |  | 30 | 36 | 0.03233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_135-13_0_2_line_38 |  | 31 | 40 | 0.0068972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_135-13_0_2_line_39 |  | 33 | 47 | 0.0029327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_135-13_0_2_line_40 |  | 35 | 43 | 0.044096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_135-13_0_2_line_41 |  | 37 | 38 | 0.017399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_135-13_0_2_line_42 |  | 37 | 39 | 0.011222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_135-13_0_2_line_43 |  | 38 | 44 | 0.023279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_135-13_0_2_line_44 |  | 39 | 45 | 0.0090407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_135-13_0_2_line_45 |  | 39 | 42 | 0.017274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_135-13_0_2_line_46 |  | 40 | 46 | 0.0070831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_135-13_0_2_line_47 |  | 41 | 42 | 2.106e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_135-13_0_2_line_48 |  | 43 | 49 | 0.017499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_135-13_0_2_line_49 |  | 44 | 50 | 0.024906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_135-13_0_2_line_50 |  | 44 | 48 | 0.013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_135-13_0_2_line_51 |  | 45 | 58 | 0.03388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_135-13_0_2_line_52 |  | 46 | 57 | 0.024188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_135-13_0_2_line_53 |  | 49 | 50 | 0.0085836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_135-13_0_2_line_54 |  | 50 | 59 | 0.008466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_135-13_0_2_line_55 |  | 52 | 71 | 0.013538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_135-13_0_2_line_56 |  | 53 | 54 | 0.027538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_135-13_0_2_line_57 |  | 54 | 55 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_135-13_0_2_line_58 |  | 55 | 56 | 0.0056315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_135-13_0_2_line_59 |  | 56 | 57 | 0.035931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_135-13_0_2_line_60 |  | 59 | 60 | 0.0063055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_135-13_0_2_line_61 |  | 60 | 61 | 0.0066137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_135-13_0_2_line_62 |  | 62 | 63 | 0.035868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_135-13_0_2_line_63 |  | 63 | 64 | 0.016457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_135-13_0_2_line_64 |  | 64 | 65 | 0.020907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_135-13_0_2_line_65 |  | 64 | 66 | 0.023093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_135-13_0_2_line_66 |  | 65 | 67 | 0.0034937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_135-13_0_2_line_67 |  | 66 | 68 | 0.013688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_135-13_0_2_line_68 |  | 67 | 72 | 0.0041832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_135-13_0_2_line_69 |  | 68 | 73 | 0.035414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_135-13_0_2_line_70 |  | 69 | 70 | 0.010656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_135-13_0_2_line_71 |  | 69 | 71 | 0.009138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_135-13_0_2_line_72 |  | 70 | 72 | 0.0043823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_135-13_0_2_line_73 |  | 71 | 74 | 0.0071048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_135-13_0_2_line_74 |  | 73 | 75 | 0.020104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_135-13_0_2_line_75 |  | 73 | 76 | 0.018421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_135-13_0_2_line_76 |  | 74 | 81 | 0.01918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_135-13_0_2_line_77 |  | 75 | 77 | 0.041977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_135-13_0_2_line_78 |  | 76 | 78 | 0.022057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_135-13_0_2_line_79 |  | 77 | 79 | 0.029537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_135-13_0_2_line_80 |  | 78 | 80 | 0.0090054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_135-13_0_2_line_81 |  | 81 | 82 | 0.01692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_135-13_0_2_line_82 |  | 82 | 83 | 0.010786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_135-13_0_2_line_83 |  | 82 | 84 | 0.016961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_135-13_0_2_line_84 |  | 83 | 85 | 0.0013248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_135-13_0_2_line_85 |  | 84 | 86 | 0.028198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_135-13_0_2_line_86 |  | 85 | 87 | 0.011171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_135-13_0_2_line_87 |  | 86 | 88 | 0.034598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_135-13_0_2_line_88 |  | 88 | 89 | 0.025165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_135-13_0_2_trafo_33 | 0.63 MVA 20/0.4 kV | 90 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2683882.4924 | 1241862.6873 | 2683882.7361 | 1241864.1576 | 2683883.4851 | 1241866.5892
1 | 2683879.3296 | 1241843.6058 | 2683882.4924 | 1241862.6873
2 | 2683889.0194 | 1241891.3995 | 2683888.6093 | 1241884.5776 | 2683887.0807 | 1241878.2626 | 2683883.4851 | 1241866.5892
3 | 2683879.3296 | 1241843.6058 | 2683888.5439 | 1241842.7088
4 | 2683879.3296 | 1241843.6058 | 2683877.9817 | 1241831.4557 | 2683877.9315 | 1241828.2778
5 | 2683884.6516 | 1241904.0691 | 2683887.8684 | 1241896.876 | 2683889.0194 | 1241891.3995
6 | 2683889.0194 | 1241891.3995 | 2683881.4102 | 1241890.0243
7 | 2683903.5302 | 1241841.25 | 2683888.5439 | 1241842.7088
8 | 2683880.9532 | 1241758.1892 | 2683884.9847 | 1241763.9615 | 2683885.8795 | 1241767.5211 | 2683886.3895 | 1241772.0872 | 2683885.2946 | 1241780.5445 | 2683885.1247 | 1241781.8653 | 2683880.3704 | 1241800.4782 | 2683878.3329 | 1241813.57 | 2683877.8222 | 1241821.3462 | 2683877.9315 | 1241828.2778
9 | 2683884.6516 | 1241904.0691 | 2683867.1548 | 1241930.908 | 2683860.7411 | 1241949.7865 | 2683858.4919 | 1241957.0317
10 | 2683884.6516 | 1241904.0691 | 2683888.5827 | 1241908.9171 | 2683883.0596 | 1241932.178 | 2683899.6513 | 1241935.6595 | 2683901.1974 | 1241928.4428 | 2683901.5851 | 1241926.6915 | 2683902.1825 | 1241924.0091
11 | 2683875.7993 | 1241893.214 | 2683881.4102 | 1241890.0243
12 | 2683862.547 | 1241777.6655 | 2683870.9278 | 1241767.2652 | 2683880.9532 | 1241758.1892
13 | 2683855.6855 | 1241966.0717 | 2683858.4919 | 1241957.0317
14 | 2683902.1825 | 1241924.0091 | 2683904.2566 | 1241914.2424
15 | 2683902.1825 | 1241924.0091 | 2683926.1053 | 1241931.9641
16 | 2683862.547 | 1241777.6655 | 2683856.9368 | 1241785.1583 | 2683851.2481 | 1241794.9961 | 2683848.637 | 1241799.4625 | 2683835.1927 | 1241825.59
17 | 2683851.856 | 1241978.4072 | 2683855.6855 | 1241966.0717
18 | 2683920.6903 | 1241941.1609 | 2683922.3554 | 1241936.759 | 2683926.1053 | 1241931.9641
19 | 2683920.6903 | 1241941.1609 | 2683914.58 | 1241959.3796
20 | 2683926.1053 | 1241931.9641 | 2683928.6202 | 1241928.4193 | 2683932.7683 | 1241923.7969 | 2683935.8204 | 1241920.2263 | 2683937.9967 | 1241915.8774
21 | 2683813.4025 | 1241888.2129 | 2683815.745 | 1241879.9005 | 2683820.6861 | 1241860.3562 | 2683826.6506 | 1241844.3733 | 2683833.7491 | 1241828.3953 | 2683835.1927 | 1241825.59
22 | 2683744.3244 | 1241891.5397 | 2683744.744 | 1241891.2118
23 | 2683760.2792 | 1241871.9119 | 2683756.6465 | 1241875.3742 | 2683756.0226 | 1241882.0814 | 2683745.1697 | 1241890.8791 | 2683744.744 | 1241891.2118
24 | 2683744.3244 | 1241891.5397 | 2683737.4559 | 1241896.9079 | 2683730.5373 | 1241904.4491 | 2683720.0735 | 1241918.3171
25 | 2683719.7488 | 1241849.2348 | 2683722.4571 | 1241851.7971 | 2683730.4297 | 1241847.2618 | 2683737.9284 | 1241843.6205 | 2683739.9259 | 1241842.9816 | 2683742.0144 | 1241842.8554 | 2683744.0728 | 1241843.2625 | 2683746.3397 | 1241844.4287 | 2683748.1362 | 1241846.2442 | 2683750.4574 | 1241850.5245 | 2683760.2792 | 1241871.9119
26 | 2683760.2792 | 1241871.9119 | 2683772.1431 | 1241892.7054 | 2683777.3875 | 1241892.9018
27 | 2683708.8792 | 1241933.1533 | 2683720.0735 | 1241918.3171
28 | 2683719.7488 | 1241849.2348 | 2683724.3812 | 1241844.5746 | 2683728.001 | 1241839.3441 | 2683731.1789 | 1241832.2171 | 2683732.8565 | 1241826.0566
29 | 2683719.7488 | 1241849.2348 | 2683716.3701 | 1241851.3109 | 2683712.6097 | 1241852.5699 | 2683709.0587 | 1241852.9312 | 2683705.5102 | 1241852.5698 | 2683701.1563 | 1241850.928
30 | 2683777.3875 | 1241892.9018 | 2683774.9399 | 1241886.6041
31 | 2683777.3875 | 1241892.9018 | 2683780.6837 | 1241899.8756 | 2683784.684 | 1241905.714 | 2683788.4118 | 1241909.436 | 2683790.8733 | 1241910.7384 | 2683794.3124 | 1241911.3429
32 | 2683708.8792 | 1241933.1533 | 2683701.6577 | 1241940.6002
33 | 2683732.8565 | 1241826.0566 | 2683737.0638 | 1241810.6067 | 2683737.7613 | 1241808.3847
34 | 2683701.1563 | 1241850.928 | 2683693.6324 | 1241884.0619
35 | 2683765.6158 | 1241862.6124 | 2683774.9399 | 1241886.6041
36 | 2683793.9791 | 1241915.1298 | 2683794.3124 | 1241911.3429
37 | 2683794.3124 | 1241911.3429 | 2683798.9481 | 1241910.1964 | 2683803.5971 | 1241907.5824 | 2683807.1387 | 1241904.141 | 2683809.8876 | 1241900.088 | 2683811.3194 | 1241895.605 | 2683813.4025 | 1241888.2129
38 | 2683701.6577 | 1241940.6002 | 2683696.8562 | 1241945.5516
39 | 2683693.6324 | 1241884.0619 | 2683696.3062 | 1241885.2665
40 | 2683793.9791 | 1241915.1298 | 2683796.7243 | 1241920.9728 | 2683808.2852 | 1241956.7935
41 | 2683752.4908 | 1241969.428 | 2683769.0974 | 1241974.6181
42 | 2683749.1189 | 1241980.1326 | 2683752.4908 | 1241969.428
43 | 2683791.3169 | 1241981.5625 | 2683769.0974 | 1241974.6181
44 | 2683749.1189 | 1241980.1326 | 2683746.5846 | 1241988.8108
45 | 2683749.1189 | 1241980.1326 | 2683732.316 | 1241976.1275
46 | 2683691.2738 | 1241949.9066 | 2683696.6573 | 1241945.7567 | 2683696.8562 | 1241945.5516
47 | 2683732.2955 | 1241976.1226 | 2683732.316 | 1241976.1275
48 | 2683813.6598 | 1241973.4464 | 2683808.2852 | 1241956.7935
49 | 2683816.2962 | 1241981.6152 | 2683791.3169 | 1241981.5625
50 | 2683791.3169 | 1241981.5625 | 2683791.991 | 1241968.2347
51 | 2683737.0874 | 1242021.3325 | 2683746.5846 | 1241988.8108
52 | 2683671.0173 | 1241963.0522 | 2683684.886 | 1241954.8306 | 2683691.2738 | 1241949.9066
53 | 2683816.2962 | 1241981.6152 | 2683813.6598 | 1241973.4464
54 | 2683816.2962 | 1241981.6152 | 2683818.7903 | 1241989.7055
55 | 2683943.3689 | 1241903.4543 | 2683938.8316 | 1241914.209 | 2683937.9967 | 1241915.8774
56 | 2683651.0047 | 1241882.4309 | 2683650.6275 | 1241888.9891 | 2683650.9433 | 1241899.8347 | 2683652.2031 | 1241909.8744
57 | 2683656.76 | 1241924.0133 | 2683652.3298 | 1241910.8845 | 2683652.2031 | 1241909.8744
58 | 2683658.5633 | 1241929.3483 | 2683658.5276 | 1241929.2517 | 2683656.76 | 1241924.0133
59 | 2683671.0173 | 1241963.0522 | 2683658.5633 | 1241929.3483
60 | 2683818.7903 | 1241989.7055 | 2683820.6479 | 1241995.7312
61 | 2683820.6479 | 1241995.7312 | 2683822.5962 | 1242002.0514
62 | 2683968.9102 | 1241842.4714 | 2683954.1224 | 1241841.3281 | 2683942.7996 | 1241839.5 | 2683933.2387 | 1241839.1663
63 | 2683968.9102 | 1241842.4714 | 2683969.5469 | 1241858.9145
64 | 2683969.5469 | 1241858.9145 | 2683964.6237 | 1241862.7366 | 2683960.2352 | 1241867.2444 | 2683957.4789 | 1241870.2076 | 2683955.6643 | 1241873.4176 | 2683955.3795 | 1241874.0005
65 | 2683969.5469 | 1241858.9145 | 2683989.1067 | 1241863.1721 | 2683992.1417 | 1241863.6699
66 | 2683955.3795 | 1241874.0005 | 2683953.8458 | 1241877.1396
67 | 2684005.6489 | 1241865.8859 | 2683999.1241 | 1241864.815 | 2683992.1417 | 1241863.6699
68 | 2683952.0974 | 1241880.9386 | 2683952.9235 | 1241879.0273 | 2683953.8458 | 1241877.1396
69 | 2684005.6489 | 1241865.8859 | 2684026.1659 | 1241869.2899 | 2684028.8286 | 1241869.7279 | 2684040.6287 | 1241872.0188
70 | 2683946.1309 | 1241894.7426 | 2683950.3587 | 1241884.9612
71 | 2683943.3689 | 1241903.4543 | 2683946.1309 | 1241894.7426
72 | 2683950.3587 | 1241884.9612 | 2683952.0974 | 1241880.9386
73 | 2683943.3689 | 1241903.4543 | 2683946.3549 | 1241909.9012
74 | 2684040.6287 | 1241872.0188 | 2684048.4559 | 1241872.9525 | 2684051.7695 | 1241873.3442 | 2684060.5929 | 1241874.3888
75 | 2684040.6287 | 1241872.0188 | 2684035.0669 | 1241889.58
76 | 2683943.0885 | 1241928.801 | 2683946.3549 | 1241909.9012
77 | 2684101.9894 | 1241880.6941 | 2684094.5518 | 1241878.4093 | 2684060.5929 | 1241874.3888
78 | 2684028.1494 | 1241910.5241 | 2684034.2256 | 1241892.2428 | 2684034.6372 | 1241890.9366 | 2684035.0669 | 1241889.58
79 | 2684101.9894 | 1241880.6941 | 2684096.5781 | 1241897.0738 | 2684092.724 | 1241908.7404
80 | 2684028.1494 | 1241910.5241 | 2684025.3091 | 1241919.0698
81 | 2683939.6459 | 1241945.3541 | 2683941.4551 | 1241938.2524 | 2683943.0885 | 1241928.801
82 | 2683939.6459 | 1241945.3541 | 2683938.5408 | 1241949.7194 | 2683938.4689 | 1241956.0021
83 | 2683939.6459 | 1241945.3541 | 2683956.2775 | 1241948.6806
84 | 2683938.4537 | 1241957.3269 | 2683938.4689 | 1241956.0021
85 | 2683969.9047 | 1241967.1244 | 2683956.8391 | 1241962.9545 | 2683955.3957 | 1241956.496 | 2683956.2775 | 1241948.6806
86 | 2683938.2675 | 1241968.4958 | 2683938.4132 | 1241960.8702 | 2683938.4537 | 1241957.3269
87 | 2684002.7692 | 1241977.9373 | 2683972.6976 | 1241968.0158 | 2683969.9047 | 1241967.1244
88 | 2684002.7692 | 1241977.9373 | 2684011.9877 | 1241954.5211

## bus_geodata
| x | y | coords
0 | 2683882.4924 | 1241862.6873
1 | 2683883.4851 | 1241866.5892
2 | 2683879.3296 | 1241843.6058
3 | 2683889.0194 | 1241891.3995
4 | 2683888.544 | 1241842.7088
5 | 2683877.9315 | 1241828.2778
6 | 2683884.6517 | 1241904.0691
7 | 2683881.4102 | 1241890.0243
8 | 2683903.5302 | 1241841.25
9 | 2683880.9532 | 1241758.1892
10 | 2683858.4919 | 1241957.0317
11 | 2683902.1825 | 1241924.0091
12 | 2683875.7993 | 1241893.214
13 | 2683862.547 | 1241777.6655
14 | 2683855.6855 | 1241966.0717
15 | 2683920.6903 | 1241941.1609
16 | 2683926.1053 | 1241931.9641
17 | 2683914.58 | 1241959.3796
18 | 2683904.2567 | 1241914.2424
19 | 2683835.1927 | 1241825.59
20 | 2683744.744 | 1241891.2118
21 | 2683744.3244 | 1241891.5397
22 | 2683760.2792 | 1241871.9119
23 | 2683720.0735 | 1241918.3171
24 | 2683719.7488 | 1241849.2348
25 | 2683777.3875 | 1241892.9018
26 | 2683708.8792 | 1241933.1533
27 | 2683732.8565 | 1241826.0566
28 | 2683701.1563 | 1241850.928
29 | 2683774.9399 | 1241886.6041
30 | 2683794.3124 | 1241911.3429
31 | 2683701.6577 | 1241940.6002
32 | 2683737.7613 | 1241808.3847
33 | 2683693.6324 | 1241884.0619
34 | 2683765.6158 | 1241862.6124
35 | 2683793.9791 | 1241915.1298
36 | 2683813.4025 | 1241888.2129
37 | 2683752.4908 | 1241969.428
38 | 2683769.0974 | 1241974.6181
39 | 2683749.1189 | 1241980.1326
40 | 2683696.8562 | 1241945.5516
41 | 2683732.2955 | 1241976.1226
42 | 2683732.316 | 1241976.1275
43 | 2683808.2852 | 1241956.7935
44 | 2683791.3169 | 1241981.5625
45 | 2683746.5846 | 1241988.8108
46 | 2683691.2738 | 1241949.9066
47 | 2683696.3062 | 1241885.2665
48 | 2683791.991 | 1241968.2347
49 | 2683813.6598 | 1241973.4464
50 | 2683816.2962 | 1241981.6152
51 | 2683851.856 | 1241978.4072
52 | 2683937.9966 | 1241915.8774
53 | 2683651.0047 | 1241882.4309
54 | 2683652.2031 | 1241909.8744
55 | 2683656.76 | 1241924.0133
56 | 2683658.5633 | 1241929.3483
57 | 2683671.0173 | 1241963.0522
58 | 2683737.0874 | 1242021.3325
59 | 2683818.7903 | 1241989.7055
60 | 2683820.6479 | 1241995.7312
61 | 2683822.5962 | 1242002.0514
62 | 2683933.2387 | 1241839.1663
63 | 2683968.9102 | 1241842.4714
64 | 2683969.5469 | 1241858.9145
65 | 2683955.3795 | 1241874.0005
66 | 2683992.1417 | 1241863.6699
67 | 2683953.8458 | 1241877.1396
68 | 2684005.649 | 1241865.8859
69 | 2683946.1309 | 1241894.7426
70 | 2683950.3587 | 1241884.9612
71 | 2683943.3689 | 1241903.4543
72 | 2683952.0974 | 1241880.9386
73 | 2684040.6287 | 1241872.0188
74 | 2683946.3549 | 1241909.9012
75 | 2684060.5929 | 1241874.3888
76 | 2684035.0669 | 1241889.58
77 | 2684101.9894 | 1241880.6941
78 | 2684028.1494 | 1241910.5241
79 | 2684092.724 | 1241908.7404
80 | 2684025.3091 | 1241919.0698
81 | 2683943.0885 | 1241928.801
82 | 2683939.6459 | 1241945.3541
83 | 2683938.4689 | 1241956.0021
84 | 2683956.2775 | 1241948.6806
85 | 2683938.4537 | 1241957.3269
86 | 2683969.9047 | 1241967.1244
87 | 2683938.2675 | 1241968.4958
88 | 2684002.7692 | 1241977.9373
89 | 2684011.9877 | 1241954.5211
90 | 2683889.0194 | 1241891.3995

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99647 | -0.066621 | 0.0036583 | 0.00091685
1 | 0.99673 | -0.061733 | 0.0050853 | 0.0012745
2 | 0.99527 | -0.08947 | 0 | 0
3 | 0.99843 | -0.029702 | 0 | 0
4 | 0.99521 | -0.090637 | 0.0035354 | 0.00088607
5 | 0.99436 | -0.10673 | 0.0074409 | 0.0018649
6 | 0.99726 | -0.05192 | 0 | 0
7 | 0.99928 | -0.013669 | 0.0054544 | 0.001367
8 | 0.99516 | -0.091599 | 0.0036293 | 0.00090958
9 | 0.99032 | -0.18345 | 0 | 0
10 | 0.99692 | -0.058391 | 0.0025528 | 0.0006398
11 | 0.99248 | -0.14339 | 0 | 0
12 | 1 | 0 | -0.24836 | -0.06334
13 | 0.98883 | -0.21208 | 0 | 0
14 | 0.99689 | -0.058996 | 0.0018247 | 0.0004573
15 | 0.99046 | -0.1824 | 0 | 0
16 | 0.99051 | -0.18132 | 0 | 0
17 | 0.99036 | -0.18432 | 0.005634 | 0.001412
18 | 0.99245 | -0.14391 | 0.0029224 | 0.00073243
19 | 0.98575 | -0.2713 | 0.0088117 | 0.0022084
20 | 0.97514 | -0.47813 | 0.0026853 | 0.000673
21 | 0.97512 | -0.47847 | 0.0064222 | 0.0016096
22 | 0.97604 | -0.46031 | 0 | 0
23 | 0.97417 | -0.4971 | 0.0060405 | 0.0015139
24 | 0.97482 | -0.48443 | 0 | 0
25 | 0.97763 | -0.42906 | 0 | 0
26 | 0.97379 | -0.50458 | 0 | 0
27 | 0.97468 | -0.48717 | 0.001523 | 0.0003817
28 | 0.97452 | -0.49025 | 0.0019358 | 0.00048516
29 | 0.97759 | -0.42989 | 0.0057552 | 0.0014424
30 | 0.97924 | -0.39772 | 0 | 0
31 | 0.97358 | -0.50876 | 0.002875 | 0.00072054
32 | 0.97461 | -0.48851 | 0.003992 | 0.0010005
33 | 0.97407 | -0.49907 | 0.0018699 | 0.00046864
34 | 0.97757 | -0.43033 | 0.00094 | 0.00023559
35 | 0.97911 | -0.40028 | 0 | 0
36 | 0.98232 | -0.33773 | 0.0085826 | 0.002151
37 | 0.97537 | -0.47363 | 0 | 0
38 | 0.97567 | -0.46782 | 0.0069694 | 0.0017467
39 | 0.97518 | -0.47737 | 0 | 0
40 | 0.97346 | -0.51117 | 0.0035584 | 0.00089183
41 | 0.97505 | -0.47997 | 0.004329 | 0.001085
42 | 0.97505 | -0.47997 | 0.0038643 | 0.00096849
43 | 0.97759 | -0.43003 | 0.0045786 | 0.0011475
44 | 0.97621 | -0.4571 | 0 | 0
45 | 0.9751 | -0.47903 | 0.0065008 | 0.0016292
46 | 0.97336 | -0.51319 | 0.0019906 | 0.00049889
47 | 0.97404 | -0.49974 | 0.01228 | 0.0030776
48 | 0.97619 | -0.45741 | 0.0012669 | 0.00031753
49 | 0.97706 | -0.4404 | 0.0027543 | 0.00069029
50 | 0.97682 | -0.44506 | 0 | 0
51 | 0.99687 | -0.059408 | 0.0018185 | 0.00045575
52 | 0.98904 | -0.20976 | 0.00099719 | 0.00024992
53 | 0.97236 | -0.53287 | 0.0034272 | 0.00085893
54 | 0.97245 | -0.53113 | 0.0035175 | 0.00088157
55 | 0.97255 | -0.52922 | 0.0037262 | 0.00093387
56 | 0.9726 | -0.52811 | 0.0028115 | 0.00070464
57 | 0.97305 | -0.51919 | 0 | 0
58 | 0.97499 | -0.48121 | 0.0035133 | 0.00088052
59 | 0.9768 | -0.44556 | 0.0011254 | 0.00028206
60 | 0.97678 | -0.44581 | 0.0011086 | 0.00027783
61 | 0.97678 | -0.44593 | 0.0010322 | 0.00025869
62 | 0.98566 | -0.27548 | 0.0046964 | 0.001177
63 | 0.98581 | -0.27246 | 0 | 0
64 | 0.98588 | -0.27108 | 0 | 0
65 | 0.98669 | -0.25543 | 0.0015064 | 0.00037753
66 | 0.98509 | -0.28643 | 0.0065584 | 0.0016437
67 | 0.98683 | -0.25273 | 0.0015682 | 0.00039303
68 | 0.98471 | -0.29393 | 0 | 0
69 | 0.98766 | -0.23657 | 0 | 0
70 | 0.98719 | -0.24575 | 0.0020217 | 0.0005067
71 | 0.98806 | -0.2287 | 0 | 0
72 | 0.987 | -0.24937 | 0.0013661 | 0.00034239
73 | 0.98371 | -0.31337 | 0 | 0
74 | 0.98787 | -0.23253 | 0.0073065 | 0.0018312
75 | 0.98332 | -0.32097 | 0.016621 | 0.0041656
76 | 0.98355 | -0.31652 | 0.0052469 | 0.001315
77 | 0.98316 | -0.32428 | 0 | 0
78 | 0.98347 | -0.31821 | 0.002126 | 0.00053283
79 | 0.98304 | -0.32661 | 0.0043717 | 0.0010956
80 | 0.98345 | -0.31856 | 0.002126 | 0.00053283
81 | 0.98746 | -0.24039 | 0.0022394 | 0.00056124
82 | 0.98714 | -0.24664 | 0 | 0
83 | 0.98706 | -0.24822 | 0.0021891 | 0.00054865
84 | 0.98695 | -0.25044 | 0.0054518 | 0.0013663
85 | 0.98705 | -0.24837 | 0.0043183 | 0.0010823
86 | 0.98677 | -0.25399 | 0.0026484 | 0.00066375
87 | 0.98704 | -0.2487 | 0.0016769 | 0.00042028
88 | 0.98663 | -0.25671 | 0 | 0
89 | 0.98652 | -0.25869 | 0.0043925 | 0.0011009
90 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.14036 | -0.036058 | 0.14039 | 0.036079 | 3.3331e-05 | 2.1227e-05 | 0.20991 | 0.20991 | 0.20991 | 0.99647 | -0.066621 | 0.99673 | -0.061733 | 28.8333
1 | 0.1367 | 0.035141 | -0.13655 | -0.035045 | 0.00015158 | 9.6509e-05 | 0.20444 | 0.20444 | 0.20444 | 0.99647 | -0.066621 | 0.99527 | -0.08947 | 28.0829
2 | -0.14548 | -0.037354 | 0.1457 | 0.037498 | 0.00022659 | 0.00014435 | 0.2175 | 0.2175 | 0.2175 | 0.99673 | -0.061733 | 0.99843 | -0.029702 | 29.8761
3 | 0.0071653 | 0.0017957 | -0.0071649 | -0.0017956 | 3.9843e-07 | 1.3469e-07 | 0.010713 | 0.010713 | 0.010713 | 0.99527 | -0.08947 | 0.99521 | -0.090637 | 2.9431
4 | 0.12938 | 0.033249 | -0.12927 | -0.03318 | 0.00010839 | 6.8972e-05 | 0.19373 | 0.19373 | 0.19373 | 0.99527 | -0.08947 | 0.99436 | -0.10673 | 26.6114
5 | 0.095206 | 0.024251 | -0.095104 | -0.024186 | 0.00010192 | 6.5052e-05 | 0.14203 | 0.14203 | 0.14203 | 0.99843 | -0.029702 | 0.99726 | -0.05192 | 39.0192
6 | -0.24091 | -0.061749 | 0.2411 | 0.061869 | 0.00018741 | 0.00011974 | 0.35953 | 0.35953 | 0.35953 | 0.99843 | -0.029702 | 0.99928 | -0.013669 | 49.3856
7 | 0.0036294 | 0.00090949 | -0.0036293 | -0.00090958 | 1.6628e-07 | -8.922e-08 | 0.0054266 | 0.0054267 | 0.0054267 | 0.99521 | -0.090637 | 0.99516 | -0.091599 | 1.4909
8 | 0.12183 | 0.031315 | -0.12138 | -0.031028 | 0.0004523 | 0.0002876 | 0.1826 | 0.1826 | 0.1826 | 0.99436 | -0.10673 | 0.99032 | -0.18345 | 25.082
9 | 0.006198 | 0.0015531 | -0.0061961 | -0.0015527 | 1.9104e-06 | 4.4574e-07 | 0.009248 | 0.0092483 | 0.0092483 | 0.99726 | -0.05192 | 0.99692 | -0.058391 | 2.5407
10 | 0.088906 | 0.022632 | -0.088516 | -0.022383 | 0.00039025 | 0.00024899 | 0.13278 | 0.13278 | 0.13278 | 0.99726 | -0.05192 | 0.99248 | -0.14339 | 36.4786
11 | -0.24655 | -0.063236 | 0.24671 | 0.06334 | 0.00016357 | 0.00010452 | 0.36765 | 0.36765 | 0.36765 | 0.99928 | -0.013669 | 1 | 0 | 50.5012
12 | 0.12138 | 0.031028 | -0.12121 | -0.030921 | 0.00016783 | 0.00010672 | 0.1826 | 0.1826 | 0.1826 | 0.99032 | -0.18345 | 0.98883 | -0.21208 | 25.0821
13 | 0.0036433 | 0.00091285 | -0.0036432 | -0.00091291 | 1.0496e-07 | -5.6238e-08 | 0.0054379 | 0.0054379 | 0.0054379 | 0.99692 | -0.058391 | 0.99689 | -0.058996 | 1.4939
14 | 0.0029225 | 0.00073234 | -0.0029224 | -0.00073243 | 7.1884e-08 | -8.3018e-08 | 0.0043816 | 0.0043817 | 0.0043817 | 0.99248 | -0.14339 | 0.99245 | -0.14391 | 1.2038
15 | 0.085594 | 0.021651 | -0.085438 | -0.021552 | 0.00015545 | 9.9162e-05 | 0.1284 | 0.1284 | 0.1284 | 0.99248 | -0.14339 | 0.99051 | -0.18132 | 35.2749
16 | 0.12121 | 0.030921 | -0.12087 | -0.030701 | 0.0003456 | 0.00021977 | 0.1826 | 0.1826 | 0.1826 | 0.98883 | -0.21208 | 0.98575 | -0.2713 | 25.0821
17 | 0.0018185 | 0.00045561 | -0.0018185 | -0.00045575 | 3.5687e-08 | -1.4556e-07 | 0.0027144 | 0.0027144 | 0.0027144 | 0.99689 | -0.058996 | 0.99687 | -0.059408 | 0.74572
18 | -0.0056345 | -0.0014121 | 0.0056348 | 0.0014121 | 2.8983e-07 | 4.6665e-08 | 0.008465 | 0.0084649 | 0.008465 | 0.99046 | -0.1824 | 0.99051 | -0.18132 | 2.3255
19 | 0.0056345 | 0.0014121 | -0.005634 | -0.001412 | 5.1636e-07 | 8.3181e-08 | 0.008465 | 0.0084651 | 0.0084651 | 0.99046 | -0.1824 | 0.99036 | -0.18432 | 2.3256
20 | 0.079803 | 0.02014 | -0.079695 | -0.020071 | 0.00010852 | 6.9193e-05 | 0.11994 | 0.11994 | 0.11994 | 0.99051 | -0.18132 | 0.98904 | -0.20976 | 32.9494
21 | 0.11205 | 0.028493 | -0.1117 | -0.028266 | 0.00035734 | 0.00022701 | 0.1693 | 0.1693 | 0.1693 | 0.98575 | -0.2713 | 0.98232 | -0.33773 | 23.2551
22 | 0.034421 | 0.0086449 | -0.034421 | -0.0086445 | 5.5105e-07 | 3.4603e-07 | 0.052532 | 0.052532 | 0.052532 | 0.97514 | -0.47813 | 0.97512 | -0.47847 | 14.4319
23 | -0.037107 | -0.0093179 | 0.037138 | 0.0093378 | 3.1587e-05 | 1.9888e-05 | 0.05663 | 0.05663 | 0.05663 | 0.97514 | -0.47813 | 0.97604 | -0.46031 | 15.5577
24 | 0.027999 | 0.007035 | -0.027974 | -0.0070195 | 2.4874e-05 | 1.5466e-05 | 0.042732 | 0.042732 | 0.042732 | 0.97512 | -0.47847 | 0.97417 | -0.4971 | 11.7396
25 | 0.021637 | 0.005435 | -0.021612 | -0.0054198 | 2.4875e-05 | 1.5159e-05 | 0.032991 | 0.032991 | 0.032991 | 0.97604 | -0.46031 | 0.97482 | -0.48443 | 9.0635
26 | -0.058775 | -0.014773 | 0.058863 | 0.014829 | 8.7819e-05 | 5.5839e-05 | 0.089621 | 0.08962 | 0.089621 | 0.97604 | -0.46031 | 0.97763 | -0.42906 | 24.621
27 | 0.021933 | 0.0055056 | -0.021926 | -0.0055008 | 7.8243e-06 | 4.7762e-06 | 0.033506 | 0.033506 | 0.033506 | 0.97417 | -0.4971 | 0.97379 | -0.50458 | 9.2048
28 | 0.0055159 | 0.0013822 | -0.0055152 | -0.0013821 | 7.2099e-07 | 1.2338e-07 | 0.0084198 | 0.0084199 | 0.0084199 | 0.97482 | -0.48443 | 0.97468 | -0.48717 | 2.3132
29 | 0.016096 | 0.0040376 | -0.016092 | -0.004035 | 4.4648e-06 | 2.6117e-06 | 0.024571 | 0.024571 | 0.024571 | 0.97482 | -0.48443 | 0.97452 | -0.49025 | 6.7504
30 | 0.0066955 | 0.0016777 | -0.0066952 | -0.0016777 | 2.6313e-07 | 8.3688e-08 | 0.010191 | 0.010191 | 0.010191 | 0.97763 | -0.42906 | 0.97759 | -0.42989 | 2.7997
31 | -0.065559 | -0.016506 | 0.065657 | 0.016569 | 9.8385e-05 | 6.2636e-05 | 0.099811 | 0.099811 | 0.099811 | 0.97763 | -0.42906 | 0.97924 | -0.39772 | 27.4207
32 | 0.021926 | 0.0055008 | -0.021921 | -0.0054982 | 4.367e-06 | 2.6659e-06 | 0.033506 | 0.033506 | 0.033506 | 0.97379 | -0.50458 | 0.97358 | -0.50876 | 9.2049
33 | 0.0039922 | 0.0010004 | -0.003992 | -0.0010005 | 2.555e-07 | -6.506e-08 | 0.0060948 | 0.0060949 | 0.0060949 | 0.97468 | -0.48717 | 0.97461 | -0.48851 | 1.6744
34 | 0.014156 | 0.0035498 | -0.01415 | -0.0035464 | 5.9533e-06 | 3.387e-06 | 0.021616 | 0.021616 | 0.021616 | 0.97452 | -0.49025 | 0.97407 | -0.49907 | 5.9384
35 | 0.00094002 | 0.00023528 | -0.00094 | -0.00023559 | 1.976e-08 | -3.1007e-07 | 0.0014307 | 0.0014308 | 0.0014308 | 0.97759 | -0.42989 | 0.97757 | -0.43033 | 0.39308
36 | 0.037162 | 0.0093567 | -0.037157 | -0.0093538 | 4.5489e-06 | 2.8635e-06 | 0.056485 | 0.056485 | 0.056485 | 0.97924 | -0.39772 | 0.97911 | -0.40028 | 15.5179
37 | -0.10282 | -0.025926 | 0.10311 | 0.026115 | 0.00029617 | 0.00018914 | 0.1563 | 0.1563 | 0.1563 | 0.97924 | -0.39772 | 0.98232 | -0.33773 | 42.9385
38 | 0.019046 | 0.0047776 | -0.019044 | -0.0047763 | 2.192e-06 | 1.3171e-06 | 0.029112 | 0.029112 | 0.029112 | 0.97358 | -0.50876 | 0.97346 | -0.51117 | 7.9977
39 | 0.01228 | 0.0030778 | -0.01228 | -0.0030776 | 3.8701e-07 | 2.1118e-07 | 0.018759 | 0.018759 | 0.018759 | 0.97407 | -0.49907 | 0.97404 | -0.49974 | 5.1536
40 | 0.037157 | 0.0093538 | -0.037104 | -0.0093206 | 5.2759e-05 | 3.3212e-05 | 0.056485 | 0.056485 | 0.056485 | 0.97911 | -0.40028 | 0.97759 | -0.43003 | 15.5179
41 | -0.018213 | -0.0045658 | 0.018218 | 0.0045688 | 5.0372e-06 | 3.0066e-06 | 0.027786 | 0.027786 | 0.027786 | 0.97537 | -0.47363 | 0.97567 | -0.46782 | 7.6335
42 | 0.018213 | 0.0045658 | -0.01821 | -0.0045639 | 3.249e-06 | 1.9393e-06 | 0.027786 | 0.027786 | 0.027786 | 0.97537 | -0.47363 | 0.97518 | -0.47737 | 7.6335
43 | -0.025187 | -0.0063155 | 0.0252 | 0.0063235 | 1.2883e-05 | 7.954e-06 | 0.038415 | 0.038415 | 0.038415 | 0.97567 | -0.46782 | 0.97621 | -0.4571 | 10.5536
44 | 0.010015 | 0.00251 | -0.010014 | -0.0025096 | 7.9178e-07 | 3.9395e-07 | 0.015282 | 0.015282 | 0.015282 | 0.97518 | -0.47737 | 0.9751 | -0.47903 | 4.1984
45 | 0.0081943 | 0.0020539 | -0.0081933 | -0.0020534 | 1.0127e-06 | 4.3267e-07 | 0.012504 | 0.012504 | 0.012504 | 0.97518 | -0.47737 | 0.97505 | -0.47997 | 3.4351
46 | 0.015486 | 0.0038845 | -0.015484 | -0.0038836 | 1.4884e-06 | 8.6456e-07 | 0.023672 | 0.023672 | 0.023672 | 0.97346 | -0.51117 | 0.97336 | -0.51319 | 6.5034
47 | -0.004329 | -0.001085 | 0.004329 | 0.001085 | 3.4249e-10 | -4.1886e-11 | 0.0066065 | 0.0066065 | 0.0066065 | 0.97505 | -0.47997 | 0.97505 | -0.47997 | 1.815
48 | 0.032526 | 0.0081731 | -0.03251 | -0.008163 | 1.6089e-05 | 1.0078e-05 | 0.049516 | 0.049516 | 0.049516 | 0.97759 | -0.43003 | 0.97706 | -0.4404 | 13.6033
49 | -0.026467 | -0.0066408 | 0.026482 | 0.0066502 | 1.5203e-05 | 9.4185e-06 | 0.040346 | 0.040346 | 0.040346 | 0.97621 | -0.4571 | 0.97682 | -0.44506 | 11.0841
50 | 0.001267 | 0.00031737 | -0.0012669 | -0.00031753 | 1.8663e-08 | -1.549e-07 | 0.0019311 | 0.0019312 | 0.0019312 | 0.97621 | -0.4571 | 0.97619 | -0.45741 | 0.53055
51 | 0.0035137 | 0.00088033 | -0.0035133 | -0.00088052 | 3.6527e-07 | -1.888e-07 | 0.0053619 | 0.005362 | 0.005362 | 0.9751 | -0.47903 | 0.97499 | -0.48121 | 1.4731
52 | 0.013493 | 0.0033847 | -0.01349 | -0.0033826 | 3.8601e-06 | 2.1699e-06 | 0.020629 | 0.020629 | 0.020629 | 0.97336 | -0.51319 | 0.97305 | -0.51919 | 5.6674
53 | 0.029755 | 0.0074728 | -0.029749 | -0.0074686 | 6.6116e-06 | 4.124e-06 | 0.045321 | 0.045321 | 0.045321 | 0.97706 | -0.4404 | 0.97682 | -0.44506 | 12.4509
54 | 0.0032663 | 0.00081838 | -0.0032662 | -0.00081844 | 7.8594e-08 | -5.5676e-08 | 0.0049755 | 0.0049756 | 0.0049756 | 0.97682 | -0.44506 | 0.9768 | -0.44556 | 1.3669
55 | 0.078698 | 0.019821 | -0.078627 | -0.019775 | 7.1214e-05 | 4.5403e-05 | 0.11844 | 0.11844 | 0.11844 | 0.98904 | -0.20976 | 0.98806 | -0.2287 | 32.5373
56 | -0.0034272 | -0.00085893 | 0.0034274 | 0.00085877 | 2.8404e-07 | -1.5983e-07 | 0.0052446 | 0.0052445 | 0.0052446 | 0.97236 | -0.53287 | 0.97245 | -0.53113 | 1.4408
57 | -0.0069449 | -0.0017403 | 0.0069456 | 0.0017406 | 6.299e-07 | 2.1858e-07 | 0.010627 | 0.010627 | 0.010627 | 0.97245 | -0.53113 | 0.97255 | -0.52922 | 2.9195
58 | -0.010672 | -0.0026744 | 0.010672 | 0.0026747 | 5.6302e-07 | 2.9045e-07 | 0.016328 | 0.016328 | 0.016328 | 0.97255 | -0.52922 | 0.9726 | -0.52811 | 4.4857
59 | -0.013484 | -0.0033794 | 0.01349 | 0.0033826 | 5.7342e-06 | 3.2238e-06 | 0.020629 | 0.020629 | 0.020629 | 0.9726 | -0.52811 | 0.97305 | -0.51919 | 5.6674
60 | 0.0021408 | 0.00053638 | -0.0021407 | -0.00053644 | 2.5147e-08 | -6.2834e-08 | 0.0032611 | 0.0032611 | 0.0032611 | 0.9768 | -0.44556 | 0.97678 | -0.44581 | 0.89592
61 | 0.0010322 | 0.00025861 | -0.0010322 | -0.00025869 | 6.1319e-09 | -7.8861e-08 | 0.0015724 | 0.0015724 | 0.0015724 | 0.97678 | -0.44581 | 0.97678 | -0.44593 | 0.43198
62 | -0.0046964 | -0.001177 | 0.0046971 | 0.001177 | 6.7613e-07 | -2.4511e-08 | 0.0070901 | 0.0070899 | 0.0070901 | 0.98566 | -0.27548 | 0.98581 | -0.27246 | 1.9478
63 | -0.0046971 | -0.001177 | 0.0046974 | 0.001177 | 3.1021e-07 | -1.1301e-08 | 0.0070899 | 0.0070898 | 0.0070899 | 0.98581 | -0.27246 | 0.98588 | -0.27108 | 1.9478
64 | -0.041824 | -0.010509 | 0.041855 | 0.010529 | 3.1252e-05 | 1.9734e-05 | 0.063136 | 0.063136 | 0.063136 | 0.98588 | -0.27108 | 0.98669 | -0.25543 | 17.345
65 | 0.037127 | 0.0093321 | -0.0371 | -0.009315 | 2.7202e-05 | 1.7115e-05 | 0.056046 | 0.056046 | 0.056046 | 0.98588 | -0.27108 | 0.98509 | -0.28643 | 15.3973
66 | -0.043362 | -0.010906 | 0.043367 | 0.01091 | 5.6049e-06 | 3.5425e-06 | 0.065408 | 0.065407 | 0.065408 | 0.98669 | -0.25543 | 0.98683 | -0.25273 | 17.9691
67 | 0.030541 | 0.0076713 | -0.03053 | -0.0076645 | 1.0927e-05 | 6.8193e-06 | 0.04614 | 0.04614 | 0.04614 | 0.98509 | -0.28643 | 0.98471 | -0.29393 | 12.6757
68 | -0.044936 | -0.011303 | 0.044943 | 0.011308 | 7.2052e-06 | 4.5579e-06 | 0.067772 | 0.067772 | 0.067772 | 0.98683 | -0.25273 | 0.987 | -0.24937 | 18.6187
69 | 0.03053 | 0.0076645 | -0.030502 | -0.0076469 | 2.8272e-05 | 1.7644e-05 | 0.04614 | 0.04614 | 0.04614 | 0.98471 | -0.29393 | 0.98371 | -0.31337 | 12.6758
70 | 0.04836 | 0.012175 | -0.048339 | -0.012162 | 2.1224e-05 | 1.3447e-05 | 0.072879 | 0.072879 | 0.072879 | 0.98766 | -0.23657 | 0.98719 | -0.24575 | 20.0218
71 | -0.04836 | -0.012175 | 0.048378 | 0.012187 | 1.8201e-05 | 1.1531e-05 | 0.072879 | 0.072879 | 0.072879 | 0.98766 | -0.23657 | 0.98806 | -0.2287 | 20.0217
72 | 0.046317 | 0.011655 | -0.046309 | -0.01165 | 8.0138e-06 | 5.0728e-06 | 0.069832 | 0.069832 | 0.069832 | 0.98719 | -0.24575 | 0.987 | -0.24937 | 19.1846
73 | 0.030248 | 0.0075887 | -0.030243 | -0.0075852 | 5.5295e-06 | 3.4479e-06 | 0.045557 | 0.045557 | 0.045557 | 0.98806 | -0.2287 | 0.98787 | -0.23253 | 12.5155
74 | 0.021001 | 0.0052657 | -0.020994 | -0.005261 | 7.6087e-06 | 4.6145e-06 | 0.031768 | 0.031768 | 0.031768 | 0.98371 | -0.31337 | 0.98332 | -0.32097 | 8.7276
75 | 0.0095008 | 0.0023812 | -0.0094993 | -0.0023805 | 1.4267e-06 | 6.7928e-07 | 0.014371 | 0.014371 | 0.014371 | 0.98371 | -0.31337 | 0.98355 | -0.31652 | 3.9482
76 | 0.022936 | 0.005754 | -0.022928 | -0.0057488 | 8.5861e-06 | 5.2497e-06 | 0.034551 | 0.034551 | 0.034551 | 0.98787 | -0.23253 | 0.98746 | -0.24039 | 9.492
77 | 0.0043728 | 0.0010955 | -0.0043722 | -0.0010956 | 6.8926e-07 | -9.1276e-08 | 0.006617 | 0.0066172 | 0.0066172 | 0.98332 | -0.32097 | 0.98316 | -0.32428 | 1.8179
78 | 0.0042524 | 0.0010655 | -0.0042521 | -0.0010656 | 3.4235e-07 | -6.0805e-08 | 0.0064334 | 0.0064335 | 0.0064335 | 0.98355 | -0.31652 | 0.98347 | -0.31821 | 1.7674
79 | 0.0043722 | 0.0010956 | -0.0043717 | -0.0010956 | 4.8502e-07 | -6.4102e-08 | 0.0066172 | 0.0066174 | 0.0066174 | 0.98316 | -0.32428 | 0.98304 | -0.32661 | 1.818
80 | 0.0021261 | 0.00053274 | -0.002126 | -0.00053283 | 3.4944e-08 | -9.1904e-08 | 0.0032168 | 0.0032168 | 0.0032168 | 0.98347 | -0.31821 | 0.98345 | -0.31856 | 0.88374
81 | 0.020688 | 0.0051875 | -0.020682 | -0.0051838 | 6.1672e-06 | 3.7306e-06 | 0.031176 | 0.031176 | 0.031176 | 0.98746 | -0.24039 | 0.98714 | -0.24664 | 8.565
82 | 0.008185 | 0.0020513 | -0.0081844 | -0.0020511 | 6.1573e-07 | 2.5619e-07 | 0.012338 | 0.012338 | 0.012338 | 0.98714 | -0.24664 | 0.98706 | -0.24822 | 3.3896
83 | 0.012497 | 0.0031325 | -0.012495 | -0.0031312 | 2.2572e-06 | 1.2278e-06 | 0.018838 | 0.018838 | 0.018838 | 0.98714 | -0.24664 | 0.98695 | -0.25044 | 5.1754
84 | 0.0059953 | 0.0015024 | -0.0059952 | -0.0015024 | 4.0582e-08 | 9.0387e-09 | 0.009038 | 0.009038 | 0.009038 | 0.98706 | -0.24822 | 0.98705 | -0.24837 | 2.483
85 | 0.0070431 | 0.0017649 | -0.0070419 | -0.0017645 | 1.1923e-06 | 4.0282e-07 | 0.010619 | 0.010619 | 0.010619 | 0.98695 | -0.25044 | 0.98677 | -0.25399 | 2.9173
86 | 0.001677 | 0.00042015 | -0.0016769 | -0.00042028 | 2.6772e-08 | -1.2564e-07 | 0.002528 | 0.0025281 | 0.0025281 | 0.98705 | -0.24837 | 0.98704 | -0.2487 | 0.69452
87 | 0.0043935 | 0.0011007 | -0.004393 | -0.0011008 | 5.6949e-07 | -7.7427e-08 | 0.0066252 | 0.0066253 | 0.0066253 | 0.98677 | -0.25399 | 0.98663 | -0.25671 | 1.8202
88 | 0.004393 | 0.0011008 | -0.0043925 | -0.0011009 | 4.1425e-07 | -5.6229e-08 | 0.0066253 | 0.0066255 | 0.0066255 | 0.98663 | -0.25671 | 0.98652 | -0.25869 | 1.8202

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25372 | 0.064683

## res_load
| p_mw | q_mvar
0 | 0.0036583 | 0.00091685
1 | 0.0050853 | 0.0012745
2 | 0.0035354 | 0.00088607
3 | 0.0074409 | 0.0018649
4 | 0.0054544 | 0.001367
5 | 0.0036293 | 0.00090958
6 | 0.0025528 | 0.0006398
7 | 0.0053571 | 0.0013426
8 | 0.0018247 | 0.0004573
9 | 0.005634 | 0.001412
10 | 0.0029224 | 0.00073243
11 | 0.0088117 | 0.0022084
12 | 0.0026853 | 0.000673
13 | 0.0064222 | 0.0016096
14 | 0.0060405 | 0.0015139
15 | 0.001523 | 0.0003817
16 | 0.0019358 | 0.00048516
17 | 0.0057552 | 0.0014424
18 | 0.002875 | 0.00072054
19 | 0.003992 | 0.0010005
20 | 0.0018699 | 0.00046864
21 | 0.00094 | 0.00023559
22 | 0.0085826 | 0.002151
23 | 0.0069694 | 0.0017467
24 | 0.0035584 | 0.00089183
25 | 0.004329 | 0.001085
26 | 0.0038643 | 0.00096849
27 | 0.0045786 | 0.0011475
28 | 0.0065008 | 0.0016292
29 | 0.0019906 | 0.00049889
30 | 0.01228 | 0.0030776
31 | 0.0012669 | 0.00031753
32 | 0.0027543 | 0.00069029
33 | 0.0018185 | 0.00045575
34 | 0.00099719 | 0.00024992
35 | 0.0034272 | 0.00085893
36 | 0.0035175 | 0.00088157
37 | 0.0037262 | 0.00093387
38 | 0.0028115 | 0.00070464
39 | 0.0035133 | 0.00088052
40 | 0.0011254 | 0.00028206
41 | 0.0011086 | 0.00027783
42 | 0.0010322 | 0.00025869
43 | 0.0046964 | 0.001177
44 | 0.0015064 | 0.00037753
45 | 0.0065584 | 0.0016437
46 | 0.0015682 | 0.00039303
47 | 0.0020217 | 0.0005067
48 | 0.0013661 | 0.00034239
49 | 0.0073065 | 0.0018312
50 | 0.016621 | 0.0041656
51 | 0.0052469 | 0.001315
52 | 0.002126 | 0.00053283
53 | 0.0043717 | 0.0010956
54 | 0.002126 | 0.00053283
55 | 0.0022394 | 0.00056124
56 | 0.0021891 | 0.00054865
57 | 0.0054518 | 0.0013663
58 | 0.0043183 | 0.0010823
59 | 0.0026484 | 0.00066375
60 | 0.0016769 | 0.00042028
61 | 0.0043925 | 0.0011009

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1