## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_135-14_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_135-14_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_135-14_0_5_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_135-14_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_135-14_0_5_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_135-14_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_135-14_0_5_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_135-14_0_5_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_135-14_0_5_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_135-14_0_5_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_135-14_0_5_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_135-14_0_5_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_135-14_0_5_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_135-14_0_5_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_135-14_0_5_node_67 | 0.4 | n |  | TRUE
15 | bus_LV_135-14_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_135-14_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_135-14_0_5_node_128 | 0.4 | n |  | TRUE
18 | bus_LV_135-14_0_5_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_135-14_0_5_node_116 | 0.4 | n |  | TRUE
20 | bus_LV_135-14_0_5_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_135-14_0_5_node_117 | 0.4 | n |  | TRUE
22 | bus_LV_135-14_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_135-14_0_5_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_135-14_0_5_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_135-14_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_135-14_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_135-14_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_135-14_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_135-14_0_5_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_135-14_0_5_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_135-14_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_135-14_0_5_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_135-14_0_5_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_135-14_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_135-14_0_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_135-14_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_135-14_0_5_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_135-14_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_135-14_0_5_node_70 | 0.4 | n |  | TRUE
40 | bus_LV_135-14_0_5_node_52 | 0.4 | n |  | TRUE
41 | bus_LV_135-14_0_5_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_135-14_0_5_node_108 | 0.4 | n |  | TRUE
43 | bus_LV_135-14_0_5_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_135-14_0_5_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_135-14_0_5_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_135-14_0_5_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_135-14_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_135-14_0_5_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_135-14_0_5_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_135-14_0_5_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_135-14_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_135-14_0_5_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_135-14_0_5_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_135-14_0_5_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_135-14_0_5_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_135-14_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_135-14_0_5_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_135-14_0_5_node_101 | 0.4 | n |  | TRUE
59 | bus_LV_135-14_0_5_node_99 | 0.4 | n |  | TRUE
60 | bus_LV_135-14_0_5_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_135-14_0_5_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_135-14_0_5_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_135-14_0_5_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_135-14_0_5_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_135-14_0_5_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_135-14_0_5_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_135-14_0_5_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_135-14_0_5_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_135-14_0_5_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_135-14_0_5_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_135-14_0_5_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_135-14_0_5_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_135-14_0_5_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_135-14_0_5_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_135-14_0_5_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_135-14_0_5_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_135-14_0_5_node_82 | 0.4 | n |  | TRUE
78 | bus_LV_135-14_0_5_node_86 | 0.4 | n |  | TRUE
79 | bus_LV_135-14_0_5_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_135-14_0_5_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_135-14_0_5_node_106 | 0.4 | n |  | TRUE
82 | bus_LV_135-14_0_5_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_135-14_0_5_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_135-14_0_5_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_135-14_0_5_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_135-14_0_5_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_135-14_0_5_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_135-14_0_5_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_135-14_0_5_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_135-14_0_5_node_85 | 0.4 | n |  | TRUE
91 | bus_LV_135-14_0_5_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_135-14_0_5_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_135-14_0_5_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_135-14_0_5_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_135-14_0_5_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_135-14_0_5_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_135-14_0_5_node_120 | 0.4 | n |  | TRUE
98 | bus_LV_135-14_0_5_node_121 | 0.4 | n |  | TRUE
99 | bus_LV_135-14_0_5_node_125 | 0.4 | n |  | TRUE
100 | bus_LV_135-14_0_5_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_135-14_0_5_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_135-14_0_5_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_135-14_0_5_node_105 | 0.4 | n |  | TRUE
104 | bus_LV_135-14_0_5_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_135-14_0_5_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_135-14_0_5_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_135-14_0_5_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_135-14_0_5_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_135-14_0_5_node_126 | 0.4 | n |  | TRUE
110 | bus_LV_135-14_0_5_node_115 | 0.4 | n |  | TRUE
111 | bus_LV_135-14_0_5_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_135-14_0_5_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_135-14_0_5_node_113 | 0.4 | n |  | TRUE
114 | bus_LV_135-14_0_5_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_135-14_0_5_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_135-14_0_5_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_135-14_0_5_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_135-14_0_5_node_123 | 0.4 | n |  | TRUE
119 | bus_MV_360_0_node_75 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_135-14_0_5_load_0 | 0 | 0.0036329 | 0.00091049 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_135-14_0_5_load_6 | 2 | 0.002422 | 0.00060702 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_135-14_0_5_load_2 | 3 | 0.018484 | 0.0046326 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_135-14_0_5_load_7 | 4 | 0.004558 | 0.0011423 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_135-14_0_5_load_8 | 5 | 0.0024544 | 0.00061513 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_135-14_0_5_load_9 | 6 | 0.005515 | 0.0013822 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_135-14_0_5_load_14 | 7 | 0.0041231 | 0.0010334 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_135-14_0_5_load_10 | 8 | 0.0029946 | 0.00075051 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_135-14_0_5_load_20 | 9 | 0.0029692 | 0.00074415 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_135-14_0_5_load_11 | 10 | 0.0039894 | 0.00099983 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_135-14_0_5_load_66 | 11 | 0.0027004 | 0.00067679 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_135-14_0_5_load_15 | 12 | 0.013698 | 0.003433 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_135-14_0_5_load_18 | 13 | 0.0028725 | 0.00071992 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_135-14_0_5_load_67 | 14 | 0.0034869 | 0.0008739 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_135-14_0_5_load_128 | 17 | 0.021449 | 0.0053756 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_135-14_0_5_load_40 | 18 | 0.0012674 | 0.00031764 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_135-14_0_5_load_116 | 19 | 0.00088093 | 0.00022078 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_135-14_0_5_load_117 | 21 | 0.002998 | 0.00075138 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_135-14_0_5_load_16 | 22 | 0.0072871 | 0.0018263 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_135-14_0_5_load_65 | 23 | 0.0024044 | 0.00060261 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_135-14_0_5_load_17 | 25 | 0.0039273 | 0.00098427 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_135-14_0_5_load_19 | 26 | 0.0059331 | 0.001487 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_135-14_0_5_load_21 | 27 | 0.0059058 | 0.0014801 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_135-14_0_5_load_22 | 28 | 0.0044003 | 0.0011028 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_135-14_0_5_load_31 | 29 | 0.0065297 | 0.0016365 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_135-14_0_5_load_32 | 30 | 0.0041161 | 0.0010316 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_135-14_0_5_load_23 | 31 | 0.0040223 | 0.0010081 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_135-14_0_5_load_24 | 32 | 0.005224 | 0.0013092 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_135-14_0_5_load_25 | 33 | 0.0088449 | 0.0022167 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_135-14_0_5_load_26 | 34 | 0.0019657 | 0.00049266 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_135-14_0_5_load_28 | 36 | 0.0026163 | 0.00065571 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_135-14_0_5_load_30 | 38 | 0.011487 | 0.0028789 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_135-14_0_5_load_70 | 39 | 0.018 | 0.0045113 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_135-14_0_5_load_44 | 41 | 0.0055317 | 0.0013864 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_135-14_0_5_load_108 | 42 | 0.010498 | 0.0026309 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_135-14_0_5_load_50 | 44 | 0.0077509 | 0.0019426 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_135-14_0_5_load_43 | 45 | 0.003765 | 0.00094361 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_135-14_0_5_load_33 | 46 | 0.0053781 | 0.0013479 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_135-14_0_5_load_35 | 48 | 0.012516 | 0.0031368 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_135-14_0_5_load_36 | 49 | 0.0086557 | 0.0021693 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_135-14_0_5_load_38 | 51 | 0.0090163 | 0.0022597 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_135-14_0_5_load_45 | 52 | 0.0041962 | 0.0010517 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_135-14_0_5_load_46 | 53 | 0.0029061 | 0.00072833 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_135-14_0_5_load_42 | 54 | 0.0016219 | 0.00040648 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_135-14_0_5_load_68 | 55 | 0.0096266 | 0.0024126 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_135-14_0_5_load_47 | 56 | 0.0042084 | 0.0010547 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_135-14_0_5_load_48 | 57 | 0.002654 | 0.00066517 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_135-14_0_5_load_101 | 58 | 0.004392 | 0.0011007 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_135-14_0_5_load_99 | 59 | 0.0013143 | 0.00032939 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_135-14_0_5_load_49 | 60 | 0.0048706 | 0.0012207 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_135-14_0_5_load_51 | 61 | 0.013097 | 0.0032824 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_135-14_0_5_load_53 | 62 | 0.0054125 | 0.0013565 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_135-14_0_5_load_55 | 63 | 0.0069401 | 0.0017394 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_135-14_0_5_load_93 | 64 | 0.0093389 | 0.0023405 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_135-14_0_5_load_62 | 67 | 0.011652 | 0.0029202 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_135-14_0_5_load_57 | 68 | 0.019406 | 0.0048635 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_135-14_0_5_load_56 | 69 | 0.0040894 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_135-14_0_5_load_61 | 72 | 0.01254 | 0.0031429 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_135-14_0_5_load_63 | 73 | 0.0030034 | 0.00075273 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_135-14_0_5_load_69 | 75 | 0.0083821 | 0.0021008 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_135-14_0_5_load_82 | 77 | 0.0024939 | 0.00062503 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_135-14_0_5_load_86 | 78 | 0.010959 | 0.0027466 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_135-14_0_5_load_81 | 80 | 0.00027715 | 6.9461e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_135-14_0_5_load_106 | 81 | 0.003394 | 0.00085061 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_135-14_0_5_load_71 | 82 | 0.0078684 | 0.001972 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_135-14_0_5_load_84 | 83 | 0.0021993 | 0.0005512 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_135-14_0_5_load_79 | 84 | 0.0020298 | 0.00050873 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_135-14_0_5_load_77 | 85 | 0.0035814 | 0.00089759 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_135-14_0_5_load_76 | 86 | 0.0015142 | 0.00037949 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_135-14_0_5_load_78 | 87 | 0.001544 | 0.00038697 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_135-14_0_5_load_80 | 88 | 0.0042251 | 0.0010589 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_135-14_0_5_load_83 | 89 | 0.013372 | 0.0033513 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_135-14_0_5_load_85 | 90 | 0.01229 | 0.0030803 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_135-14_0_5_load_87 | 91 | 0.0048855 | 0.0012244 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_135-14_0_5_load_92 | 95 | 0.0063915 | 0.0016018 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_135-14_0_5_load_121 | 98 | 0.0028938 | 0.00072525 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_135-14_0_5_load_125 | 99 | 0.00029151 | 7.306e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_135-14_0_5_load_97 | 100 | 0.0072115 | 0.0018074 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_135-14_0_5_load_107 | 102 | 0.0050631 | 0.0012689 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_135-14_0_5_load_105 | 103 | 0.0079581 | 0.0019945 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_135-14_0_5_load_98 | 104 | 0.0015329 | 0.00038418 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_135-14_0_5_load_100 | 105 | 0.0021479 | 0.00053832 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_135-14_0_5_load_109 | 108 | 0.00061941 | 0.00015524 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_135-14_0_5_load_126 | 109 | 0.00017866 | 4.4776e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_135-14_0_5_load_110 | 111 | 0.00040073 | 0.00010043 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_135-14_0_5_load_114 | 114 | 0.0014286 | 0.00035805 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_135-14_0_5_load_118 | 115 | 0.0019712 | 0.00049403 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_135-14_0_5_load_119 | 116 | 0.00069934 | 0.00017527 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_135-14_0_5_load_122 | 117 | 0.011211 | 0.0028097 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_135-14_0_5_load_123 | 118 | 0.00045415 | 0.00011382 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_135-14_0_5_line_0 |  | 0 | 1 | 0.0787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_135-14_0_5_line_1 |  | 0 | 2 | 0.084577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_135-14_0_5_line_2 |  | 1 | 3 | 0.034369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_135-14_0_5_line_3 |  | 2 | 4 | 0.0028909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_135-14_0_5_line_4 |  | 4 | 5 | 0.016231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_135-14_0_5_line_5 |  | 5 | 6 | 0.0086958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_135-14_0_5_line_6 |  | 6 | 7 | 0.013526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_135-14_0_5_line_7 |  | 7 | 12 | 0.025115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_135-14_0_5_line_8 |  | 8 | 9 | 0.024419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_135-14_0_5_line_9 |  | 9 | 13 | 0.024966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_135-14_0_5_line_10 |  | 10 | 11 | 0.016177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_135-14_0_5_line_11 |  | 11 | 14 | 0.0086304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_135-14_0_5_line_12 |  | 12 | 22 | 0.011814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_135-14_0_5_line_13 |  | 13 | 25 | 0.016749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_135-14_0_5_line_14 |  | 14 | 74 | 0.025001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_135-14_0_5_line_15 |  | 15 | 16 | 0.058113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_135-14_0_5_line_16 |  | 15 | 17 | 0.1514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_135-14_0_5_line_17 |  | 16 | 18 | 0.082122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_135-14_0_5_line_18 |  | 16 | 19 | 0.0268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_135-14_0_5_line_19 |  | 18 | 20 | 0.016428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_135-14_0_5_line_20 |  | 19 | 21 | 0.0041073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_135-14_0_5_line_21 |  | 20 | 47 | 0.004892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_135-14_0_5_line_22 |  | 21 | 115 | 0.0047458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_135-14_0_5_line_23 |  | 22 | 23 | 0.024943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_135-14_0_5_line_24 |  | 23 | 24 | 0.037588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_135-14_0_5_line_25 |  | 24 | 55 | 9.9866e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_135-14_0_5_line_26 |  | 24 | 51 | 0.025449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_135-14_0_5_line_27 |  | 25 | 26 | 0.0095613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_135-14_0_5_line_28 |  | 26 | 27 | 0.023478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_135-14_0_5_line_29 |  | 27 | 28 | 0.014194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_135-14_0_5_line_30 |  | 28 | 29 | 0.012263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_135-14_0_5_line_31 |  | 29 | 30 | 0.025498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_135-14_0_5_line_32 |  | 30 | 36 | 0.0021795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_135-14_0_5_line_33 |  | 31 | 32 | 0.013232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_135-14_0_5_line_34 |  | 31 | 33 | 0.026051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_135-14_0_5_line_35 |  | 32 | 34 | 0.0037808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_135-14_0_5_line_36 |  | 33 | 35 | 0.036288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_135-14_0_5_line_37 |  | 34 | 36 | 0.020762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_135-14_0_5_line_38 |  | 35 | 37 | 0.029527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_135-14_0_5_line_39 |  | 35 | 38 | 0.0030715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_135-14_0_5_line_40 |  | 37 | 39 | 0.029603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_135-14_0_5_line_41 |  | 37 | 40 | 0.005306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_135-14_0_5_line_42 |  | 38 | 41 | 0.032707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_135-14_0_5_line_43 |  | 39 | 42 | 0.037261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_135-14_0_5_line_44 |  | 40 | 43 | 0.039777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_135-14_0_5_line_45 |  | 40 | 44 | 0.019612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_135-14_0_5_line_46 |  | 41 | 45 | 0.013385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_135-14_0_5_line_47 |  | 42 | 81 | 0.014531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_135-14_0_5_line_48 |  | 43 | 64 | 0.0019139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_135-14_0_5_line_49 |  | 44 | 60 | 0.010647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_135-14_0_5_line_50 |  | 45 | 54 | 0.01628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_135-14_0_5_line_51 |  | 46 | 47 | 0.038716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_135-14_0_5_line_52 |  | 46 | 48 | 0.025308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_135-14_0_5_line_53 |  | 47 | 49 | 0.038676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_135-14_0_5_line_54 |  | 49 | 50 | 0.048408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_135-14_0_5_line_55 |  | 50 | 52 | 0.0137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_135-14_0_5_line_56 |  | 50 | 53 | 0.040155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_135-14_0_5_line_57 |  | 50 | 54 | 0.02791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_135-14_0_5_line_58 |  | 52 | 56 | 0.033144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_135-14_0_5_line_59 |  | 53 | 57 | 0.024983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_135-14_0_5_line_60 |  | 55 | 56 | 0.042312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_135-14_0_5_line_61 |  | 57 | 58 | 0.031443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_135-14_0_5_line_62 |  | 58 | 59 | 0.023235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_135-14_0_5_line_63 |  | 59 | 104 | 0.0070866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_135-14_0_5_line_64 |  | 60 | 61 | 0.039719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_135-14_0_5_line_65 |  | 61 | 62 | 0.018206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_135-14_0_5_line_66 |  | 62 | 63 | 0.033482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_135-14_0_5_line_67 |  | 63 | 65 | 0.013536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_135-14_0_5_line_68 |  | 64 | 66 | 0.038412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_135-14_0_5_line_69 |  | 65 | 67 | 0.0525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_135-14_0_5_line_70 |  | 65 | 68 | 0.039173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_135-14_0_5_line_71 |  | 66 | 93 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_135-14_0_5_line_72 |  | 67 | 75 | 0.019471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_135-14_0_5_line_73 |  | 68 | 69 | 0.043373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_135-14_0_5_line_74 |  | 69 | 70 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_135-14_0_5_line_75 |  | 70 | 71 | 0.01852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_135-14_0_5_line_76 |  | 70 | 72 | 0.0056689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_135-14_0_5_line_77 |  | 71 | 73 | 0.016512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_135-14_0_5_line_78 |  | 72 | 74 | 0.0082488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_135-14_0_5_line_79 |  | 73 | 76 | 0.0044846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_135-14_0_5_line_80 |  | 75 | 77 | 0.017362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_135-14_0_5_line_81 |  | 76 | 78 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_135-14_0_5_line_82 |  | 76 | 79 | 0.031048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_135-14_0_5_line_83 |  | 77 | 80 | 0.0072944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_135-14_0_5_line_84 |  | 78 | 83 | 0.00092252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_135-14_0_5_line_85 |  | 79 | 82 | 0.0048049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_135-14_0_5_line_86 |  | 80 | 88 | 0.00022824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_135-14_0_5_line_87 |  | 81 | 101 | 0.02169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_135-14_0_5_line_88 |  | 83 | 89 | 0.035877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_135-14_0_5_line_89 |  | 84 | 85 | 0.00027732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_135-14_0_5_line_90 |  | 85 | 86 | 0.014265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_135-14_0_5_line_91 |  | 86 | 87 | 0.018226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_135-14_0_5_line_92 |  | 87 | 88 | 0.0053667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_135-14_0_5_line_93 |  | 89 | 90 | 0.011595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_135-14_0_5_line_94 |  | 91 | 92 | 0.025466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_135-14_0_5_line_95 |  | 91 | 93 | 0.028687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_135-14_0_5_line_96 |  | 92 | 94 | 0.061979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_135-14_0_5_line_97 |  | 94 | 95 | 0.039064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_135-14_0_5_line_98 |  | 95 | 96 | 0.011143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_135-14_0_5_line_99 |  | 96 | 97 | 0.034614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_135-14_0_5_line_100 |  | 97 | 98 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_135-14_0_5_line_101 |  | 97 | 99 | 0.041895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_135-14_0_5_line_102 |  | 98 | 117 | 0.01206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_135-14_0_5_line_103 |  | 99 | 118 | 0.010296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_135-14_0_5_line_104 |  | 100 | 101 | 0.013166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_135-14_0_5_line_105 |  | 101 | 103 | 0.016434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_135-14_0_5_line_106 |  | 102 | 103 | 0.024677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_135-14_0_5_line_107 |  | 104 | 105 | 0.020067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_135-14_0_5_line_108 |  | 105 | 106 | 6.7743e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_135-14_0_5_line_109 |  | 106 | 107 | 0.003393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_135-14_0_5_line_110 |  | 107 | 108 | 0.016996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_135-14_0_5_line_111 |  | 108 | 109 | 0.020563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_135-14_0_5_line_112 |  | 109 | 110 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_135-14_0_5_line_113 |  | 110 | 113 | 0.063423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_135-14_0_5_line_114 |  | 111 | 112 | 0.017588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_135-14_0_5_line_115 |  | 112 | 113 | 0.028253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_135-14_0_5_line_116 |  | 113 | 114 | 0.029903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_135-14_0_5_line_117 |  | 115 | 116 | 0.00070462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_135-14_0_5_trafo_28 | 0.63 MVA 20/0.4 kV | 119 | 36 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2683150.7275 | 1241606.6177 | 2683160.3778 | 1241612.3793 | 2683176.5545 | 1241613.7291 | 2683195.8993 | 1241614.0004 | 2683208.361 | 1241612.3071 | 2683217.8647 | 1241605.8691 | 2683223.878 | 1241600.8609
1 | 2683298.2943 | 1241641.0543 | 2683223.878 | 1241600.8609
2 | 2683150.7275 | 1241606.6177 | 2683146.4479 | 1241621.7242 | 2683136.5959 | 1241637.5805
3 | 2683298.2943 | 1241641.0543 | 2683297.1987 | 1241643.7296
4 | 2683297.1987 | 1241643.7296 | 2683296.1433 | 1241646.3072 | 2683291.6264 | 1241658.9718
5 | 2683288.7053 | 1241667.1623 | 2683288.7053 | 1241667.1623 | 2683291.6264 | 1241658.9718
6 | 2683285.6946 | 1241680.3489 | 2683288.7053 | 1241667.1623
7 | 2683285.6946 | 1241680.3489 | 2683283.8796 | 1241688.2987 | 2683281.5644 | 1241705.1005
8 | 2683333.6145 | 1241657.0457 | 2683333.8634 | 1241652.3409 | 2683335.4082 | 1241632.6943
9 | 2683333.6145 | 1241657.0457 | 2683332.6382 | 1241675.5071 | 2683333.4289 | 1241681.937
10 | 2683359.304 | 1241636.4577 | 2683360.1839 | 1241640.4463 | 2683362.8828 | 1241644.7762 | 2683368.6647 | 1241648.7047
11 | 2683377.1867 | 1241650.0686 | 2683368.6647 | 1241648.7047 | 2683368.6647 | 1241648.7047
12 | 2683281.5644 | 1241705.1005 | 2683281.5644 | 1241705.1005 | 2683281.782 | 1241716.9122
13 | 2683335.4733 | 1241698.5608 | 2683333.4289 | 1241681.937
14 | 2683401.8734 | 1241654.0194 | 2683377.1867 | 1241650.0686
15 | 2683056.5854 | 1241815.05 | 2683071.5556 | 1241830.7152 | 2683090.6336 | 1241842.9688 | 2683104.2857 | 1241844.7723
16 | 2683056.5854 | 1241815.05 | 2682931.0506 | 1241730.4117
17 | 2683104.2857 | 1241844.7723 | 2683123.2847 | 1241847.0066 | 2683167.2123 | 1241850.2464 | 2683185.0539 | 1241856.6187
18 | 2683104.2857 | 1241844.7723 | 2683103.3909 | 1241858.4474 | 2683102.7011 | 1241871.525 | 2683102.7011 | 1241871.525
19 | 2683200.5243 | 1241862.144 | 2683185.0539 | 1241856.6187
20 | 2683102.7011 | 1241871.525 | 2683104.2051 | 1241873.1917 | 2683106.0522 | 1241873.4299
21 | 2683200.5243 | 1241862.144 | 2683205.4294 | 1241862.2684
22 | 2683106.0522 | 1241873.4299 | 2683110.7589 | 1241874.0371
23 | 2683281.782 | 1241716.9122 | 2683281.8819 | 1241722.3396 | 2683283.0425 | 1241741.8199
24 | 2683285.1341 | 1241779.3486 | 2683284.77 | 1241770.8151 | 2683283.0425 | 1241741.8199
25 | 2683285.1341 | 1241779.3486 | 2683285.1317 | 1241779.4484
26 | 2683285.1341 | 1241779.3486 | 2683261.0336 | 1241774.2624 | 2683260.7323 | 1241775.0221
27 | 2683336.6886 | 1241708.0438 | 2683336.4653 | 1241706.6277 | 2683335.4733 | 1241698.5608
28 | 2683336.6886 | 1241708.0438 | 2683340.3455 | 1241731.2358
29 | 2683343.5081 | 1241745.0408 | 2683341.4152 | 1241738.0198 | 2683340.3455 | 1241731.2358
30 | 2683343.5081 | 1241745.0408 | 2683347.0113 | 1241756.7928
31 | 2683354.2953 | 1241781.228 | 2683347.0113 | 1241756.7928
32 | 2683354.2953 | 1241781.228 | 2683354.9179 | 1241783.3167
33 | 2683361.929 | 1241806.8363 | 2683365.7089 | 1241819.5166
34 | 2683373.1508 | 1241844.4815 | 2683365.7089 | 1241819.5166
35 | 2683361.929 | 1241806.8363 | 2683360.8489 | 1241803.213
36 | 2683383.5172 | 1241879.2574 | 2683373.1508 | 1241844.4815
37 | 2683360.8489 | 1241803.213 | 2683354.9179 | 1241783.3167
38 | 2683383.5172 | 1241879.2574 | 2683410.9575 | 1241890.362
39 | 2683383.5172 | 1241879.2574 | 2683380.5082 | 1241878.6412
40 | 2683410.9575 | 1241890.362 | 2683399.768 | 1241917.769 | 2683399.768 | 1241917.769
41 | 2683410.9575 | 1241890.362 | 2683415.8893 | 1241892.355
42 | 2683348.1454 | 1241874.1436 | 2683369.932 | 1241876.4756 | 2683380.5082 | 1241878.6412
43 | 2683399.768 | 1241917.769 | 2683377.7984 | 1241926.2665 | 2683372.6303 | 1241938.9603
44 | 2683449.7306 | 1241913.3346 | 2683438.3227 | 1241905.1906 | 2683415.8893 | 1241892.355
45 | 2683415.8893 | 1241892.355 | 2683415.2274 | 1241872.7539
46 | 2683348.1454 | 1241874.1436 | 2683334.8369 | 1241872.719
47 | 2683372.6303 | 1241938.9603 | 2683367.151 | 1241952.4185
48 | 2683449.7306 | 1241913.3346 | 2683451.2743 | 1241914.4659
49 | 2683414.868 | 1241862.1126 | 2683415.2274 | 1241872.7539
50 | 2683318.6498 | 1241870.9863 | 2683334.8369 | 1241872.719
51 | 2683205.4294 | 1241862.2684 | 2683205.8068 | 1241839.1348 | 2683205.9893 | 1241823.5563
52 | 2683207.9186 | 1241798.5463 | 2683206.2274 | 1241803.2259 | 2683205.9893 | 1241823.5563
53 | 2683205.4294 | 1241862.2684 | 2683207.4467 | 1241865.0654 | 2683210.9699 | 1241866.1489 | 2683242.5029 | 1241866.8854
54 | 2683290.898 | 1241868.0156 | 2683242.5029 | 1241866.8854
55 | 2683290.898 | 1241868.0156 | 2683288.2696 | 1241854.5702
56 | 2683290.898 | 1241868.0156 | 2683292.249 | 1241885.4138 | 2683292.5581 | 1241908.1159
57 | 2683290.898 | 1241868.0156 | 2683318.6498 | 1241870.9863
58 | 2683284.1782 | 1241821.7477 | 2683284.378 | 1241828.8959 | 2683285.7062 | 1241841.457 | 2683288.2696 | 1241854.5702
59 | 2683292.5581 | 1241908.1159 | 2683292.8982 | 1241933.0966
60 | 2683285.1317 | 1241779.4484 | 2683284.1364 | 1241820.253 | 2683284.1782 | 1241821.7477
61 | 2683293.3263 | 1241964.5366 | 2683292.8982 | 1241933.0966
62 | 2683293.6427 | 1241987.7693 | 2683293.3263 | 1241964.5366
63 | 2683293.7391 | 1241994.8552 | 2683293.6427 | 1241987.7693
64 | 2683414.868 | 1241862.1126 | 2683413.5274 | 1241822.4157
65 | 2683413.5274 | 1241822.4157 | 2683413.1776 | 1241812.0589 | 2683413.1071 | 1241804.2158
66 | 2683412.806 | 1241770.735 | 2683413.1071 | 1241804.2158
67 | 2683416.8814 | 1241757.8274 | 2683412.806 | 1241770.735 | 2683412.806 | 1241770.735
68 | 2683481.4154 | 1241938.1759 | 2683478.5111 | 1241935.0216 | 2683460.7762 | 1241921.4291 | 2683451.2743 | 1241914.4659
69 | 2683416.8814 | 1241757.8274 | 2683421.6164 | 1241775.4288 | 2683426.8907 | 1241783.7201 | 2683434.1354 | 1241788.9924 | 2683442.3679 | 1241791.7656 | 2683449.1574 | 1241792.1304
70 | 2683416.8814 | 1241757.8274 | 2683414.1241 | 1241737.2182 | 2683412.5502 | 1241718.9056
71 | 2683489.346 | 1241946.8047 | 2683481.4154 | 1241938.1759
72 | 2683449.1574 | 1241792.1304 | 2683454.4258 | 1241792.4134 | 2683466.1116 | 1241792.0997 | 2683468.5724 | 1241791.6332
73 | 2683413.0554 | 1241675.5699 | 2683412.0869 | 1241693.9028 | 2683412.2918 | 1241715.8993 | 2683412.5502 | 1241718.9056
74 | 2683415.4555 | 1241657.0569 | 2683413.0554 | 1241675.5699
75 | 2683433.8198 | 1241659.8392 | 2683415.4555 | 1241657.0569
76 | 2683415.4555 | 1241657.0569 | 2683409.9233 | 1241655.8197
77 | 2683433.8198 | 1241659.8392 | 2683450.1818 | 1241662.0631
78 | 2683401.8734 | 1241654.0194 | 2683409.9233 | 1241655.8197
79 | 2683454.6255 | 1241662.667 | 2683450.1818 | 1241662.0631
80 | 2683485.6304 | 1241788.3996 | 2683468.5724 | 1241791.6332
81 | 2683454.6255 | 1241662.667 | 2683451.4645 | 1241680.7374
82 | 2683454.6255 | 1241662.667 | 2683467.8152 | 1241664.5761 | 2683485.3425 | 1241667.1911
83 | 2683492.6179 | 1241786.3391 | 2683487.1338 | 1241788.1146 | 2683485.6304 | 1241788.3996
84 | 2683451.4645 | 1241680.7374 | 2683451.3055 | 1241681.6461
85 | 2683485.3425 | 1241667.1911 | 2683490.0402 | 1241668.2007
86 | 2683492.6179 | 1241786.3391 | 2683492.835 | 1241786.2688
87 | 2683373.3781 | 1241972.3377 | 2683365.9736 | 1241955.3103 | 2683367.151 | 1241952.4185
88 | 2683451.4041 | 1241715.3709 | 2683451.4041 | 1241715.3709 | 2683448.9746 | 1241713.9357 | 2683447.1751 | 1241710.1743 | 2683447.1845 | 1241705.2042 | 2683451.3055 | 1241681.6461
89 | 2683518.3731 | 1241762.4722 | 2683518.4704 | 1241762.2125
90 | 2683513.0615 | 1241775.6917 | 2683514.2801 | 1241773.397 | 2683518.3731 | 1241762.4722
91 | 2683513.0615 | 1241775.6917 | 2683511.7715 | 1241778.1206 | 2683506.9806 | 1241781.6892 | 2683497.9408 | 1241784.6158
92 | 2683497.9408 | 1241784.6158 | 2683492.835 | 1241786.2688
93 | 2683462.881 | 1241717.0223 | 2683451.4041 | 1241715.3709
94 | 2683541.0294 | 1241960.8198 | 2683531.4243 | 1241960.5066 | 2683516.6339 | 1241954.792
95 | 2683489.346 | 1241946.8047 | 2683497.5256 | 1241947.4091 | 2683516.6339 | 1241954.792
96 | 2683541.0294 | 1241960.8198 | 2683582.5517 | 1241914.7043
97 | 2683582.5517 | 1241914.7043 | 2683577.4414 | 1241908.2166 | 2683571.3078 | 1241903.5268 | 2683565.1463 | 1241900.2711 | 2683554.4956 | 1241897.9639 | 2683549.6229 | 1241896.0969
98 | 2683540.7587 | 1241889.8536 | 2683544.7345 | 1241894.2238 | 2683549.6229 | 1241896.0969
99 | 2683528.076 | 1241868.0816 | 2683527.3271 | 1241879.9241 | 2683528.7956 | 1241890.5413 | 2683533.6608 | 1241889.7425 | 2683540.7587 | 1241889.8536
100 | 2683528.076 | 1241868.0816 | 2683521.7426 | 1241866.8361 | 2683516.1744 | 1241864.4004
101 | 2683528.076 | 1241868.0816 | 2683538.9285 | 1241827.6163
102 | 2683505.8318 | 1241869.2028 | 2683507.5371 | 1241866.7584 | 2683512.0717 | 1241864.7429 | 2683516.1744 | 1241864.4004
103 | 2683538.9285 | 1241827.6163 | 2683544.5913 | 1241819.0176
104 | 2683373.3781 | 1241972.3377 | 2683385.5242 | 1241977.4193
105 | 2683373.3781 | 1241972.3377 | 2683367.1573 | 1241987.5492
106 | 2683367.1573 | 1241987.5492 | 2683363.7163 | 1241995.9635 | 2683368.6593 | 1242010.7451
107 | 2683293.7391 | 1241994.8552 | 2683294.0123 | 1242014.9199
108 | 2683294.0133 | 1242014.9876 | 2683294.0123 | 1242014.9199
109 | 2683294.0133 | 1242014.9876 | 2683290.6103 | 1242015.0399
110 | 2683290.6103 | 1242015.0399 | 2683274.45 | 1242015.2911 | 2683273.6165 | 1242015.3043
111 | 2683253.0537 | 1242015.4378 | 2683272.5897 | 1242015.3206 | 2683273.6165 | 1242015.3043
112 | 2683239.8424 | 1242015.517 | 2683253.0537 | 1242015.4378
113 | 2683176.4401 | 1242017.1294 | 2683184.7142 | 1242016.923 | 2683239.8424 | 1242015.517
114 | 2683148.3205 | 1242016.7463 | 2683146.6074 | 1242014.8988 | 2683140.9846 | 1242000.9186
115 | 2683148.3205 | 1242016.7463 | 2683150.8612 | 1242017.7938 | 2683176.4401 | 1242017.1294
116 | 2683176.4401 | 1242017.1294 | 2683176.6735 | 1242012.8852 | 2683182.3376 | 1241987.8662
117 | 2683111.4578 | 1241874.1272 | 2683110.7589 | 1241874.0371

## bus_geodata
| x | y | coords
0 | 2683223.878 | 1241600.8609
1 | 2683150.7275 | 1241606.6177
2 | 2683298.2943 | 1241641.0543
3 | 2683136.5959 | 1241637.5805
4 | 2683297.1987 | 1241643.7296
5 | 2683291.6264 | 1241658.9718
6 | 2683288.7053 | 1241667.1623
7 | 2683285.6946 | 1241680.3489
8 | 2683335.4082 | 1241632.6943
9 | 2683333.6145 | 1241657.0457
10 | 2683359.304 | 1241636.4577
11 | 2683368.6647 | 1241648.7047
12 | 2683281.5644 | 1241705.1005
13 | 2683333.4289 | 1241681.937
14 | 2683377.1867 | 1241650.0686
15 | 2683056.5854 | 1241815.05
16 | 2683104.2857 | 1241844.7723
17 | 2682931.0506 | 1241730.4117
18 | 2683185.0539 | 1241856.6187
19 | 2683102.7011 | 1241871.525
20 | 2683200.5243 | 1241862.144
21 | 2683106.0522 | 1241873.4299
22 | 2683281.782 | 1241716.9122
23 | 2683283.0425 | 1241741.8199
24 | 2683285.1341 | 1241779.3486
25 | 2683335.4733 | 1241698.5608
26 | 2683336.6886 | 1241708.0438
27 | 2683340.3455 | 1241731.2358
28 | 2683343.5081 | 1241745.0408
29 | 2683347.0113 | 1241756.7928
30 | 2683354.2953 | 1241781.228
31 | 2683365.7089 | 1241819.5166
32 | 2683361.929 | 1241806.8363
33 | 2683373.1508 | 1241844.4815
34 | 2683360.8489 | 1241803.213
35 | 2683383.5172 | 1241879.2574
36 | 2683354.9179 | 1241783.3167
37 | 2683410.9575 | 1241890.362
38 | 2683380.5082 | 1241878.6412
39 | 2683399.768 | 1241917.769
40 | 2683415.8893 | 1241892.355
41 | 2683348.1454 | 1241874.1436
42 | 2683372.6303 | 1241938.9603
43 | 2683449.7306 | 1241913.3346
44 | 2683415.2274 | 1241872.7539
45 | 2683334.8369 | 1241872.719
46 | 2683205.9893 | 1241823.5563
47 | 2683205.4294 | 1241862.2684
48 | 2683207.9186 | 1241798.5463
49 | 2683242.5029 | 1241866.8854
50 | 2683290.898 | 1241868.0156
51 | 2683260.7323 | 1241775.0221
52 | 2683288.2696 | 1241854.5702
53 | 2683292.5581 | 1241908.1159
54 | 2683318.6498 | 1241870.9863
55 | 2683285.1317 | 1241779.4484
56 | 2683284.1782 | 1241821.7477
57 | 2683292.8982 | 1241933.0966
58 | 2683293.3263 | 1241964.5366
59 | 2683293.6427 | 1241987.7693
60 | 2683414.868 | 1241862.1126
61 | 2683413.5274 | 1241822.4157
62 | 2683413.1071 | 1241804.2158
63 | 2683412.806 | 1241770.735
64 | 2683451.2743 | 1241914.4659
65 | 2683416.8814 | 1241757.8274
66 | 2683481.4154 | 1241938.1759
67 | 2683449.1574 | 1241792.1304
68 | 2683412.5502 | 1241718.9056
69 | 2683413.0554 | 1241675.5699
70 | 2683415.4555 | 1241657.0569
71 | 2683433.8198 | 1241659.8392
72 | 2683409.9233 | 1241655.8197
73 | 2683450.1818 | 1241662.0631
74 | 2683401.8734 | 1241654.0194
75 | 2683468.5724 | 1241791.6332
76 | 2683454.6255 | 1241662.667
77 | 2683485.6304 | 1241788.3996
78 | 2683451.4645 | 1241680.7374
79 | 2683485.3425 | 1241667.1911
80 | 2683492.6179 | 1241786.3391
81 | 2683367.151 | 1241952.4185
82 | 2683490.0402 | 1241668.2007
83 | 2683451.3055 | 1241681.6461
84 | 2683518.4704 | 1241762.2125
85 | 2683518.3731 | 1241762.4722
86 | 2683513.0615 | 1241775.6917
87 | 2683497.9408 | 1241784.6158
88 | 2683492.835 | 1241786.2688
89 | 2683451.4041 | 1241715.3709
90 | 2683462.881 | 1241717.0223
91 | 2683516.6339 | 1241954.792
92 | 2683541.0294 | 1241960.8198
93 | 2683489.346 | 1241946.8047
94 | 2683582.5517 | 1241914.7043
95 | 2683549.6229 | 1241896.0969
96 | 2683540.7587 | 1241889.8536
97 | 2683528.076 | 1241868.0816
98 | 2683516.1744 | 1241864.4004
99 | 2683538.9285 | 1241827.6163
100 | 2683385.5242 | 1241977.4193
101 | 2683373.3781 | 1241972.3377
102 | 2683368.6593 | 1242010.7451
103 | 2683367.1573 | 1241987.5492
104 | 2683293.7391 | 1241994.8552
105 | 2683294.0123 | 1242014.9199
106 | 2683294.0133 | 1242014.9876
107 | 2683290.6103 | 1242015.0399
108 | 2683273.6165 | 1242015.3043
109 | 2683253.0537 | 1242015.4378
110 | 2683239.8424 | 1242015.517
111 | 2683140.9846 | 1242000.9186
112 | 2683148.3205 | 1242016.7463
113 | 2683176.4401 | 1242017.1294
114 | 2683182.3376 | 1241987.8662
115 | 2683110.7589 | 1241874.0371
116 | 2683111.4578 | 1241874.1272
117 | 2683505.8318 | 1241869.2028
118 | 2683544.5913 | 1241819.0176
119 | 2683383.5172 | 1241879.2574

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97262 | -0.5283 | 0.0036329 | 0.00091049
1 | 0.97126 | -0.55514 | 0 | 0
2 | 0.97437 | -0.49389 | 0.002422 | 0.00060702
3 | 0.97067 | -0.56688 | 0.018484 | 0.0046326
4 | 0.97443 | -0.49258 | 0.004558 | 0.0011423
5 | 0.97487 | -0.48392 | 0.0024544 | 0.00061513
6 | 0.97513 | -0.47888 | 0.005515 | 0.0013822
7 | 0.9756 | -0.4697 | 0.0041231 | 0.0010334
8 | 0.99761 | -0.045926 | 0.0029946 | 0.00075051
9 | 0.99768 | -0.044645 | 0.0029692 | 0.00074415
10 | 0.97385 | -0.50399 | 0.0039894 | 0.00099983
11 | 0.97391 | -0.50281 | 0.0027004 | 0.00067679
12 | 0.97656 | -0.45077 | 0.013698 | 0.003433
13 | 0.99781 | -0.042038 | 0.0028725 | 0.00071992
14 | 0.97396 | -0.50174 | 0.0034869 | 0.0008739
15 | 0.97771 | -0.42847 | 0 | 0
16 | 0.97887 | -0.40576 | 0 | 0
17 | 0.97469 | -0.48787 | 0.021449 | 0.0053756
18 | 0.98101 | -0.36402 | 0.0012674 | 0.00031764
19 | 0.97871 | -0.40896 | 0.00088093 | 0.00022078
20 | 0.98146 | -0.35531 | 0 | 0
21 | 0.97869 | -0.40938 | 0.002998 | 0.00075138
22 | 0.97716 | -0.43892 | 0.0072871 | 0.0018263
23 | 0.97861 | -0.41065 | 0.0024044 | 0.00060261
24 | 0.98087 | -0.36657 | 0 | 0
25 | 0.99795 | -0.039447 | 0.0039273 | 0.00098427
26 | 0.99806 | -0.037311 | 0.0059331 | 0.001487
27 | 0.99846 | -0.029632 | 0.0059058 | 0.0014801
28 | 0.99878 | -0.023528 | 0.0044003 | 0.0011028
29 | 0.9991 | -0.017315 | 0.0065297 | 0.0016365
30 | 0.99992 | -0.0015064 | 0.0041161 | 0.0010316
31 | 0.99596 | -0.076376 | 0.0040223 | 0.0010081
32 | 0.99736 | -0.049812 | 0.005224 | 0.0013092
33 | 0.99322 | -0.12843 | 0.0088449 | 0.0022167
34 | 0.99776 | -0.042148 | 0.0019657 | 0.00049266
35 | 0.98948 | -0.2 | 0 | 0
36 | 1 | 0 | -0.51465 | -0.13187
37 | 0.98772 | -0.23387 | 0 | 0
38 | 0.98935 | -0.20256 | 0.011487 | 0.0028789
39 | 0.9863 | -0.26148 | 0.018 | 0.0045113
40 | 0.98747 | -0.23873 | 0 | 0
41 | 0.98801 | -0.22822 | 0.0055317 | 0.0013864
42 | 0.98513 | -0.28429 | 0.010498 | 0.0026309
43 | 0.98617 | -0.26399 | 0 | 0
44 | 0.9867 | -0.25362 | 0.0077509 | 0.0019426
45 | 0.98749 | -0.23841 | 0.003765 | 0.00094361
46 | 0.98095 | -0.36526 | 0.0053781 | 0.0013479
47 | 0.98159 | -0.35272 | 0 | 0
48 | 0.98066 | -0.371 | 0.012516 | 0.0031368
49 | 0.98328 | -0.31977 | 0.0086557 | 0.0021693
50 | 0.98579 | -0.27118 | 0 | 0
51 | 0.98066 | -0.37073 | 0.0090163 | 0.0022597
52 | 0.9855 | -0.27681 | 0.0041962 | 0.0010517
53 | 0.98514 | -0.28385 | 0.0029061 | 0.00072833
54 | 0.98686 | -0.25054 | 0.0016219 | 0.00040648
55 | 0.98088 | -0.36644 | 0.0096266 | 0.0024126
56 | 0.98415 | -0.30285 | 0.0042084 | 0.0010547
57 | 0.9848 | -0.29044 | 0.002654 | 0.00066517
58 | 0.98445 | -0.29723 | 0.004392 | 0.0011007
59 | 0.98429 | -0.30042 | 0.0013143 | 0.00032939
60 | 0.9863 | -0.26134 | 0.0048706 | 0.0012207
61 | 0.98485 | -0.28933 | 0.013097 | 0.0032824
62 | 0.98424 | -0.30111 | 0.0054125 | 0.0013565
63 | 0.9828 | -0.32897 | 0.0069401 | 0.0017394
64 | 0.98611 | -0.26521 | 0.0093389 | 0.0023405
65 | 0.98225 | -0.3397 | 0 | 0
66 | 0.98518 | -0.28322 | 0 | 0
67 | 0.98052 | -0.37362 | 0.011652 | 0.0029202
68 | 0.97875 | -0.40781 | 0.019406 | 0.0048635
69 | 0.97566 | -0.46838 | 0.0040894 | 0.0010249
70 | 0.97439 | -0.49316 | 0 | 0
71 | 0.97354 | -0.51007 | 0 | 0
72 | 0.97427 | -0.49553 | 0.01254 | 0.0031429
73 | 0.97277 | -0.52518 | 0.0030034 | 0.00075273
74 | 0.9742 | -0.49707 | 0 | 0
75 | 0.98008 | -0.38211 | 0.0083821 | 0.0021008
76 | 0.97257 | -0.52904 | 0 | 0
77 | 0.97983 | -0.38705 | 0.0024939 | 0.00062503
78 | 0.97191 | -0.54217 | 0.010959 | 0.0027466
79 | 0.97235 | -0.53354 | 0 | 0
80 | 0.97974 | -0.38879 | 0.00027715 | 6.9461e-05
81 | 0.98482 | -0.29046 | 0.003394 | 0.00085061
82 | 0.97231 | -0.53424 | 0.0078684 | 0.001972
83 | 0.97189 | -0.54264 | 0.0021993 | 0.0005512
84 | 0.9795 | -0.39351 | 0.0020298 | 0.00050873
85 | 0.9795 | -0.3935 | 0.0035814 | 0.00089759
86 | 0.97958 | -0.39205 | 0.0015142 | 0.00037949
87 | 0.9797 | -0.38969 | 0.001544 | 0.00038697
88 | 0.97974 | -0.38884 | 0.0042251 | 0.0010589
89 | 0.97103 | -0.55965 | 0.013372 | 0.0033513
90 | 0.97089 | -0.56228 | 0.01229 | 0.0030803
91 | 0.9842 | -0.3022 | 0.0048855 | 0.0012244
92 | 0.9837 | -0.31194 | 0 | 0
93 | 0.9849 | -0.28872 | 0 | 0
94 | 0.98249 | -0.33569 | 0 | 0
95 | 0.98172 | -0.35069 | 0.0063915 | 0.0016018
96 | 0.98157 | -0.35368 | 0 | 0
97 | 0.98109 | -0.36299 | 0 | 0
98 | 0.98093 | -0.36619 | 0.0028938 | 0.00072525
99 | 0.98106 | -0.36355 | 0.00029151 | 7.306e-05
100 | 0.98432 | -0.30006 | 0.0072115 | 0.0018074
101 | 0.98441 | -0.29835 | 0 | 0
102 | 0.9841 | -0.30445 | 0.0050631 | 0.0012689
103 | 0.98421 | -0.3022 | 0.0079581 | 0.0019945
104 | 0.98425 | -0.30123 | 0.0015329 | 0.00038418
105 | 0.98416 | -0.30295 | 0.0021479 | 0.00053832
106 | 0.98416 | -0.30296 | 0 | 0
107 | 0.98415 | -0.30312 | 0 | 0
108 | 0.98411 | -0.30392 | 0.00061941 | 0.00015524
109 | 0.98407 | -0.30467 | 0.00017866 | 4.4776e-05
110 | 0.98405 | -0.3051 | 0 | 0
111 | 0.98393 | -0.30753 | 0.00040073 | 0.00010043
112 | 0.98393 | -0.3074 | 0 | 0
113 | 0.98394 | -0.3072 | 0 | 0
114 | 0.9839 | -0.30797 | 0.0014286 | 0.00035805
115 | 0.97868 | -0.40961 | 0.0019712 | 0.00049403
116 | 0.97868 | -0.40962 | 0.00069934 | 0.00017527
117 | 0.9808 | -0.36864 | 0.011211 | 0.0028097
118 | 0.98106 | -0.36364 | 0.00045415 | 0.00011382
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.018518 | 0.004653 | -0.018495 | -0.0046388 | 2.3696e-05 | 1.419e-05 | 0.028336 | 0.028336 | 0.028336 | 0.97262 | -0.5283 | 0.97126 | -0.55514 | 7.7846
1 | -0.022151 | -0.0055635 | 0.022188 | 0.0055857 | 3.6434e-05 | 2.2266e-05 | 0.033893 | 0.033893 | 0.033893 | 0.97262 | -0.5283 | 0.97437 | -0.49389 | 9.3114
2 | 0.018495 | 0.0046388 | -0.018484 | -0.0046326 | 1.0348e-05 | 6.1978e-06 | 0.028336 | 0.028336 | 0.028336 | 0.97126 | -0.55514 | 0.97067 | -0.56688 | 7.7846
3 | -0.02461 | -0.0061927 | 0.024611 | 0.0061937 | 1.532e-06 | 9.4447e-07 | 0.037592 | 0.037592 | 0.037592 | 0.97437 | -0.49389 | 0.97443 | -0.49258 | 10.3275
4 | -0.029169 | -0.007336 | 0.029181 | 0.0073436 | 1.2082e-05 | 7.5299e-06 | 0.044552 | 0.044552 | 0.044552 | 0.97443 | -0.49258 | 0.97487 | -0.48392 | 12.2396
5 | -0.031636 | -0.0079587 | 0.031643 | 0.0079634 | 7.6069e-06 | 4.76e-06 | 0.048298 | 0.048298 | 0.048298 | 0.97487 | -0.48392 | 0.97513 | -0.47888 | 13.2688
6 | -0.037158 | -0.0093456 | 0.037175 | 0.0093559 | 1.6315e-05 | 1.0273e-05 | 0.056714 | 0.056714 | 0.056714 | 0.97513 | -0.47888 | 0.9756 | -0.4697 | 15.5808
7 | -0.041298 | -0.010389 | 0.041335 | 0.010413 | 3.7384e-05 | 2.3612e-05 | 0.063003 | 0.063003 | 0.063003 | 0.9756 | -0.4697 | 0.97656 | -0.45077 | 17.3085
8 | -0.0029946 | -0.00075051 | 0.0029948 | 0.00075031 | 1.8269e-07 | -2.0193e-07 | 0.0044666 | 0.0044665 | 0.0044666 | 0.99761 | -0.045926 | 0.99768 | -0.044645 | 1.2271
9 | -0.005964 | -0.0014945 | 0.0059647 | 0.0014946 | 7.4073e-07 | 1.4801e-07 | 0.008895 | 0.0088949 | 0.008895 | 0.99768 | -0.044645 | 0.99781 | -0.042038 | 2.4437
10 | -0.0039894 | -0.00099983 | 0.0039896 | 0.00099977 | 2.2541e-07 | -5.7026e-08 | 0.0060957 | 0.0060956 | 0.0060957 | 0.97385 | -0.50399 | 0.97391 | -0.50281 | 1.6746
11 | -0.00669 | -0.0016766 | 0.0066904 | 0.0016767 | 3.3814e-07 | 1.0901e-07 | 0.010222 | 0.010222 | 0.010222 | 0.97391 | -0.50281 | 0.97396 | -0.50174 | 2.8081
12 | -0.055033 | -0.013846 | 0.055064 | 0.013866 | 3.1166e-05 | 1.9798e-05 | 0.083875 | 0.083875 | 0.083875 | 0.97656 | -0.45077 | 0.97716 | -0.43892 | 23.0425
13 | -0.0088372 | -0.0022145 | 0.0088383 | 0.002215 | 1.0908e-06 | 4.7933e-07 | 0.013179 | 0.013179 | 0.013179 | 0.99781 | -0.042038 | 0.99795 | -0.039447 | 3.6205
14 | -0.010177 | -0.0025506 | 0.01018 | 0.0025517 | 2.2666e-06 | 1.1394e-06 | 0.015549 | 0.015549 | 0.015549 | 0.97396 | -0.50174 | 0.9742 | -0.49707 | 4.2717
15 | -0.02151 | -0.0054126 | 0.021533 | 0.0054268 | 2.3365e-05 | 1.4224e-05 | 0.032744 | 0.032744 | 0.032744 | 0.97771 | -0.42847 | 0.97887 | -0.40576 | 8.9956
16 | 0.02151 | 0.0054126 | -0.021449 | -0.0053756 | 6.0875e-05 | 3.7067e-05 | 0.032744 | 0.032745 | 0.032745 | 0.97771 | -0.42847 | 0.97469 | -0.48787 | 8.9958
17 | -0.028084 | -0.0070686 | 0.02814 | 0.0071035 | 5.6153e-05 | 3.4904e-05 | 0.042702 | 0.042701 | 0.042702 | 0.97887 | -0.40576 | 0.98101 | -0.36402 | 11.7312
18 | 0.0065507 | 0.0016417 | -0.0065497 | -0.0016414 | 9.9657e-07 | 3.0096e-07 | 0.0099579 | 0.009958 | 0.009958 | 0.97887 | -0.40576 | 0.97871 | -0.40896 | 2.7357
19 | -0.029407 | -0.0074211 | 0.029419 | 0.0074288 | 1.2267e-05 | 7.6433e-06 | 0.044624 | 0.044624 | 0.044624 | 0.98101 | -0.36402 | 0.98146 | -0.35531 | 12.2592
20 | 0.0056687 | 0.0014207 | -0.0056686 | -0.0014206 | 1.1441e-07 | 2.1609e-08 | 0.0086186 | 0.0086187 | 0.0086187 | 0.97871 | -0.40896 | 0.97869 | -0.40938 | 2.3678
21 | -0.029419 | -0.0074288 | 0.029423 | 0.007431 | 3.653e-06 | 2.2761e-06 | 0.044624 | 0.044624 | 0.044624 | 0.98146 | -0.35531 | 0.98159 | -0.35272 | 12.2592
22 | 0.0026706 | 0.00066926 | -0.0026706 | -0.0006693 | 2.9341e-08 | -4.0857e-08 | 0.0040604 | 0.0040604 | 0.0040604 | 0.97869 | -0.40938 | 0.97868 | -0.40961 | 1.1155
23 | -0.062351 | -0.015692 | 0.062436 | 0.015746 | 8.4366e-05 | 5.3681e-05 | 0.094971 | 0.094971 | 0.094971 | 0.97716 | -0.43892 | 0.97861 | -0.41065 | 26.091
24 | -0.06484 | -0.016348 | 0.064977 | 0.016436 | 0.00013711 | 8.7278e-05 | 0.098627 | 0.098627 | 0.098627 | 0.97861 | -0.41065 | 0.98087 | -0.36657 | 27.0954
25 | -0.073995 | -0.018696 | 0.073996 | 0.018696 | 4.7236e-07 | 3.0105e-07 | 0.11231 | 0.11231 | 0.11231 | 0.98087 | -0.36657 | 0.98088 | -0.36644 | 30.8538
26 | 0.009018 | 0.0022605 | -0.0090163 | -0.0022597 | 1.7862e-06 | 8.2201e-07 | 0.013681 | 0.013681 | 0.013681 | 0.98087 | -0.36657 | 0.98066 | -0.37073 | 3.7585
27 | -0.012766 | -0.0031993 | 0.012767 | 0.0032 | 1.2991e-06 | 7.0646e-07 | 0.019034 | 0.019034 | 0.019034 | 0.99795 | -0.039447 | 0.99806 | -0.037311 | 5.2292
28 | -0.0187 | -0.004687 | 0.018707 | 0.004691 | 6.8437e-06 | 4.073e-06 | 0.02788 | 0.02788 | 0.02788 | 0.99806 | -0.037311 | 0.99846 | -0.029632 | 7.6594
29 | -0.024613 | -0.0061712 | 0.02462 | 0.0061756 | 7.162e-06 | 4.398e-06 | 0.036681 | 0.036681 | 0.036681 | 0.99846 | -0.029632 | 0.99878 | -0.023528 | 10.0773
30 | -0.02902 | -0.0072784 | 0.029029 | 0.0072837 | 8.5969e-06 | 5.3415e-06 | 0.043237 | 0.043237 | 0.043237 | 0.99878 | -0.023528 | 0.9991 | -0.017315 | 11.8783
31 | -0.035558 | -0.0089202 | 0.035585 | 0.008937 | 2.682e-05 | 1.6831e-05 | 0.052962 | 0.052962 | 0.052962 | 0.9991 | -0.017315 | 0.99992 | -0.0015064 | 14.55
32 | -0.039701 | -0.0099686 | 0.039704 | 0.0099704 | 2.8535e-06 | 1.7976e-06 | 0.059087 | 0.059087 | 0.059087 | 0.99992 | -0.0015064 | 1 | 0 | 16.2328
33 | -0.46436 | -0.11899 | 0.46496 | 0.11937 | 0.00059869 | 0.00038247 | 0.69472 | 0.69471 | 0.69472 | 0.99596 | -0.076376 | 0.99736 | -0.049812 | 47.714
34 | 0.46034 | 0.11798 | -0.45918 | -0.11724 | 0.0011584 | 0.00074002 | 0.68871 | 0.68871 | 0.68871 | 0.99596 | -0.076376 | 0.99322 | -0.12843 | 47.3013
35 | -0.47019 | -0.12068 | 0.47036 | 0.12079 | 0.00017493 | 0.00011176 | 0.70251 | 0.70251 | 0.70251 | 0.99736 | -0.049812 | 0.99776 | -0.042148 | 48.2492
36 | 0.45034 | 0.11502 | -0.44879 | -0.11403 | 0.0015521 | 0.00099149 | 0.67546 | 0.67546 | 0.67546 | 0.99322 | -0.12843 | 0.98948 | -0.2 | 46.3912
37 | -0.47233 | -0.12128 | 0.4733 | 0.1219 | 0.00096861 | 0.00061883 | 0.70544 | 0.70544 | 0.70544 | 0.99776 | -0.042148 | 1 | 0 | 48.4506
38 | 0.25959 | 0.065941 | -0.25916 | -0.065672 | 0.00042252 | 0.0002689 | 0.39069 | 0.39069 | 0.39069 | 0.98948 | -0.2 | 0.98772 | -0.23387 | 26.833
39 | 0.1892 | 0.048089 | -0.18918 | -0.048075 | 2.3351e-05 | 1.4787e-05 | 0.28477 | 0.28477 | 0.28477 | 0.98948 | -0.2 | 0.98935 | -0.20256 | 19.5582
40 | 0.052249 | 0.013141 | -0.05218 | -0.013097 | 6.8809e-05 | 4.3659e-05 | 0.07873 | 0.07873 | 0.07873 | 0.98772 | -0.23387 | 0.9863 | -0.26148 | 21.629
41 | 0.20691 | 0.052531 | -0.20687 | -0.052501 | 4.841e-05 | 3.0711e-05 | 0.31196 | 0.31196 | 0.31196 | 0.98772 | -0.23387 | 0.98747 | -0.23873 | 21.4258
42 | 0.17769 | 0.045196 | -0.17747 | -0.045057 | 0.0002194 | 0.00013874 | 0.26749 | 0.26749 | 0.26749 | 0.98935 | -0.20256 | 0.98801 | -0.22822 | 18.3717
43 | 0.034179 | 0.0085861 | -0.034142 | -0.0085627 | 3.7165e-05 | 2.3311e-05 | 0.051573 | 0.051573 | 0.051573 | 0.9863 | -0.26148 | 0.98513 | -0.28429 | 14.1684
44 | 0.035619 | 0.0089818 | -0.035576 | -0.0089548 | 4.3004e-05 | 2.7014e-05 | 0.053694 | 0.053694 | 0.053694 | 0.98747 | -0.23873 | 0.98617 | -0.26399 | 14.7511
45 | 0.17125 | 0.043519 | -0.17112 | -0.043441 | 0.00012264 | 7.7487e-05 | 0.25827 | 0.25827 | 0.25827 | 0.98747 | -0.23873 | 0.9867 | -0.25362 | 17.7381
46 | 0.17194 | 0.043671 | -0.17186 | -0.043617 | 8.4278e-05 | 5.3253e-05 | 0.25916 | 0.25916 | 0.25916 | 0.98801 | -0.22822 | 0.98749 | -0.23841 | 17.7995
47 | 0.023645 | 0.0059318 | -0.023638 | -0.0059276 | 6.9513e-06 | 4.2639e-06 | 0.035717 | 0.035717 | 0.035717 | 0.98513 | -0.28429 | 0.98482 | -0.29046 | 9.8123
48 | 0.035576 | 0.0089548 | -0.035574 | -0.0089535 | 2.0692e-06 | 1.2999e-06 | 0.053694 | 0.053694 | 0.053694 | 0.98617 | -0.26399 | 0.98611 | -0.26521 | 14.7511
49 | 0.16337 | 0.041499 | -0.16331 | -0.04146 | 6.0691e-05 | 3.8298e-05 | 0.24658 | 0.24658 | 0.24658 | 0.9867 | -0.25362 | 0.9863 | -0.26134 | 16.9353
50 | 0.16809 | 0.042674 | -0.16799 | -0.042612 | 9.8068e-05 | 6.1931e-05 | 0.25349 | 0.25349 | 0.25349 | 0.98749 | -0.23841 | 0.98686 | -0.25054 | 17.4099
51 | -0.017897 | -0.0044865 | 0.017908 | 0.0044929 | 1.0701e-05 | 6.3598e-06 | 0.027149 | 0.027149 | 0.027149 | 0.98095 | -0.36526 | 0.98159 | -0.35272 | 7.4586
52 | 0.012519 | 0.0031387 | -0.012516 | -0.0031368 | 3.4229e-06 | 1.8712e-06 | 0.018991 | 0.018991 | 0.018991 | 0.98095 | -0.36526 | 0.98066 | -0.371 | 5.2174
53 | -0.047331 | -0.011924 | 0.047406 | 0.011971 | 7.4712e-05 | 4.7326e-05 | 0.071773 | 0.071772 | 0.071773 | 0.98159 | -0.35272 | 0.98328 | -0.31977 | 19.7178
54 | -0.056062 | -0.014141 | 0.056192 | 0.014224 | 0.00013076 | 8.307e-05 | 0.084871 | 0.084871 | 0.084871 | 0.98328 | -0.31977 | 0.98579 | -0.27118 | 23.3163
55 | 0.092418 | 0.023464 | -0.092393 | -0.023448 | 2.5034e-05 | 1.5323e-05 | 0.13961 | 0.13961 | 0.13961 | 0.98579 | -0.27118 | 0.9855 | -0.27681 | 9.5886
56 | 0.017596 | 0.004414 | -0.017585 | -0.0044077 | 1.0624e-05 | 6.2879e-06 | 0.026562 | 0.026562 | 0.026562 | 0.98579 | -0.27118 | 0.98514 | -0.28385 | 7.2973
57 | -0.16621 | -0.042101 | 0.16637 | 0.042205 | 0.0001649 | 0.00010411 | 0.25104 | 0.25104 | 0.25104 | 0.98579 | -0.27118 | 0.98686 | -0.25054 | 17.242
58 | 0.088197 | 0.022397 | -0.088086 | -0.022327 | 0.00011038 | 6.98e-05 | 0.13327 | 0.13327 | 0.13327 | 0.9855 | -0.27681 | 0.98415 | -0.30285 | 18.3069
59 | 0.014679 | 0.0036794 | -0.014675 | -0.0036767 | 4.6059e-06 | 2.6298e-06 | 0.022173 | 0.022173 | 0.022173 | 0.98514 | -0.28385 | 0.9848 | -0.29044 | 6.0914
60 | -0.083622 | -0.021109 | 0.083878 | 0.021272 | 0.00025556 | 0.00016302 | 0.12691 | 0.12691 | 0.12691 | 0.98088 | -0.36644 | 0.98415 | -0.30285 | 34.8659
61 | 0.012021 | 0.0030116 | -0.012017 | -0.0030095 | 3.8897e-06 | 2.0895e-06 | 0.018163 | 0.018163 | 0.018163 | 0.9848 | -0.29044 | 0.98445 | -0.29723 | 4.9898
62 | 0.0076248 | 0.0019087 | -0.0076236 | -0.0019083 | 1.1572e-06 | 4.4522e-07 | 0.011524 | 0.011524 | 0.011524 | 0.98445 | -0.29723 | 0.98429 | -0.30042 | 3.166
63 | 0.0063094 | 0.0015789 | -0.0063091 | -0.0015788 | 2.4173e-07 | 6.4639e-08 | 0.0095374 | 0.0095375 | 0.0095375 | 0.98429 | -0.30042 | 0.98425 | -0.30123 | 2.6202
64 | 0.15844 | 0.04024 | -0.15823 | -0.040105 | 0.00021311 | 0.00013437 | 0.23923 | 0.23923 | 0.23923 | 0.9863 | -0.26134 | 0.98485 | -0.28933 | 16.4306
65 | 0.14513 | 0.036823 | -0.14505 | -0.036771 | 8.2192e-05 | 5.1677e-05 | 0.21944 | 0.21944 | 0.21944 | 0.98485 | -0.28933 | 0.98424 | -0.30111 | 15.0716
66 | 0.13964 | 0.035415 | -0.13945 | -0.035296 | 0.00018679 | 0.00011827 | 0.21126 | 0.21126 | 0.21126 | 0.98424 | -0.30111 | 0.9828 | -0.32897 | 19.3461
67 | 0.13251 | 0.033557 | -0.13244 | -0.033514 | 6.8188e-05 | 4.3126e-05 | 0.20075 | 0.20075 | 0.20075 | 0.9828 | -0.32897 | 0.98225 | -0.3397 | 18.3839
68 | 0.026235 | 0.0066129 | -0.026212 | -0.006599 | 2.2591e-05 | 1.3969e-05 | 0.039602 | 0.039602 | 0.039602 | 0.98611 | -0.26521 | 0.98518 | -0.28322 | 10.8796
69 | 0.035773 | 0.0089927 | -0.035715 | -0.0089563 | 5.7841e-05 | 3.6355e-05 | 0.054203 | 0.054203 | 0.054203 | 0.98225 | -0.3397 | 0.98052 | -0.37362 | 14.8909
70 | 0.096669 | 0.024521 | -0.096353 | -0.02432 | 0.00031549 | 0.00020142 | 0.14655 | 0.14655 | 0.14655 | 0.98225 | -0.3397 | 0.97875 | -0.40781 | 40.2609
71 | 0.026212 | 0.006599 | -0.026206 | -0.0065947 | 6.8833e-06 | 4.2563e-06 | 0.039602 | 0.039602 | 0.039602 | 0.98518 | -0.28322 | 0.9849 | -0.28872 | 10.8796
72 | 0.024064 | 0.0060362 | -0.024054 | -0.0060302 | 9.7385e-06 | 5.9871e-06 | 0.036521 | 0.036521 | 0.036521 | 0.98052 | -0.37362 | 0.98008 | -0.38211 | 10.0332
73 | 0.076948 | 0.019456 | -0.076725 | -0.019314 | 0.00022283 | 0.00014207 | 0.11705 | 0.11705 | 0.11705 | 0.97875 | -0.40781 | 0.97566 | -0.46838 | 32.1558
74 | 0.072635 | 0.018289 | -0.072549 | -0.018235 | 8.5958e-05 | 5.478e-05 | 0.11081 | 0.11081 | 0.11081 | 0.97566 | -0.46838 | 0.97439 | -0.49316 | 30.4424
75 | 0.049826 | 0.012538 | -0.049786 | -0.012513 | 4.0229e-05 | 2.5516e-05 | 0.076109 | 0.076109 | 0.076109 | 0.97439 | -0.49316 | 0.97354 | -0.51007 | 20.909
76 | 0.022723 | 0.0056966 | -0.022721 | -0.005695 | 2.5599e-06 | 1.5677e-06 | 0.034702 | 0.034702 | 0.034702 | 0.97439 | -0.49316 | 0.97427 | -0.49553 | 9.5334
77 | 0.049786 | 0.012513 | -0.04975 | -0.01249 | 3.5868e-05 | 2.2751e-05 | 0.076109 | 0.076109 | 0.076109 | 0.97354 | -0.51007 | 0.97277 | -0.52518 | 20.909
78 | 0.01018 | 0.0025521 | -0.01018 | -0.0025517 | 7.4784e-07 | 3.759e-07 | 0.015549 | 0.015549 | 0.015549 | 0.97427 | -0.49553 | 0.9742 | -0.49707 | 4.2716
79 | 0.046747 | 0.011737 | -0.046738 | -0.011732 | 8.601e-06 | 5.449e-06 | 0.071515 | 0.071515 | 0.071515 | 0.97277 | -0.52518 | 0.97257 | -0.52904 | 19.6469
80 | 0.015672 | 0.0039294 | -0.015668 | -0.0039273 | 3.6862e-06 | 2.1405e-06 | 0.023795 | 0.023795 | 0.023795 | 0.98008 | -0.38211 | 0.97983 | -0.38705 | 6.537
81 | 0.038868 | 0.0097588 | -0.038843 | -0.0097434 | 2.4332e-05 | 1.5345e-05 | 0.059473 | 0.059473 | 0.059473 | 0.97257 | -0.52904 | 0.97191 | -0.54217 | 16.3388
82 | 0.0078703 | 0.0019728 | -0.0078686 | -0.0019721 | 1.6883e-06 | 6.9528e-07 | 0.012042 | 0.012042 | 0.012042 | 0.97257 | -0.52904 | 0.97235 | -0.53354 | 3.3082
83 | 0.013174 | 0.0033023 | -0.013173 | -0.0033017 | 1.095e-06 | 6.0891e-07 | 0.020007 | 0.020007 | 0.020007 | 0.97983 | -0.38705 | 0.97974 | -0.38879 | 5.4965
84 | 0.027884 | 0.0069968 | -0.027884 | -0.0069964 | 6.306e-07 | 3.9215e-07 | 0.042695 | 0.042695 | 0.042695 | 0.97191 | -0.54217 | 0.97189 | -0.54264 | 11.7293
85 | 0.0078686 | 0.0019721 | -0.0078684 | -0.001972 | 2.6127e-07 | 1.0762e-07 | 0.012042 | 0.012042 | 0.012042 | 0.97235 | -0.53354 | 0.97231 | -0.53424 | 3.3082
86 | 0.012896 | 0.0032322 | -0.012896 | -0.0032322 | 3.2835e-08 | 1.814e-08 | 0.019586 | 0.019586 | 0.019586 | 0.97974 | -0.38879 | 0.97974 | -0.38884 | 5.3809
87 | 0.020244 | 0.0050769 | -0.020236 | -0.0050724 | 7.6105e-06 | 4.5949e-06 | 0.030589 | 0.030589 | 0.030589 | 0.98482 | -0.29046 | 0.98441 | -0.29835 | 8.4035
88 | 0.025684 | 0.0064452 | -0.025664 | -0.0064324 | 2.0809e-05 | 1.2873e-05 | 0.039327 | 0.039328 | 0.039328 | 0.97189 | -0.54264 | 0.97103 | -0.55965 | 10.8043
89 | -0.0020298 | -0.00050873 | 0.0020298 | 0.00050872 | 9.8895e-10 | -2.8576e-09 | 0.0030837 | 0.0030837 | 0.0030837 | 0.9795 | -0.39351 | 0.9795 | -0.3935 | 0.84716
90 | -0.0056113 | -0.0014063 | 0.0056117 | 0.0014064 | 3.887e-07 | 6.9206e-08 | 0.0085244 | 0.0085243 | 0.0085244 | 0.9795 | -0.3935 | 0.97958 | -0.39205 | 2.3419
91 | -0.0071258 | -0.0017859 | 0.0071266 | 0.0017862 | 8.008e-07 | 2.8304e-07 | 0.010824 | 0.010824 | 0.010824 | 0.97958 | -0.39205 | 0.9797 | -0.38969 | 2.9737
92 | -0.0086707 | -0.0021731 | 0.008671 | 0.0021733 | 3.4904e-07 | 1.558e-07 | 0.013169 | 0.013169 | 0.013169 | 0.9797 | -0.38969 | 0.97974 | -0.38884 | 3.618
93 | 0.012292 | 0.0030811 | -0.01229 | -0.0030803 | 1.5428e-06 | 8.4397e-07 | 0.018837 | 0.018837 | 0.018837 | 0.97103 | -0.55965 | 0.97089 | -0.56228 | 5.1749
94 | 0.021303 | 0.0053599 | -0.021293 | -0.0053538 | 9.9113e-06 | 6.0198e-06 | 0.032216 | 0.032216 | 0.032216 | 0.9842 | -0.3022 | 0.9837 | -0.31194 | 8.8505
95 | -0.026189 | -0.0065843 | 0.026206 | 0.0065947 | 1.6871e-05 | 1.0433e-05 | 0.039602 | 0.039602 | 0.039602 | 0.9842 | -0.3022 | 0.9849 | -0.28872 | 10.8797
96 | 0.021293 | 0.0053538 | -0.021269 | -0.0053392 | 2.4122e-05 | 1.4652e-05 | 0.032216 | 0.032216 | 0.032216 | 0.9837 | -0.31194 | 0.98249 | -0.33569 | 8.8506
97 | 0.021269 | 0.0053392 | -0.021254 | -0.0053299 | 1.5204e-05 | 9.2363e-06 | 0.032216 | 0.032216 | 0.032216 | 0.98249 | -0.33569 | 0.98172 | -0.35069 | 8.8506
98 | 0.014863 | 0.0037281 | -0.01486 | -0.0037269 | 2.1208e-06 | 1.2165e-06 | 0.022529 | 0.022529 | 0.022529 | 0.98172 | -0.35069 | 0.98157 | -0.35368 | 6.1892
99 | 0.01486 | 0.0037269 | -0.014854 | -0.0037231 | 6.5879e-06 | 3.779e-06 | 0.022529 | 0.022529 | 0.022529 | 0.98157 | -0.35368 | 0.98109 | -0.36299 | 6.1892
100 | 0.014108 | 0.0035369 | -0.014106 | -0.0035356 | 2.1519e-06 | 1.219e-06 | 0.021398 | 0.021398 | 0.021398 | 0.98109 | -0.36299 | 0.98093 | -0.36619 | 5.8786
101 | 0.00074569 | 0.00018624 | -0.00074567 | -0.00018675 | 2.0091e-08 | -5.1618e-07 | 0.0011307 | 0.0011309 | 0.0011309 | 0.98109 | -0.36299 | 0.98106 | -0.36355 | 0.3107
102 | 0.011212 | 0.0028104 | -0.011211 | -0.0028097 | 1.3083e-06 | 6.8507e-07 | 0.017008 | 0.017008 | 0.017008 | 0.98093 | -0.36619 | 0.9808 | -0.36864 | 4.6726
103 | 0.00045415 | 0.00011369 | -0.00045415 | -0.00011382 | 1.8319e-09 | -1.2883e-07 | 0.00068879 | 0.00068883 | 0.00068883 | 0.98106 | -0.36355 | 0.98106 | -0.36364 | 0.18924
104 | -0.0072115 | -0.0018074 | 0.0072121 | 0.0018076 | 5.8679e-07 | 2.0817e-07 | 0.010902 | 0.010902 | 0.010902 | 0.98432 | -0.30006 | 0.98441 | -0.29835 | 2.995
105 | 0.013024 | 0.0032648 | -0.013022 | -0.0032634 | 2.3887e-06 | 1.3198e-06 | 0.019687 | 0.019687 | 0.019687 | 0.98441 | -0.29835 | 0.98421 | -0.3022 | 5.4086
106 | -0.0050631 | -0.0012689 | 0.0050636 | 0.001269 | 5.4235e-07 | 3.354e-08 | 0.0076557 | 0.0076556 | 0.0076557 | 0.9841 | -0.30445 | 0.98421 | -0.3022 | 2.1032
107 | 0.0047762 | 0.0011947 | -0.0047758 | -0.0011947 | 3.9227e-07 | -3.9566e-09 | 0.00722 | 0.0072201 | 0.0072201 | 0.98425 | -0.30123 | 0.98416 | -0.30295 | 1.9835
108 | 0.0026279 | 0.00065634 | -0.0026279 | -0.00065634 | 4.0172e-10 | -6.0273e-10 | 0.0039725 | 0.0039725 | 0.0039725 | 0.98416 | -0.30295 | 0.98416 | -0.30296 | 1.0913
109 | 0.0026279 | 0.00065634 | -0.0026279 | -0.00065637 | 2.0079e-08 | -3.0264e-08 | 0.0039725 | 0.0039725 | 0.0039725 | 0.98416 | -0.30296 | 0.98415 | -0.30312 | 1.0914
110 | 0.0026279 | 0.00065637 | -0.0026278 | -0.00065653 | 1.0058e-07 | -1.5158e-07 | 0.0039725 | 0.0039726 | 0.0039726 | 0.98415 | -0.30312 | 0.98411 | -0.30392 | 1.0914
111 | 0.0020084 | 0.00050129 | -0.0020083 | -0.0005015 | 7.108e-08 | -2.1577e-07 | 0.003036 | 0.0030361 | 0.0030361 | 0.98411 | -0.30392 | 0.98407 | -0.30467 | 0.8341
112 | 0.0018297 | 0.00045673 | -0.0018296 | -0.00045687 | 3.7904e-08 | -1.4359e-07 | 0.002766 | 0.002766 | 0.002766 | 0.98407 | -0.30467 | 0.98405 | -0.3051 | 0.7599
113 | 0.0018296 | 0.00045687 | -0.0018294 | -0.00045756 | 1.8198e-07 | -6.8917e-07 | 0.002766 | 0.0027663 | 0.0027663 | 0.98405 | -0.3051 | 0.98394 | -0.3072 | 0.75998
114 | -0.00040073 | -0.00010043 | 0.00040073 | 0.00010021 | 2.422e-09 | -2.2184e-07 | 0.00060603 | 0.00060595 | 0.00060603 | 0.98393 | -0.30753 | 0.98393 | -0.3074 | 0.16649
115 | -0.00040073 | -0.00010021 | 0.00040073 | 9.9853e-05 | 3.8893e-09 | -3.5636e-07 | 0.00060595 | 0.00060582 | 0.00060595 | 0.98393 | -0.3074 | 0.98394 | -0.3072 | 0.16647
116 | 0.0014287 | 0.00035771 | -0.0014286 | -0.00035805 | 5.2345e-08 | -3.4629e-07 | 0.0021605 | 0.0021606 | 0.0021606 | 0.98394 | -0.3072 | 0.9839 | -0.30797 | 0.59358
117 | 0.00069934 | 0.00017526 | -0.00069934 | -0.00017527 | 2.9887e-10 | -8.6629e-09 | 0.0010633 | 0.0010633 | 0.0010633 | 0.97868 | -0.40961 | 0.97868 | -0.40962 | 0.29212

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51727 | 0.13253

## res_load
| p_mw | q_mvar
0 | 0.0036329 | 0.00091049
1 | 0.002422 | 0.00060702
2 | 0.018484 | 0.0046326
3 | 0.004558 | 0.0011423
4 | 0.0024544 | 0.00061513
5 | 0.005515 | 0.0013822
6 | 0.0041231 | 0.0010334
7 | 0.0029946 | 0.00075051
8 | 0.0029692 | 0.00074415
9 | 0.0039894 | 0.00099983
10 | 0.0027004 | 0.00067679
11 | 0.013698 | 0.003433
12 | 0.0028725 | 0.00071992
13 | 0.0034869 | 0.0008739
14 | 0.021449 | 0.0053756
15 | 0.0012674 | 0.00031764
16 | 0.00088093 | 0.00022078
17 | 0.002998 | 0.00075138
18 | 0.0072871 | 0.0018263
19 | 0.0024044 | 0.00060261
20 | 0.0039273 | 0.00098427
21 | 0.0059331 | 0.001487
22 | 0.0059058 | 0.0014801
23 | 0.0044003 | 0.0011028
24 | 0.0065297 | 0.0016365
25 | 0.0041161 | 0.0010316
26 | 0.0040223 | 0.0010081
27 | 0.005224 | 0.0013092
28 | 0.0088449 | 0.0022167
29 | 0.0019657 | 0.00049266
30 | 0.0026163 | 0.00065571
31 | 0.011487 | 0.0028789
32 | 0.018 | 0.0045113
33 | 0.0055317 | 0.0013864
34 | 0.010498 | 0.0026309
35 | 0.0077509 | 0.0019426
36 | 0.003765 | 0.00094361
37 | 0.0053781 | 0.0013479
38 | 0.012516 | 0.0031368
39 | 0.0086557 | 0.0021693
40 | 0.0090163 | 0.0022597
41 | 0.0041962 | 0.0010517
42 | 0.0029061 | 0.00072833
43 | 0.0016219 | 0.00040648
44 | 0.0096266 | 0.0024126
45 | 0.0042084 | 0.0010547
46 | 0.002654 | 0.00066517
47 | 0.004392 | 0.0011007
48 | 0.0013143 | 0.00032939
49 | 0.0048706 | 0.0012207
50 | 0.013097 | 0.0032824
51 | 0.0054125 | 0.0013565
52 | 0.0069401 | 0.0017394
53 | 0.0093389 | 0.0023405
54 | 0.011652 | 0.0029202
55 | 0.019406 | 0.0048635
56 | 0.0040894 | 0.0010249
57 | 0.01254 | 0.0031429
58 | 0.0030034 | 0.00075273
59 | 0.0083821 | 0.0021008
60 | 0.0024939 | 0.00062503
61 | 0.010959 | 0.0027466
62 | 0.00027715 | 6.9461e-05
63 | 0.003394 | 0.00085061
64 | 0.0078684 | 0.001972
65 | 0.0021993 | 0.0005512
66 | 0.0020298 | 0.00050873
67 | 0.0035814 | 0.00089759
68 | 0.0015142 | 0.00037949
69 | 0.001544 | 0.00038697
70 | 0.0042251 | 0.0010589
71 | 0.013372 | 0.0033513
72 | 0.01229 | 0.0030803
73 | 0.0048855 | 0.0012244
74 | 0.0063915 | 0.0016018
75 | 0.0028938 | 0.00072525
76 | 0.00029151 | 7.306e-05
77 | 0.0072115 | 0.0018074
78 | 0.0050631 | 0.0012689
79 | 0.0079581 | 0.0019945
80 | 0.0015329 | 0.00038418
81 | 0.0021479 | 0.00053832
82 | 0.00061941 | 0.00015524
83 | 0.00017866 | 4.4776e-05
84 | 0.00040073 | 0.00010043
85 | 0.0014286 | 0.00035805
86 | 0.0019712 | 0.00049403
87 | 0.00069934 | 0.00017527
88 | 0.011211 | 0.0028097
89 | 0.00045415 | 0.00011382

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1