## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_135-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_135-3_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_135-3_0_3_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_135-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_135-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_135-3_0_3_node_133 | 0.4 | n |  | TRUE
6 | bus_LV_135-3_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_135-3_0_3_node_134 | 0.4 | n |  | TRUE
8 | bus_LV_135-3_0_3_node_135 | 0.4 | n |  | TRUE
9 | bus_LV_135-3_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_135-3_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_135-3_0_3_node_80 | 0.4 | n |  | TRUE
12 | bus_LV_135-3_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_135-3_0_3_node_145 | 0.4 | n |  | TRUE
14 | bus_LV_135-3_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_135-3_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_135-3_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_135-3_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_135-3_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_135-3_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_135-3_0_3_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_135-3_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_135-3_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_135-3_0_3_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_135-3_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_135-3_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_135-3_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_135-3_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_135-3_0_3_node_84 | 0.4 | n |  | TRUE
29 | bus_LV_135-3_0_3_node_70 | 0.4 | n |  | TRUE
30 | bus_LV_135-3_0_3_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_135-3_0_3_node_68 | 0.4 | n |  | TRUE
32 | bus_LV_135-3_0_3_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_135-3_0_3_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_135-3_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_135-3_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_135-3_0_3_node_141 | 0.4 | n |  | TRUE
37 | bus_LV_135-3_0_3_node_126 | 0.4 | n |  | TRUE
38 | bus_LV_135-3_0_3_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_135-3_0_3_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_135-3_0_3_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_135-3_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_135-3_0_3_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_135-3_0_3_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_135-3_0_3_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_135-3_0_3_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_135-3_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_135-3_0_3_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_135-3_0_3_node_140 | 0.4 | n |  | TRUE
49 | bus_LV_135-3_0_3_node_132 | 0.4 | n |  | TRUE
50 | bus_LV_135-3_0_3_node_104 | 0.4 | n |  | TRUE
51 | bus_LV_135-3_0_3_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_135-3_0_3_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_135-3_0_3_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_135-3_0_3_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_135-3_0_3_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_135-3_0_3_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_135-3_0_3_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_135-3_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_135-3_0_3_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_135-3_0_3_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_135-3_0_3_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_135-3_0_3_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_135-3_0_3_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_135-3_0_3_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_135-3_0_3_node_146 | 0.4 | n |  | TRUE
66 | bus_LV_135-3_0_3_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_135-3_0_3_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_135-3_0_3_node_147 | 0.4 | n |  | TRUE
69 | bus_LV_135-3_0_3_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_135-3_0_3_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_135-3_0_3_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_135-3_0_3_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_135-3_0_3_node_95 | 0.4 | n |  | TRUE
74 | bus_LV_135-3_0_3_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_135-3_0_3_node_128 | 0.4 | n |  | TRUE
76 | bus_LV_135-3_0_3_node_129 | 0.4 | n |  | TRUE
77 | bus_LV_135-3_0_3_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_135-3_0_3_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_135-3_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_135-3_0_3_node_98 | 0.4 | n |  | TRUE
81 | bus_LV_135-3_0_3_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_135-3_0_3_node_96 | 0.4 | n |  | TRUE
83 | bus_LV_135-3_0_3_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_135-3_0_3_node_148 | 0.4 | n |  | TRUE
85 | bus_LV_135-3_0_3_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_135-3_0_3_node_97 | 0.4 | n |  | TRUE
87 | bus_LV_135-3_0_3_node_100 | 0.4 | n |  | TRUE
88 | bus_LV_135-3_0_3_node_94 | 0.4 | n |  | TRUE
89 | bus_LV_135-3_0_3_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_135-3_0_3_node_60 | 0.4 | n |  | TRUE
91 | bus_LV_135-3_0_3_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_135-3_0_3_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_135-3_0_3_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_135-3_0_3_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_135-3_0_3_node_69 | 0.4 | n |  | TRUE
96 | bus_LV_135-3_0_3_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_135-3_0_3_node_73 | 0.4 | n |  | TRUE
98 | bus_LV_135-3_0_3_node_115 | 0.4 | n |  | TRUE
99 | bus_LV_135-3_0_3_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_135-3_0_3_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_135-3_0_3_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_135-3_0_3_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_135-3_0_3_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_135-3_0_3_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_135-3_0_3_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_135-3_0_3_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_135-3_0_3_node_83 | 0.4 | n |  | TRUE
108 | bus_LV_135-3_0_3_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_135-3_0_3_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_135-3_0_3_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_135-3_0_3_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_135-3_0_3_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_135-3_0_3_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_135-3_0_3_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_135-3_0_3_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_135-3_0_3_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_135-3_0_3_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_135-3_0_3_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_135-3_0_3_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_135-3_0_3_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_135-3_0_3_node_149 | 0.4 | n |  | TRUE
122 | bus_LV_135-3_0_3_node_150 | 0.4 | n |  | TRUE
123 | bus_LV_135-3_0_3_node_101 | 0.4 | n |  | TRUE
124 | bus_LV_135-3_0_3_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_135-3_0_3_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_135-3_0_3_node_103 | 0.4 | n |  | TRUE
127 | bus_LV_135-3_0_3_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_135-3_0_3_node_151 | 0.4 | n |  | TRUE
129 | bus_LV_135-3_0_3_node_152 | 0.4 | n |  | TRUE
130 | bus_LV_135-3_0_3_node_113 | 0.4 | n |  | TRUE
131 | bus_LV_135-3_0_3_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_135-3_0_3_node_118 | 0.4 | n |  | TRUE
133 | bus_LV_135-3_0_3_node_119 | 0.4 | n |  | TRUE
134 | bus_LV_135-3_0_3_node_120 | 0.4 | n |  | TRUE
135 | bus_LV_135-3_0_3_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_135-3_0_3_node_122 | 0.4 | n |  | TRUE
137 | bus_LV_135-3_0_3_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_135-3_0_3_node_153 | 0.4 | n |  | TRUE
139 | bus_LV_135-3_0_3_node_154 | 0.4 | n |  | TRUE
140 | bus_LV_135-3_0_3_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_135-3_0_3_node_130 | 0.4 | n |  | TRUE
142 | bus_LV_135-3_0_3_node_131 | 0.4 | n |  | TRUE
143 | bus_LV_135-3_0_3_node_143 | 0.4 | n |  | TRUE
144 | bus_LV_135-3_0_3_node_144 | 0.4 | n |  | TRUE
145 | bus_LV_135-3_0_3_node_136 | 0.4 | n |  | TRUE
146 | bus_LV_135-3_0_3_node_142 | 0.4 | n |  | TRUE
147 | bus_LV_135-3_0_3_node_137 | 0.4 | n |  | TRUE
148 | bus_LV_135-3_0_3_node_138 | 0.4 | n |  | TRUE
149 | bus_LV_135-3_0_3_node_139 | 0.4 | n |  | TRUE
150 | bus_MV_359_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_135-3_0_3_load_0 | 0 | 0.034604 | 0.0086726 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_135-3_0_3_load_1 | 2 | 0.00036 | 9.0224e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_135-3_0_3_load_3 | 3 | 0.00038121 | 9.5541e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_135-3_0_3_load_4 | 4 | 0.00069763 | 0.00017484 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_135-3_0_3_load_9 | 6 | 0.00041792 | 0.00010474 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_135-3_0_3_load_135 | 8 | 0.00036 | 9.0224e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_135-3_0_3_load_7 | 9 | 0.00069763 | 0.00017484 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_135-3_0_3_load_80 | 11 | 0.001828 | 0.00045814 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_135-3_0_3_load_145 | 13 | 0.00080784 | 0.00020246 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_135-3_0_3_load_6 | 14 | 0.00069788 | 0.0001749 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_135-3_0_3_load_10 | 16 | 0.001219 | 0.00030552 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_135-3_0_3_load_18 | 18 | 0.0016133 | 0.00040433 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_135-3_0_3_load_24 | 19 | 0.0010042 | 0.00025168 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_135-3_0_3_load_33 | 20 | 0.00098316 | 0.0002464 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_135-3_0_3_load_31 | 23 | 0.0027226 | 0.00068235 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_135-3_0_3_load_12 | 24 | 0.010452 | 0.0026196 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_135-3_0_3_load_16 | 27 | 0.0068809 | 0.0017245 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_135-3_0_3_load_84 | 28 | 0.0036956 | 0.0009262 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_135-3_0_3_load_68 | 31 | 0.0068493 | 0.0017166 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_135-3_0_3_load_28 | 34 | 0.00071395 | 0.00017893 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_135-3_0_3_load_29 | 35 | 0.0027478 | 0.00068866 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_135-3_0_3_load_141 | 36 | 0.00067518 | 0.00016922 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_135-3_0_3_load_20 | 38 | 0.002347 | 0.00058821 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_135-3_0_3_load_21 | 39 | 0.002316 | 0.00058045 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_135-3_0_3_load_23 | 40 | 0.0015051 | 0.00037722 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_135-3_0_3_load_25 | 41 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_135-3_0_3_load_26 | 42 | 0.0034631 | 0.00086793 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_135-3_0_3_load_45 | 44 | 0.0024407 | 0.0006117 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_135-3_0_3_load_44 | 45 | 0.0025997 | 0.00065154 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_135-3_0_3_load_47 | 47 | 0.0026856 | 0.00067307 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_135-3_0_3_load_30 | 51 | 0.0019191 | 0.00048097 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_135-3_0_3_load_32 | 52 | 0.0016207 | 0.00040618 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_135-3_0_3_load_34 | 53 | 0.0011928 | 0.00029893 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_135-3_0_3_load_35 | 54 | 0.0014619 | 0.0003664 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_135-3_0_3_load_36 | 55 | 0.0013193 | 0.00033065 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_135-3_0_3_load_37 | 56 | 0.0016195 | 0.00040589 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_135-3_0_3_load_43 | 57 | 0.002272 | 0.00056942 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_135-3_0_3_load_41 | 58 | 0.0019245 | 0.00048233 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_135-3_0_3_load_38 | 59 | 0.0024395 | 0.00061141 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_135-3_0_3_load_39 | 60 | 0.0024416 | 0.00061193 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_135-3_0_3_load_40 | 61 | 0.003337 | 0.00083632 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_135-3_0_3_load_42 | 62 | 0.0024418 | 0.00061197 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_135-3_0_3_load_146 | 65 | 0.0065241 | 0.0016351 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_135-3_0_3_load_147 | 68 | 0.0044494 | 0.0011151 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_135-3_0_3_load_51 | 72 | 0.0022339 | 0.00055988 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_135-3_0_3_load_95 | 73 | 0.00071644 | 0.00017956 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_135-3_0_3_load_93 | 74 | 0.00075856 | 0.00019011 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_135-3_0_3_load_128 | 75 | 0.0070311 | 0.0017622 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_135-3_0_3_load_129 | 76 | 0.0019104 | 0.0004788 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_135-3_0_3_load_53 | 77 | 0.0021675 | 0.00054323 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_135-3_0_3_load_66 | 78 | 0.0020987 | 0.00052599 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_135-3_0_3_load_63 | 79 | 0.002081 | 0.00052154 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_135-3_0_3_load_98 | 80 | 0.002046 | 0.00051277 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_135-3_0_3_load_96 | 82 | 0.0021061 | 0.00052785 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_135-3_0_3_load_148 | 84 | 0.0084533 | 0.0021186 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_135-3_0_3_load_64 | 85 | 0.0021057 | 0.00052775 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_135-3_0_3_load_97 | 86 | 0.0020791 | 0.00052108 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_135-3_0_3_load_100 | 87 | 0.0043141 | 0.0010812 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_135-3_0_3_load_94 | 88 | 0.0052318 | 0.0013112 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_135-3_0_3_load_99 | 89 | 0.0020811 | 0.00052156 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_135-3_0_3_load_60 | 90 | 0.0020117 | 0.00050418 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_135-3_0_3_load_59 | 91 | 0.002081 | 0.00052154 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_135-3_0_3_load_61 | 92 | 0.0020809 | 0.00052153 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_135-3_0_3_load_65 | 93 | 0.0040995 | 0.0010274 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_135-3_0_3_load_67 | 94 | 0.0045752 | 0.0011466 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_135-3_0_3_load_73 | 97 | 0.0045752 | 0.0011466 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_135-3_0_3_load_115 | 98 | 0.004497 | 0.001127 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_135-3_0_3_load_75 | 100 | 0.0049642 | 0.0012442 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_135-3_0_3_load_76 | 101 | 0.010284 | 0.0025774 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_135-3_0_3_load_77 | 102 | 0.0049145 | 0.0012317 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_135-3_0_3_load_79 | 103 | 0.0032501 | 0.00081454 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_135-3_0_3_load_91 | 106 | 0.020804 | 0.0052139 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_135-3_0_3_load_92 | 108 | 0.003566 | 0.00089373 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_135-3_0_3_load_90 | 110 | 0.0042003 | 0.0010527 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_135-3_0_3_load_87 | 111 | 0.0041582 | 0.0010421 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_135-3_0_3_load_86 | 112 | 0.0032731 | 0.00082031 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_135-3_0_3_load_108 | 113 | 0.0044458 | 0.0011142 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_135-3_0_3_load_110 | 114 | 0.0047505 | 0.0011906 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_135-3_0_3_load_109 | 115 | 0.0030068 | 0.00075357 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_135-3_0_3_load_111 | 116 | 0.0028046 | 0.00070289 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_135-3_0_3_load_106 | 119 | 0.0054704 | 0.001371 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_135-3_0_3_load_116 | 120 | 0.0038017 | 0.00095279 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_135-3_0_3_load_150 | 122 | 0.0048707 | 0.0012207 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_135-3_0_3_load_101 | 123 | 0.0049032 | 0.0012289 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_135-3_0_3_load_107 | 124 | 0.012086 | 0.003029 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_135-3_0_3_load_117 | 125 | 0.0037255 | 0.00093369 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_135-3_0_3_load_103 | 126 | 0.012867 | 0.0032247 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_135-3_0_3_load_124 | 127 | 0.0048795 | 0.0012229 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_135-3_0_3_load_151 | 128 | 0.0040638 | 0.0010185 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_135-3_0_3_load_114 | 131 | 0.0051022 | 0.0012787 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_135-3_0_3_load_118 | 132 | 0.0037533 | 0.00094066 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_135-3_0_3_load_119 | 133 | 0.0026892 | 0.00067397 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_135-3_0_3_load_120 | 134 | 0.0010363 | 0.00025973 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_135-3_0_3_load_122 | 136 | 0.0012479 | 0.00031275 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_135-3_0_3_load_153 | 138 | 0.0041938 | 0.0010511 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_135-3_0_3_load_154 | 139 | 0.0014896 | 0.00037334 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_135-3_0_3_load_130 | 141 | 0.0019103 | 0.00047877 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_135-3_0_3_load_131 | 142 | 0.0019103 | 0.00047876 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_135-3_0_3_load_143 | 143 | 0.0023518 | 0.00058941 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_135-3_0_3_load_136 | 145 | 0.00080768 | 0.00020242 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_135-3_0_3_load_142 | 146 | 0.00062758 | 0.00015729 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_135-3_0_3_load_137 | 147 | 0.00038121 | 9.5541e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_135-3_0_3_load_138 | 148 | 0.00036 | 9.0224e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_135-3_0_3_load_139 | 149 | 0.00036025 | 9.0287e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 122 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_135-3_0_3_line_0 |  | 0 | 1 | 0.015858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_135-3_0_3_line_1 |  | 1 | 4 | 0.035774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_135-3_0_3_line_2 |  | 2 | 3 | 0.0079011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_135-3_0_3_line_3 |  | 3 | 5 | 0.010099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_135-3_0_3_line_4 |  | 4 | 6 | 0.026649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_135-3_0_3_line_5 |  | 5 | 7 | 0.029337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_135-3_0_3_line_6 |  | 5 | 8 | 0.014086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_135-3_0_3_line_7 |  | 6 | 9 | 0.024132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_135-3_0_3_line_8 |  | 7 | 13 | 0.019856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_135-3_0_3_line_9 |  | 8 | 145 | 0.0024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_135-3_0_3_line_10 |  | 9 | 14 | 0.030101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_135-3_0_3_line_11 |  | 10 | 11 | 0.018355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_135-3_0_3_line_12 |  | 10 | 12 | 0.046625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_135-3_0_3_line_13 |  | 11 | 33 | 0.0072037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_135-3_0_3_line_14 |  | 12 | 24 | 0.023226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_135-3_0_3_line_15 |  | 14 | 15 | 0.053492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_135-3_0_3_line_16 |  | 15 | 16 | 0.028859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_135-3_0_3_line_17 |  | 15 | 17 | 0.007826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_135-3_0_3_line_18 |  | 16 | 18 | 0.001584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_135-3_0_3_line_19 |  | 17 | 19 | 0.035481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_135-3_0_3_line_20 |  | 17 | 20 | 0.052224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_135-3_0_3_line_21 |  | 18 | 21 | 0.050605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_135-3_0_3_line_22 |  | 19 | 22 | 0.016595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_135-3_0_3_line_23 |  | 20 | 23 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_135-3_0_3_line_24 |  | 21 | 34 | 0.024046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_135-3_0_3_line_25 |  | 21 | 35 | 0.010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_135-3_0_3_line_26 |  | 22 | 38 | 0.0090266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_135-3_0_3_line_27 |  | 23 | 51 | 0.016376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_135-3_0_3_line_28 |  | 24 | 25 | 0.042011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_135-3_0_3_line_29 |  | 25 | 26 | 0.016218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_135-3_0_3_line_30 |  | 25 | 27 | 0.030176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_135-3_0_3_line_31 |  | 26 | 28 | 0.023086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_135-3_0_3_line_32 |  | 28 | 32 | 0.0022562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_135-3_0_3_line_33 |  | 29 | 30 | 0.031403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_135-3_0_3_line_34 |  | 29 | 31 | 0.028829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_135-3_0_3_line_35 |  | 30 | 98 | 0.026161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_135-3_0_3_line_36 |  | 31 | 94 | 0.039469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_135-3_0_3_line_37 |  | 32 | 111 | 0.0097298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_135-3_0_3_line_38 |  | 33 | 104 | 0.062499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_135-3_0_3_line_39 |  | 33 | 101 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_135-3_0_3_line_40 |  | 34 | 36 | 0.0026571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_135-3_0_3_line_41 |  | 35 | 37 | 0.020277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_135-3_0_3_line_42 |  | 36 | 48 | 0.019663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_135-3_0_3_line_43 |  | 37 | 49 | 0.039444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_135-3_0_3_line_44 |  | 37 | 50 | 0.006954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_135-3_0_3_line_45 |  | 38 | 39 | 0.025704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_135-3_0_3_line_46 |  | 39 | 40 | 0.014008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_135-3_0_3_line_47 |  | 40 | 41 | 0.0092365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_135-3_0_3_line_48 |  | 41 | 42 | 0.028981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_135-3_0_3_line_49 |  | 42 | 43 | 0.021593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_135-3_0_3_line_50 |  | 43 | 44 | 0.012574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_135-3_0_3_line_51 |  | 44 | 45 | 0.0025131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_135-3_0_3_line_52 |  | 45 | 46 | 0.0035006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_135-3_0_3_line_53 |  | 46 | 47 | 0.026584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_135-3_0_3_line_54 |  | 48 | 146 | 0.015637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_135-3_0_3_line_55 |  | 48 | 149 | 0.0050878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_135-3_0_3_line_56 |  | 49 | 142 | 0.04577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_135-3_0_3_line_57 |  | 50 | 127 | 0.028002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_135-3_0_3_line_58 |  | 50 | 118 | 0.02035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_135-3_0_3_line_59 |  | 51 | 52 | 0.024218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_135-3_0_3_line_60 |  | 52 | 53 | 0.005038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_135-3_0_3_line_61 |  | 53 | 54 | 0.0038962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_135-3_0_3_line_62 |  | 54 | 55 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_135-3_0_3_line_63 |  | 55 | 56 | 0.00084028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_135-3_0_3_line_64 |  | 56 | 57 | 0.034105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_135-3_0_3_line_65 |  | 57 | 58 | 0.0040014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_135-3_0_3_line_66 |  | 58 | 60 | 0.0095036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_135-3_0_3_line_67 |  | 59 | 60 | 0.0030866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_135-3_0_3_line_68 |  | 59 | 61 | 0.011787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_135-3_0_3_line_69 |  | 61 | 62 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_135-3_0_3_line_70 |  | 62 | 63 | 0.014797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_135-3_0_3_line_71 |  | 63 | 64 | 0.006269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_135-3_0_3_line_72 |  | 64 | 65 | 0.040845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_135-3_0_3_line_73 |  | 64 | 66 | 0.067801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_135-3_0_3_line_74 |  | 66 | 73 | 0.041384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_135-3_0_3_line_75 |  | 66 | 74 | 0.017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_135-3_0_3_line_76 |  | 66 | 67 | 0.076716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_135-3_0_3_line_77 |  | 67 | 68 | 0.024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_135-3_0_3_line_78 |  | 67 | 69 | 0.036893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_135-3_0_3_line_79 |  | 69 | 70 | 0.013066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_135-3_0_3_line_80 |  | 69 | 71 | 0.036788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_135-3_0_3_line_81 |  | 69 | 72 | 0.013418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_135-3_0_3_line_82 |  | 70 | 78 | 0.008813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_135-3_0_3_line_83 |  | 70 | 79 | 0.018661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_135-3_0_3_line_84 |  | 71 | 80 | 0.026725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_135-3_0_3_line_85 |  | 71 | 81 | 0.066862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_135-3_0_3_line_86 |  | 71 | 82 | 0.018003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_135-3_0_3_line_87 |  | 72 | 77 | 0.0034178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_135-3_0_3_line_88 |  | 73 | 87 | 0.00098552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_135-3_0_3_line_89 |  | 74 | 88 | 0.0010331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_135-3_0_3_line_90 |  | 75 | 76 | 0.040083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_135-3_0_3_line_91 |  | 76 | 140 | 0.026067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_135-3_0_3_line_92 |  | 79 | 85 | 0.0047472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_135-3_0_3_line_93 |  | 81 | 83 | 0.011471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_135-3_0_3_line_94 |  | 81 | 84 | 0.002567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_135-3_0_3_line_95 |  | 82 | 86 | 0.0042235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_135-3_0_3_line_96 |  | 83 | 89 | 0.004095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_135-3_0_3_line_97 |  | 83 | 90 | 0.0037785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_135-3_0_3_line_98 |  | 85 | 93 | 0.011521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_135-3_0_3_line_99 |  | 90 | 91 | 0.010627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_135-3_0_3_line_100 |  | 91 | 92 | 0.0072648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_135-3_0_3_line_101 |  | 94 | 95 | 0.0244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_135-3_0_3_line_102 |  | 95 | 96 | 0.009157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_135-3_0_3_line_103 |  | 96 | 97 | 0.024632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_135-3_0_3_line_104 |  | 98 | 99 | 0.0056354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_135-3_0_3_line_105 |  | 99 | 131 | 0.023273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_135-3_0_3_line_106 |  | 99 | 116 | 0.012665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_135-3_0_3_line_107 |  | 100 | 101 | 0.0071023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_135-3_0_3_line_108 |  | 100 | 102 | 0.01679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_135-3_0_3_line_109 |  | 102 | 103 | 0.013034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_135-3_0_3_line_110 |  | 103 | 105 | 0.044042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_135-3_0_3_line_111 |  | 104 | 106 | 0.015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_135-3_0_3_line_112 |  | 105 | 109 | 0.015417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_135-3_0_3_line_113 |  | 105 | 110 | 0.0082806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_135-3_0_3_line_114 |  | 106 | 107 | 0.021399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_135-3_0_3_line_115 |  | 107 | 108 | 0.021276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_135-3_0_3_line_116 |  | 109 | 117 | 0.059658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_135-3_0_3_line_117 |  | 109 | 118 | 0.044626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_135-3_0_3_line_118 |  | 109 | 119 | 0.024034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_135-3_0_3_line_119 |  | 110 | 120 | 0.016379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_135-3_0_3_line_120 |  | 111 | 114 | 0.026047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_135-3_0_3_line_121 |  | 112 | 113 | 0.02672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_135-3_0_3_line_122 |  | 113 | 115 | 0.024027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_135-3_0_3_line_123 |  | 114 | 116 | 0.022847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_135-3_0_3_line_124 |  | 115 | 130 | 0.01494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_135-3_0_3_line_125 |  | 117 | 121 | 0.002105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_135-3_0_3_line_126 |  | 117 | 122 | 0.014868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_135-3_0_3_line_127 |  | 118 | 123 | 0.026248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_135-3_0_3_line_128 |  | 119 | 124 | 0.025312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_135-3_0_3_line_129 |  | 120 | 125 | 0.0089405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_135-3_0_3_line_130 |  | 121 | 128 | 0.016383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_135-3_0_3_line_131 |  | 121 | 129 | 0.024217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_135-3_0_3_line_132 |  | 123 | 126 | 0.032318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_135-3_0_3_line_133 |  | 125 | 132 | 0.037543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_135-3_0_3_line_134 |  | 129 | 139 | 0.015153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_135-3_0_3_line_135 |  | 129 | 137 | 0.006788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_135-3_0_3_line_136 |  | 130 | 131 | 0.0029989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_135-3_0_3_line_137 |  | 132 | 133 | 0.022809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_135-3_0_3_line_138 |  | 134 | 135 | 0.019288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_135-3_0_3_line_139 |  | 135 | 136 | 0.0136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_135-3_0_3_line_140 |  | 135 | 137 | 0.029401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_135-3_0_3_line_141 |  | 137 | 138 | 0.011421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_135-3_0_3_line_142 |  | 140 | 141 | 0.017222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_135-3_0_3_line_143 |  | 141 | 142 | 0.041365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_135-3_0_3_line_144 |  | 143 | 144 | 0.016622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_135-3_0_3_line_145 |  | 144 | 146 | 0.017402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_135-3_0_3_line_146 |  | 145 | 147 | 0.0061556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_135-3_0_3_line_147 |  | 147 | 148 | 0.020042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_135-3_0_3_line_148 |  | 148 | 149 | 0.018252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_135-3_0_3_trafo_150 | 0.63 MVA 20/0.4 kV | 150 | 122 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2682928.3441 | 1242618.8591 | 2682943.7602 | 1242615.1415
1 | 2682928.3441 | 1242618.8591 | 2682920.7877 | 1242598.0719 | 2682916.1213 | 1242585.2375
2 | 2682984.1909 | 1242591.4825 | 2682983.2663 | 1242589.083 | 2682982.206 | 1242583.8599
3 | 2682980.1969 | 1242573.9625 | 2682982.206 | 1242583.8599
4 | 2682908.0312 | 1242559.8586 | 2682912.86 | 1242576.2676 | 2682916.1213 | 1242585.2375
5 | 2682980.1969 | 1242573.9625 | 2682994.1726 | 1242568.1871 | 2683006.2761 | 1242560.6064
6 | 2682980.1969 | 1242573.9625 | 2682973.4984 | 1242561.571
7 | 2682908.0312 | 1242559.8586 | 2682901.2187 | 1242536.7083
8 | 2683006.2761 | 1242560.6064 | 2683011.9209 | 1242579.6429
9 | 2682972.7504 | 1242559.2781 | 2682973.4984 | 1242561.571
10 | 2682893.7242 | 1242507.562 | 2682899.0178 | 1242529.2292 | 2682901.2187 | 1242536.7083
11 | 2683126.8339 | 1242570.7343 | 2683117.1661 | 1242555.1313
12 | 2683126.8339 | 1242570.7343 | 2683128.2078 | 1242566.5616 | 2683132.2703 | 1242562.0375 | 2683136.3318 | 1242558.6697 | 2683139.7307 | 1242556.727 | 2683148.7955 | 1242531.3356
13 | 2683113.372 | 1242549.0078 | 2683117.1661 | 1242555.1313
14 | 2683148.7955 | 1242531.3356 | 2683156.6021 | 1242509.4612
15 | 2682891.7428 | 1242454.7516 | 2682889.0387 | 1242469.1909 | 2682890.494 | 1242494.3405 | 2682893.7242 | 1242507.562
16 | 2682891.7428 | 1242454.7516 | 2682896.0288 | 1242455.8678 | 2682896.7962 | 1242452.8875 | 2682909.6118 | 1242456.5691 | 2682917.4182 | 1242458.4017
17 | 2682891.7428 | 1242454.7516 | 2682893.603 | 1242447.1498
18 | 2682917.4182 | 1242458.4017 | 2682918.9766 | 1242458.6859
19 | 2682893.603 | 1242447.1498 | 2682887.8425 | 1242443.8893 | 2682882.1648 | 1242437.9501 | 2682877.2775 | 1242417.8913
20 | 2682893.603 | 1242447.1498 | 2682904.8859 | 1242424.7246 | 2682922.5128 | 1242404.1139
21 | 2682968.8824 | 1242466.7825 | 2682956.5519 | 1242465.7205 | 2682927.5137 | 1242460.3553 | 2682923.6921 | 1242459.5458 | 2682918.9766 | 1242458.6859
22 | 2682873.3489 | 1242401.7676 | 2682877.2775 | 1242417.8913
23 | 2682922.5128 | 1242404.1139 | 2682933.5764 | 1242391.1775
24 | 2682968.8824 | 1242466.7825 | 2682960.5678 | 1242489.345
25 | 2682968.8824 | 1242466.7825 | 2682978.8828 | 1242467.6403
26 | 2682873.3489 | 1242401.7676 | 2682871.2113 | 1242392.9978
27 | 2682944.2198 | 1242378.7326 | 2682933.5764 | 1242391.1775
28 | 2683170.8316 | 1242469.9333 | 2683159.9223 | 1242500.1579 | 2683156.6021 | 1242509.4612
29 | 2683170.8316 | 1242469.9333 | 2683176.8339 | 1242454.8621
30 | 2683170.8316 | 1242469.9333 | 2683191.8517 | 1242477.7669 | 2683199.3689 | 1242479.6273
31 | 2683176.8339 | 1242454.8621 | 2683155.2052 | 1242446.7897
32 | 2683153.0914 | 1242446.0008 | 2683155.2052 | 1242446.7897
33 | 2683193.0284 | 1242408.967 | 2683199.4245 | 1242378.2233
34 | 2683193.0284 | 1242408.967 | 2683221.21 | 1242415.0442
35 | 2683199.4245 | 1242378.2233 | 2683187.5912 | 1242382.127 | 2683186.6959 | 1242385.0499 | 2683176.3771 | 1242382.4406
36 | 2683248.0304 | 1242432.5975 | 2683238.0812 | 1242429.7803 | 2683239.8831 | 1242424.7464 | 2683220.3659 | 1242418.0902 | 2683221.21 | 1242415.0442
37 | 2683153.0914 | 1242446.0008 | 2683156.1436 | 1242436.7621
38 | 2683092.072 | 1242596.7775 | 2683092.2705 | 1242563.723 | 2683097.2728 | 1242554.175 | 2683106.442 | 1242547.2206 | 2683113.372 | 1242549.0078
39 | 2683113.372 | 1242549.0078 | 2683109.6395 | 1242527.818 | 2683109.6395 | 1242527.818
40 | 2682959.649 | 1242491.8382 | 2682960.5678 | 1242489.345
41 | 2682999.0858 | 1242469.3733 | 2682978.8828 | 1242467.6403
42 | 2682963.8634 | 1242511.0443 | 2682959.649 | 1242491.8382
43 | 2682999.0858 | 1242469.3733 | 2683010.5532 | 1242431.6286
44 | 2683006.0509 | 1242469.7376 | 2682999.0858 | 1242469.3733
45 | 2682865.1242 | 1242368.025 | 2682871.2113 | 1242392.9978
46 | 2682861.8068 | 1242354.4151 | 2682865.1242 | 1242368.025
47 | 2682861.8068 | 1242354.4151 | 2682859.6194 | 1242345.4413
48 | 2682854.6331 | 1242316.9332 | 2682856.9392 | 1242334.4455 | 2682859.6194 | 1242345.4413
49 | 2682854.6876 | 1242295.3859 | 2682854.089 | 1242312.8012 | 2682854.6331 | 1242316.9332
50 | 2682854.6876 | 1242295.3859 | 2682857.5538 | 1242283.1429
51 | 2682858.1266 | 1242280.6959 | 2682857.5538 | 1242283.1429
52 | 2682858.9246 | 1242277.2875 | 2682858.1266 | 1242280.6959
53 | 2682858.9246 | 1242277.2875 | 2682859.0411 | 1242273.82 | 2682854.7252 | 1242251.1122
54 | 2682963.8634 | 1242511.0443 | 2682979.3038 | 1242513.5175
55 | 2682963.8634 | 1242511.0443 | 2682964.0295 | 1242516.1294
56 | 2683010.5532 | 1242431.6286 | 2683011.8927 | 1242427.2108 | 2683027.8996 | 1242389.2974
57 | 2683006.0509 | 1242469.7376 | 2683009.4817 | 1242456.8763 | 2683013.6052 | 1242442.7756
58 | 2683006.0509 | 1242469.7376 | 2683026.4324 | 1242470.8235
59 | 2682944.2198 | 1242378.7326 | 2682957.5096 | 1242363.1932 | 2682959.0787 | 1242359.7644
60 | 2682961.1752 | 1242355.1834 | 2682959.0787 | 1242359.7644
61 | 2682961.1752 | 1242355.1834 | 2682962.7966 | 1242351.6406
62 | 2682962.7966 | 1242351.6406 | 2682967.9204 | 1242340.4445 | 2682969.182 | 1242334.7579
63 | 2682969.364 | 1242333.9376 | 2682969.182 | 1242334.7579
64 | 2682973.9884 | 1242300.3003 | 2682973.5767 | 1242314.9496 | 2682969.364 | 1242333.9376
65 | 2682974.1008 | 1242296.3005 | 2682973.9884 | 1242300.3003
66 | 2682974.1008 | 1242296.3005 | 2682974.3677 | 1242286.8007
67 | 2682974.4544 | 1242283.7153 | 2682974.3677 | 1242286.8007
68 | 2682974.4544 | 1242283.7153 | 2682974.7855 | 1242271.933
69 | 2682975.2474 | 1242255.4957 | 2682974.7855 | 1242271.933
70 | 2682980.2767 | 1242241.8683 | 2682977.7526 | 1242245.5801 | 2682976.0934 | 1242249.6154 | 2682975.2627 | 1242254.9521 | 2682975.2474 | 1242255.4957
71 | 2682978.6301 | 1242235.8187 | 2682980.2767 | 1242241.8683
72 | 2682962.1051 | 1242205.4325 | 2682972.9724 | 1242208.9869 | 2682972.2787 | 1242229.3919 | 2682978.6301 | 1242235.8187
73 | 2682978.6301 | 1242235.8187 | 2682979.7886 | 1242187.589 | 2682979.7717 | 1242184.4754 | 2682978.5581 | 1242180.9781 | 2682981.2197 | 1242168.5175
74 | 2682981.2197 | 1242168.5175 | 2682984.3266 | 1242133.9582 | 2682978.5557 | 1242130.5826
75 | 2682981.2197 | 1242168.5175 | 2682969.9209 | 1242166.08 | 2682968.9707 | 1242160.0466
76 | 2682981.2197 | 1242168.5175 | 2682978.5581 | 1242180.9781 | 2682975.5766 | 1242178.468 | 2682952.8439 | 1242172.9907 | 2682942.669 | 1242163.1637 | 2682939.1735 | 1242158.4892 | 2682931.2443 | 1242143.779
77 | 2682931.2443 | 1242143.779 | 2682942.8029 | 1242137.3692 | 2682946.0732 | 1242126.2513
78 | 2682900.0671 | 1242134.4701 | 2682908.5623 | 1242136.2789 | 2682913.8752 | 1242133.718 | 2682916.3993 | 1242138.1231 | 2682917.8082 | 1242137.3866 | 2682929.7188 | 1242140.9556 | 2682931.2443 | 1242143.779
79 | 2682900.0671 | 1242134.4701 | 2682895.796 | 1242133.3541 | 2682891.6001 | 1242125.7678
80 | 2682883.5509 | 1242165.0837 | 2682885.2476 | 1242159.4478 | 2682887.156 | 1242153.8037 | 2682888.8611 | 1242147.5675 | 2682893.7467 | 1242144.1999 | 2682900.5183 | 1242137.3451 | 2682900.0671 | 1242134.4701
81 | 2682900.0671 | 1242134.4701 | 2682911.8935 | 1242128.1308
82 | 2682887.3381 | 1242118.0471 | 2682891.6001 | 1242125.7678
83 | 2682891.6001 | 1242125.7678 | 2682873.6295 | 1242120.7378
84 | 2682883.5509 | 1242165.0837 | 2682877.6413 | 1242152.4588 | 2682869.5587 | 1242150.3333 | 2682867.7179 | 1242146.2713
85 | 2682883.5509 | 1242165.0837 | 2682885.2476 | 1242159.4478 | 2682887.156 | 1242153.8037 | 2682892.2047 | 1242155.5421 | 2682890.563 | 1242162.1128 | 2682903.7458 | 1242187.7043 | 2682905.689 | 1242191.4786 | 2682896.9015 | 1242195.9813
86 | 2682883.5509 | 1242165.0837 | 2682867.3244 | 1242172.8816
87 | 2682914.9058 | 1242126.516 | 2682911.8935 | 1242128.1308
88 | 2682977.705 | 1242130.085 | 2682978.5557 | 1242130.5826
89 | 2682968.81 | 1242159.026 | 2682968.9707 | 1242160.0466
90 | 2683052.9542 | 1242268.3678 | 2683051.8131 | 1242295.741 | 2683050.6984 | 1242308.3778
91 | 2683047.2686 | 1242334.1385 | 2683048.9733 | 1242327.9356 | 2683050.6984 | 1242308.3778
92 | 2682869.0408 | 1242119.5233 | 2682871.1538 | 1242120.0448 | 2682873.6295 | 1242120.7378
93 | 2682896.9015 | 1242195.9813 | 2682886.6673 | 1242201.22
94 | 2682896.9015 | 1242195.9813 | 2682898.1935 | 1242198.201
95 | 2682863.5177 | 1242174.711 | 2682867.3244 | 1242172.8816
96 | 2682885.9677 | 1242197.1851 | 2682886.6673 | 1242201.22
97 | 2682886.6673 | 1242201.22 | 2682883.0455 | 1242200.1429
98 | 2682858.523 | 1242115.5319 | 2682860.5529 | 1242117.4283 | 2682869.0408 | 1242119.5233
99 | 2682872.8594 | 1242197.1136 | 2682883.0455 | 1242200.1429
100 | 2682869.5422 | 1242201.3032 | 2682870.6607 | 1242196.4597 | 2682872.8594 | 1242197.1136
101 | 2683271.507 | 1242439.2449 | 2683248.0304 | 1242432.5975
102 | 2683268.8288 | 1242448.0026 | 2683271.507 | 1242439.2449
103 | 2683268.8288 | 1242448.0026 | 2683262.9363 | 1242467.623 | 2683261.724 | 1242471.5875
104 | 2683170.9136 | 1242381.0592 | 2683176.3771 | 1242382.4406
105 | 2683170.9136 | 1242381.0592 | 2683148.3509 | 1242375.3549
106 | 2683170.9136 | 1242381.0592 | 2683167.4411 | 1242392.0184 | 2683168.4356 | 1242392.2659 | 2683168.3917 | 1242392.4028
107 | 2683111.6399 | 1242521.0033 | 2683109.6395 | 1242527.818
108 | 2683111.6399 | 1242521.0033 | 2683116.3689 | 1242504.8926
109 | 2683120.0401 | 1242492.3859 | 2683116.3689 | 1242504.8926
110 | 2683086.436 | 1242474.021 | 2683121.8971 | 1242486.0595 | 2683120.0401 | 1242492.3859
111 | 2683092.072 | 1242596.7775 | 2683076.9715 | 1242596.4233
112 | 2683070.9951 | 1242473.1931 | 2683086.436 | 1242474.021
113 | 2683086.436 | 1242474.021 | 2683089.4279 | 1242468.2142 | 2683090.6933 | 1242467.0077
114 | 2683055.5779 | 1242595.9216 | 2683076.9715 | 1242596.4233
115 | 2683055.5779 | 1242595.9216 | 2683034.3059 | 1242595.5272
116 | 2683061.8923 | 1242436.5281 | 2683057.1272 | 1242448.0364 | 2683057.0539 | 1242453.2725 | 2683058.6263 | 1242459.2099 | 2683058.0282 | 1242462.5151 | 2683056.3382 | 1242464.971 | 2683052.3053 | 1242466.8381 | 2683051.3766 | 1242472.1512 | 2683070.9951 | 1242473.1931
117 | 2683026.4324 | 1242470.8235 | 2683051.3766 | 1242472.1512 | 2683070.9951 | 1242473.1931
118 | 2683070.9951 | 1242473.1931 | 2683067.7226 | 1242487.7023 | 2683069.7328 | 1242496.6392
119 | 2683103.1912 | 1242456.4998 | 2683097.979 | 1242460.0614 | 2683090.6933 | 1242467.0077
120 | 2683156.1436 | 1242436.7621 | 2683160.8285 | 1242422.5812 | 2683158.9021 | 1242421.9426 | 2683162.3375 | 1242413.5351
121 | 2683135.8348 | 1242430.7036 | 2683134.0682 | 1242429.9894 | 2683137.3583 | 1242421.2514 | 2683135.5172 | 1242420.4584 | 2683140.17 | 1242407.8144
122 | 2683140.17 | 1242407.8144 | 2683138.9434 | 1242407.4081 | 2683141.3567 | 1242400.8149 | 2683139.5092 | 1242399.9439 | 2683143.8639 | 1242386.9845
123 | 2683162.3375 | 1242413.5351 | 2683163.9437 | 1242409.6043 | 2683163.028 | 1242409.1356 | 2683168.3917 | 1242392.4028
124 | 2683145.4434 | 1242374.6199 | 2683143.7952 | 1242378.9444 | 2683145.3651 | 1242379.6669 | 2683142.7873 | 1242386.6692 | 2683143.8639 | 1242386.9845
125 | 2683061.8923 | 1242436.5281 | 2683062.6983 | 1242434.5825
126 | 2683050.494 | 1242427.7401 | 2683052.8441 | 1242431.598 | 2683058.139 | 1242435.1635 | 2683061.8923 | 1242436.5281
127 | 2683026.4324 | 1242470.8235 | 2683031.1862 | 1242479.5629 | 2683032.5279 | 1242495.8072
128 | 2683067.4216 | 1242519.988 | 2683072.989 | 1242511.1151 | 2683069.7328 | 1242496.6392
129 | 2683103.1912 | 1242456.4998 | 2683104.0701 | 1242455.8992 | 2683105.7579 | 1242448.2061
130 | 2683062.6983 | 1242434.5825 | 2683075.5175 | 1242437.9977 | 2683078.2832 | 1242436.4686
131 | 2683067.0727 | 1242411.5715 | 2683066.058 | 1242412.2244 | 2683063.7489 | 1242418.9414 | 2683064.4665 | 1242427.0796 | 2683063.4181 | 1242432.8468 | 2683062.6983 | 1242434.5825
132 | 2683031.3872 | 1242527.8451 | 2683033.9529 | 1242513.0592 | 2683032.5279 | 1242495.8072
133 | 2683105.7579 | 1242448.2061 | 2683105.7579 | 1242448.2061 | 2683102.8523 | 1242445.1522 | 2683102.2143 | 1242441.5851 | 2683109.7298 | 1242429.1146 | 2683109.7863 | 1242425.0792 | 2683108.1731 | 1242417.7402 | 2683109.1509 | 1242414.2818
134 | 2683067.0727 | 1242411.5715 | 2683064.5711 | 1242408.2786 | 2683063.6122 | 1242404.9516 | 2683063.8988 | 1242400.1411 | 2683063.6421 | 1242397.4133
135 | 2683073.3527 | 1242409.5802 | 2683069.819 | 1242409.8087 | 2683067.0727 | 1242411.5715
136 | 2683145.4434 | 1242374.6199 | 2683148.3509 | 1242375.3549
137 | 2683117.4226 | 1242393.7412 | 2683116.1676 | 1242395.3582 | 2683116.0479 | 1242399.0481 | 2683114.4001 | 1242403.884 | 2683111.0604 | 1242407.5288 | 2683109.1509 | 1242414.2818
138 | 2683077.4672 | 1242382.9963 | 2683074.9559 | 1242377.157 | 2683074.3415 | 1242369.743 | 2683073.0156 | 1242366.7112 | 2683074.7082 | 1242365.3326
139 | 2683077.4672 | 1242382.9963 | 2683086.261 | 1242383.4309 | 2683090.6147 | 1242381.3347
140 | 2683073.3527 | 1242409.5802 | 2683070.2561 | 1242405.0447 | 2683069.817 | 1242400.2351 | 2683073.4164 | 1242394.7704 | 2683075.7074 | 1242390.4326 | 2683077.4672 | 1242382.9963
141 | 2683084.7222 | 1242410.7068 | 2683075.2065 | 1242409.4616 | 2683073.3527 | 1242409.5802
142 | 2683047.2686 | 1242334.1385 | 2683042.7102 | 1242350.7461
143 | 2683042.7102 | 1242350.7461 | 2683039.9873 | 1242360.6669 | 2683027.8996 | 1242389.2974
144 | 2682996.6631 | 1242512.3038 | 2682997.5996 | 1242495.7078
145 | 2682996.6631 | 1242512.3038 | 2682979.3038 | 1242513.5175
146 | 2682972.7504 | 1242559.2781 | 2682970.8414 | 1242553.426
147 | 2682964.6257 | 1242534.3718 | 2682964.6257 | 1242534.3718 | 2682970.8414 | 1242553.426
148 | 2682964.6257 | 1242534.3718 | 2682964.0295 | 1242516.1294

## bus_geodata
| x | y | coords
0 | 2682943.7602 | 1242615.1415
1 | 2682928.3441 | 1242618.8591
2 | 2682984.1909 | 1242591.4825
3 | 2682982.206 | 1242583.8599
4 | 2682916.1213 | 1242585.2375
5 | 2682980.1969 | 1242573.9625
6 | 2682908.0312 | 1242559.8586
7 | 2683006.2761 | 1242560.6064
8 | 2682973.4984 | 1242561.571
9 | 2682901.2187 | 1242536.7083
10 | 2683126.8339 | 1242570.7343
11 | 2683117.1661 | 1242555.1313
12 | 2683148.7955 | 1242531.3356
13 | 2683011.9209 | 1242579.6429
14 | 2682893.7242 | 1242507.562
15 | 2682891.7428 | 1242454.7516
16 | 2682917.4182 | 1242458.4017
17 | 2682893.603 | 1242447.1498
18 | 2682918.9766 | 1242458.6859
19 | 2682877.2775 | 1242417.8913
20 | 2682922.5128 | 1242404.1139
21 | 2682968.8824 | 1242466.7825
22 | 2682873.3489 | 1242401.7676
23 | 2682933.5764 | 1242391.1775
24 | 2683156.6021 | 1242509.4612
25 | 2683170.8316 | 1242469.9333
26 | 2683176.8339 | 1242454.8621
27 | 2683199.3689 | 1242479.6273
28 | 2683155.2052 | 1242446.7897
29 | 2683193.0284 | 1242408.967
30 | 2683199.4245 | 1242378.2233
31 | 2683221.21 | 1242415.0442
32 | 2683153.0914 | 1242446.0008
33 | 2683113.372 | 1242549.0078
34 | 2682960.5678 | 1242489.345
35 | 2682978.8828 | 1242467.6403
36 | 2682959.649 | 1242491.8382
37 | 2682999.0858 | 1242469.3733
38 | 2682871.2113 | 1242392.9978
39 | 2682865.1242 | 1242368.025
40 | 2682861.8068 | 1242354.4151
41 | 2682859.6194 | 1242345.4413
42 | 2682854.6331 | 1242316.9332
43 | 2682854.6876 | 1242295.3859
44 | 2682857.5538 | 1242283.1429
45 | 2682858.1266 | 1242280.6959
46 | 2682858.9246 | 1242277.2875
47 | 2682854.7252 | 1242251.1122
48 | 2682963.8634 | 1242511.0443
49 | 2683010.5532 | 1242431.6286
50 | 2683006.0509 | 1242469.7376
51 | 2682944.2198 | 1242378.7326
52 | 2682959.0787 | 1242359.7644
53 | 2682961.1752 | 1242355.1834
54 | 2682962.7966 | 1242351.6406
55 | 2682969.182 | 1242334.7579
56 | 2682969.364 | 1242333.9376
57 | 2682973.9884 | 1242300.3003
58 | 2682974.1008 | 1242296.3005
59 | 2682974.4544 | 1242283.7153
60 | 2682974.3677 | 1242286.8007
61 | 2682974.7855 | 1242271.933
62 | 2682975.2474 | 1242255.4957
63 | 2682980.2767 | 1242241.8683
64 | 2682978.6301 | 1242235.8187
65 | 2682962.1051 | 1242205.4325
66 | 2682981.2197 | 1242168.5175
67 | 2682931.2443 | 1242143.779
68 | 2682946.0732 | 1242126.2513
69 | 2682900.0671 | 1242134.4701
70 | 2682891.6001 | 1242125.7678
71 | 2682883.5509 | 1242165.0837
72 | 2682911.8935 | 1242128.1308
73 | 2682978.5557 | 1242130.5826
74 | 2682968.9707 | 1242160.0466
75 | 2683052.9542 | 1242268.3678
76 | 2683050.6984 | 1242308.3778
77 | 2682914.9058 | 1242126.516
78 | 2682887.3381 | 1242118.0471
79 | 2682873.6295 | 1242120.7378
80 | 2682867.7178 | 1242146.2713
81 | 2682896.9015 | 1242195.9813
82 | 2682867.3244 | 1242172.8816
83 | 2682886.6673 | 1242201.22
84 | 2682898.1935 | 1242198.201
85 | 2682869.0408 | 1242119.5233
86 | 2682863.5177 | 1242174.711
87 | 2682977.705 | 1242130.085
88 | 2682968.81 | 1242159.026
89 | 2682885.9677 | 1242197.1851
90 | 2682883.0455 | 1242200.1429
91 | 2682872.8594 | 1242197.1136
92 | 2682869.5422 | 1242201.3032
93 | 2682858.523 | 1242115.5319
94 | 2683248.0304 | 1242432.5975
95 | 2683271.507 | 1242439.2449
96 | 2683268.8288 | 1242448.0026
97 | 2683261.724 | 1242471.5875
98 | 2683176.3771 | 1242382.4406
99 | 2683170.9136 | 1242381.0592
100 | 2683111.6399 | 1242521.0033
101 | 2683109.6395 | 1242527.818
102 | 2683116.3689 | 1242504.8926
103 | 2683120.0401 | 1242492.3859
104 | 2683092.072 | 1242596.7775
105 | 2683086.436 | 1242474.021
106 | 2683076.9715 | 1242596.4233
107 | 2683055.5779 | 1242595.9216
108 | 2683034.3059 | 1242595.5272
109 | 2683070.9951 | 1242473.1931
110 | 2683090.6933 | 1242467.0077
111 | 2683156.1436 | 1242436.7621
112 | 2683135.8348 | 1242430.7036
113 | 2683140.17 | 1242407.8144
114 | 2683162.3375 | 1242413.5351
115 | 2683143.8639 | 1242386.9845
116 | 2683168.3917 | 1242392.4028
117 | 2683061.8923 | 1242436.5281
118 | 2683026.4324 | 1242470.8235
119 | 2683069.7328 | 1242496.6392
120 | 2683103.1912 | 1242456.4998
121 | 2683062.6983 | 1242434.5825
122 | 2683050.494 | 1242427.7401
123 | 2683032.5279 | 1242495.8072
124 | 2683067.4216 | 1242519.988
125 | 2683105.7579 | 1242448.2062
126 | 2683031.3872 | 1242527.8451
127 | 2683013.6052 | 1242442.7756
128 | 2683078.2832 | 1242436.4686
129 | 2683067.0727 | 1242411.5715
130 | 2683145.4434 | 1242374.6199
131 | 2683148.3509 | 1242375.3549
132 | 2683109.1509 | 1242414.2818
133 | 2683117.4226 | 1242393.7413
134 | 2683074.7082 | 1242365.3326
135 | 2683077.4672 | 1242382.9963
136 | 2683090.6147 | 1242381.3347
137 | 2683073.3527 | 1242409.5802
138 | 2683084.7222 | 1242410.7068
139 | 2683063.6421 | 1242397.4133
140 | 2683047.2686 | 1242334.1385
141 | 2683042.7102 | 1242350.7461
142 | 2683027.8996 | 1242389.2974
143 | 2682997.5996 | 1242495.7078
144 | 2682996.6631 | 1242512.3038
145 | 2682972.7504 | 1242559.2781
146 | 2682979.3038 | 1242513.5175
147 | 2682970.8414 | 1242553.426
148 | 2682964.6257 | 1242534.3718
149 | 2682964.0295 | 1242516.1294
150 | 2683061.8923 | 1242436.5281

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97639 | -0.4545 | 0.034604 | 0.0086726
1 | 0.9769 | -0.44447 | 0 | 0
2 | 0.98577 | -0.27168 | 0.00036 | 9.0224e-05
3 | 0.98578 | -0.27162 | 0.00038121 | 9.5541e-05
4 | 0.97805 | -0.42189 | 0.00069763 | 0.00017484
5 | 0.98578 | -0.27149 | 0 | 0
6 | 0.97893 | -0.40476 | 0.00041792 | 0.00010474
7 | 0.98576 | -0.27192 | 0 | 0
8 | 0.9858 | -0.2711 | 0.00036 | 9.0224e-05
9 | 0.97973 | -0.3891 | 0.00069763 | 0.00017484
10 | 0.98471 | -0.29202 | 0 | 0
11 | 0.98589 | -0.26925 | 0.001828 | 0.00045814
12 | 0.98171 | -0.35009 | 0 | 0
13 | 0.98575 | -0.2722 | 0.00080784 | 0.00020246
14 | 0.98074 | -0.36921 | 0.00069788 | 0.0001749
15 | 0.98259 | -0.3333 | 0 | 0
16 | 0.98389 | -0.3081 | 0.001219 | 0.00030552
17 | 0.98233 | -0.33839 | 0 | 0
18 | 0.98396 | -0.30671 | 0.0016133 | 0.00040433
19 | 0.98165 | -0.35166 | 0.0010042 | 0.00025168
20 | 0.98091 | -0.36594 | 0.00098316 | 0.0002464
21 | 0.98628 | -0.26183 | 0 | 0
22 | 0.98135 | -0.35756 | 0 | 0
23 | 0.98046 | -0.37483 | 0.0027226 | 0.00068235
24 | 0.98022 | -0.37915 | 0.010452 | 0.0026196
25 | 0.97793 | -0.42394 | 0 | 0
26 | 0.97714 | -0.43924 | 0 | 0
27 | 0.97773 | -0.42772 | 0.0068809 | 0.0017245
28 | 0.97603 | -0.46108 | 0.0036956 | 0.0009262
29 | 0.9722 | -0.53657 | 0 | 0
30 | 0.97267 | -0.52731 | 0 | 0
31 | 0.97177 | -0.54509 | 0.0068493 | 0.0017166
32 | 0.97593 | -0.46306 | 0 | 0
33 | 0.98637 | -0.2601 | 0 | 0
34 | 0.9861 | -0.26536 | 0.00071395 | 0.00017893
35 | 0.98676 | -0.25247 | 0.0027478 | 0.00068866
36 | 0.98608 | -0.26572 | 0.00067518 | 0.00016922
37 | 0.98776 | -0.23324 | 0 | 0
38 | 0.98118 | -0.36078 | 0.002347 | 0.00058821
39 | 0.98077 | -0.36885 | 0.002316 | 0.00058045
40 | 0.98058 | -0.37266 | 0.0015051 | 0.00037722
41 | 0.98046 | -0.37492 | 0.0023148 | 0.00058014
42 | 0.98016 | -0.3808 | 0.0034631 | 0.00086793
43 | 0.98001 | -0.38383 | 0 | 0
44 | 0.97992 | -0.38559 | 0.0024407 | 0.0006117
45 | 0.9799 | -0.38583 | 0.0025997 | 0.00065154
46 | 0.9799 | -0.38601 | 0 | 0
47 | 0.97983 | -0.3873 | 0.0026856 | 0.00067307
48 | 0.98596 | -0.26812 | 0 | 0
49 | 0.9873 | -0.24224 | 0 | 0
50 | 0.98813 | -0.22613 | 0 | 0
51 | 0.98003 | -0.38312 | 0.0019191 | 0.00048097
52 | 0.97942 | -0.39512 | 0.0016207 | 0.00040618
53 | 0.97929 | -0.39757 | 0.0011928 | 0.00029893
54 | 0.9792 | -0.39943 | 0.0014619 | 0.0003664
55 | 0.97876 | -0.40796 | 0.0013193 | 0.00033065
56 | 0.97874 | -0.40835 | 0.0016195 | 0.00040589
57 | 0.97795 | -0.4238 | 0.002272 | 0.00056942
58 | 0.97786 | -0.42556 | 0.0019245 | 0.00048233
59 | 0.97759 | -0.4309 | 0.0024395 | 0.00061141
60 | 0.97766 | -0.42963 | 0.0024416 | 0.00061193
61 | 0.97735 | -0.4356 | 0.003337 | 0.00083632
62 | 0.97703 | -0.44182 | 0.0024418 | 0.00061197
63 | 0.97676 | -0.44721 | 0 | 0
64 | 0.97664 | -0.44949 | 0 | 0
65 | 0.9764 | -0.45436 | 0.0065241 | 0.0016351
66 | 0.97552 | -0.4715 | 0 | 0
67 | 0.97452 | -0.49128 | 0 | 0
68 | 0.97442 | -0.4933 | 0.0044494 | 0.0011151
69 | 0.97409 | -0.4998 | 0 | 0
70 | 0.97405 | -0.50063 | 0 | 0
71 | 0.97383 | -0.50497 | 0 | 0
72 | 0.97403 | -0.50089 | 0.0022339 | 0.00055988
73 | 0.97533 | -0.47531 | 0.00071644 | 0.00017956
74 | 0.97543 | -0.47343 | 0.00075856 | 0.00019011
75 | 0.98573 | -0.27273 | 0.0070311 | 0.0017622
76 | 0.98599 | -0.26768 | 0.0019104 | 0.0004788
77 | 0.97403 | -0.50102 | 0.0021675 | 0.00054323
78 | 0.97403 | -0.50097 | 0.0020987 | 0.00052599
79 | 0.97397 | -0.50206 | 0.002081 | 0.00052154
80 | 0.97378 | -0.50598 | 0.002046 | 0.00051277
81 | 0.97348 | -0.51182 | 0 | 0
82 | 0.97376 | -0.50636 | 0.0021061 | 0.00052785
83 | 0.97345 | -0.5124 | 0 | 0
84 | 0.97347 | -0.51202 | 0.0084533 | 0.0021186
85 | 0.97395 | -0.5026 | 0.0021057 | 0.00052775
86 | 0.97375 | -0.50652 | 0.0020791 | 0.00052108
87 | 0.97533 | -0.47539 | 0.0043141 | 0.0010812
88 | 0.97542 | -0.47353 | 0.0052318 | 0.0013112
89 | 0.97345 | -0.51246 | 0.0020811 | 0.00052156
90 | 0.97344 | -0.51255 | 0.0020117 | 0.00050418
91 | 0.97342 | -0.51295 | 0.002081 | 0.00052154
92 | 0.97341 | -0.51323 | 0.0020809 | 0.00052153
93 | 0.9739 | -0.50346 | 0.0040995 | 0.0010274
94 | 0.97143 | -0.55175 | 0.0045752 | 0.0011466
95 | 0.97133 | -0.55382 | 0 | 0
96 | 0.97129 | -0.55459 | 0 | 0
97 | 0.97118 | -0.55667 | 0.0045752 | 0.0011466
98 | 0.97306 | -0.5196 | 0.004497 | 0.001127
99 | 0.97316 | -0.51747 | 0 | 0
100 | 0.98862 | -0.21675 | 0.0049642 | 0.0012442
101 | 0.98827 | -0.22344 | 0.010284 | 0.0025774
102 | 0.98919 | -0.20573 | 0.0049145 | 0.0012317
103 | 0.98966 | -0.19679 | 0.0032501 | 0.00081454
104 | 0.98496 | -0.28742 | 0 | 0
105 | 0.99127 | -0.16583 | 0 | 0
106 | 0.98463 | -0.29404 | 0.020804 | 0.0052139
107 | 0.98456 | -0.29541 | 0 | 0
108 | 0.98449 | -0.29678 | 0.003566 | 0.00089373
109 | 0.99192 | -0.15336 | 0 | 0
110 | 0.99113 | -0.1685 | 0.0042003 | 0.0010527
111 | 0.97549 | -0.47162 | 0.0041582 | 0.0010421
112 | 0.97239 | -0.53283 | 0.0032731 | 0.00082031
113 | 0.97247 | -0.53122 | 0.0044458 | 0.0011142
114 | 0.97443 | -0.49258 | 0.0047505 | 0.0011906
115 | 0.97264 | -0.5278 | 0.0030068 | 0.00075357
116 | 0.97359 | -0.50901 | 0.0028046 | 0.00070289
117 | 0.99834 | -0.031233 | 0 | 0
118 | 0.98924 | -0.20475 | 0 | 0
119 | 0.99154 | -0.16084 | 0.0054704 | 0.001371
120 | 0.99092 | -0.17256 | 0.0038017 | 0.00095279
121 | 0.99832 | -0.031676 | 0 | 0
122 | 1 | 0 | -0.36883 | -0.094437
123 | 0.98881 | -0.21307 | 0.0049032 | 0.0012289
124 | 0.99126 | -0.16627 | 0.012086 | 0.003029
125 | 0.99084 | -0.17418 | 0.0037255 | 0.00093369
126 | 0.98843 | -0.22048 | 0.012867 | 0.0032247
127 | 0.988 | -0.22857 | 0.0048795 | 0.0012229
128 | 0.99826 | -0.032841 | 0.0040638 | 0.0010185
129 | 0.99815 | -0.035053 | 0 | 0
130 | 0.97279 | -0.52485 | 0 | 0
131 | 0.97282 | -0.52426 | 0.0051022 | 0.0012787
132 | 0.99062 | -0.17847 | 0.0037533 | 0.00094066
133 | 0.99056 | -0.17956 | 0.0026892 | 0.00067397
134 | 0.99803 | -0.037348 | 0.0010363 | 0.00025973
135 | 0.99805 | -0.036998 | 0 | 0
136 | 0.99803 | -0.037295 | 0.0012479 | 0.00031275
137 | 0.99811 | -0.035822 | 0 | 0
138 | 0.99806 | -0.03666 | 0.0041938 | 0.0010511
139 | 0.99813 | -0.035448 | 0.0014896 | 0.00037334
140 | 0.98621 | -0.2635 | 0 | 0
141 | 0.98635 | -0.26074 | 0.0019103 | 0.00047877
142 | 0.98676 | -0.2527 | 0.0019103 | 0.00047876
143 | 0.98584 | -0.27039 | 0.0023518 | 0.00058941
144 | 0.98588 | -0.26969 | 0 | 0
145 | 0.98581 | -0.27102 | 0.00080768 | 0.00020242
146 | 0.98591 | -0.26895 | 0.00062758 | 0.00015729
147 | 0.98582 | -0.27071 | 0.00038121 | 9.5541e-05
148 | 0.98588 | -0.2696 | 0.00036 | 9.0224e-05
149 | 0.98594 | -0.26847 | 0.00036025 | 9.0287e-05
150 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034604 | -0.0086726 | 0.034621 | 0.008683 | 1.6539e-05 | 1.0386e-05 | 0.052736 | 0.052736 | 0.052736 | 0.97639 | -0.4545 | 0.9769 | -0.44447 | 14.488
1 | -0.034621 | -0.008683 | 0.034658 | 0.0087064 | 3.731e-05 | 2.343e-05 | 0.052736 | 0.052736 | 0.052736 | 0.9769 | -0.44447 | 0.97805 | -0.42189 | 14.488
2 | -0.00036 | -9.0224e-05 | 0.00036 | 9.0123e-05 | 8.7488e-10 | -1.0017e-07 | 0.00054341 | 0.00054338 | 0.00054341 | 0.98577 | -0.27168 | 0.98578 | -0.27162 | 0.14929
3 | -0.00074121 | -0.00018566 | 0.00074121 | 0.00018554 | 4.7404e-09 | -1.2572e-07 | 0.0011188 | 0.0011188 | 0.0011188 | 0.98578 | -0.27162 | 0.98578 | -0.27149 | 0.30737
4 | -0.035356 | -0.0088813 | 0.035385 | 0.0088995 | 2.8923e-05 | 1.8176e-05 | 0.053798 | 0.053797 | 0.053798 | 0.97805 | -0.42189 | 0.97893 | -0.40476 | 14.7796
5 | 0.00080787 | 0.00020186 | -0.00080785 | -0.00020222 | 1.6356e-08 | -3.6354e-07 | 0.0012192 | 0.0012194 | 0.0012194 | 0.98578 | -0.27149 | 0.98576 | -0.27192 | 0.33499
6 | -0.0015491 | -0.00038739 | 0.0015491 | 0.00038723 | 2.8874e-08 | -1.6111e-07 | 0.002338 | 0.0023379 | 0.002338 | 0.98578 | -0.27149 | 0.9858 | -0.2711 | 0.64231
7 | -0.035802 | -0.0090042 | 0.035829 | 0.009021 | 2.6813e-05 | 1.6857e-05 | 0.054433 | 0.054433 | 0.054433 | 0.97893 | -0.40476 | 0.97973 | -0.3891 | 14.9541
8 | 0.00080785 | 0.00020222 | -0.00080784 | -0.00020246 | 1.1072e-08 | -2.4604e-07 | 0.0012194 | 0.0012195 | 0.0012195 | 0.98576 | -0.27192 | 0.98575 | -0.2722 | 0.33502
9 | -0.0019091 | -0.00047746 | 0.0019091 | 0.00047743 | 7.5088e-09 | -2.5945e-08 | 0.0028813 | 0.0028813 | 0.0028813 | 0.9858 | -0.2711 | 0.98581 | -0.27102 | 0.79158
10 | -0.036527 | -0.0091959 | 0.036562 | 0.0092178 | 3.4759e-05 | 2.1867e-05 | 0.055492 | 0.055492 | 0.055492 | 0.97973 | -0.3891 | 0.98074 | -0.36921 | 15.2451
11 | -0.069725 | -0.017725 | 0.069802 | 0.017773 | 7.6544e-05 | 4.8754e-05 | 0.10545 | 0.10545 | 0.10545 | 0.98471 | -0.29202 | 0.98589 | -0.26925 | 28.9706
12 | 0.069725 | 0.017725 | -0.069531 | -0.017601 | 0.00019443 | 0.00012385 | 0.10545 | 0.10545 | 0.10545 | 0.98471 | -0.29202 | 0.98171 | -0.35009 | 28.9706
13 | -0.07163 | -0.018232 | 0.071661 | 0.018252 | 3.1633e-05 | 2.0153e-05 | 0.10821 | 0.10821 | 0.10821 | 0.98589 | -0.26925 | 0.98637 | -0.2601 | 29.7285
14 | 0.069531 | 0.017601 | -0.069434 | -0.017539 | 9.6854e-05 | 6.1694e-05 | 0.10545 | 0.10545 | 0.10545 | 0.98171 | -0.35009 | 0.98022 | -0.37915 | 28.9707
15 | -0.03726 | -0.0093927 | 0.037324 | 0.009433 | 6.4151e-05 | 4.038e-05 | 0.056551 | 0.056551 | 0.056551 | 0.98074 | -0.36921 | 0.98259 | -0.3333 | 15.536
16 | -0.14603 | -0.036886 | 0.1462 | 0.036998 | 0.00017657 | 0.00011191 | 0.22124 | 0.22124 | 0.22124 | 0.98259 | -0.3333 | 0.98389 | -0.3081 | 20.2602
17 | 0.1087 | 0.027453 | -0.10867 | -0.027437 | 2.6533e-05 | 1.6684e-05 | 0.16469 | 0.16469 | 0.16469 | 0.98259 | -0.3333 | 0.98233 | -0.33839 | 15.0816
18 | -0.14742 | -0.037304 | 0.14743 | 0.03731 | 9.854e-06 | 6.2462e-06 | 0.22308 | 0.22308 | 0.22308 | 0.98389 | -0.3081 | 0.98396 | -0.30671 | 20.429
19 | 0.020714 | 0.0052034 | -0.020701 | -0.0051955 | 1.3103e-05 | 7.9371e-06 | 0.031381 | 0.031381 | 0.031381 | 0.98233 | -0.33839 | 0.98165 | -0.35166 | 8.6213
20 | 0.087961 | 0.022233 | -0.087845 | -0.022161 | 0.00011601 | 7.2268e-05 | 0.13331 | 0.13331 | 0.13331 | 0.98233 | -0.33839 | 0.98091 | -0.36594 | 12.2079
21 | -0.14904 | -0.037714 | 0.14937 | 0.037918 | 0.00032173 | 0.00020398 | 0.22552 | 0.22552 | 0.22552 | 0.98396 | -0.30671 | 0.98628 | -0.26183 | 20.6524
22 | 0.019696 | 0.0049438 | -0.019691 | -0.0049405 | 5.5485e-06 | 3.3413e-06 | 0.029859 | 0.029859 | 0.029859 | 0.98165 | -0.35166 | 0.98135 | -0.35756 | 8.2031
23 | 0.086862 | 0.021914 | -0.086825 | -0.021891 | 3.6973e-05 | 2.3018e-05 | 0.13182 | 0.13182 | 0.13182 | 0.98091 | -0.36594 | 0.98046 | -0.37483 | 12.0714
24 | 0.0081898 | 0.0020508 | -0.0081884 | -0.0020503 | 1.3765e-06 | 5.7418e-07 | 0.012355 | 0.012356 | 0.012356 | 0.98628 | -0.26183 | 0.9861 | -0.26536 | 3.3944
25 | -0.15756 | -0.039969 | 0.15763 | 0.040014 | 7.0996e-05 | 4.5053e-05 | 0.23788 | 0.23788 | 0.23788 | 0.98628 | -0.26183 | 0.98676 | -0.25247 | 21.7838
26 | 0.019691 | 0.0049405 | -0.019688 | -0.0049387 | 3.018e-06 | 1.8175e-06 | 0.029859 | 0.029859 | 0.029859 | 0.98135 | -0.35756 | 0.98118 | -0.36078 | 8.2031
27 | 0.084102 | 0.021209 | -0.084069 | -0.021188 | 3.3373e-05 | 2.074e-05 | 0.12769 | 0.12769 | 0.12769 | 0.98046 | -0.37483 | 0.98003 | -0.38312 | 11.693
28 | 0.058982 | 0.01492 | -0.058855 | -0.014839 | 0.00012644 | 8.0392e-05 | 0.089586 | 0.089586 | 0.089586 | 0.98022 | -0.37915 | 0.97793 | -0.42394 | 24.6117
29 | 0.051973 | 0.013114 | -0.051935 | -0.01309 | 3.8066e-05 | 2.4159e-05 | 0.079115 | 0.079115 | 0.079115 | 0.97793 | -0.42394 | 0.97714 | -0.43924 | 21.7348
30 | 0.0068822 | 0.0017249 | -0.0068809 | -0.0017245 | 1.241e-06 | 4.1569e-07 | 0.010472 | 0.010472 | 0.010472 | 0.97793 | -0.42394 | 0.97773 | -0.42772 | 2.877
31 | 0.051935 | 0.01309 | -0.051881 | -0.013056 | 5.4187e-05 | 3.4391e-05 | 0.079115 | 0.079115 | 0.079115 | 0.97714 | -0.43924 | 0.97603 | -0.46108 | 21.7348
32 | 0.048185 | 0.012129 | -0.048181 | -0.012127 | 4.5683e-06 | 2.8955e-06 | 0.073481 | 0.073481 | 0.073481 | 0.97603 | -0.46108 | 0.97593 | -0.46306 | 20.187
33 | -0.01601 | -0.004015 | 0.016017 | 0.0040192 | 7.0718e-06 | 4.1364e-06 | 0.024506 | 0.024505 | 0.024506 | 0.9722 | -0.53657 | 0.97267 | -0.52731 | 6.7323
34 | 0.01601 | 0.004015 | -0.016004 | -0.0040112 | 6.4923e-06 | 3.7977e-06 | 0.024506 | 0.024506 | 0.024506 | 0.9722 | -0.53657 | 0.97177 | -0.54509 | 6.7323
35 | -0.016017 | -0.0040192 | 0.016023 | 0.0040226 | 5.8913e-06 | 3.4456e-06 | 0.024505 | 0.024505 | 0.024505 | 0.97267 | -0.52731 | 0.97306 | -0.5196 | 6.7323
36 | 0.0091543 | 0.0022946 | -0.0091514 | -0.0022933 | 2.9083e-06 | 1.3725e-06 | 0.014018 | 0.014018 | 0.014018 | 0.97177 | -0.54509 | 0.97143 | -0.55175 | 3.8511
37 | 0.048181 | 0.012127 | -0.048161 | -0.012114 | 1.9701e-05 | 1.2487e-05 | 0.073481 | 0.073481 | 0.073481 | 0.97593 | -0.46306 | 0.97549 | -0.47162 | 20.187
38 | 0.02441 | 0.0061317 | -0.024378 | -0.0061122 | 3.179e-05 | 1.9549e-05 | 0.036829 | 0.03683 | 0.03683 | 0.98637 | -0.2601 | 0.98496 | -0.28742 | 10.118
39 | -0.096071 | -0.024383 | 0.096241 | 0.024492 | 0.00016974 | 0.00010836 | 0.14504 | 0.14504 | 0.14504 | 0.98637 | -0.2601 | 0.98827 | -0.22344 | 39.8464
40 | 0.0074744 | 0.0018713 | -0.0074743 | -0.0018713 | 1.2674e-07 | 4.7219e-08 | 0.011278 | 0.011278 | 0.011278 | 0.9861 | -0.26536 | 0.98608 | -0.26572 | 3.0984
41 | -0.16037 | -0.040703 | 0.16052 | 0.040797 | 0.00014847 | 9.4241e-05 | 0.24202 | 0.24202 | 0.24202 | 0.98676 | -0.25247 | 0.98776 | -0.23324 | 22.1633
42 | 0.0067991 | 0.0017021 | -0.0067984 | -0.0017018 | 7.7611e-07 | 2.4591e-07 | 0.010259 | 0.010259 | 0.010259 | 0.98608 | -0.26572 | 0.98596 | -0.26812 | 2.8185
43 | 0.012783 | 0.003209 | -0.012777 | -0.003206 | 5.4861e-06 | 3.0065e-06 | 0.019259 | 0.019259 | 0.019259 | 0.98776 | -0.23324 | 0.9873 | -0.24224 | 5.2909
44 | -0.17331 | -0.044006 | 0.17336 | 0.044044 | 5.9342e-05 | 3.7712e-05 | 0.26128 | 0.26128 | 0.26128 | 0.98776 | -0.23324 | 0.98813 | -0.22613 | 23.9268
45 | 0.017341 | 0.0043505 | -0.017334 | -0.0043465 | 6.6673e-06 | 3.9425e-06 | 0.0263 | 0.0263 | 0.0263 | 0.98118 | -0.36078 | 0.98077 | -0.36885 | 7.2253
46 | 0.015018 | 0.0037661 | -0.015016 | -0.0037645 | 2.7275e-06 | 1.5689e-06 | 0.022786 | 0.022786 | 0.022786 | 0.98077 | -0.36885 | 0.98058 | -0.37266 | 6.26
47 | 0.01351 | 0.0033873 | -0.013509 | -0.0033865 | 1.456e-06 | 8.1531e-07 | 0.020502 | 0.020502 | 0.020502 | 0.98058 | -0.37266 | 0.98046 | -0.37492 | 5.6325
48 | 0.011194 | 0.0028063 | -0.011191 | -0.0028047 | 3.1369e-06 | 1.6422e-06 | 0.016989 | 0.016989 | 0.016989 | 0.98046 | -0.37492 | 0.98016 | -0.3808 | 4.6674
49 | 0.007728 | 0.0019368 | -0.0077269 | -0.0019363 | 1.1146e-06 | 4.412e-07 | 0.011732 | 0.011732 | 0.011732 | 0.98016 | -0.3808 | 0.98001 | -0.38383 | 3.2231
50 | 0.0077269 | 0.0019363 | -0.0077262 | -0.0019361 | 6.4903e-07 | 2.5696e-07 | 0.011732 | 0.011732 | 0.011732 | 0.98001 | -0.38383 | 0.97992 | -0.38559 | 3.2231
51 | 0.0052855 | 0.0013244 | -0.0052855 | -0.0013244 | 6.0708e-08 | 7.1942e-09 | 0.008026 | 0.008026 | 0.008026 | 0.97992 | -0.38559 | 0.9799 | -0.38583 | 2.205
52 | 0.0026858 | 0.00067281 | -0.0026857 | -0.00067284 | 2.1834e-08 | -3.0124e-08 | 0.0040783 | 0.0040783 | 0.0040783 | 0.9799 | -0.38583 | 0.9799 | -0.38601 | 1.1204
53 | 0.0026857 | 0.00067284 | -0.0026856 | -0.00067307 | 1.6582e-07 | -2.2873e-07 | 0.0040783 | 0.0040785 | 0.0040785 | 0.9799 | -0.38601 | 0.97983 | -0.3873 | 1.1205
54 | 0.0029796 | 0.00074624 | -0.0029795 | -0.00074637 | 1.1857e-07 | -1.2353e-07 | 0.0044967 | 0.0044968 | 0.0044968 | 0.98596 | -0.26812 | 0.98591 | -0.26895 | 1.2354
55 | 0.0038187 | 0.00095556 | -0.0038186 | -0.00095559 | 6.336e-08 | -2.4335e-08 | 0.0057627 | 0.0057627 | 0.0057627 | 0.98596 | -0.26812 | 0.98594 | -0.26847 | 1.5832
56 | 0.012777 | 0.003206 | -0.012771 | -0.0032025 | 6.3662e-06 | 3.4894e-06 | 0.019259 | 0.019259 | 0.019259 | 0.9873 | -0.24224 | 0.98676 | -0.2527 | 5.2909
57 | 0.0048801 | 0.0012229 | -0.0048795 | -0.0012229 | 5.6711e-07 | 4.2968e-09 | 0.0073488 | 0.007349 | 0.007349 | 0.98813 | -0.22613 | 0.988 | -0.22857 | 2.0189
58 | -0.17824 | -0.045267 | 0.17843 | 0.045383 | 0.00018356 | 0.0001167 | 0.26863 | 0.26863 | 0.26863 | 0.98813 | -0.22613 | 0.98924 | -0.20475 | 24.5998
59 | 0.08215 | 0.020707 | -0.082103 | -0.020678 | 4.713e-05 | 2.9248e-05 | 0.12477 | 0.12477 | 0.12477 | 0.98003 | -0.38312 | 0.97942 | -0.39512 | 11.4262
60 | 0.080482 | 0.020272 | -0.080473 | -0.020266 | 9.4212e-06 | 5.8394e-06 | 0.12231 | 0.12231 | 0.12231 | 0.97942 | -0.39512 | 0.97929 | -0.39757 | 11.2007
61 | 0.07928 | 0.019967 | -0.079273 | -0.019963 | 7.0716e-06 | 4.3788e-06 | 0.1205 | 0.1205 | 0.1205 | 0.97929 | -0.39757 | 0.9792 | -0.39943 | 11.0347
62 | 0.077811 | 0.019596 | -0.077779 | -0.019577 | 3.1718e-05 | 1.9615e-05 | 0.11828 | 0.11828 | 0.11828 | 0.9792 | -0.39943 | 0.97876 | -0.40796 | 10.8313
63 | 0.07646 | 0.019246 | -0.076458 | -0.019245 | 1.42e-06 | 8.7712e-07 | 0.11627 | 0.11627 | 0.11627 | 0.97876 | -0.40796 | 0.97874 | -0.40835 | 10.6477
64 | 0.074839 | 0.018839 | -0.074784 | -0.018805 | 5.5219e-05 | 3.4055e-05 | 0.11381 | 0.11381 | 0.11381 | 0.97874 | -0.40835 | 0.97795 | -0.4238 | 10.4222
65 | 0.072512 | 0.018236 | -0.072506 | -0.018232 | 6.091e-06 | 3.7477e-06 | 0.11035 | 0.11035 | 0.11035 | 0.97795 | -0.4238 | 0.97786 | -0.42556 | 10.1056
66 | 0.070581 | 0.01775 | -0.070567 | -0.017741 | 1.3709e-05 | 8.4162e-06 | 0.10743 | 0.10743 | 0.10743 | 0.97786 | -0.42556 | 0.97766 | -0.42963 | 9.8375
67 | -0.068122 | -0.017127 | 0.068126 | 0.017129 | 4.1498e-06 | 2.5398e-06 | 0.10371 | 0.10371 | 0.10371 | 0.97759 | -0.4309 | 0.97766 | -0.42963 | 9.4972
68 | 0.065682 | 0.016515 | -0.065667 | -0.016507 | 1.4732e-05 | 8.9855e-06 | 0.099996 | 0.099996 | 0.099996 | 0.97759 | -0.4309 | 0.97735 | -0.4356 | 9.1571
69 | 0.06233 | 0.01567 | -0.062312 | -0.015659 | 1.8518e-05 | 1.1233e-05 | 0.094915 | 0.094916 | 0.094916 | 0.97735 | -0.4356 | 0.97703 | -0.44182 | 8.6919
70 | 0.05987 | 0.015047 | -0.059855 | -0.015038 | 1.5383e-05 | 9.2892e-06 | 0.091197 | 0.091197 | 0.091197 | 0.97703 | -0.44182 | 0.97676 | -0.44721 | 8.3514
71 | 0.059855 | 0.015038 | -0.059848 | -0.015034 | 6.5173e-06 | 3.9357e-06 | 0.091197 | 0.091197 | 0.091197 | 0.97676 | -0.44721 | 0.97664 | -0.44949 | 8.3514
72 | 0.0065256 | 0.0016355 | -0.0065241 | -0.0016351 | 1.5141e-06 | 4.5805e-07 | 0.0099424 | 0.0099426 | 0.0099426 | 0.97664 | -0.44949 | 0.9764 | -0.45436 | 2.7315
73 | 0.053323 | 0.013398 | -0.053267 | -0.013365 | 5.5956e-05 | 3.3269e-05 | 0.081255 | 0.081256 | 0.081256 | 0.97664 | -0.44949 | 0.97552 | -0.4715 | 7.441
74 | 0.0050315 | 0.0012608 | -0.0050306 | -0.0012608 | 9.1412e-07 | 6.8456e-08 | 0.0076747 | 0.0076749 | 0.0076749 | 0.97552 | -0.4715 | 0.97533 | -0.47531 | 2.1085
75 | 0.005991 | 0.0015015 | -0.0059904 | -0.0015013 | 5.5324e-07 | 1.3353e-07 | 0.0091383 | 0.0091384 | 0.0091384 | 0.97552 | -0.4715 | 0.97543 | -0.47343 | 2.5105
76 | 0.042244 | 0.010603 | -0.042204 | -0.01058 | 3.9824e-05 | 2.2617e-05 | 0.064443 | 0.064444 | 0.064444 | 0.97552 | -0.4715 | 0.97452 | -0.49128 | 5.9014
77 | 0.0044499 | 0.0011151 | -0.0044494 | -0.0011151 | 4.2894e-07 | -3.414e-08 | 0.0067946 | 0.0067947 | 0.0067947 | 0.97452 | -0.49128 | 0.97442 | -0.4933 | 1.8667
78 | 0.037754 | 0.0094649 | -0.037739 | -0.0094565 | 1.5327e-05 | 8.4306e-06 | 0.057649 | 0.05765 | 0.05765 | 0.97452 | -0.49128 | 0.97409 | -0.4998 | 5.2793
79 | 0.010386 | 0.0026023 | -0.010386 | -0.0026025 | 4.1113e-07 | -2.248e-07 | 0.015866 | 0.015866 | 0.015866 | 0.97409 | -0.4998 | 0.97405 | -0.50063 | 1.4529
80 | 0.022951 | 0.0057511 | -0.022946 | -0.0057489 | 5.6526e-06 | 2.2442e-06 | 0.03506 | 0.03506 | 0.03506 | 0.97409 | -0.4998 | 0.97383 | -0.50497 | 3.2107
81 | 0.0044017 | 0.0011031 | -0.0044015 | -0.0011031 | 2.275e-07 | -2.1423e-08 | 0.006724 | 0.006724 | 0.006724 | 0.97409 | -0.4998 | 0.97403 | -0.50089 | 1.8473
82 | 0.0020988 | 0.0005259 | -0.0020987 | -0.00052599 | 3.3973e-08 | -8.7952e-08 | 0.0032062 | 0.0032062 | 0.0032062 | 0.97405 | -0.50063 | 0.97403 | -0.50097 | 0.88082
83 | 0.0082871 | 0.0020766 | -0.0082865 | -0.0020767 | 5.6079e-07 | -1.0562e-07 | 0.01266 | 0.01266 | 0.01266 | 0.97405 | -0.50063 | 0.97397 | -0.50206 | 1.739
84 | 0.0020461 | 0.0005125 | -0.002046 | -0.00051277 | 9.7956e-08 | -2.6979e-07 | 0.0031263 | 0.0031264 | 0.0031264 | 0.97383 | -0.50497 | 0.97378 | -0.50598 | 0.85891
85 | 0.016714 | 0.0041876 | -0.016708 | -0.0041866 | 5.4513e-06 | 9.9409e-07 | 0.025538 | 0.025539 | 0.025539 | 0.97383 | -0.50497 | 0.97348 | -0.51182 | 2.3388
86 | 0.0041856 | 0.0010488 | -0.0041853 | -0.0010489 | 2.7614e-07 | -4.7238e-08 | 0.0063955 | 0.0063956 | 0.0063956 | 0.97383 | -0.50497 | 0.97376 | -0.50636 | 1.757
87 | 0.0021675 | 0.0005432 | -0.0021675 | -0.00054323 | 1.4053e-08 | -3.3547e-08 | 0.0033113 | 0.0033113 | 0.0033113 | 0.97403 | -0.50089 | 0.97403 | -0.50102 | 0.9097
88 | 0.0043141 | 0.0010812 | -0.0043141 | -0.0010812 | 1.601e-08 | -2.0529e-09 | 0.0065819 | 0.0065819 | 0.0065819 | 0.97533 | -0.47531 | 0.97533 | -0.47539 | 1.8082
89 | 0.0052318 | 0.0013112 | -0.0052318 | -0.0013112 | 2.4678e-08 | 2.8984e-09 | 0.0079812 | 0.0079812 | 0.0079812 | 0.97543 | -0.47343 | 0.97542 | -0.47353 | 2.1926
90 | -0.0070311 | -0.0017622 | 0.0070328 | 0.0017627 | 1.6933e-06 | 5.726e-07 | 0.010614 | 0.010614 | 0.010614 | 0.98573 | -0.27273 | 0.98599 | -0.26768 | 2.9159
91 | -0.0089433 | -0.0022415 | 0.008945 | 0.0022423 | 1.7806e-06 | 8.0707e-07 | 0.013497 | 0.013497 | 0.013497 | 0.98599 | -0.26768 | 0.98621 | -0.2635 | 3.7079
92 | 0.0062055 | 0.0015552 | -0.0062054 | -0.0015551 | 1.6001e-07 | 4.3327e-08 | 0.0094807 | 0.0094807 | 0.0094807 | 0.97397 | -0.50206 | 0.97395 | -0.5026 | 2.6046
93 | 0.008255 | 0.002068 | -0.0082548 | -0.0020683 | 2.2829e-07 | -2.8172e-07 | 0.012618 | 0.012618 | 0.012618 | 0.97348 | -0.51182 | 0.97345 | -0.5124 | 1.1555
94 | 0.0084534 | 0.0021186 | -0.0084533 | -0.0021186 | 8.0362e-08 | -1.2397e-08 | 0.012921 | 0.012921 | 0.012921 | 0.97348 | -0.51182 | 0.97347 | -0.51202 | 1.7749
95 | 0.0020791 | 0.00052104 | -0.0020791 | -0.00052108 | 1.5988e-08 | -4.2307e-08 | 0.0031772 | 0.0031772 | 0.0031772 | 0.97376 | -0.50636 | 0.97375 | -0.50652 | 0.87285
96 | 0.0020811 | 0.00052141 | -0.0020811 | -0.00052156 | 5.1799e-09 | -1.4941e-07 | 0.0031811 | 0.0031811 | 0.0031811 | 0.97345 | -0.5124 | 0.97345 | -0.51246 | 0.29131
97 | 0.0061737 | 0.0015469 | -0.0061737 | -0.001547 | 4.2064e-08 | -1.14e-07 | 0.009437 | 0.0094371 | 0.0094371 | 0.97345 | -0.5124 | 0.97344 | -0.51255 | 0.8642
98 | 0.0040997 | 0.0010274 | -0.0040995 | -0.0010274 | 1.6949e-07 | -3.4889e-08 | 0.0062635 | 0.0062636 | 0.0062636 | 0.97395 | -0.5026 | 0.9739 | -0.50346 | 1.7208
99 | 0.004162 | 0.0010428 | -0.0041619 | -0.001043 | 8.0649e-08 | -2.126e-07 | 0.006362 | 0.0063621 | 0.0063621 | 0.97344 | -0.51255 | 0.97342 | -0.51295 | 0.87391
100 | 0.002081 | 0.00052146 | -0.0020809 | -0.00052153 | 2.7567e-08 | -7.2666e-08 | 0.003181 | 0.0031811 | 0.0031811 | 0.97342 | -0.51295 | 0.97341 | -0.51323 | 0.87392
101 | 0.0045762 | 0.0011466 | -0.0045758 | -0.0011466 | 4.4959e-07 | -1.4306e-08 | 0.0070097 | 0.0070098 | 0.0070098 | 0.97143 | -0.55175 | 0.97133 | -0.55382 | 1.9258
102 | 0.0045758 | 0.0011466 | -0.0045756 | -0.0011466 | 1.6873e-07 | -5.3498e-09 | 0.0070098 | 0.0070098 | 0.0070098 | 0.97133 | -0.55382 | 0.97129 | -0.55459 | 1.9258
103 | 0.0045756 | 0.0011466 | -0.0045752 | -0.0011466 | 4.5389e-07 | -1.4339e-08 | 0.0070098 | 0.0070099 | 0.0070099 | 0.97129 | -0.55459 | 0.97118 | -0.55667 | 1.9258
104 | -0.02052 | -0.0051497 | 0.020522 | 0.0051509 | 2.0812e-06 | 1.262e-06 | 0.031382 | 0.031382 | 0.031382 | 0.97306 | -0.5196 | 0.97316 | -0.51747 | 8.6215
105 | 0.015836 | 0.0039711 | -0.015831 | -0.0039681 | 5.1174e-06 | 2.9861e-06 | 0.024215 | 0.024215 | 0.024215 | 0.97316 | -0.51747 | 0.97282 | -0.52426 | 6.6525
106 | -0.036358 | -0.009122 | 0.036373 | 0.0091312 | 1.468e-05 | 9.238e-06 | 0.055597 | 0.055597 | 0.055597 | 0.97316 | -0.51747 | 0.97359 | -0.50901 | 15.274
107 | 0.10656 | 0.027091 | -0.10652 | -0.027069 | 3.4315e-05 | 2.1779e-05 | 0.16052 | 0.16052 | 0.16052 | 0.98862 | -0.21675 | 0.98827 | -0.22344 | 22.0501
108 | -0.11152 | -0.028335 | 0.11158 | 0.028372 | 5.9234e-05 | 3.7264e-05 | 0.168 | 0.168 | 0.168 | 0.98862 | -0.21675 | 0.98919 | -0.20573 | 15.3843
109 | -0.1165 | -0.029604 | 0.11655 | 0.029636 | 5.0119e-05 | 3.1574e-05 | 0.17539 | 0.17539 | 0.17539 | 0.98919 | -0.20573 | 0.98966 | -0.19679 | 16.0613
110 | -0.1198 | -0.03045 | 0.11998 | 0.030563 | 0.00017892 | 0.00011281 | 0.18028 | 0.18028 | 0.18028 | 0.98966 | -0.19679 | 0.99127 | -0.16583 | 16.5088
111 | 0.024378 | 0.0061122 | -0.02437 | -0.0061074 | 7.6831e-06 | 4.725e-06 | 0.03683 | 0.03683 | 0.03683 | 0.98496 | -0.28742 | 0.98463 | -0.29404 | 10.118
112 | -0.13815 | -0.03512 | 0.13824 | 0.035173 | 8.3024e-05 | 5.2539e-05 | 0.20756 | 0.20756 | 0.20756 | 0.99127 | -0.16583 | 0.99192 | -0.15336 | 19.0075
113 | 0.018177 | 0.0045572 | -0.018175 | -0.0045558 | 2.312e-06 | 1.373e-06 | 0.027287 | 0.027287 | 0.027287 | 0.99127 | -0.16583 | 0.99113 | -0.1685 | 7.4963
114 | 0.0035665 | 0.00089349 | -0.0035663 | -0.00089361 | 2.3312e-07 | -1.2296e-07 | 0.0053898 | 0.0053899 | 0.0053899 | 0.98463 | -0.29404 | 0.98456 | -0.29541 | 1.4807
115 | 0.0035663 | 0.00089361 | -0.003566 | -0.00089373 | 2.3178e-07 | -1.2221e-07 | 0.0053899 | 0.0053899 | 0.0053899 | 0.98456 | -0.29541 | 0.98449 | -0.29678 | 1.4808
116 | -0.3525 | -0.089731 | 0.35459 | 0.091066 | 0.0020891 | 0.0013347 | 0.52929 | 0.52929 | 0.52929 | 0.99192 | -0.15336 | 0.99834 | -0.031233 | 48.4698
117 | 0.1967 | 0.050153 | -0.19621 | -0.049844 | 0.00048669 | 0.00030976 | 0.29538 | 0.29538 | 0.29538 | 0.99192 | -0.15336 | 0.98924 | -0.20475 | 27.0492
118 | 0.017566 | 0.0044054 | -0.017559 | -0.0044017 | 6.2586e-06 | 3.6954e-06 | 0.026352 | 0.026352 | 0.026352 | 0.99192 | -0.15336 | 0.99154 | -0.16084 | 7.2395
119 | 0.013974 | 0.0035032 | -0.013972 | -0.0035016 | 2.7037e-06 | 1.5193e-06 | 0.020981 | 0.020981 | 0.020981 | 0.99113 | -0.1685 | 0.99092 | -0.17256 | 5.7639
120 | 0.044003 | 0.011072 | -0.043959 | -0.011044 | 4.4027e-05 | 2.7852e-05 | 0.067138 | 0.067138 | 0.067138 | 0.97549 | -0.47162 | 0.97443 | -0.49258 | 18.4445
121 | -0.0032731 | -0.00082031 | 0.0032733 | 0.00082014 | 2.5137e-07 | -1.7061e-07 | 0.0050087 | 0.0050086 | 0.0050087 | 0.97239 | -0.53283 | 0.97247 | -0.53122 | 1.376
122 | -0.0077191 | -0.0019344 | 0.0077204 | 0.0019349 | 1.257e-06 | 5.063e-07 | 0.011811 | 0.011811 | 0.011811 | 0.97247 | -0.53122 | 0.97264 | -0.5278 | 3.2448
123 | 0.039208 | 0.0098535 | -0.039178 | -0.0098341 | 3.0723e-05 | 1.9379e-05 | 0.059884 | 0.059884 | 0.059884 | 0.97443 | -0.49258 | 0.97359 | -0.50901 | 16.4516
124 | -0.010727 | -0.0026884 | 0.010729 | 0.0026892 | 1.5089e-06 | 7.8022e-07 | 0.016411 | 0.016411 | 0.016411 | 0.97264 | -0.5278 | 0.97279 | -0.52485 | 4.5086
125 | 0.012034 | 0.003015 | -0.012033 | -0.0030149 | 2.5394e-07 | 1.3499e-07 | 0.017936 | 0.017936 | 0.017936 | 0.99834 | -0.031233 | 0.99832 | -0.031676 | 4.9274
126 | -0.36662 | -0.094081 | 0.36718 | 0.094437 | 0.00055654 | 0.0003556 | 0.54722 | 0.54722 | 0.54722 | 0.99834 | -0.031233 | 1 | 0 | 50.1121
127 | 0.017782 | 0.0044602 | -0.017775 | -0.0044561 | 7.0425e-06 | 4.1704e-06 | 0.026748 | 0.026748 | 0.026748 | 0.98924 | -0.20475 | 0.98881 | -0.21307 | 7.3485
128 | 0.012089 | 0.0030307 | -0.012086 | -0.003029 | 3.1243e-06 | 1.6732e-06 | 0.018142 | 0.018143 | 0.018143 | 0.99154 | -0.16084 | 0.99126 | -0.16627 | 4.9842
129 | 0.01017 | 0.0025489 | -0.010169 | -0.0025485 | 7.8196e-07 | 3.8529e-07 | 0.015272 | 0.015272 | 0.015272 | 0.99092 | -0.17256 | 0.99084 | -0.17418 | 4.1956
130 | 0.004064 | 0.0010184 | -0.0040638 | -0.0010185 | 2.2543e-07 | -6.9924e-08 | 0.0060575 | 0.0060575 | 0.0060575 | 0.99832 | -0.031676 | 0.99826 | -0.032841 | 1.6642
131 | 0.0079695 | 0.0019965 | -0.0079682 | -0.001996 | 1.2813e-06 | 5.0347e-07 | 0.011878 | 0.011878 | 0.011878 | 0.99832 | -0.031676 | 0.99815 | -0.035053 | 3.2633
132 | 0.012871 | 0.0032272 | -0.012867 | -0.0032247 | 4.547e-06 | 2.4957e-06 | 0.01937 | 0.01937 | 0.01937 | 0.98881 | -0.21307 | 0.98843 | -0.22048 | 5.3214
133 | 0.0064439 | 0.0016148 | -0.0064426 | -0.0016144 | 1.3185e-06 | 3.6036e-07 | 0.0096772 | 0.0096773 | 0.0096773 | 0.99084 | -0.17418 | 0.99062 | -0.17847 | 2.6586
134 | 0.0014897 | 0.00037316 | -0.0014896 | -0.00037334 | 2.8023e-08 | -1.8012e-07 | 0.0022207 | 0.0022208 | 0.0022208 | 0.99815 | -0.035053 | 0.99813 | -0.035448 | 0.6101
135 | 0.0064785 | 0.0016228 | -0.0064783 | -0.0016228 | 2.3742e-07 | 6.3232e-08 | 0.0096577 | 0.0096578 | 0.0096578 | 0.99815 | -0.035053 | 0.99811 | -0.035822 | 2.6532
136 | -0.010729 | -0.0026892 | 0.010729 | 0.0026894 | 3.0288e-07 | 1.5661e-07 | 0.016411 | 0.016411 | 0.016411 | 0.97279 | -0.52485 | 0.97282 | -0.52426 | 4.5085
137 | 0.0026893 | 0.00067377 | -0.0026892 | -0.00067397 | 1.3958e-07 | -2.043e-07 | 0.0040395 | 0.0040396 | 0.0040396 | 0.99062 | -0.17847 | 0.99056 | -0.17956 | 1.1098
138 | -0.0010363 | -0.00025973 | 0.0010363 | 0.00025949 | 1.7267e-08 | -2.41e-07 | 0.0015451 | 0.001545 | 0.0015451 | 0.99803 | -0.037348 | 0.99805 | -0.036998 | 0.42448
139 | 0.0012479 | 0.00031258 | -0.0012479 | -0.00031275 | 1.7653e-08 | -1.6642e-07 | 0.0018605 | 0.0018605 | 0.0018605 | 0.99805 | -0.036998 | 0.99803 | -0.037295 | 0.51113
140 | -0.0022842 | -0.00057207 | 0.0022844 | 0.00057176 | 1.2786e-07 | -3.0241e-07 | 0.0034055 | 0.0034053 | 0.0034055 | 0.99805 | -0.036998 | 0.99811 | -0.035822 | 0.93557
141 | 0.0041939 | 0.001051 | -0.0041938 | -0.0010511 | 1.6743e-07 | -4.2106e-08 | 0.0062524 | 0.0062525 | 0.0062525 | 0.99811 | -0.035822 | 0.99806 | -0.03666 | 1.7177
142 | -0.008945 | -0.0022423 | 0.0089462 | 0.0022429 | 1.1764e-06 | 5.3313e-07 | 0.013497 | 0.013497 | 0.013497 | 0.98621 | -0.2635 | 0.98635 | -0.26074 | 3.7079
143 | -0.010857 | -0.0027216 | 0.010861 | 0.0027238 | 4.1611e-06 | 2.1349e-06 | 0.016379 | 0.016378 | 0.016379 | 0.98635 | -0.26074 | 0.98676 | -0.2527 | 4.4996
144 | -0.0023518 | -0.00058941 | 0.0023519 | 0.00058925 | 7.8544e-08 | -1.6168e-07 | 0.0035498 | 0.0035497 | 0.0035498 | 0.98584 | -0.27039 | 0.98588 | -0.26969 | 0.97521
145 | -0.0023519 | -0.00058925 | 0.0023519 | 0.00058908 | 8.2223e-08 | -1.6928e-07 | 0.0035497 | 0.0035496 | 0.0035497 | 0.98588 | -0.26969 | 0.98591 | -0.26895 | 0.97519
146 | -0.0027168 | -0.00067985 | 0.0027168 | 0.0006798 | 3.8812e-08 | -5.3642e-08 | 0.0041005 | 0.0041004 | 0.0041005 | 0.98581 | -0.27102 | 0.98582 | -0.27071 | 1.1265
147 | -0.003098 | -0.00077534 | 0.0030982 | 0.00077519 | 1.6432e-07 | -1.5039e-07 | 0.0046759 | 0.0046758 | 0.0046759 | 0.98582 | -0.27071 | 0.98588 | -0.2696 | 1.2846
148 | -0.0034582 | -0.00086542 | 0.0034584 | 0.0008653 | 1.8644e-07 | -1.1343e-07 | 0.0052191 | 0.005219 | 0.0052191 | 0.98588 | -0.2696 | 0.98594 | -0.26847 | 1.4338

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3737 | 0.095658

## res_load
| p_mw | q_mvar
0 | 0.034604 | 0.0086726
1 | 0.00036 | 9.0224e-05
2 | 0.00038121 | 9.5541e-05
3 | 0.00069763 | 0.00017484
4 | 0.00041792 | 0.00010474
5 | 0.00036 | 9.0224e-05
6 | 0.00069763 | 0.00017484
7 | 0.001828 | 0.00045814
8 | 0.00080784 | 0.00020246
9 | 0.00069788 | 0.0001749
10 | 0.001219 | 0.00030552
11 | 0.0016133 | 0.00040433
12 | 0.0010042 | 0.00025168
13 | 0.00098316 | 0.0002464
14 | 0.0027226 | 0.00068235
15 | 0.010452 | 0.0026196
16 | 0.0068809 | 0.0017245
17 | 0.0036956 | 0.0009262
18 | 0.0068493 | 0.0017166
19 | 0.00071395 | 0.00017893
20 | 0.0027478 | 0.00068866
21 | 0.00067518 | 0.00016922
22 | 0.002347 | 0.00058821
23 | 0.002316 | 0.00058045
24 | 0.0015051 | 0.00037722
25 | 0.0023148 | 0.00058014
26 | 0.0034631 | 0.00086793
27 | 0.0024407 | 0.0006117
28 | 0.0025997 | 0.00065154
29 | 0.0026856 | 0.00067307
30 | 0.0019191 | 0.00048097
31 | 0.0016207 | 0.00040618
32 | 0.0011928 | 0.00029893
33 | 0.0014619 | 0.0003664
34 | 0.0013193 | 0.00033065
35 | 0.0016195 | 0.00040589
36 | 0.002272 | 0.00056942
37 | 0.0019245 | 0.00048233
38 | 0.0024395 | 0.00061141
39 | 0.0024416 | 0.00061193
40 | 0.003337 | 0.00083632
41 | 0.0024418 | 0.00061197
42 | 0.0065241 | 0.0016351
43 | 0.0044494 | 0.0011151
44 | 0.0022339 | 0.00055988
45 | 0.00071644 | 0.00017956
46 | 0.00075856 | 0.00019011
47 | 0.0070311 | 0.0017622
48 | 0.0019104 | 0.0004788
49 | 0.0021675 | 0.00054323
50 | 0.0020987 | 0.00052599
51 | 0.002081 | 0.00052154
52 | 0.002046 | 0.00051277
53 | 0.0021061 | 0.00052785
54 | 0.0084533 | 0.0021186
55 | 0.0021057 | 0.00052775
56 | 0.0020791 | 0.00052108
57 | 0.0043141 | 0.0010812
58 | 0.0052318 | 0.0013112
59 | 0.0020811 | 0.00052156
60 | 0.0020117 | 0.00050418
61 | 0.002081 | 0.00052154
62 | 0.0020809 | 0.00052153
63 | 0.0040995 | 0.0010274
64 | 0.0045752 | 0.0011466
65 | 0.0045752 | 0.0011466
66 | 0.004497 | 0.001127
67 | 0.0049642 | 0.0012442
68 | 0.010284 | 0.0025774
69 | 0.0049145 | 0.0012317
70 | 0.0032501 | 0.00081454
71 | 0.020804 | 0.0052139
72 | 0.003566 | 0.00089373
73 | 0.0042003 | 0.0010527
74 | 0.0041582 | 0.0010421
75 | 0.0032731 | 0.00082031
76 | 0.0044458 | 0.0011142
77 | 0.0047505 | 0.0011906
78 | 0.0030068 | 0.00075357
79 | 0.0028046 | 0.00070289
80 | 0.0054704 | 0.001371
81 | 0.0038017 | 0.00095279
82 | 0.0048707 | 0.0012207
83 | 0.0049032 | 0.0012289
84 | 0.012086 | 0.003029
85 | 0.0037255 | 0.00093369
86 | 0.012867 | 0.0032247
87 | 0.0048795 | 0.0012229
88 | 0.0040638 | 0.0010185
89 | 0.0051022 | 0.0012787
90 | 0.0037533 | 0.00094066
91 | 0.0026892 | 0.00067397
92 | 0.0010363 | 0.00025973
93 | 0.0012479 | 0.00031275
94 | 0.0041938 | 0.0010511
95 | 0.0014896 | 0.00037334
96 | 0.0019103 | 0.00047877
97 | 0.0019103 | 0.00047876
98 | 0.0023518 | 0.00058941
99 | 0.00080768 | 0.00020242
100 | 0.00062758 | 0.00015729
101 | 0.00038121 | 9.5541e-05
102 | 0.00036 | 9.0224e-05
103 | 0.00036025 | 9.0287e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1