## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_136-1_1_2_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_136-1_1_2_node_8 | 0.4 | n |  | TRUE
2 | bus_LV_136-1_1_2_node_48 | 0.4 | n |  | TRUE
3 | bus_LV_136-1_1_2_node_49 | 0.4 | n |  | TRUE
4 | bus_LV_136-1_1_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_136-1_1_2_node_74 | 0.4 | n |  | TRUE
6 | bus_LV_136-1_1_2_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_136-1_1_2_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_136-1_1_2_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_136-1_1_2_node_68 | 0.4 | n |  | TRUE
10 | bus_LV_136-1_1_2_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_136-1_1_2_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_136-1_1_2_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_136-1_1_2_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_136-1_1_2_node_60 | 0.4 | n |  | TRUE
15 | bus_LV_136-1_1_2_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_136-1_1_2_node_50 | 0.4 | n |  | TRUE
17 | bus_LV_136-1_1_2_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_136-1_1_2_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_136-1_1_2_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_136-1_1_2_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_136-1_1_2_node_69 | 0.4 | n |  | TRUE
22 | bus_LV_136-1_1_2_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_136-1_1_2_node_54 | 0.4 | n |  | TRUE
24 | bus_LV_136-1_1_2_node_59 | 0.4 | n |  | TRUE
25 | bus_LV_136-1_1_2_node_57 | 0.4 | n |  | TRUE
26 | bus_LV_136-1_1_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_136-1_1_2_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_136-1_1_2_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_136-1_1_2_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_136-1_1_2_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_136-1_1_2_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_136-1_1_2_node_65 | 0.4 | n |  | TRUE
33 | bus_LV_136-1_1_2_node_67 | 0.4 | n |  | TRUE
34 | bus_LV_136-1_1_2_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_136-1_1_2_node_73 | 0.4 | n |  | TRUE
36 | bus_LV_136-1_1_2_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_136-1_1_2_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_136-1_1_2_node_84 | 0.4 | n |  | TRUE
39 | bus_LV_136-1_1_2_node_82 | 0.4 | n |  | TRUE
40 | bus_LV_136-1_1_2_node_81 | 0.4 | n |  | TRUE
41 | bus_LV_136-1_1_2_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_136-1_1_2_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_136-1_1_2_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_136-1_1_2_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_136-1_1_2_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_136-1_1_2_node_89 | 0.4 | n |  | TRUE
47 | bus_LV_136-1_1_2_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_136-1_1_2_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_136-1_1_2_node_95 | 0.4 | n |  | TRUE
50 | bus_LV_136-1_1_2_node_86 | 0.4 | n |  | TRUE
51 | bus_LV_136-1_1_2_node_79 | 0.4 | n |  | TRUE
52 | bus_LV_136-1_1_2_node_80 | 0.4 | n |  | TRUE
53 | bus_LV_136-1_1_2_node_93 | 0.4 | n |  | TRUE
54 | bus_LV_136-1_1_2_node_91 | 0.4 | n |  | TRUE
55 | bus_LV_136-1_1_2_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_136-1_1_2_node_90 | 0.4 | n |  | TRUE
57 | bus_LV_136-1_1_2_node_92 | 0.4 | n |  | TRUE
58 | bus_LV_136-1_1_2_node_94 | 0.4 | n |  | TRUE
59 | bus_MV_349_2_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_136-1_1_2_load_48 | 2 | 0.0018665 | 0.00046779 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_136-1_1_2_load_49 | 3 | 0.002701 | 0.00067693 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_136-1_1_2_load_74 | 5 | 0.0067481 | 0.0016912 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_136-1_1_2_load_71 | 6 | 0.015574 | 0.0039031 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_136-1_1_2_load_68 | 9 | 0.015891 | 0.0039827 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_136-1_1_2_load_56 | 11 | 0.0098392 | 0.0024659 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_136-1_1_2_load_53 | 13 | 0.005465 | 0.0013697 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_136-1_1_2_load_60 | 14 | 0.0044419 | 0.0011133 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_136-1_1_2_load_50 | 16 | 0.0017313 | 0.0004339 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_136-1_1_2_load_46 | 19 | 0.0020917 | 0.00052423 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_136-1_1_2_load_69 | 21 | 0.012889 | 0.0032304 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_136-1_1_2_load_54 | 23 | 0.0050454 | 0.0012645 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_136-1_1_2_load_59 | 24 | 0.0042007 | 0.0010528 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_136-1_1_2_load_57 | 25 | 0.016375 | 0.0041039 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_136-1_1_2_load_66 | 26 | 0.0052822 | 0.0013238 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_136-1_1_2_load_44 | 27 | 0.0018121 | 0.00045416 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_136-1_1_2_load_45 | 28 | 0.0022424 | 0.000562 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_136-1_1_2_load_55 | 29 | 0.01277 | 0.0032003 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_136-1_1_2_load_63 | 30 | 0.0091819 | 0.0023012 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_136-1_1_2_load_64 | 31 | 0.0014826 | 0.00037157 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_136-1_1_2_load_85 | 34 | 0.0040032 | 0.0010033 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_136-1_1_2_load_98 | 36 | 0.0030204 | 0.00075697 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_136-1_1_2_load_84 | 38 | 0.0018438 | 0.00046209 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_136-1_1_2_load_82 | 39 | 0.0044082 | 0.0011048 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_136-1_1_2_load_81 | 40 | 0.0033179 | 0.00083154 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_136-1_1_2_load_75 | 42 | 0.0021154 | 0.00053017 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_136-1_1_2_load_78 | 45 | 0.0018054 | 0.00045247 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_136-1_1_2_load_87 | 47 | 0.0040032 | 0.0010033 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_136-1_1_2_load_97 | 48 | 0.0040025 | 0.0010031 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_136-1_1_2_load_95 | 49 | 0.0030591 | 0.00076669 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_136-1_1_2_load_79 | 51 | 0.0033613 | 0.00084243 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_136-1_1_2_load_80 | 52 | 0.0038121 | 0.0009554 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_136-1_1_2_load_93 | 53 | 0.011696 | 0.0029312 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_136-1_1_2_load_91 | 54 | 0.0056818 | 0.001424 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_136-1_1_2_load_90 | 56 | 0.0039087 | 0.00097962 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_136-1_1_2_load_94 | 58 | 0.0026422 | 0.0006622 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_136-1_1_2_line_0 |  | 0 | 1 | 0.011721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_136-1_1_2_line_1 |  | 0 | 2 | 0.014834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_136-1_1_2_line_2 |  | 1 | 3 | 0.015614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_136-1_1_2_line_3 |  | 2 | 19 | 0.011627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_136-1_1_2_line_4 |  | 3 | 15 | 0.021039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_136-1_1_2_line_5 |  | 4 | 5 | 0.029602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_136-1_1_2_line_6 |  | 4 | 6 | 0.03944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_136-1_1_2_line_7 |  | 6 | 20 | 0.044854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_136-1_1_2_line_8 |  | 7 | 8 | 0.033391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_136-1_1_2_line_9 |  | 7 | 9 | 0.010224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_136-1_1_2_line_10 |  | 8 | 21 | 0.057142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_136-1_1_2_line_11 |  | 8 | 22 | 0.024618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_136-1_1_2_line_12 |  | 8 | 12 | 0.03138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_136-1_1_2_line_13 |  | 10 | 11 | 0.028149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_136-1_1_2_line_14 |  | 10 | 12 | 0.037899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_136-1_1_2_line_15 |  | 10 | 13 | 0.056453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_136-1_1_2_line_16 |  | 11 | 17 | 0.026287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_136-1_1_2_line_17 |  | 12 | 14 | 0.016984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_136-1_1_2_line_18 |  | 13 | 23 | 0.017644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_136-1_1_2_line_19 |  | 14 | 24 | 0.024017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_136-1_1_2_line_20 |  | 15 | 16 | 0.044797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_136-1_1_2_line_21 |  | 15 | 17 | 0.2545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_136-1_1_2_line_22 |  | 17 | 18 | 0.027576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_136-1_1_2_line_23 |  | 18 | 25 | 0.041569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_136-1_1_2_line_24 |  | 19 | 27 | 0.0073612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_136-1_1_2_line_25 |  | 20 | 37 | 0.032829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_136-1_1_2_line_26 |  | 20 | 21 | 0.024519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_136-1_1_2_line_27 |  | 22 | 26 | 0.024159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_136-1_1_2_line_28 |  | 23 | 29 | 0.00074855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_136-1_1_2_line_29 |  | 27 | 28 | 0.01521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_136-1_1_2_line_30 |  | 30 | 31 | 0.001423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_136-1_1_2_line_31 |  | 30 | 32 | 0.028477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_136-1_1_2_line_32 |  | 32 | 33 | 0.004441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_136-1_1_2_line_33 |  | 33 | 34 | 0.019862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_136-1_1_2_line_34 |  | 34 | 38 | 0.034234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_136-1_1_2_line_35 |  | 35 | 36 | 0.035374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_136-1_1_2_line_36 |  | 35 | 37 | 0.030242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_136-1_1_2_line_37 |  | 36 | 41 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_136-1_1_2_line_38 |  | 37 | 39 | 0.012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_136-1_1_2_line_39 |  | 38 | 50 | 0.0034614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_136-1_1_2_line_40 |  | 39 | 40 | 0.016521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_136-1_1_2_line_41 |  | 40 | 51 | 6.2818e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_136-1_1_2_line_42 |  | 41 | 48 | 0.018032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_136-1_1_2_line_43 |  | 42 | 43 | 0.011161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_136-1_1_2_line_44 |  | 43 | 44 | 0.033292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_136-1_1_2_line_45 |  | 43 | 45 | 0.018266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_136-1_1_2_line_46 |  | 44 | 46 | 0.028724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_136-1_1_2_line_47 |  | 44 | 47 | 0.031449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_136-1_1_2_line_48 |  | 46 | 48 | 0.025485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_136-1_1_2_line_49 |  | 46 | 49 | 0.02084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_136-1_1_2_line_50 |  | 47 | 50 | 0.007565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_136-1_1_2_line_51 |  | 49 | 55 | 0.0031861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_136-1_1_2_line_52 |  | 51 | 52 | 0.019397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_136-1_1_2_line_53 |  | 53 | 54 | 0.0013708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_136-1_1_2_line_54 |  | 54 | 56 | 0.029417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_136-1_1_2_line_55 |  | 55 | 58 | 0.034748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_136-1_1_2_line_56 |  | 56 | 57 | 0.0090204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_136-1_1_2_line_57 |  | 57 | 58 | 0.027971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_136-1_1_2_trafo_69 | 0.63 MVA 20/0.4 kV | 59 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2682959.5333 | 1237731.2393 | 2682957.4666 | 1237724.8281 | 2682961.1154 | 1237721.4322
1 | 2682959.5333 | 1237731.2393 | 2682964.0763 | 1237745.361
2 | 2682961.1154 | 1237721.4322 | 2682972.5482 | 1237710.7971
3 | 2682964.0763 | 1237745.361 | 2682965.5806 | 1237750.0371 | 2682964.1152 | 1237756.5897
4 | 2682987.9529 | 1237696.4671 | 2682972.5482 | 1237710.7971
5 | 2682790.6706 | 1237720.8093 | 2682790.5724 | 1237727.8463 | 2682797.8053 | 1237727.8582 | 2682797.7513 | 1237731.7269 | 2682809.2089 | 1237732.0518
6 | 2682790.6706 | 1237720.8093 | 2682790.9169 | 1237703.1447 | 2682788.1786 | 1237703.1065 | 2682788.1347 | 1237693.777 | 2682786.5449 | 1237693.8438 | 2682786.59 | 1237685.7297
7 | 2682786.12 | 1237641.8454 | 2682785.8894 | 1237652.4164 | 2682786.7757 | 1237652.3398 | 2682786.59 | 1237685.7297
8 | 2682853.018 | 1237664.6943 | 2682856.865 | 1237644.3891 | 2682859.1281 | 1237631.8674
9 | 2682853.018 | 1237664.6943 | 2682847.9538 | 1237663.7897 | 2682847.1548 | 1237668.8066
10 | 2682859.1281 | 1237631.8674 | 2682834.0591 | 1237633.6746 | 2682814.2615 | 1237633.4762 | 2682814.2401 | 1237635.0103 | 2682803.5664 | 1237634.8614
11 | 2682863.514 | 1237607.6447 | 2682859.1281 | 1237631.8674
12 | 2682859.1281 | 1237631.8674 | 2682856.865 | 1237644.3891 | 2682875.2355 | 1237647.6366
13 | 2682913.067 | 1237647.0085 | 2682932.3087 | 1237642.5851 | 2682940.091 | 1237639.4101
14 | 2682875.2355 | 1237647.6366 | 2682894.0566 | 1237648.4109 | 2682906.7882 | 1237647.4768 | 2682913.067 | 1237647.0085
15 | 2682913.067 | 1237647.0085 | 2682914.8127 | 1237656.3617 | 2682914.294 | 1237664.249 | 2682908.4616 | 1237692.8879 | 2682900.0829 | 1237697.9857
16 | 2682963.1323 | 1237626.9266 | 2682960.7935 | 1237628.6174 | 2682947.6189 | 1237636.3389 | 2682940.091 | 1237639.4101
17 | 2682875.2355 | 1237647.6366 | 2682877.2464 | 1237630.7723
18 | 2682900.0829 | 1237697.9857 | 2682895.2441 | 1237699.9084 | 2682884.5057 | 1237693.6336
19 | 2682880.0901 | 1237606.9242 | 2682877.2464 | 1237630.7723
20 | 2682987.9529 | 1237696.4671 | 2683013.0207 | 1237718.533 | 2683020.1462 | 1237727.4329
21 | 2682963.1323 | 1237626.9266 | 2682974.7194 | 1237618.5603 | 2683012.974 | 1237581.7464 | 2683014.2349 | 1237587.3458 | 2683071.6959 | 1237649.7934 | 2683057.9983 | 1237656.4955 | 2683014.7479 | 1237675.6378 | 2683002.9271 | 1237683.9452 | 2682987.9529 | 1237696.4671
22 | 2682963.1323 | 1237626.9266 | 2682961.0004 | 1237654.4163
23 | 2682961.0004 | 1237654.4163 | 2682958.1757 | 1237690.8694 | 2682953.179 | 1237690.555
24 | 2682961.3592 | 1237763.3402 | 2682963.4661 | 1237759.492 | 2682964.1152 | 1237756.5897
25 | 2682756.6401 | 1237646.3712 | 2682757.2256 | 1237644.5336 | 2682776.0448 | 1237643.8175 | 2682775.9886 | 1237641.8821 | 2682786.12 | 1237641.8454
26 | 2682786.12 | 1237641.8454 | 2682789.5703 | 1237641.838 | 2682789.532 | 1237638.6129 | 2682793.7392 | 1237638.5826 | 2682793.7728 | 1237636.1703 | 2682803.4695 | 1237636.3834 | 2682803.5664 | 1237634.8614
27 | 2682863.514 | 1237607.6447 | 2682852.064 | 1237606.1951 | 2682839.6762 | 1237603.7984
28 | 2682884.5057 | 1237693.6336 | 2682883.8594 | 1237693.2559
29 | 2682961.3592 | 1237763.3402 | 2682956.3309 | 1237772.5238 | 2682955.2847 | 1237777.1464
30 | 2682787.5301 | 1237551.1071 | 2682787.9879 | 1237549.7598
31 | 2682778.3689 | 1237578.07 | 2682787.5301 | 1237551.1071
32 | 2682776.9408 | 1237582.2753 | 2682778.3689 | 1237578.07
33 | 2682776.9408 | 1237582.2753 | 2682759.8212 | 1237576.6661 | 2682758.0306 | 1237577.1176
34 | 2682731.9402 | 1237564.7026 | 2682733.318 | 1237566.8233 | 2682733.0052 | 1237572.434 | 2682752.7598 | 1237578.4468 | 2682758.0306 | 1237577.1176
35 | 2682765.0348 | 1237617.3231 | 2682732.7733 | 1237602.8147
36 | 2682765.0348 | 1237617.3231 | 2682761.6682 | 1237628.1617 | 2682757.2256 | 1237644.5336 | 2682756.6401 | 1237646.3712
37 | 2682718.6887 | 1237594.7949 | 2682718.0864 | 1237596.2098 | 2682732.7733 | 1237602.8147
38 | 2682756.6401 | 1237646.3712 | 2682744.6367 | 1237641.7452
39 | 2682728.6408 | 1237563.6559 | 2682731.9402 | 1237564.7026
40 | 2682744.6367 | 1237641.7452 | 2682744.6367 | 1237641.7452 | 2682735.3152 | 1237634.1544 | 2682733.2541 | 1237630.154
41 | 2682733.2254 | 1237630.0981 | 2682733.2541 | 1237630.154
42 | 2682718.6887 | 1237594.7949 | 2682702.0449 | 1237587.857
43 | 2682707.5193 | 1237524.8676 | 2682713.2003 | 1237515.2608
44 | 2682707.5193 | 1237524.8676 | 2682691.0754 | 1237553.837
45 | 2682707.5193 | 1237524.8676 | 2682692.0497 | 1237515.1544
46 | 2682678.0853 | 1237579.2965 | 2682679.2249 | 1237574.6201 | 2682691.0754 | 1237553.837
47 | 2682691.0754 | 1237553.837 | 2682714.3846 | 1237561.0555 | 2682721.4241 | 1237561.3871
48 | 2682678.0853 | 1237579.2965 | 2682689.0503 | 1237582.4402 | 2682702.0449 | 1237587.857
49 | 2682678.0853 | 1237579.2965 | 2682673.1307 | 1237599.5388
50 | 2682728.6408 | 1237563.6559 | 2682721.4241 | 1237561.3871
51 | 2682672.3732 | 1237602.6335 | 2682673.1307 | 1237599.5388
52 | 2682733.2254 | 1237630.0981 | 2682729.4586 | 1237622.787 | 2682728.1335 | 1237615.2632 | 2682728.0386 | 1237611.7319
53 | 2682713.196 | 1237688.9236 | 2682714.2729 | 1237689.7716
54 | 2682691.2404 | 1237669.4814 | 2682695.3209 | 1237674.3482 | 2682706.2181 | 1237683.4286 | 2682713.196 | 1237688.9236
55 | 2682672.3732 | 1237602.6335 | 2682671.0595 | 1237614.3902 | 2682671.9594 | 1237628.0013 | 2682674.4097 | 1237636.9496
56 | 2682685.4449 | 1237662.5691 | 2682691.2404 | 1237669.4814
57 | 2682685.4449 | 1237662.5691 | 2682679.9169 | 1237652.0513 | 2682675.2786 | 1237640.1228 | 2682674.4097 | 1237636.9496

## bus_geodata
| x | y | coords
0 | 2682959.5333 | 1237731.2393
1 | 2682961.1154 | 1237721.4322
2 | 2682964.0763 | 1237745.361
3 | 2682972.5482 | 1237710.7971
4 | 2682790.6706 | 1237720.8093
5 | 2682809.2089 | 1237732.0518
6 | 2682786.59 | 1237685.7297
7 | 2682853.018 | 1237664.6943
8 | 2682859.1281 | 1237631.8674
9 | 2682847.1548 | 1237668.8066
10 | 2682913.067 | 1237647.0085
11 | 2682940.091 | 1237639.4101
12 | 2682875.2355 | 1237647.6366
13 | 2682900.0829 | 1237697.9857
14 | 2682877.2464 | 1237630.7723
15 | 2682987.9529 | 1237696.4671
16 | 2683020.1462 | 1237727.4329
17 | 2682963.1323 | 1237626.9266
18 | 2682961.0004 | 1237654.4163
19 | 2682964.1152 | 1237756.5897
20 | 2682786.12 | 1237641.8454
21 | 2682803.5664 | 1237634.8614
22 | 2682863.514 | 1237607.6447
23 | 2682884.5057 | 1237693.6336
24 | 2682880.0901 | 1237606.9242
25 | 2682953.179 | 1237690.555
26 | 2682839.6762 | 1237603.7984
27 | 2682961.3592 | 1237763.3402
28 | 2682955.2847 | 1237777.1464
29 | 2682883.8594 | 1237693.2559
30 | 2682787.5301 | 1237551.1071
31 | 2682787.9879 | 1237549.7598
32 | 2682778.3689 | 1237578.07
33 | 2682776.9408 | 1237582.2753
34 | 2682758.0306 | 1237577.1176
35 | 2682765.0349 | 1237617.3231
36 | 2682732.7733 | 1237602.8147
37 | 2682756.6401 | 1237646.3712
38 | 2682731.9402 | 1237564.7026
39 | 2682744.6367 | 1237641.7452
40 | 2682733.2541 | 1237630.154
41 | 2682718.6887 | 1237594.7949
42 | 2682713.2002 | 1237515.2608
43 | 2682707.5193 | 1237524.8676
44 | 2682691.0754 | 1237553.837
45 | 2682692.0497 | 1237515.1544
46 | 2682678.0853 | 1237579.2965
47 | 2682721.4241 | 1237561.3871
48 | 2682702.0449 | 1237587.857
49 | 2682673.1307 | 1237599.5388
50 | 2682728.6408 | 1237563.6559
51 | 2682733.2254 | 1237630.0981
52 | 2682728.0386 | 1237611.7319
53 | 2682714.2729 | 1237689.7716
54 | 2682713.196 | 1237688.9236
55 | 2682672.3732 | 1237602.6335
56 | 2682691.2404 | 1237669.4814
57 | 2682685.4449 | 1237662.5691
58 | 2682674.4097 | 1237636.9496
59 | 2682786.12 | 1237641.8454

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.986 | -0.26991 | 0 | 0
1 | 0.98608 | -0.26822 | 0 | 0
2 | 0.98589 | -0.27204 | 0.0018665 | 0.00046779
3 | 0.9862 | -0.26598 | 0.002701 | 0.00067693
4 | 0.9967 | -0.063196 | 0 | 0
5 | 0.99652 | -0.066701 | 0.0067481 | 0.0016912
6 | 0.99694 | -0.058526 | 0.015574 | 0.0039031
7 | 0.99471 | -0.10119 | 0 | 0
8 | 0.9952 | -0.091851 | 0 | 0
9 | 0.99457 | -0.10406 | 0.015891 | 0.0039827
10 | 0.99101 | -0.1725 | 0 | 0
11 | 0.99001 | -0.19184 | 0.0098392 | 0.0024659
12 | 0.99317 | -0.13092 | 0 | 0
13 | 0.98981 | -0.19586 | 0.005465 | 0.0013697
14 | 0.99303 | -0.13351 | 0.0044419 | 0.0011133
15 | 0.98641 | -0.26194 | 0 | 0
16 | 0.98633 | -0.26333 | 0.0017313 | 0.0004339
17 | 0.98932 | -0.20533 | 0 | 0
18 | 0.9889 | -0.21338 | 0 | 0
19 | 0.98582 | -0.27332 | 0.0020917 | 0.00052423
20 | 0.99785 | -0.040982 | 0 | 0
21 | 1 | 0 | -0.19069 | -0.047986
22 | 0.99508 | -0.09414 | 0 | 0
23 | 0.98952 | -0.20145 | 0.0050454 | 0.0012645
24 | 0.99294 | -0.1353 | 0.0042007 | 0.0010528
25 | 0.98828 | -0.22552 | 0.016375 | 0.0041039
26 | 0.99496 | -0.096387 | 0.0052822 | 0.0013238
27 | 0.98579 | -0.27385 | 0.0018121 | 0.00045416
28 | 0.98576 | -0.27447 | 0.0022424 | 0.000562
29 | 0.98951 | -0.20162 | 0.01277 | 0.0032003
30 | 0.98672 | -0.25566 | 0.0091819 | 0.0023012
31 | 0.98672 | -0.2557 | 0.0014826 | 0.00037157
32 | 0.987 | -0.25023 | 0 | 0
33 | 0.98704 | -0.24938 | 0 | 0
34 | 0.98724 | -0.24559 | 0.0040032 | 0.0010033
35 | 0.99402 | -0.11437 | 0 | 0
36 | 0.99212 | -0.15092 | 0.0030204 | 0.00075697
37 | 0.99564 | -0.083235 | 0 | 0
38 | 0.9877 | -0.23661 | 0.0018438 | 0.00046209
39 | 0.99547 | -0.086606 | 0.0044082 | 0.0011048
40 | 0.99531 | -0.089655 | 0.0033179 | 0.00083154
41 | 0.99122 | -0.16825 | 0 | 0
42 | 0.98832 | -0.22459 | 0.0021154 | 0.00053017
43 | 0.98834 | -0.22417 | 0 | 0
44 | 0.98846 | -0.22184 | 0 | 0
45 | 0.98831 | -0.22476 | 0.0018054 | 0.00045247
46 | 0.9891 | -0.20933 | 0 | 0
47 | 0.98786 | -0.23336 | 0.0040032 | 0.0010033
48 | 0.9903 | -0.186 | 0.0040025 | 0.0010031
49 | 0.98858 | -0.21935 | 0.0030591 | 0.00076669
50 | 0.98775 | -0.23559 | 0 | 0
51 | 0.99531 | -0.089663 | 0.0033613 | 0.00084243
52 | 0.99524 | -0.090964 | 0.0038121 | 0.0009554
53 | 0.98654 | -0.25907 | 0.011696 | 0.0029312
54 | 0.98656 | -0.25879 | 0.0056818 | 0.001424
55 | 0.98851 | -0.22071 | 0 | 0
56 | 0.98703 | -0.24964 | 0.0039087 | 0.00097962
57 | 0.9872 | -0.2462 | 0 | 0
58 | 0.98775 | -0.23556 | 0.0026422 | 0.0006622
59 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0080141 | -0.0020084 | 0.0080147 | 0.0020087 | 6.4291e-07 | 2.6196e-07 | 0.012094 | 0.012094 | 0.012094 | 0.986 | -0.26991 | 0.98608 | -0.26822 | 3.3226
1 | 0.0080141 | 0.0020084 | -0.0080133 | -0.0020081 | 8.1372e-07 | 3.316e-07 | 0.012094 | 0.012094 | 0.012094 | 0.986 | -0.26991 | 0.98589 | -0.27204 | 3.3227
2 | -0.0080147 | -0.0020087 | 0.0080156 | 0.002009 | 8.5649e-07 | 3.4894e-07 | 0.012094 | 0.012094 | 0.012094 | 0.98608 | -0.26822 | 0.9862 | -0.26598 | 3.3226
3 | 0.0061468 | 0.0015403 | -0.0061464 | -0.0015402 | 3.7526e-07 | 9.192e-08 | 0.0092773 | 0.0092774 | 0.0092774 | 0.98589 | -0.27204 | 0.98582 | -0.27332 | 2.5487
4 | -0.010717 | -0.002686 | 0.010719 | 0.002687 | 2.0628e-06 | 1.0517e-06 | 0.01617 | 0.01617 | 0.01617 | 0.9862 | -0.26598 | 0.98641 | -0.26194 | 4.4422
5 | 0.0067493 | 0.0016916 | -0.0067481 | -0.0016912 | 1.1271e-06 | 3.3561e-07 | 0.010076 | 0.010076 | 0.010076 | 0.9967 | -0.063196 | 0.99652 | -0.066701 | 2.7683
6 | -0.0067493 | -0.0016916 | 0.0067508 | 0.001692 | 1.5016e-06 | 4.469e-07 | 0.010076 | 0.010076 | 0.010076 | 0.9967 | -0.063196 | 0.99694 | -0.058526 | 2.7682
7 | -0.022325 | -0.0055952 | 0.022343 | 0.0056065 | 1.8675e-05 | 1.1367e-05 | 0.033321 | 0.033321 | 0.033321 | 0.99694 | -0.058526 | 0.99785 | -0.040982 | 9.1542
8 | -0.015893 | -0.0039839 | 0.0159 | 0.003988 | 7.0779e-06 | 4.0962e-06 | 0.023775 | 0.023775 | 0.023775 | 0.99471 | -0.10119 | 0.9952 | -0.091851 | 6.5316
9 | 0.015893 | 0.0039839 | -0.015891 | -0.0039827 | 2.1673e-06 | 1.2544e-06 | 0.023775 | 0.023775 | 0.023775 | 0.99471 | -0.10119 | 0.99457 | -0.10406 | 6.5317
10 | -0.092162 | -0.023247 | 0.092569 | 0.023506 | 0.00040721 | 0.00025987 | 0.13785 | 0.13785 | 0.13785 | 0.9952 | -0.091851 | 1 | 0 | 37.8718
11 | 0.0052834 | 0.0013239 | -0.0052828 | -0.0013239 | 5.761e-07 | 4.8868e-08 | 0.0078996 | 0.0078997 | 0.0078997 | 0.9952 | -0.091851 | 0.99508 | -0.09414 | 2.1702
12 | 0.070979 | 0.017935 | -0.070846 | -0.01785 | 0.00013267 | 8.4499e-05 | 0.10618 | 0.10618 | 0.10618 | 0.9952 | -0.091851 | 0.99317 | -0.13092 | 29.17
13 | 0.038768 | 0.0097518 | -0.038732 | -0.0097293 | 3.5783e-05 | 2.2539e-05 | 0.058223 | 0.058223 | 0.058223 | 0.99101 | -0.1725 | 0.99001 | -0.19184 | 15.9953
14 | -0.062078 | -0.015605 | 0.062202 | 0.015684 | 0.00012352 | 7.8566e-05 | 0.093228 | 0.093228 | 0.093228 | 0.99101 | -0.1725 | 0.99317 | -0.13092 | 25.6121
15 | 0.023311 | 0.0058533 | -0.023285 | -0.0058374 | 2.5941e-05 | 1.5876e-05 | 0.035005 | 0.035006 | 0.035006 | 0.99101 | -0.1725 | 0.98981 | -0.19586 | 9.6169
16 | 0.028893 | 0.0072633 | -0.028874 | -0.0072518 | 1.8597e-05 | 1.1564e-05 | 0.043434 | 0.043434 | 0.043434 | 0.99001 | -0.19184 | 0.98932 | -0.20533 | 11.9325
17 | 0.008644 | 0.0021664 | -0.008643 | -0.002166 | 1.0683e-06 | 4.6393e-07 | 0.012951 | 0.012951 | 0.012951 | 0.99317 | -0.13092 | 0.99303 | -0.13351 | 3.558
18 | 0.01782 | 0.0044677 | -0.017815 | -0.0044649 | 4.7487e-06 | 2.8124e-06 | 0.02679 | 0.02679 | 0.02679 | 0.98981 | -0.19586 | 0.98952 | -0.20145 | 7.3598
19 | 0.004201 | 0.0010527 | -0.0042007 | -0.0010528 | 3.569e-07 | -8.2264e-08 | 0.006295 | 0.0062951 | 0.0062951 | 0.99303 | -0.13351 | 0.99294 | -0.1353 | 1.7294
20 | 0.0017314 | 0.00043341 | -0.0017313 | -0.0004339 | 1.1459e-07 | -4.9845e-07 | 0.0026117 | 0.0026119 | 0.0026119 | 0.98641 | -0.26194 | 0.98633 | -0.26333 | 0.71755
21 | -0.01245 | -0.0031204 | 0.012484 | 0.0031387 | 3.3662e-05 | 1.8285e-05 | 0.018781 | 0.01878 | 0.018781 | 0.98641 | -0.26194 | 0.98932 | -0.20533 | 5.1597
22 | 0.01639 | 0.0041131 | -0.016384 | -0.0041094 | 6.2857e-06 | 3.6689e-06 | 0.024654 | 0.024654 | 0.024654 | 0.98932 | -0.20533 | 0.9889 | -0.21338 | 6.7732
23 | 0.016384 | 0.0041094 | -0.016375 | -0.0041039 | 9.4754e-06 | 5.5313e-06 | 0.024654 | 0.024655 | 0.024655 | 0.9889 | -0.21338 | 0.98828 | -0.22552 | 6.7733
24 | 0.0040547 | 0.001016 | -0.0040546 | -0.001016 | 1.034e-07 | -2.7678e-08 | 0.0061202 | 0.0061202 | 0.0061202 | 0.98582 | -0.27332 | 0.98579 | -0.27385 | 1.6814
25 | 0.073935 | 0.018752 | -0.073785 | -0.018657 | 0.00014986 | 9.5485e-05 | 0.11033 | 0.11033 | 0.11033 | 0.99785 | -0.040982 | 0.99564 | -0.083235 | 30.311
26 | -0.096278 | -0.024359 | 0.096468 | 0.02448 | 0.00018975 | 0.00012112 | 0.14365 | 0.14365 | 0.14365 | 0.99785 | -0.040982 | 1 | 0 | 39.4651
27 | 0.0052828 | 0.0013239 | -0.0052822 | -0.0013238 | 5.6538e-07 | 4.8041e-08 | 0.0078997 | 0.0078998 | 0.0078998 | 0.99508 | -0.09414 | 0.99496 | -0.096387 | 2.1703
28 | 0.01277 | 0.0032004 | -0.01277 | -0.0032003 | 1.0351e-07 | 5.6629e-08 | 0.019203 | 0.019203 | 0.019203 | 0.98952 | -0.20145 | 0.98951 | -0.20162 | 5.2754
29 | 0.0022425 | 0.00056184 | -0.0022424 | -0.000562 | 6.5348e-08 | -1.5208e-07 | 0.0033848 | 0.0033849 | 0.0033849 | 0.98579 | -0.27385 | 0.98576 | -0.27447 | 0.92992
30 | 0.0014826 | 0.00037155 | -0.0014826 | -0.00037157 | 2.6677e-09 | -1.6469e-08 | 0.0022358 | 0.0022358 | 0.0022358 | 0.98672 | -0.25566 | 0.98672 | -0.2557 | 0.61423
31 | -0.010665 | -0.0026728 | 0.010667 | 0.0026742 | 2.762e-06 | 1.4039e-06 | 0.016083 | 0.016082 | 0.016083 | 0.98672 | -0.25566 | 0.987 | -0.25023 | 4.4183
32 | -0.010667 | -0.0026742 | 0.010668 | 0.0026744 | 4.3074e-07 | 2.1891e-07 | 0.016082 | 0.016082 | 0.016082 | 0.987 | -0.25023 | 0.98704 | -0.24938 | 4.4183
33 | -0.010668 | -0.0026744 | 0.01067 | 0.0026754 | 1.9264e-06 | 9.7899e-07 | 0.016082 | 0.016082 | 0.016082 | 0.98704 | -0.24938 | 0.98724 | -0.24559 | 4.4183
34 | -0.014673 | -0.0036787 | 0.014679 | 0.0036822 | 6.2791e-06 | 3.5807e-06 | 0.022116 | 0.022116 | 0.022116 | 0.98724 | -0.24559 | 0.9877 | -0.23661 | 6.0759
35 | 0.058794 | 0.014865 | -0.058691 | -0.014799 | 0.00010286 | 6.5373e-05 | 0.088058 | 0.088058 | 0.088058 | 0.99402 | -0.11437 | 0.99212 | -0.15092 | 24.1918
36 | -0.058794 | -0.014865 | 0.058881 | 0.014921 | 8.7938e-05 | 5.5888e-05 | 0.088058 | 0.088058 | 0.088058 | 0.99402 | -0.11437 | 0.99564 | -0.083235 | 24.1918
37 | 0.05567 | 0.014042 | -0.055624 | -0.014013 | 4.6156e-05 | 2.9312e-05 | 0.083528 | 0.083528 | 0.083528 | 0.99212 | -0.15092 | 0.99122 | -0.16825 | 22.9473
38 | 0.014904 | 0.0037362 | -0.014901 | -0.0037348 | 2.3934e-06 | 1.3645e-06 | 0.022274 | 0.022274 | 0.022274 | 0.99564 | -0.083235 | 0.99547 | -0.086606 | 6.1193
39 | -0.016523 | -0.0041443 | 0.016524 | 0.0041448 | 8.0439e-07 | 4.7051e-07 | 0.024894 | 0.024894 | 0.024894 | 0.9877 | -0.23661 | 0.98775 | -0.23559 | 6.8389
40 | 0.010493 | 0.00263 | -0.010492 | -0.0026293 | 1.5242e-06 | 7.6075e-07 | 0.015685 | 0.015685 | 0.015685 | 0.99547 | -0.086606 | 0.99531 | -0.089655 | 4.3091
41 | 0.0071737 | 0.0017977 | -0.0071737 | -0.0017977 | 2.71e-09 | 9.1756e-10 | 0.010725 | 0.010725 | 0.010725 | 0.99531 | -0.089655 | 0.99531 | -0.089663 | 2.9464
42 | 0.055624 | 0.014013 | -0.055577 | -0.013983 | 4.7178e-05 | 2.9962e-05 | 0.083528 | 0.083528 | 0.083528 | 0.99122 | -0.16825 | 0.9903 | -0.186 | 22.9473
43 | -0.0021154 | -0.00053017 | 0.0021155 | 0.00053006 | 4.2456e-08 | -1.1585e-07 | 0.003185 | 0.0031849 | 0.003185 | 0.98832 | -0.22459 | 0.98834 | -0.22417 | 0.875
44 | -0.0039209 | -0.00098233 | 0.0039213 | 0.00098218 | 4.3503e-07 | -1.4827e-07 | 0.0059031 | 0.0059029 | 0.0059031 | 0.98834 | -0.22417 | 0.98846 | -0.22184 | 1.6217
45 | 0.0018054 | 0.00045227 | -0.0018054 | -0.00045247 | 5.0611e-08 | -2.0169e-07 | 0.0027181 | 0.0027182 | 0.0027182 | 0.98834 | -0.22417 | 0.98831 | -0.22476 | 0.74677
46 | -0.024461 | -0.0061381 | 0.024476 | 0.0061471 | 1.4608e-05 | 8.9808e-06 | 0.036827 | 0.036826 | 0.036827 | 0.98846 | -0.22184 | 0.9891 | -0.20933 | 10.1172
47 | 0.02054 | 0.005156 | -0.020529 | -0.0051491 | 1.1278e-05 | 6.8148e-06 | 0.030924 | 0.030924 | 0.030924 | 0.98846 | -0.22184 | 0.98786 | -0.23336 | 8.4955
48 | -0.051517 | -0.012943 | 0.051574 | 0.01298 | 5.7422e-05 | 3.6423e-05 | 0.077514 | 0.077514 | 0.077514 | 0.9891 | -0.20933 | 0.9903 | -0.186 | 21.2951
49 | 0.027041 | 0.0067964 | -0.027028 | -0.0067883 | 1.2938e-05 | 8.0128e-06 | 0.040688 | 0.040688 | 0.040688 | 0.9891 | -0.20933 | 0.98858 | -0.21935 | 11.178
50 | 0.016525 | 0.0041458 | -0.016524 | -0.0041448 | 1.758e-06 | 1.0283e-06 | 0.024894 | 0.024894 | 0.024894 | 0.98786 | -0.23336 | 0.98775 | -0.23559 | 6.8389
51 | 0.023969 | 0.0060217 | -0.023968 | -0.0060207 | 1.5556e-06 | 9.5474e-07 | 0.036083 | 0.036083 | 0.036083 | 0.98858 | -0.21935 | 0.98851 | -0.22071 | 9.913
52 | 0.0038123 | 0.0009553 | -0.0038121 | -0.0009554 | 2.3628e-07 | -1.0085e-07 | 0.0056995 | 0.0056996 | 0.0056996 | 0.99531 | -0.089663 | 0.99524 | -0.090964 | 1.5658
53 | -0.011696 | -0.0029312 | 0.011696 | 0.0029313 | 1.5997e-07 | 8.4876e-08 | 0.017641 | 0.017641 | 0.017641 | 0.98654 | -0.25907 | 0.98656 | -0.25879 | 4.8464
54 | -0.017378 | -0.0043553 | 0.017385 | 0.0043598 | 7.5786e-06 | 4.4745e-06 | 0.026211 | 0.026211 | 0.026211 | 0.98656 | -0.25879 | 0.98703 | -0.24964 | 7.2007
55 | 0.023968 | 0.0060207 | -0.023951 | -0.0060103 | 1.6966e-05 | 1.0413e-05 | 0.036083 | 0.036084 | 0.036084 | 0.98851 | -0.22071 | 0.98775 | -0.23556 | 9.9131
56 | -0.021294 | -0.0053394 | 0.021298 | 0.0053415 | 3.4862e-06 | 2.1159e-06 | 0.032103 | 0.032103 | 0.032103 | 0.98703 | -0.24964 | 0.9872 | -0.2462 | 8.8196
57 | -0.021298 | -0.0053415 | 0.021308 | 0.0053481 | 1.081e-05 | 6.5606e-06 | 0.032103 | 0.032103 | 0.032103 | 0.9872 | -0.2462 | 0.98775 | -0.23556 | 8.8196

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20358 | 0.051217

## res_load
| p_mw | q_mvar
0 | 0.0018665 | 0.00046779
1 | 0.002701 | 0.00067693
2 | 0.0067481 | 0.0016912
3 | 0.015574 | 0.0039031
4 | 0.015891 | 0.0039827
5 | 0.0098392 | 0.0024659
6 | 0.005465 | 0.0013697
7 | 0.0044419 | 0.0011133
8 | 0.0017313 | 0.0004339
9 | 0.0020917 | 0.00052423
10 | 0.012889 | 0.0032304
11 | 0.0050454 | 0.0012645
12 | 0.0042007 | 0.0010528
13 | 0.016375 | 0.0041039
14 | 0.0052822 | 0.0013238
15 | 0.0018121 | 0.00045416
16 | 0.0022424 | 0.000562
17 | 0.01277 | 0.0032003
18 | 0.0091819 | 0.0023012
19 | 0.0014826 | 0.00037157
20 | 0.0040032 | 0.0010033
21 | 0.0030204 | 0.00075697
22 | 0.0018438 | 0.00046209
23 | 0.0044082 | 0.0011048
24 | 0.0033179 | 0.00083154
25 | 0.0021154 | 0.00053017
26 | 0.0018054 | 0.00045247
27 | 0.0040032 | 0.0010033
28 | 0.0040025 | 0.0010031
29 | 0.0030591 | 0.00076669
30 | 0.0033613 | 0.00084243
31 | 0.0038121 | 0.0009554
32 | 0.011696 | 0.0029312
33 | 0.0056818 | 0.001424
34 | 0.0039087 | 0.00097962
35 | 0.0026422 | 0.0006622

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1