## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_137-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_137-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_137-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_137-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_137-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_137-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_137-3_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_137-3_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_137-3_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_137-3_0_4_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_137-3_0_4_node_120 | 0.4 | n |  | TRUE
11 | bus_LV_137-3_0_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_137-3_0_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_137-3_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_137-3_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_137-3_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_137-3_0_4_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_137-3_0_4_node_118 | 0.4 | n |  | TRUE
18 | bus_LV_137-3_0_4_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_137-3_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_137-3_0_4_node_117 | 0.4 | n |  | TRUE
21 | bus_LV_137-3_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_137-3_0_4_node_112 | 0.4 | n |  | TRUE
23 | bus_LV_137-3_0_4_node_114 | 0.4 | n |  | TRUE
24 | bus_LV_137-3_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_137-3_0_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_137-3_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_137-3_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_137-3_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_137-3_0_4_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_137-3_0_4_node_106 | 0.4 | n |  | TRUE
31 | bus_LV_137-3_0_4_node_11 | 0.4 | n |  | TRUE
32 | bus_LV_137-3_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_137-3_0_4_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_137-3_0_4_node_66 | 0.4 | n |  | TRUE
35 | bus_LV_137-3_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_137-3_0_4_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_137-3_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_137-3_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_137-3_0_4_node_91 | 0.4 | n |  | TRUE
40 | bus_LV_137-3_0_4_node_51 | 0.4 | n |  | TRUE
41 | bus_LV_137-3_0_4_node_94 | 0.4 | n |  | TRUE
42 | bus_LV_137-3_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_137-3_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_137-3_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_137-3_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_137-3_0_4_node_123 | 0.4 | n |  | TRUE
47 | bus_LV_137-3_0_4_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_137-3_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_137-3_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_137-3_0_4_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_137-3_0_4_node_90 | 0.4 | n |  | TRUE
52 | bus_LV_137-3_0_4_node_78 | 0.4 | n |  | TRUE
53 | bus_LV_137-3_0_4_node_10 | 0.4 | n |  | TRUE
54 | bus_LV_137-3_0_4_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_137-3_0_4_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_137-3_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_137-3_0_4_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_137-3_0_4_node_110 | 0.4 | n |  | TRUE
59 | bus_LV_137-3_0_4_node_115 | 0.4 | n |  | TRUE
60 | bus_LV_137-3_0_4_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_137-3_0_4_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_137-3_0_4_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_137-3_0_4_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_137-3_0_4_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_137-3_0_4_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_137-3_0_4_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_137-3_0_4_node_121 | 0.4 | n |  | TRUE
68 | bus_LV_137-3_0_4_node_89 | 0.4 | n |  | TRUE
69 | bus_LV_137-3_0_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_137-3_0_4_node_124 | 0.4 | n |  | TRUE
71 | bus_LV_137-3_0_4_node_99 | 0.4 | n |  | TRUE
72 | bus_LV_137-3_0_4_node_80 | 0.4 | n |  | TRUE
73 | bus_LV_137-3_0_4_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_137-3_0_4_node_96 | 0.4 | n |  | TRUE
75 | bus_LV_137-3_0_4_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_137-3_0_4_node_95 | 0.4 | n |  | TRUE
77 | bus_LV_137-3_0_4_node_88 | 0.4 | n |  | TRUE
78 | bus_LV_137-3_0_4_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_137-3_0_4_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_137-3_0_4_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_137-3_0_4_node_84 | 0.4 | n |  | TRUE
82 | bus_LV_137-3_0_4_node_92 | 0.4 | n |  | TRUE
83 | bus_LV_137-3_0_4_node_34 | 0.4 | n |  | TRUE
84 | bus_LV_137-3_0_4_node_35 | 0.4 | n |  | TRUE
85 | bus_LV_137-3_0_4_node_37 | 0.4 | n |  | TRUE
86 | bus_LV_137-3_0_4_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_137-3_0_4_node_39 | 0.4 | n |  | TRUE
88 | bus_LV_137-3_0_4_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_137-3_0_4_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_137-3_0_4_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_137-3_0_4_node_62 | 0.4 | n |  | TRUE
92 | bus_LV_137-3_0_4_node_59 | 0.4 | n |  | TRUE
93 | bus_LV_137-3_0_4_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_137-3_0_4_node_60 | 0.4 | n |  | TRUE
95 | bus_LV_137-3_0_4_node_55 | 0.4 | n |  | TRUE
96 | bus_LV_137-3_0_4_node_56 | 0.4 | n |  | TRUE
97 | bus_LV_137-3_0_4_node_57 | 0.4 | n |  | TRUE
98 | bus_LV_137-3_0_4_node_58 | 0.4 | n |  | TRUE
99 | bus_LV_137-3_0_4_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_137-3_0_4_node_61 | 0.4 | n |  | TRUE
101 | bus_LV_137-3_0_4_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_137-3_0_4_node_74 | 0.4 | n |  | TRUE
103 | bus_LV_137-3_0_4_node_65 | 0.4 | n |  | TRUE
104 | bus_LV_137-3_0_4_node_71 | 0.4 | n |  | TRUE
105 | bus_LV_137-3_0_4_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_137-3_0_4_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_137-3_0_4_node_108 | 0.4 | n |  | TRUE
108 | bus_LV_137-3_0_4_node_73 | 0.4 | n |  | TRUE
109 | bus_LV_137-3_0_4_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_137-3_0_4_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_137-3_0_4_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_137-3_0_4_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_137-3_0_4_node_122 | 0.4 | n |  | TRUE
114 | bus_LV_137-3_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_137-3_0_4_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_137-3_0_4_node_105 | 0.4 | n |  | TRUE
117 | bus_LV_137-3_0_4_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_137-3_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_137-3_0_4_node_113 | 0.4 | n |  | TRUE
120 | bus_MV_491_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_137-3_0_4_load_0 | 0 | 0.009251 | 0.0023185 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_137-3_0_4_load_1 | 1 | 0.0018146 | 0.00045479 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_137-3_0_4_load_2 | 2 | 0.0016722 | 0.00041911 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_137-3_0_4_load_3 | 3 | 0.0096657 | 0.0024224 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_137-3_0_4_load_4 | 4 | 0.0091473 | 0.0022925 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_137-3_0_4_load_5 | 5 | 0.0028204 | 0.00070685 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_137-3_0_4_load_7 | 6 | 0.0037887 | 0.00094953 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_137-3_0_4_load_6 | 7 | 0.0084867 | 0.002127 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_137-3_0_4_load_120 | 10 | 0.0089936 | 0.002254 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_137-3_0_4_load_9 | 13 | 0.0081153 | 0.0020339 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_137-3_0_4_load_12 | 14 | 0.0030377 | 0.00076132 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_137-3_0_4_load_118 | 17 | 0.002941 | 0.00073707 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_137-3_0_4_load_43 | 18 | 0.0046576 | 0.0011673 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_137-3_0_4_load_117 | 20 | 0.0014058 | 0.00035232 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_137-3_0_4_load_114 | 23 | 0.0015751 | 0.00039477 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_137-3_0_4_load_42 | 25 | 0.0074599 | 0.0018696 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_137-3_0_4_load_41 | 26 | 0.0082922 | 0.0020782 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_137-3_0_4_load_77 | 29 | 0.0016159 | 0.00040498 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_137-3_0_4_load_106 | 30 | 0.0035965 | 0.00090136 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_137-3_0_4_load_72 | 33 | 0.0040269 | 0.0010092 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_137-3_0_4_load_69 | 35 | 0.0050218 | 0.0012586 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_137-3_0_4_load_48 | 36 | 0.00081855 | 0.00020515 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_137-3_0_4_load_91 | 39 | 0.0012143 | 0.00030433 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_137-3_0_4_load_94 | 41 | 0.0024521 | 0.00061454 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_137-3_0_4_load_40 | 43 | 0.0035908 | 0.00089995 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_137-3_0_4_load_123 | 46 | 0.0050171 | 0.0012574 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_137-3_0_4_load_90 | 51 | 0.0011355 | 0.00028459 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_137-3_0_4_load_78 | 52 | 0.0040052 | 0.0010038 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_137-3_0_4_load_10 | 53 | 0.001016 | 0.00025464 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_137-3_0_4_load_47 | 54 | 0.00456 | 0.0011428 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_137-3_0_4_load_68 | 55 | 0.0043331 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_137-3_0_4_load_44 | 56 | 0.0058219 | 0.0014591 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_137-3_0_4_load_119 | 57 | 0.0027306 | 0.00068436 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_137-3_0_4_load_110 | 58 | 0.0039312 | 0.00098526 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_137-3_0_4_load_115 | 59 | 0.0038953 | 0.00097624 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_137-3_0_4_load_63 | 60 | 0.0012446 | 0.00031192 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_137-3_0_4_load_64 | 61 | 0.0044667 | 0.0011195 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_137-3_0_4_load_70 | 62 | 0.0034636 | 0.00086807 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_137-3_0_4_load_54 | 64 | 0.0051056 | 0.0012796 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_137-3_0_4_load_49 | 65 | 0.0035263 | 0.00088377 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_137-3_0_4_load_93 | 66 | 0.0024511 | 0.00061431 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_137-3_0_4_load_121 | 67 | 0.0029944 | 0.00075047 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_137-3_0_4_load_89 | 68 | 0.0011355 | 0.00028459 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_137-3_0_4_load_124 | 70 | 0.00077463 | 0.00019414 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_137-3_0_4_load_80 | 72 | 0.0010838 | 0.00027163 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_137-3_0_4_load_50 | 73 | 0.001823 | 0.0004569 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_137-3_0_4_load_98 | 75 | 0.0012456 | 0.00031219 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_137-3_0_4_load_95 | 76 | 0.002035 | 0.00051002 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_137-3_0_4_load_81 | 80 | 0.0055232 | 0.0013842 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_137-3_0_4_load_92 | 82 | 0.0035608 | 0.00089242 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_137-3_0_4_load_34 | 83 | 0.0085049 | 0.0021315 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_137-3_0_4_load_35 | 84 | 0.0037081 | 0.00092935 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_137-3_0_4_load_37 | 85 | 0.014315 | 0.0035877 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_137-3_0_4_load_46 | 86 | 0.043307 | 0.010854 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_137-3_0_4_load_39 | 87 | 0.0051147 | 0.0012819 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_137-3_0_4_load_87 | 89 | 0.0047019 | 0.0011784 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_137-3_0_4_load_62 | 91 | 0.0020686 | 0.00051844 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_137-3_0_4_load_59 | 92 | 0.0043706 | 0.0010954 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_137-3_0_4_load_60 | 94 | 0.0049977 | 0.0012525 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_137-3_0_4_load_55 | 95 | 0.0028004 | 0.00070185 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_137-3_0_4_load_56 | 96 | 0.0030363 | 0.00076096 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_137-3_0_4_load_58 | 98 | 0.0028946 | 0.00072544 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_137-3_0_4_load_61 | 100 | 0.004071 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_137-3_0_4_load_74 | 102 | 0.0033935 | 0.0008505 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_137-3_0_4_load_65 | 103 | 0.0093425 | 0.0023415 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_137-3_0_4_load_107 | 105 | 0.0019483 | 0.00048828 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_137-3_0_4_load_125 | 106 | 0.0031975 | 0.00080136 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_137-3_0_4_load_108 | 107 | 0.0012974 | 0.00032517 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_137-3_0_4_load_73 | 108 | 0.0066489 | 0.0016664 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_137-3_0_4_load_116 | 109 | 0.0021769 | 0.00054559 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_137-3_0_4_load_97 | 110 | 0.0020125 | 0.00050437 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_137-3_0_4_load_122 | 113 | 0.0021983 | 0.00055094 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_137-3_0_4_load_104 | 114 | 0.0016837 | 0.00042198 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_137-3_0_4_load_103 | 115 | 0.0014488 | 0.00036311 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_137-3_0_4_load_105 | 116 | 0.0010917 | 0.0002736 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_137-3_0_4_load_109 | 117 | 0.0021615 | 0.00054174 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_137-3_0_4_load_111 | 118 | 0.0026785 | 0.00067129 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_137-3_0_4_load_113 | 119 | 0.0036014 | 0.0009026 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 84 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_137-3_0_4_line_0 |  | 0 | 1 | 0.015339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_137-3_0_4_line_1 |  | 0 | 2 | 0.0076279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_137-3_0_4_line_2 |  | 1 | 3 | 0.012213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_137-3_0_4_line_3 |  | 2 | 4 | 0.013874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_137-3_0_4_line_4 |  | 3 | 5 | 0.0097845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_137-3_0_4_line_5 |  | 4 | 6 | 0.015698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_137-3_0_4_line_6 |  | 5 | 7 | 0.037056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_137-3_0_4_line_7 |  | 6 | 8 | 0.02145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_137-3_0_4_line_8 |  | 7 | 9 | 0.02431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_137-3_0_4_line_9 |  | 8 | 12 | 0.011734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_137-3_0_4_line_10 |  | 8 | 13 | 0.027448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_137-3_0_4_line_11 |  | 9 | 10 | 0.0077874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_137-3_0_4_line_12 |  | 9 | 11 | 0.035034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_137-3_0_4_line_13 |  | 10 | 25 | 0.029855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_137-3_0_4_line_14 |  | 11 | 43 | 0.035664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_137-3_0_4_line_15 |  | 11 | 83 | 0.035507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_137-3_0_4_line_16 |  | 12 | 16 | 0.028914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_137-3_0_4_line_17 |  | 12 | 17 | 0.022053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_137-3_0_4_line_18 |  | 13 | 53 | 0.03204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_137-3_0_4_line_19 |  | 14 | 15 | 0.0377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_137-3_0_4_line_20 |  | 15 | 18 | 0.0073382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_137-3_0_4_line_21 |  | 16 | 56 | 0.029609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_137-3_0_4_line_22 |  | 16 | 19 | 0.028351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_137-3_0_4_line_23 |  | 17 | 57 | 0.028141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_137-3_0_4_line_24 |  | 18 | 27 | 0.0065205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_137-3_0_4_line_25 |  | 19 | 20 | 0.020687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_137-3_0_4_line_26 |  | 21 | 22 | 0.00696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_137-3_0_4_line_27 |  | 21 | 23 | 0.024258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_137-3_0_4_line_28 |  | 22 | 58 | 0.014103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_137-3_0_4_line_29 |  | 22 | 42 | 0.025975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_137-3_0_4_line_30 |  | 23 | 59 | 0.0097579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_137-3_0_4_line_31 |  | 24 | 25 | 0.032695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_137-3_0_4_line_32 |  | 24 | 26 | 0.032999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_137-3_0_4_line_33 |  | 26 | 27 | 0.022111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_137-3_0_4_line_34 |  | 28 | 29 | 0.038264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_137-3_0_4_line_35 |  | 28 | 30 | 0.027168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_137-3_0_4_line_36 |  | 28 | 31 | 0.054385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_137-3_0_4_line_37 |  | 29 | 60 | 0.0070014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_137-3_0_4_line_38 |  | 30 | 33 | 0.018977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_137-3_0_4_line_39 |  | 31 | 36 | 0.025646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_137-3_0_4_line_40 |  | 32 | 33 | 0.0032591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_137-3_0_4_line_41 |  | 32 | 34 | 0.003054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_137-3_0_4_line_42 |  | 32 | 35 | 0.041068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_137-3_0_4_line_43 |  | 34 | 61 | 0.022525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_137-3_0_4_line_44 |  | 34 | 55 | 0.013172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_137-3_0_4_line_45 |  | 35 | 62 | 0.027729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_137-3_0_4_line_46 |  | 36 | 54 | 0.012496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_137-3_0_4_line_47 |  | 37 | 38 | 0.062174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_137-3_0_4_line_48 |  | 37 | 39 | 0.054451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_137-3_0_4_line_49 |  | 38 | 40 | 0.003152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_137-3_0_4_line_50 |  | 38 | 41 | 0.085889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_137-3_0_4_line_51 |  | 40 | 63 | 0.019537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_137-3_0_4_line_52 |  | 40 | 64 | 0.0075252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_137-3_0_4_line_53 |  | 40 | 65 | 0.089979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_137-3_0_4_line_54 |  | 41 | 66 | 0.028873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_137-3_0_4_line_55 |  | 42 | 43 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_137-3_0_4_line_56 |  | 44 | 45 | 0.062315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_137-3_0_4_line_57 |  | 44 | 46 | 0.017959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_137-3_0_4_line_58 |  | 45 | 52 | 0.00448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_137-3_0_4_line_59 |  | 46 | 47 | 0.033496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_137-3_0_4_line_60 |  | 47 | 48 | 0.049618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_137-3_0_4_line_61 |  | 48 | 72 | 0.016179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_137-3_0_4_line_62 |  | 48 | 73 | 0.06121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_137-3_0_4_line_63 |  | 49 | 50 | 0.012178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_137-3_0_4_line_64 |  | 49 | 51 | 0.018167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_137-3_0_4_line_65 |  | 50 | 77 | 0.006635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_137-3_0_4_line_66 |  | 50 | 78 | 0.0081775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_137-3_0_4_line_67 |  | 50 | 79 | 0.045422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_137-3_0_4_line_68 |  | 50 | 67 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_137-3_0_4_line_69 |  | 51 | 68 | 0.011356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_137-3_0_4_line_70 |  | 52 | 78 | 0.034158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_137-3_0_4_line_71 |  | 54 | 86 | 0.026329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_137-3_0_4_line_72 |  | 58 | 117 | 0.00031207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_137-3_0_4_line_73 |  | 59 | 109 | 0.0098991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_137-3_0_4_line_74 |  | 60 | 100 | 0.019522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_137-3_0_4_line_75 |  | 62 | 104 | 0.019111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_137-3_0_4_line_76 |  | 63 | 91 | 0.0070525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_137-3_0_4_line_77 |  | 63 | 92 | 0.011196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_137-3_0_4_line_78 |  | 66 | 76 | 0.027629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_137-3_0_4_line_79 |  | 69 | 70 | 0.014739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_137-3_0_4_line_80 |  | 69 | 71 | 0.012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_137-3_0_4_line_81 |  | 71 | 111 | 0.079165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_137-3_0_4_line_82 |  | 71 | 110 | 0.054571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_137-3_0_4_line_83 |  | 74 | 75 | 0.017705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_137-3_0_4_line_84 |  | 74 | 76 | 0.052254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_137-3_0_4_line_85 |  | 75 | 110 | 0.0022998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_137-3_0_4_line_86 |  | 77 | 109 | 0.050777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_137-3_0_4_line_87 |  | 78 | 80 | 0.006699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_137-3_0_4_line_88 |  | 79 | 81 | 0.012065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_137-3_0_4_line_89 |  | 79 | 82 | 0.035355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_137-3_0_4_line_90 |  | 81 | 99 | 0.003741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_137-3_0_4_line_91 |  | 81 | 98 | 0.015971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_137-3_0_4_line_92 |  | 84 | 85 | 0.0028343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_137-3_0_4_line_93 |  | 85 | 86 | 0.028714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_137-3_0_4_line_94 |  | 87 | 88 | 0.028982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_137-3_0_4_line_95 |  | 88 | 89 | 0.017023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_137-3_0_4_line_96 |  | 88 | 90 | 0.003393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_137-3_0_4_line_97 |  | 89 | 99 | 0.0033779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_137-3_0_4_line_98 |  | 90 | 104 | 0.003504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_137-3_0_4_line_99 |  | 90 | 103 | 0.019849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_137-3_0_4_line_100 |  | 91 | 93 | 0.014457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_137-3_0_4_line_101 |  | 92 | 94 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_137-3_0_4_line_102 |  | 93 | 101 | 0.03202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_137-3_0_4_line_103 |  | 93 | 102 | 0.023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_137-3_0_4_line_104 |  | 94 | 100 | 0.02762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_137-3_0_4_line_105 |  | 95 | 96 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_137-3_0_4_line_106 |  | 96 | 97 | 0.033402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_137-3_0_4_line_107 |  | 97 | 98 | 0.020207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_137-3_0_4_line_108 |  | 101 | 106 | 0.036586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_137-3_0_4_line_109 |  | 102 | 108 | 0.01284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_137-3_0_4_line_110 |  | 104 | 105 | 0.0035172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_137-3_0_4_line_111 |  | 105 | 107 | 0.029608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_137-3_0_4_line_112 |  | 111 | 114 | 0.049191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_137-3_0_4_line_113 |  | 111 | 112 | 0.094191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_137-3_0_4_line_114 |  | 112 | 113 | 0.0023562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_137-3_0_4_line_115 |  | 114 | 115 | 0.0032805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_137-3_0_4_line_116 |  | 115 | 116 | 0.0059647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_137-3_0_4_line_117 |  | 117 | 118 | 0.021242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_137-3_0_4_line_118 |  | 118 | 119 | 0.0014829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_137-3_0_4_trafo_35 | 0.63 MVA 20/0.4 kV | 120 | 84 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2686194.5476 | 1236577.7382 | 2686189.721 | 1236592.2984
1 | 2686194.5476 | 1236577.7382 | 2686195.5483 | 1236574.7194 | 2686196.9733 | 1236570.5064
2 | 2686185.8781 | 1236603.8915 | 2686189.721 | 1236592.2984
3 | 2686202.1237 | 1236557.6622 | 2686199.7548 | 1236562.2827 | 2686196.9733 | 1236570.5064
4 | 2686185.8781 | 1236603.8915 | 2686182.7993 | 1236613.179
5 | 2686202.1237 | 1236557.6622 | 2686207.7844 | 1236546.6213 | 2686209.5687 | 1236543.8568
6 | 2686182.7993 | 1236613.179 | 2686182.1814 | 1236615.0432 | 2686173.6867 | 1236630.9536 | 2686166.6773 | 1236638.3906 | 2686161.057 | 1236642.2829
7 | 2686221.2009 | 1236525.8345 | 2686209.5687 | 1236543.8568
8 | 2686138.3534 | 1236648.2202 | 2686153.7508 | 1236647.3429 | 2686161.057 | 1236642.2829
9 | 2686221.2009 | 1236525.8345 | 2686223.9956 | 1236521.5053 | 2686230.3663 | 1236523.1545
10 | 2686221.2009 | 1236525.8345 | 2686200.9004 | 1236507.3611
11 | 2686138.3534 | 1236648.2202 | 2686141.4888 | 1236655.3486
12 | 2686104.9249 | 1236637.4724 | 2686124.2453 | 1236644.2128 | 2686138.3534 | 1236648.2202
13 | 2686166.645 | 1236670.885 | 2686158.3854 | 1236667.9693 | 2686151.5399 | 1236662.5439 | 2686141.4888 | 1236655.3486 | 2686141.4888 | 1236655.3486
14 | 2686104.9249 | 1236637.4724 | 2686089.3891 | 1236664.0774 | 2686086.5384 | 1236668.0071
15 | 2686104.9249 | 1236637.4724 | 2686106.6362 | 1236602.0072
16 | 2686249.1376 | 1236544.7869 | 2686247.4013 | 1236540.8477 | 2686242.6717 | 1236534.5857 | 2686235.6477 | 1236527.9012 | 2686230.3663 | 1236523.1545
17 | 2686230.3663 | 1236523.1545 | 2686213.5726 | 1236508.8607
18 | 2686200.9004 | 1236507.3611 | 2686199.4962 | 1236506.0832 | 2686183.9552 | 1236492.3257 | 2686176.9472 | 1236486.0816
19 | 2686235.8336 | 1236625.0289 | 2686235.2994 | 1236615.9591 | 2686234.6808 | 1236605.4092 | 2686238.2947 | 1236587.7282
20 | 2686235.8336 | 1236625.0289 | 2686232.1953 | 1236631.4016
21 | 2686249.1376 | 1236544.7869 | 2686250.0023 | 1236546.7341 | 2686251.4039 | 1236552.87 | 2686251.456 | 1236559.1864 | 2686250.0086 | 1236570.2622 | 2686249.246 | 1236573.881
22 | 2686266.2577 | 1236531.6149 | 2686252.2813 | 1236531.0227 | 2686252.2539 | 1236532.3899 | 2686251.6548 | 1236537.685 | 2686250.372 | 1236543.1592 | 2686249.1376 | 1236544.7869
23 | 2686213.5726 | 1236508.8607 | 2686203.3733 | 1236500.1797 | 2686192.6779 | 1236490.026
24 | 2686229.9414 | 1236637.3411 | 2686230.0099 | 1236635.2294 | 2686232.1953 | 1236631.4016
25 | 2686266.2577 | 1236531.6149 | 2686286.8602 | 1236533.4786
26 | 2686047.5769 | 1236665.7951 | 2686053.6103 | 1236669.2961
27 | 2686047.5769 | 1236665.7951 | 2686026.595 | 1236653.6214
28 | 2686053.6103 | 1236669.2961 | 2686060.6914 | 1236657.1002
29 | 2686076.1308 | 1236682.3539 | 2686053.6103 | 1236669.2961
30 | 2686026.595 | 1236653.6214 | 2686018.1549 | 1236648.7244
31 | 2686197.4751 | 1236681.7684 | 2686166.645 | 1236670.885
32 | 2686197.4751 | 1236681.7684 | 2686213.9203 | 1236658.7572 | 2686216.5509 | 1236654.8438
33 | 2686229.9414 | 1236637.3411 | 2686224.4238 | 1236643.1318 | 2686216.5509 | 1236654.8438
34 | 2686080.2109 | 1236454.706 | 2686069.1688 | 1236455.2798 | 2686045.3572 | 1236455.535 | 2686042.1624 | 1236456.6798
35 | 2686080.2109 | 1236454.706 | 2686077.8129 | 1236461.4205 | 2686067.7334 | 1236478.7387
36 | 2686080.2109 | 1236454.706 | 2686086.2924 | 1236454.3828 | 2686089.9812 | 1236449.9775 | 2686094.0691 | 1236446.7567 | 2686118.8345 | 1236443.8802 | 2686126.2449 | 1236444.8105 | 2686124.6182 | 1236449.4791
37 | 2686035.5714 | 1236459.0414 | 2686042.1624 | 1236456.6798
38 | 2686067.7334 | 1236478.7387 | 2686067.2114 | 1236479.6355 | 2686056.1995 | 1236493.7972
39 | 2686124.6182 | 1236449.4791 | 2686116.1915 | 1236473.7014
40 | 2686058.8587 | 1236495.6815 | 2686056.1995 | 1236493.7972
41 | 2686061.4149 | 1236497.3642 | 2686058.8587 | 1236495.6815
42 | 2686058.8587 | 1236495.6815 | 2686033.3408 | 1236527.8596
43 | 2686061.4149 | 1236497.3642 | 2686054.5591 | 1236506.2045 | 2686047.5893 | 1236515.1467
44 | 2686061.4149 | 1236497.3642 | 2686069.4879 | 1236486.9562
45 | 2686033.3408 | 1236527.8596 | 2686029.6204 | 1236532.551 | 2686017.7168 | 1236550.744
46 | 2686116.1915 | 1236473.7014 | 2686112.0855 | 1236485.5039
47 | 2685924.9872 | 1236400.5093 | 2685930.4305 | 1236400.3657 | 2685932.8975 | 1236405.6051 | 2685960.1166 | 1236427.7035 | 2685962.1712 | 1236435.2831 | 2685962.6076 | 1236443.2951
48 | 2685924.9872 | 1236400.5093 | 2685920.129 | 1236403.6302 | 2685894.0052 | 1236444.7032
49 | 2685962.6076 | 1236443.2951 | 2685965.6768 | 1236444.0512
50 | 2685962.6076 | 1236443.2951 | 2685961.0899 | 1236447.2427 | 2685954.1003 | 1236456.4481 | 2685940.1871 | 1236469.256 | 2685918.7473 | 1236484.4679 | 2685897.0038 | 1236496.6066
51 | 2685970.6938 | 1236462.3702 | 2685969.3611 | 1236449.3527 | 2685965.6768 | 1236444.0512
52 | 2685965.6768 | 1236444.0512 | 2685966.3614 | 1236440.1472 | 2685965.4607 | 1236436.7013
53 | 2685965.6768 | 1236444.0512 | 2685962.4072 | 1236450.8643 | 2685956.2678 | 1236459.3704 | 2685937.5534 | 1236475.5446 | 2685922.4461 | 1236486.1559 | 2685898.5147 | 1236501.4986 | 2685898.259 | 1236501.6697
54 | 2685874.2573 | 1236514.2752 | 2685877.6849 | 1236510.6485 | 2685897.0038 | 1236496.6066
55 | 2686076.1308 | 1236682.3539 | 2686086.5384 | 1236668.0071
56 | 2685886.3842 | 1236665.7294 | 2685897.0487 | 1236657.7445 | 2685902.1223 | 1236626.6512 | 2685915.5232 | 1236626.7228 | 2685915.9604 | 1236622.6596
57 | 2685886.3842 | 1236665.7294 | 2685883.3047 | 1236664.1281 | 2685870.4504 | 1236657.4444
58 | 2685915.9604 | 1236622.6596 | 2685920.4216 | 1236623.0692
59 | 2685845.7968 | 1236637.7005 | 2685848.5065 | 1236646.0345 | 2685870.4504 | 1236657.4444
60 | 2685845.7968 | 1236637.7005 | 2685834.6592 | 1236645.434 | 2685814.307 | 1236664.5092 | 2685811.7655 | 1236662.3376 | 2685815.2418 | 1236658.9965
61 | 2685815.2418 | 1236658.9965 | 2685826.8953 | 1236647.7733
62 | 2685815.2418 | 1236658.9965 | 2685812.1443 | 1236658.1178 | 2685809.4615 | 1236656.3 | 2685801.6119 | 1236647.5471 | 2685800.0996 | 1236643.2777 | 2685798.552 | 1236635.1607 | 2685799.9787 | 1236627.0311 | 2685809.9096 | 1236607.4609
63 | 2685953.0338 | 1236632.0469 | 2685958.679 | 1236624.7345 | 2685961.4024 | 1236625.8414
64 | 2685953.0338 | 1236632.0469 | 2685951.9595 | 1236645.0963 | 2685951.2583 | 1236650.1216
65 | 2685964.7696 | 1236620.1193 | 2685961.4024 | 1236625.8414
66 | 2685953.8266 | 1236622.7629 | 2685958.679 | 1236624.7345 | 2685961.4024 | 1236625.8414
67 | 2685961.4024 | 1236625.8414 | 2685958.679 | 1236624.7345 | 2685961.9212 | 1236618.7549 | 2685980.8091 | 1236588.4844
68 | 2685961.4024 | 1236625.8414 | 2685955.5719 | 1236641.7684 | 2685955.1373 | 1236643.9483
69 | 2685949.6245 | 1236661.3559 | 2685949.781 | 1236660.7092 | 2685951.2583 | 1236650.1216
70 | 2685953.8266 | 1236622.7629 | 2685947.8754 | 1236625.5899 | 2685920.4216 | 1236623.0692
71 | 2686103.4345 | 1236510.3711 | 2686112.0855 | 1236485.5039
72 | 2686060.8481 | 1236656.8303 | 2686060.6914 | 1236657.1002
73 | 2686009.5926 | 1236643.7565 | 2686018.1549 | 1236648.7244
74 | 2686017.2833 | 1236465.8649 | 2686023.9125 | 1236463.2189 | 2686035.5714 | 1236459.0414
75 | 2686006.014 | 1236565.6774 | 2686010.7529 | 1236561.3873 | 2686017.7168 | 1236550.744
76 | 2685970.6938 | 1236462.3702 | 2685971.0831 | 1236469.412
77 | 2685970.6938 | 1236462.3702 | 2685978.8565 | 1236470.0334
78 | 2685874.2573 | 1236514.2752 | 2685858.1644 | 1236531.3033 | 2685855.451 | 1236534.5089
79 | 2685749.5473 | 1236554.8515 | 2685755.3345 | 1236547.6521 | 2685757.0756 | 1236546.5653 | 2685760.5375 | 1236546.8488
80 | 2685760.5375 | 1236546.8488 | 2685763.9986 | 1236535.1349
81 | 2685796.1307 | 1236462.8583 | 2685778.4027 | 1236498.7835 | 2685775.0255 | 1236506.7849 | 2685763.9986 | 1236535.1349
82 | 2685763.9986 | 1236535.1349 | 2685767.5776 | 1236534.1191 | 2685772.1169 | 1236533.6844 | 2685779.3383 | 1236536.1682 | 2685797.7625 | 1236553.6467 | 2685807.5057 | 1236562.6374
83 | 2685822.9207 | 1236575.3811 | 2685809.1959 | 1236564.1971 | 2685809.1959 | 1236564.1971
84 | 2685822.9207 | 1236575.3811 | 2685841.5113 | 1236550.9767 | 2685855.451 | 1236534.5089
85 | 2685807.5057 | 1236562.6374 | 2685809.1959 | 1236564.1971
86 | 2685964.7696 | 1236620.1193 | 2685996.3874 | 1236635.2099 | 2686004.0216 | 1236640.5242 | 2686009.5926 | 1236643.7565
87 | 2685958.049 | 1236617.5536 | 2685953.8266 | 1236622.7629
88 | 2685980.8091 | 1236588.4844 | 2685985.6095 | 1236579.9478 | 2685987.3859 | 1236578.5169
89 | 2685980.8091 | 1236588.4844 | 2685966.7378 | 1236585.0561 | 2685951.5288 | 1236577.6196 | 2685949.654 | 1236581.0873
90 | 2685990.011 | 1236581.1901 | 2685987.3859 | 1236578.5169
91 | 2685987.3859 | 1236578.5169 | 2685984.7311 | 1236575.8099 | 2685986.6973 | 1236572.7695 | 2685987.9474 | 1236569.5297 | 2685987.7789 | 1236566.0137 | 2685987.5966 | 1236564.4585
92 | 2686093.0685 | 1236540.1677 | 2686093.9998 | 1236537.4907
93 | 2686103.4345 | 1236510.3711 | 2686093.9998 | 1236537.4907
94 | 2686006.8555 | 1236570.2706 | 2686030.4583 | 1236587.0887
95 | 2686006.8555 | 1236570.2706 | 2686002.9367 | 1236572.282 | 2685997.9937 | 1236573.945 | 2685992.5122 | 1236578.92
96 | 2686006.8555 | 1236570.2706 | 2686008.9526 | 1236567.5991
97 | 2685990.011 | 1236581.1901 | 2685992.5122 | 1236578.92
98 | 2686008.9526 | 1236567.5991 | 2686006.014 | 1236565.6774
99 | 2686008.9526 | 1236567.5991 | 2686013.4246 | 1236561.8819 | 2686020.624 | 1236551.5527
100 | 2685971.8812 | 1236483.8472 | 2685971.0831 | 1236469.412
101 | 2685978.8565 | 1236470.0334 | 2685979.9443 | 1236471.0547 | 2685981.7909 | 1236473.1385 | 2685991.5901 | 1236475.5259
102 | 2685971.8812 | 1236483.8472 | 2685982.9944 | 1236513.885
103 | 2685971.8812 | 1236483.8472 | 2685959.6636 | 1236489.3076 | 2685951.2954 | 1236495.2822
104 | 2685991.5901 | 1236475.5259 | 2685992.5143 | 1236475.7511 | 2686017.2833 | 1236465.8649
105 | 2685946.7331 | 1236545.4363 | 2685956.2489 | 1236539.0826 | 2685957.2575 | 1236540.5474
106 | 2685985.7543 | 1236544.3467 | 2685979.9053 | 1236545.3405 | 2685972.867 | 1236547.4624 | 2685963.0232 | 1236548.921 | 2685957.2575 | 1236540.5474
107 | 2685985.7543 | 1236544.3467 | 2685985.7818 | 1236546.6265 | 2685986.3847 | 1236554.1183 | 2685987.5966 | 1236564.4585
108 | 2685982.9944 | 1236513.885 | 2685967.4604 | 1236513.2041 | 2685947.8301 | 1236521.0368
109 | 2685940.8456 | 1236502.7431 | 2685951.2954 | 1236495.2822
110 | 2686006.014 | 1236565.6774 | 2686003.0755 | 1236563.7446
111 | 2685992.537 | 1236542.6325 | 2685994.1312 | 1236561.6136 | 2685995.8846 | 1236563.8628 | 2685998.5942 | 1236564.8805 | 2686001.4554 | 1236564.833 | 2686003.0755 | 1236563.7446
112 | 2685796.1307 | 1236462.8583 | 2685838.9769 | 1236438.6927
113 | 2685733.3452 | 1236486.7246 | 2685757.0183 | 1236450.4626 | 2685762.5038 | 1236441.1129 | 2685796.1307 | 1236462.8583
114 | 2685733.3452 | 1236486.7246 | 2685731.5664 | 1236488.2699
115 | 2685841.8343 | 1236437.0811 | 2685838.9769 | 1236438.6927
116 | 2685847.0297 | 1236434.1509 | 2685841.8343 | 1236437.0811
117 | 2686060.8481 | 1236656.8303 | 2686071.5138 | 1236638.4604
118 | 2686072.2584 | 1236637.178 | 2686071.5138 | 1236638.4604

## bus_geodata
| x | y | coords
0 | 2686194.5476 | 1236577.7382
1 | 2686189.721 | 1236592.2984
2 | 2686196.9733 | 1236570.5064
3 | 2686185.8781 | 1236603.8915
4 | 2686202.1237 | 1236557.6622
5 | 2686182.7993 | 1236613.179
6 | 2686209.5687 | 1236543.8568
7 | 2686161.057 | 1236642.2829
8 | 2686221.2009 | 1236525.8345
9 | 2686138.3534 | 1236648.2202
10 | 2686141.4888 | 1236655.3486
11 | 2686104.9249 | 1236637.4724
12 | 2686230.3663 | 1236523.1545
13 | 2686200.9004 | 1236507.3611
14 | 2686238.2947 | 1236587.7282
15 | 2686235.8336 | 1236625.0289
16 | 2686249.1376 | 1236544.7869
17 | 2686213.5726 | 1236508.8607
18 | 2686232.1953 | 1236631.4016
19 | 2686266.2577 | 1236531.6149
20 | 2686286.8602 | 1236533.4786
21 | 2686047.5769 | 1236665.7951
22 | 2686053.6103 | 1236669.2961
23 | 2686026.595 | 1236653.6214
24 | 2686197.4751 | 1236681.7684
25 | 2686166.645 | 1236670.885
26 | 2686216.5509 | 1236654.8438
27 | 2686229.9414 | 1236637.3411
28 | 2686080.2109 | 1236454.706
29 | 2686042.1624 | 1236456.6798
30 | 2686067.7334 | 1236478.7387
31 | 2686124.6182 | 1236449.4791
32 | 2686058.8587 | 1236495.6815
33 | 2686056.1995 | 1236493.7972
34 | 2686061.4149 | 1236497.3642
35 | 2686033.3408 | 1236527.8596
36 | 2686116.1915 | 1236473.7014
37 | 2685924.9872 | 1236400.5093
38 | 2685962.6076 | 1236443.2951
39 | 2685894.0052 | 1236444.7032
40 | 2685965.6768 | 1236444.0512
41 | 2685897.0038 | 1236496.6066
42 | 2686076.1308 | 1236682.3539
43 | 2686086.5384 | 1236668.0071
44 | 2685886.3842 | 1236665.7294
45 | 2685915.9604 | 1236622.6596
46 | 2685870.4504 | 1236657.4444
47 | 2685845.7968 | 1236637.7005
48 | 2685815.2418 | 1236658.9965
49 | 2685953.0338 | 1236632.0469
50 | 2685961.4024 | 1236625.8414
51 | 2685951.2583 | 1236650.1216
52 | 2685920.4216 | 1236623.0692
53 | 2686176.9472 | 1236486.0816
54 | 2686112.0855 | 1236485.5039
55 | 2686069.4879 | 1236486.9562
56 | 2686249.246 | 1236573.881
57 | 2686192.6779 | 1236490.026
58 | 2686060.6914 | 1236657.1002
59 | 2686018.1549 | 1236648.7244
60 | 2686035.5714 | 1236459.0414
61 | 2686047.5893 | 1236515.1467
62 | 2686017.7168 | 1236550.744
63 | 2685970.6937 | 1236462.3702
64 | 2685965.4607 | 1236436.7013
65 | 2685898.259 | 1236501.6697
66 | 2685874.2573 | 1236514.2752
67 | 2685955.1373 | 1236643.9483
68 | 2685949.6245 | 1236661.3559
69 | 2685760.5375 | 1236546.8488
70 | 2685749.5473 | 1236554.8515
71 | 2685763.9986 | 1236535.1349
72 | 2685826.8953 | 1236647.7733
73 | 2685809.9096 | 1236607.4609
74 | 2685822.9207 | 1236575.3811
75 | 2685809.1959 | 1236564.1971
76 | 2685855.451 | 1236534.5089
77 | 2685964.7696 | 1236620.1193
78 | 2685953.8266 | 1236622.7629
79 | 2685980.8091 | 1236588.4844
80 | 2685958.049 | 1236617.5536
81 | 2685987.3859 | 1236578.5169
82 | 2685949.654 | 1236581.0873
83 | 2686106.6362 | 1236602.0072
84 | 2686093.0685 | 1236540.1677
85 | 2686093.9998 | 1236537.4907
86 | 2686103.4345 | 1236510.3711
87 | 2686030.4583 | 1236587.0887
88 | 2686006.8555 | 1236570.2706
89 | 2685992.5122 | 1236578.92
90 | 2686008.9526 | 1236567.5991
91 | 2685971.0831 | 1236469.412
92 | 2685978.8565 | 1236470.0334
93 | 2685971.8812 | 1236483.8472
94 | 2685991.5901 | 1236475.5259
95 | 2685946.7331 | 1236545.4363
96 | 2685957.2575 | 1236540.5474
97 | 2685985.7543 | 1236544.3467
98 | 2685987.5966 | 1236564.4585
99 | 2685990.011 | 1236581.1901
100 | 2686017.2833 | 1236465.8649
101 | 2685982.9944 | 1236513.885
102 | 2685951.2954 | 1236495.2822
103 | 2686020.624 | 1236551.5527
104 | 2686006.014 | 1236565.6774
105 | 2686003.0755 | 1236563.7446
106 | 2685947.8301 | 1236521.0368
107 | 2685992.537 | 1236542.6325
108 | 2685940.8456 | 1236502.7431
109 | 2686009.5926 | 1236643.7565
110 | 2685807.5057 | 1236562.6374
111 | 2685796.1307 | 1236462.8583
112 | 2685733.3452 | 1236486.7246
113 | 2685731.5664 | 1236488.2699
114 | 2685838.9769 | 1236438.6927
115 | 2685841.8343 | 1236437.0811
116 | 2685847.0297 | 1236434.1508
117 | 2686060.8481 | 1236656.8303
118 | 2686071.5138 | 1236638.4604
119 | 2686072.2584 | 1236637.178
120 | 2686124.6182 | 1236449.4791

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97271 | -0.52625 | 0.009251 | 0.0023185
1 | 0.97287 | -0.52301 | 0.0018146 | 0.00045479
2 | 0.97258 | -0.52882 | 0.0016722 | 0.00041911
3 | 0.97301 | -0.52032 | 0.0096657 | 0.0024224
4 | 0.97235 | -0.53329 | 0.0091473 | 0.0022925
5 | 0.97314 | -0.51774 | 0.0028204 | 0.00070685
6 | 0.97197 | -0.54077 | 0.0037887 | 0.00094953
7 | 0.97366 | -0.50748 | 0.0084867 | 0.002127
8 | 0.97153 | -0.5495 | 0 | 0
9 | 0.97405 | -0.49981 | 0 | 0
10 | 0.97381 | -0.50445 | 0.0089936 | 0.002254
11 | 0.97488 | -0.48355 | 0 | 0
12 | 0.97139 | -0.55229 | 0 | 0
13 | 0.9713 | -0.55413 | 0.0081153 | 0.0020339
14 | 0.97185 | -0.54327 | 0.0030377 | 0.00076132
15 | 0.97196 | -0.54116 | 0 | 0
16 | 0.9712 | -0.55616 | 0 | 0
17 | 0.97128 | -0.5546 | 0.002941 | 0.00073707
18 | 0.97198 | -0.54074 | 0.0046576 | 0.0011673
19 | 0.97116 | -0.55689 | 0 | 0
20 | 0.97113 | -0.55743 | 0.0014058 | 0.00035232
21 | 0.97714 | -0.43902 | 0 | 0
22 | 0.97694 | -0.44301 | 0 | 0
23 | 0.97785 | -0.42512 | 0.0015751 | 0.00039477
24 | 0.97267 | -0.52695 | 0 | 0
25 | 0.97316 | -0.51733 | 0.0074599 | 0.0018696
26 | 0.97218 | -0.53668 | 0.0082922 | 0.0020782
27 | 0.97202 | -0.53982 | 0 | 0
28 | 0.99003 | -0.18935 | 0 | 0
29 | 0.98795 | -0.2295 | 0.0016159 | 0.00040498
30 | 0.98867 | -0.21543 | 0.0035965 | 0.00090136
31 | 0.99349 | -0.12321 | 0 | 0
32 | 0.98758 | -0.23642 | 0 | 0
33 | 0.98774 | -0.23339 | 0.0040269 | 0.0010092
34 | 0.98755 | -0.2369 | 0 | 0
35 | 0.98568 | -0.27304 | 0.0050218 | 0.0012586
36 | 0.99513 | -0.092172 | 0.00081855 | 0.00020515
37 | 0.98358 | -0.31465 | 0 | 0
38 | 0.98365 | -0.31329 | 0 | 0
39 | 0.98352 | -0.31584 | 0.0012143 | 0.00030433
40 | 0.9837 | -0.31223 | 0 | 0
41 | 0.98227 | -0.34026 | 0.0024521 | 0.00061454
42 | 0.97625 | -0.45645 | 0 | 0
43 | 0.97579 | -0.46563 | 0.0035908 | 0.00089995
44 | 0.97923 | -0.39841 | 0 | 0
45 | 0.97968 | -0.38943 | 0 | 0
46 | 0.9791 | -0.401 | 0.0050171 | 0.0012574
47 | 0.97901 | -0.40277 | 0 | 0
48 | 0.97887 | -0.4054 | 0 | 0
49 | 0.9802 | -0.37929 | 0 | 0
50 | 0.98023 | -0.37879 | 0 | 0
51 | 0.98016 | -0.38004 | 0.0011355 | 0.00028459
52 | 0.97972 | -0.38878 | 0.0040052 | 0.0010038
53 | 0.97127 | -0.55473 | 0.001016 | 0.00025464
54 | 0.99592 | -0.077042 | 0.00456 | 0.0011428
55 | 0.9875 | -0.23792 | 0.0043331 | 0.001086
56 | 0.97104 | -0.55934 | 0.0058219 | 0.0014591
57 | 0.9712 | -0.55602 | 0.0027306 | 0.00068436
58 | 0.97678 | -0.4462 | 0.0039312 | 0.00098526
59 | 0.97814 | -0.41947 | 0.0038953 | 0.00097624
60 | 0.98758 | -0.23666 | 0.0012446 | 0.00031192
61 | 0.98746 | -0.2387 | 0.0044667 | 0.0011195
62 | 0.98443 | -0.29723 | 0.0034636 | 0.00086807
63 | 0.98419 | -0.30264 | 0 | 0
64 | 0.98367 | -0.31292 | 0.0051056 | 0.0012796
65 | 0.98341 | -0.31795 | 0.0035263 | 0.00088377
66 | 0.98187 | -0.34806 | 0.0024511 | 0.00061431
67 | 0.98017 | -0.37983 | 0.0029944 | 0.00075047
68 | 0.98015 | -0.38028 | 0.0011355 | 0.00028459
69 | 0.98048 | -0.37525 | 0 | 0
70 | 0.98047 | -0.37546 | 0.00077463 | 0.00019414
71 | 0.98049 | -0.37508 | 0 | 0
72 | 0.97886 | -0.40571 | 0.0010838 | 0.00027163
73 | 0.97877 | -0.40743 | 0.001823 | 0.0004569
74 | 0.98104 | -0.36421 | 0 | 0
75 | 0.98087 | -0.36757 | 0.0012456 | 0.00031219
76 | 0.98155 | -0.35431 | 0.002035 | 0.00051002
77 | 0.98002 | -0.3828 | 0 | 0
78 | 0.98009 | -0.38138 | 0 | 0
79 | 0.98188 | -0.34671 | 0 | 0
80 | 0.98006 | -0.38205 | 0.0055232 | 0.0013842
81 | 0.98232 | -0.33801 | 0 | 0
82 | 0.98176 | -0.34898 | 0.0035608 | 0.00089242
83 | 0.97459 | -0.48909 | 0.0085049 | 0.0021315
84 | 1 | 0 | -0.3447 | -0.088112
85 | 0.99978 | -0.0041699 | 0.014315 | 0.0035877
86 | 0.99763 | -0.044719 | 0.043307 | 0.010854
87 | 0.98315 | -0.32199 | 0.0051147 | 0.0012819
88 | 0.98329 | -0.31931 | 0 | 0
89 | 0.9826 | -0.3326 | 0.0047019 | 0.0011784
90 | 0.98343 | -0.31659 | 0 | 0
91 | 0.98409 | -0.30458 | 0.0020686 | 0.00051844
92 | 0.98463 | -0.29407 | 0.0043706 | 0.0010954
93 | 0.98392 | -0.30803 | 0 | 0
94 | 0.98525 | -0.28195 | 0.0049977 | 0.0012525
95 | 0.98187 | -0.34685 | 0.0028004 | 0.00070185
96 | 0.98191 | -0.34618 | 0.0030363 | 0.00076096
97 | 0.98209 | -0.34266 | 0 | 0
98 | 0.9822 | -0.34053 | 0.0028946 | 0.00072544
99 | 0.98247 | -0.33516 | 0 | 0
100 | 0.98658 | -0.25622 | 0.004071 | 0.0010203
101 | 0.98382 | -0.30987 | 0 | 0
102 | 0.9837 | -0.31231 | 0.0033935 | 0.0008505
103 | 0.98326 | -0.31993 | 0.0093425 | 0.0023415
104 | 0.98358 | -0.31363 | 0 | 0
105 | 0.98357 | -0.31384 | 0.0019483 | 0.00048828
106 | 0.98371 | -0.31198 | 0.0031975 | 0.00080136
107 | 0.98353 | -0.31453 | 0.0012974 | 0.00032517
108 | 0.98362 | -0.31385 | 0.0066489 | 0.0016664
109 | 0.97844 | -0.41356 | 0.0021769 | 0.00054559
110 | 0.98085 | -0.36795 | 0.0020125 | 0.00050437
111 | 0.98002 | -0.38431 | 0 | 0
112 | 0.97983 | -0.38807 | 0 | 0
113 | 0.97982 | -0.38816 | 0.0021983 | 0.00055094
114 | 0.97983 | -0.38808 | 0.0016837 | 0.00042198
115 | 0.97982 | -0.38823 | 0.0014488 | 0.00036311
116 | 0.97981 | -0.38835 | 0.0010917 | 0.0002736
117 | 0.97678 | -0.44625 | 0.0021615 | 0.00054174
118 | 0.97665 | -0.44868 | 0.0026785 | 0.00067129
119 | 0.97665 | -0.44878 | 0.0036014 | 0.0009026
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.045927 | -0.011521 | 0.045934 | 0.011525 | 7.0992e-06 | 3.7817e-06 | 0.070261 | 0.070261 | 0.070261 | 0.97271 | -0.52625 | 0.97287 | -0.52301 | 4.8256
1 | 0.036676 | 0.0092025 | -0.036672 | -0.0091998 | 4.5027e-06 | 2.6924e-06 | 0.056109 | 0.05611 | 0.05611 | 0.97271 | -0.52625 | 0.97258 | -0.52882 | 7.7074
2 | -0.047749 | -0.01198 | 0.047755 | 0.011983 | 6.1079e-06 | 3.3023e-06 | 0.073037 | 0.073036 | 0.073037 | 0.97287 | -0.52301 | 0.97301 | -0.52032 | 5.0162
3 | 0.034999 | 0.0087807 | -0.034992 | -0.0087763 | 7.4599e-06 | 4.4301e-06 | 0.053551 | 0.053551 | 0.053551 | 0.97258 | -0.52882 | 0.97235 | -0.53329 | 7.3559
4 | -0.057421 | -0.014405 | 0.057428 | 0.014409 | 7.0742e-06 | 4.0413e-06 | 0.087818 | 0.087818 | 0.087818 | 0.97301 | -0.52032 | 0.97314 | -0.51774 | 6.0315
5 | 0.025845 | 0.0064838 | -0.025835 | -0.0064781 | 9.2093e-06 | 5.6993e-06 | 0.039553 | 0.039553 | 0.039553 | 0.97235 | -0.53329 | 0.97197 | -0.54077 | 10.8662
6 | -0.060248 | -0.015116 | 0.060277 | 0.015133 | 2.9487e-05 | 1.7029e-05 | 0.09213 | 0.09213 | 0.09213 | 0.97314 | -0.51774 | 0.97366 | -0.50748 | 6.3276
7 | 0.022047 | 0.0055286 | -0.022037 | -0.005523 | 9.1639e-06 | 5.5992e-06 | 0.033753 | 0.033753 | 0.033753 | 0.97197 | -0.54077 | 0.97153 | -0.5495 | 9.2728
8 | -0.068764 | -0.01726 | 0.068789 | 0.017275 | 2.5174e-05 | 1.4901e-05 | 0.1051 | 0.1051 | 0.1051 | 0.97366 | -0.50748 | 0.97405 | -0.49981 | 7.2184
9 | 0.012904 | 0.0032339 | -0.012902 | -0.0032329 | 1.7188e-06 | 9.5473e-07 | 0.019764 | 0.019764 | 0.019764 | 0.97153 | -0.5495 | 0.97139 | -0.55229 | 5.4297
10 | 0.0091334 | 0.0022891 | -0.0091314 | -0.0022881 | 2.0142e-06 | 9.4929e-07 | 0.013989 | 0.013989 | 0.013989 | 0.97153 | -0.5495 | 0.9713 | -0.55413 | 3.8431
11 | 0.032479 | 0.0081528 | -0.032472 | -0.0081482 | 7.1907e-06 | 4.5051e-06 | 0.049622 | 0.049622 | 0.049622 | 0.97405 | -0.49981 | 0.97381 | -0.50445 | 13.6324
12 | -0.10127 | -0.025428 | 0.10135 | 0.025477 | 7.8625e-05 | 4.8574e-05 | 0.15472 | 0.15472 | 0.15472 | 0.97405 | -0.49981 | 0.97488 | -0.48355 | 10.6265
13 | 0.023478 | 0.0058942 | -0.023464 | -0.0058854 | 1.4412e-05 | 8.8528e-06 | 0.035879 | 0.035879 | 0.035879 | 0.97381 | -0.50445 | 0.97316 | -0.51733 | 9.857
14 | -0.10985 | -0.027609 | 0.10995 | 0.027667 | 9.4035e-05 | 5.8402e-05 | 0.16771 | 0.1677 | 0.16771 | 0.97488 | -0.48355 | 0.97579 | -0.46563 | 11.5182
15 | 0.0085071 | 0.0021325 | -0.0085049 | -0.0021315 | 2.2451e-06 | 9.9428e-07 | 0.012985 | 0.012985 | 0.012985 | 0.97488 | -0.48355 | 0.97459 | -0.48909 | 3.5674
16 | 0.00723 | 0.0018116 | -0.0072286 | -0.0018111 | 1.3299e-06 | 4.9329e-07 | 0.011075 | 0.011075 | 0.011075 | 0.97139 | -0.55229 | 0.9712 | -0.55616 | 3.0426
17 | 0.0056724 | 0.0014213 | -0.0056718 | -0.0014212 | 6.2439e-07 | 1.2664e-07 | 0.0086891 | 0.0086892 | 0.0086892 | 0.97139 | -0.55229 | 0.97128 | -0.5546 | 2.3871
18 | 0.001016 | 0.00025426 | -0.001016 | -0.00025464 | 2.9108e-08 | -3.7792e-07 | 0.0015564 | 0.0015566 | 0.0015566 | 0.9713 | -0.55413 | 0.97127 | -0.55473 | 0.42762
19 | -0.0030377 | -0.00076132 | 0.003038 | 0.00076105 | 3.0582e-07 | -2.7147e-07 | 0.0046511 | 0.0046509 | 0.0046511 | 0.97185 | -0.54327 | 0.97196 | -0.54116 | 1.2778
20 | -0.003038 | -0.00076105 | 0.0030381 | 0.000761 | 5.9525e-08 | -5.2854e-08 | 0.0046509 | 0.0046509 | 0.0046509 | 0.97196 | -0.54116 | 0.97198 | -0.54074 | 1.2777
21 | 0.0058228 | 0.0014593 | -0.0058219 | -0.0014591 | 8.8375e-07 | 1.9926e-07 | 0.0089213 | 0.0089215 | 0.0089215 | 0.9712 | -0.55616 | 0.97104 | -0.55934 | 2.451
22 | 0.0014059 | 0.00035177 | -0.0014058 | -0.00035209 | 4.932e-08 | -3.1924e-07 | 0.0021538 | 0.0021539 | 0.0021539 | 0.9712 | -0.55616 | 0.97116 | -0.55689 | 0.59173
23 | 0.0027308 | 0.00068413 | -0.0027306 | -0.00068436 | 1.8471e-07 | -2.3005e-07 | 0.0041836 | 0.0041837 | 0.0041837 | 0.97128 | -0.5546 | 0.9712 | -0.55602 | 1.1494
24 | -0.0076957 | -0.0019283 | 0.007696 | 0.0019284 | 3.3939e-07 | 1.3639e-07 | 0.011781 | 0.011781 | 0.011781 | 0.97198 | -0.54074 | 0.97202 | -0.53982 | 3.2366
25 | 0.0014058 | 0.00035209 | -0.0014058 | -0.00035232 | 3.5991e-08 | -2.3292e-07 | 0.0021539 | 0.002154 | 0.002154 | 0.97116 | -0.55689 | 0.97113 | -0.55743 | 0.59176
26 | 0.12606 | 0.031761 | -0.12604 | -0.031746 | 2.4061e-05 | 1.505e-05 | 0.19203 | 0.19203 | 0.19203 | 0.97714 | -0.43902 | 0.97694 | -0.44301 | 13.1888
27 | -0.12606 | -0.031761 | 0.12615 | 0.031813 | 8.386e-05 | 5.2454e-05 | 0.19203 | 0.19203 | 0.19203 | 0.97714 | -0.43902 | 0.97785 | -0.42512 | 13.1888
28 | 0.012375 | 0.0031021 | -0.012373 | -0.0031011 | 1.879e-06 | 1.026e-06 | 0.01885 | 0.01885 | 0.01885 | 0.97694 | -0.44301 | 0.97678 | -0.4462 | 5.1785
29 | 0.11366 | 0.028644 | -0.11359 | -0.028598 | 7.3034e-05 | 4.5442e-05 | 0.17318 | 0.17318 | 0.17318 | 0.97694 | -0.44301 | 0.97625 | -0.45645 | 11.8943
30 | -0.12772 | -0.032208 | 0.12776 | 0.03223 | 3.4581e-05 | 2.1642e-05 | 0.19443 | 0.19443 | 0.19443 | 0.97785 | -0.42512 | 0.97814 | -0.41947 | 13.3534
31 | -0.015997 | -0.0040115 | 0.016004 | 0.0040158 | 7.3431e-06 | 4.2936e-06 | 0.024473 | 0.024473 | 0.024473 | 0.97267 | -0.52695 | 0.97316 | -0.51733 | 6.7234
32 | 0.015997 | 0.0040115 | -0.015989 | -0.0040071 | 7.4115e-06 | 4.334e-06 | 0.024473 | 0.024473 | 0.024473 | 0.97267 | -0.52695 | 0.97218 | -0.53668 | 6.7234
33 | 0.0076972 | 0.0019289 | -0.007696 | -0.0019284 | 1.1508e-06 | 4.6242e-07 | 0.011781 | 0.011781 | 0.011781 | 0.97218 | -0.53668 | 0.97202 | -0.53982 | 3.2366
34 | 0.059209 | 0.014967 | -0.059095 | -0.014895 | 0.00011375 | 7.2309e-05 | 0.089036 | 0.089036 | 0.089036 | 0.99003 | -0.18935 | 0.98795 | -0.2295 | 24.4605
35 | 0.21817 | 0.055653 | -0.21789 | -0.055478 | 0.00027444 | 0.00017425 | 0.32825 | 0.32826 | 0.32826 | 0.99003 | -0.18935 | 0.98867 | -0.21543 | 22.545
36 | -0.27738 | -0.070619 | 0.27826 | 0.071185 | 0.00088782 | 0.00056539 | 0.41729 | 0.41729 | 0.41729 | 0.99003 | -0.18935 | 0.99349 | -0.12321 | 28.6601
37 | 0.057479 | 0.01449 | -0.057459 | -0.014477 | 1.9691e-05 | 1.2513e-05 | 0.086602 | 0.086602 | 0.086602 | 0.98795 | -0.2295 | 0.98758 | -0.23666 | 23.7919
38 | 0.2143 | 0.054577 | -0.21411 | -0.054459 | 0.00018543 | 0.0001177 | 0.32284 | 0.32284 | 0.32284 | 0.98867 | -0.21543 | 0.98774 | -0.23339 | 22.1733
39 | -0.27826 | -0.071185 | 0.27868 | 0.071451 | 0.00041867 | 0.00026662 | 0.41729 | 0.41729 | 0.41729 | 0.99349 | -0.12321 | 0.99513 | -0.092172 | 28.66
40 | -0.21005 | -0.053431 | 0.21008 | 0.05345 | 3.066e-05 | 1.9456e-05 | 0.31678 | 0.31678 | 0.31678 | 0.98758 | -0.23642 | 0.98774 | -0.23339 | 21.7566
41 | 0.0088006 | 0.0022054 | -0.0088004 | -0.0022054 | 2.0137e-07 | 8.9799e-08 | 0.01326 | 0.01326 | 0.01326 | 0.98758 | -0.23642 | 0.98755 | -0.2369 | 3.6429
42 | 0.20125 | 0.051225 | -0.2009 | -0.051 | 0.00035468 | 0.0002249 | 0.30352 | 0.30352 | 0.30352 | 0.98758 | -0.23642 | 0.98568 | -0.27304 | 20.8459
43 | 0.0044671 | 0.0011194 | -0.0044667 | -0.0011195 | 3.8268e-07 | -4.3258e-08 | 0.0067308 | 0.0067309 | 0.0067309 | 0.98755 | -0.2369 | 0.98746 | -0.2387 | 1.8492
44 | 0.0043333 | 0.0010859 | -0.0043331 | -0.001086 | 2.1058e-07 | -3.3755e-08 | 0.0065292 | 0.0065293 | 0.0065293 | 0.98755 | -0.2369 | 0.9875 | -0.23792 | 1.7938
45 | 0.19588 | 0.049742 | -0.19565 | -0.049597 | 0.00022767 | 0.00014429 | 0.29594 | 0.29594 | 0.29594 | 0.98568 | -0.27304 | 0.98443 | -0.29723 | 20.3253
46 | -0.2795 | -0.071657 | 0.27971 | 0.071787 | 0.0002052 | 0.00013068 | 0.41851 | 0.41851 | 0.41851 | 0.99513 | -0.092172 | 0.99592 | -0.077042 | 28.744
47 | -0.0012143 | -0.00030368 | 0.0012144 | 0.00030294 | 7.8657e-08 | -7.3882e-07 | 0.0018369 | 0.0018366 | 0.0018369 | 0.98358 | -0.31465 | 0.98365 | -0.31329 | 0.50464
48 | 0.0012143 | 0.00030368 | -0.0012143 | -0.00030433 | 6.8908e-08 | -6.4695e-07 | 0.0018369 | 0.0018371 | 0.0018371 | 0.98358 | -0.31465 | 0.98352 | -0.31584 | 0.50471
49 | -0.018653 | -0.0046842 | 0.018654 | 0.0046848 | 9.4134e-07 | 5.6244e-07 | 0.02822 | 0.02822 | 0.02822 | 0.98365 | -0.31329 | 0.9837 | -0.31223 | 7.7529
50 | 0.017438 | 0.0043813 | -0.017416 | -0.004368 | 2.2421e-05 | 1.3261e-05 | 0.026384 | 0.026384 | 0.026384 | 0.98365 | -0.31329 | 0.98227 | -0.34026 | 7.2484
51 | -0.027287 | -0.0068476 | 0.027299 | 0.0068553 | 1.2484e-05 | 7.7415e-06 | 0.041279 | 0.041279 | 0.041279 | 0.9837 | -0.31223 | 0.98419 | -0.30264 | 11.3404
52 | 0.0051057 | 0.0012796 | -0.0051056 | -0.0012796 | 1.6833e-07 | 1.22e-08 | 0.0077233 | 0.0077233 | 0.0077233 | 0.9837 | -0.31223 | 0.98367 | -0.31292 | 2.1218
53 | 0.0035272 | 0.00088324 | -0.0035263 | -0.00088377 | 9.6055e-07 | -5.272e-07 | 0.0053353 | 0.0053357 | 0.0053357 | 0.9837 | -0.31223 | 0.98341 | -0.31795 | 1.4658
54 | 0.014964 | 0.0037535 | -0.014958 | -0.0037503 | 5.5644e-06 | 3.1959e-06 | 0.02267 | 0.02267 | 0.02267 | 0.98227 | -0.34026 | 0.98187 | -0.34806 | 6.228
55 | 0.11359 | 0.028598 | -0.11354 | -0.028567 | 4.9835e-05 | 3.1009e-05 | 0.17318 | 0.17318 | 0.17318 | 0.97625 | -0.45645 | 0.97579 | -0.46563 | 11.8943
56 | -0.0079258 | -0.0019848 | 0.0079291 | 0.0019862 | 3.3892e-06 | 1.3848e-06 | 0.012043 | 0.012043 | 0.012043 | 0.97923 | -0.39841 | 0.97968 | -0.38943 | 3.3086
57 | 0.0079258 | 0.0019848 | -0.0079248 | -0.0019844 | 9.768e-07 | 3.9926e-07 | 0.012043 | 0.012043 | 0.012043 | 0.97923 | -0.39841 | 0.9791 | -0.401 | 3.3086
58 | -0.0079291 | -0.0019862 | 0.0079294 | 0.0019863 | 2.4366e-07 | 9.9527e-08 | 0.012043 | 0.012043 | 0.012043 | 0.97968 | -0.38943 | 0.97972 | -0.38878 | 3.3085
59 | 0.0029077 | 0.00072702 | -0.0029074 | -0.00072729 | 2.4523e-07 | -2.6428e-07 | 0.0044184 | 0.0044186 | 0.0044186 | 0.9791 | -0.401 | 0.97901 | -0.40277 | 1.2139
60 | 0.0029074 | 0.00072729 | -0.0029071 | -0.00072768 | 3.6329e-07 | -3.9131e-07 | 0.0044186 | 0.0044188 | 0.0044188 | 0.97901 | -0.40277 | 0.97887 | -0.4054 | 1.214
61 | 0.0010838 | 0.00027144 | -0.0010838 | -0.00027163 | 1.6469e-08 | -1.9284e-07 | 0.0016475 | 0.0016476 | 0.0016476 | 0.97887 | -0.4054 | 0.97886 | -0.40571 | 0.45263
62 | 0.0018232 | 0.00045624 | -0.001823 | -0.0004569 | 1.763e-07 | -6.5654e-07 | 0.0027713 | 0.0027715 | 0.0027715 | 0.97887 | -0.4054 | 0.97877 | -0.40743 | 0.76141
63 | -0.0022712 | -0.00056888 | 0.0022712 | 0.00056876 | 5.4281e-08 | -1.1876e-07 | 0.0034477 | 0.0034476 | 0.0034477 | 0.9802 | -0.37929 | 0.98023 | -0.37879 | 0.94717
64 | 0.0022712 | 0.00056888 | -0.0022711 | -0.00056905 | 8.0983e-08 | -1.7716e-07 | 0.0034477 | 0.0034478 | 0.0034478 | 0.9802 | -0.37929 | 0.98016 | -0.38004 | 0.94719
65 | 0.13409 | 0.033915 | -0.13406 | -0.033899 | 2.58e-05 | 1.6178e-05 | 0.20366 | 0.20366 | 0.20366 | 0.98023 | -0.37879 | 0.98002 | -0.3828 | 13.9877
66 | 0.017464 | 0.0043779 | -0.017462 | -0.0043766 | 2.1554e-06 | 1.2764e-06 | 0.026512 | 0.026512 | 0.026512 | 0.98023 | -0.37879 | 0.98009 | -0.38138 | 7.2835
67 | -0.15682 | -0.039612 | 0.15706 | 0.039764 | 0.00024154 | 0.00015229 | 0.23817 | 0.23817 | 0.23817 | 0.98023 | -0.37879 | 0.98188 | -0.34671 | 16.3576
68 | 0.0029946 | 0.00075033 | -0.0029944 | -0.00075047 | 1.4866e-07 | -1.4667e-07 | 0.0045458 | 0.0045459 | 0.0045459 | 0.98023 | -0.37879 | 0.98017 | -0.37983 | 1.2489
69 | 0.0011356 | 0.00028446 | -0.0011355 | -0.00028459 | 1.2655e-08 | -1.3502e-07 | 0.0017239 | 0.0017239 | 0.0017239 | 0.98016 | -0.38004 | 0.98015 | -0.38028 | 0.47361
70 | -0.011935 | -0.0029901 | 0.011939 | 0.0029924 | 4.2085e-06 | 2.2632e-06 | 0.018126 | 0.018126 | 0.018126 | 0.97972 | -0.38878 | 0.98009 | -0.38138 | 4.9797
71 | -0.28427 | -0.07293 | 0.28471 | 0.073214 | 0.00044653 | 0.00028441 | 0.42533 | 0.42533 | 0.42533 | 0.99592 | -0.077042 | 0.99763 | -0.044719 | 29.2119
72 | 0.0084422 | 0.0021158 | -0.0084422 | -0.0021158 | 1.9356e-08 | 8.482e-09 | 0.012861 | 0.012861 | 0.012861 | 0.97678 | -0.4462 | 0.97678 | -0.44625 | 3.5332
73 | -0.13165 | -0.033206 | 0.13169 | 0.033229 | 3.7252e-05 | 2.3344e-05 | 0.20035 | 0.20035 | 0.20035 | 0.97814 | -0.41947 | 0.97844 | -0.41356 | 13.7604
74 | 0.056215 | 0.014165 | -0.056162 | -0.014132 | 5.2555e-05 | 3.3386e-05 | 0.084727 | 0.084727 | 0.084727 | 0.98758 | -0.23666 | 0.98658 | -0.25622 | 23.2767
75 | 0.19219 | 0.048729 | -0.19203 | -0.048633 | 0.00015141 | 9.5932e-05 | 0.2907 | 0.2907 | 0.2907 | 0.98443 | -0.29723 | 0.98358 | -0.31363 | 19.9657
76 | 0.015315 | 0.0038394 | -0.015314 | -0.0038385 | 1.418e-06 | 8.1793e-07 | 0.023156 | 0.023156 | 0.023156 | 0.98419 | -0.30264 | 0.98409 | -0.30458 | 6.3614
77 | -0.042614 | -0.010695 | 0.042632 | 0.010706 | 1.7432e-05 | 1.1014e-05 | 0.064435 | 0.064434 | 0.064435 | 0.98419 | -0.30264 | 0.98463 | -0.29407 | 17.7018
78 | 0.012507 | 0.003136 | -0.012503 | -0.0031339 | 3.7227e-06 | 2.0332e-06 | 0.018955 | 0.018955 | 0.018955 | 0.98187 | -0.34806 | 0.98155 | -0.35431 | 5.2075
79 | 0.00077464 | 0.00019396 | -0.00077463 | -0.00019414 | 7.6386e-09 | -1.81e-07 | 0.0011756 | 0.0011756 | 0.0011756 | 0.98048 | -0.37525 | 0.98047 | -0.37546 | 0.32297
80 | -0.00077464 | -0.00019396 | 0.00077465 | 0.00019381 | 6.3294e-09 | -1.4999e-07 | 0.0011756 | 0.0011755 | 0.0011756 | 0.98048 | -0.37525 | 0.98049 | -0.37508 | 0.32296
81 | 0.0064265 | 0.0016092 | -0.0064237 | -0.0016084 | 2.8237e-06 | 8.0918e-07 | 0.0097525 | 0.0097529 | 0.0097529 | 0.98049 | -0.37508 | 0.98002 | -0.38431 | 2.6794
82 | -0.0072011 | -0.0018031 | 0.0072036 | 0.0018039 | 2.4438e-06 | 8.7551e-07 | 0.010928 | 0.010928 | 0.010928 | 0.98049 | -0.37508 | 0.98085 | -0.36795 | 3.0022
83 | 0.010464 | 0.0026214 | -0.010462 | -0.0026206 | 1.6722e-06 | 8.4672e-07 | 0.01587 | 0.01587 | 0.01587 | 0.98104 | -0.36421 | 0.98087 | -0.36757 | 4.36
84 | -0.010464 | -0.0026214 | 0.010468 | 0.0026239 | 4.9354e-06 | 2.4985e-06 | 0.01587 | 0.01587 | 0.01587 | 0.98104 | -0.36421 | 0.98155 | -0.35431 | 4.36
85 | 0.0092162 | 0.0023084 | -0.0092161 | -0.0023083 | 1.6858e-07 | 7.886e-08 | 0.013981 | 0.013981 | 0.013981 | 0.98087 | -0.36757 | 0.98085 | -0.36795 | 3.8409
86 | 0.13406 | 0.033899 | -0.13386 | -0.033775 | 0.00019745 | 0.00012381 | 0.20366 | 0.20366 | 0.20366 | 0.98002 | -0.3828 | 0.97844 | -0.41356 | 13.9878
87 | 0.0055234 | 0.0013843 | -0.0055232 | -0.0013842 | 1.7666e-07 | 2.8641e-08 | 0.0083858 | 0.0083858 | 0.0083858 | 0.98009 | -0.38138 | 0.98006 | -0.38205 | 2.3038
88 | -0.16062 | -0.040657 | 0.16069 | 0.040699 | 6.7099e-05 | 4.2333e-05 | 0.24356 | 0.24356 | 0.24356 | 0.98188 | -0.34671 | 0.98232 | -0.33801 | 16.7282
89 | 0.0035612 | 0.00089222 | -0.0035608 | -0.00089242 | 3.8616e-07 | -1.9997e-07 | 0.0053968 | 0.005397 | 0.005397 | 0.98188 | -0.34671 | 0.98176 | -0.34898 | 1.4827
90 | -0.16942 | -0.042888 | 0.16944 | 0.042902 | 2.3127e-05 | 1.4612e-05 | 0.25679 | 0.25679 | 0.25679 | 0.98232 | -0.33801 | 0.98247 | -0.33516 | 17.6368
91 | 0.0087339 | 0.0021889 | -0.0087329 | -0.0021885 | 1.0483e-06 | 4.6876e-07 | 0.01323 | 0.01323 | 0.01323 | 0.98232 | -0.33801 | 0.9822 | -0.34053 | 3.6347
92 | 0.34305 | 0.088112 | -0.34298 | -0.088068 | 6.9444e-05 | 4.4296e-05 | 0.51122 | 0.51122 | 0.51122 | 1 | 0 | 0.99978 | -0.0041699 | 35.1115
93 | 0.32867 | 0.08448 | -0.32802 | -0.084068 | 0.00064612 | 0.00041201 | 0.48992 | 0.48992 | 0.48992 | 0.99978 | -0.0041699 | 0.99763 | -0.044719 | 33.6482
94 | -0.0051147 | -0.0012819 | 0.0051153 | 0.0012819 | 6.5127e-07 | 4.9248e-08 | 0.0077412 | 0.007741 | 0.0077412 | 0.98315 | -0.32199 | 0.98329 | -0.31931 | 2.1267
95 | 0.17428 | 0.044164 | -0.17417 | -0.044094 | 0.00011115 | 7.0274e-05 | 0.26391 | 0.26391 | 0.26391 | 0.98329 | -0.31931 | 0.9826 | -0.3326 | 18.1258
96 | -0.17939 | -0.045446 | 0.17942 | 0.045461 | 2.3474e-05 | 1.4851e-05 | 0.27165 | 0.27165 | 0.27165 | 0.98329 | -0.31931 | 0.98343 | -0.31659 | 18.6575
97 | 0.16947 | 0.042916 | -0.16944 | -0.042902 | 2.0882e-05 | 1.3193e-05 | 0.25679 | 0.25679 | 0.25679 | 0.9826 | -0.3326 | 0.98247 | -0.33516 | 17.6368
98 | -0.18876 | -0.047803 | 0.18879 | 0.04782 | 2.6831e-05 | 1.6994e-05 | 0.28579 | 0.28579 | 0.28579 | 0.98343 | -0.31659 | 0.98358 | -0.31363 | 19.6285
99 | 0.009344 | 0.0023422 | -0.0093425 | -0.0023415 | 1.4879e-06 | 7.0047e-07 | 0.014139 | 0.014139 | 0.014139 | 0.98343 | -0.31659 | 0.98326 | -0.31993 | 3.8842
100 | 0.013245 | 0.0033201 | -0.013243 | -0.0033189 | 2.1746e-06 | 1.2081e-06 | 0.020028 | 0.020028 | 0.020028 | 0.98409 | -0.30458 | 0.98392 | -0.30803 | 5.5022
101 | -0.047002 | -0.011801 | 0.04703 | 0.011818 | 2.718e-05 | 1.7213e-05 | 0.07104 | 0.071039 | 0.07104 | 0.98463 | -0.29407 | 0.98525 | -0.28195 | 19.5164
102 | 0.0031981 | 0.00080087 | -0.0031978 | -0.0008011 | 2.8086e-07 | -2.2688e-07 | 0.0048363 | 0.0048365 | 0.0048365 | 0.98392 | -0.30803 | 0.98382 | -0.30987 | 1.3287
103 | 0.010045 | 0.002518 | -0.010043 | -0.002517 | 2.048e-06 | 1.0102e-06 | 0.015192 | 0.015192 | 0.015192 | 0.98392 | -0.30803 | 0.9837 | -0.31231 | 4.1735
104 | -0.052027 | -0.013071 | 0.052091 | 0.013111 | 6.3968e-05 | 4.0587e-05 | 0.078587 | 0.078587 | 0.078587 | 0.98525 | -0.28195 | 0.98658 | -0.25622 | 21.5899
105 | -0.0028004 | -0.00070185 | 0.0028005 | 0.00070174 | 8.9294e-08 | -1.1007e-07 | 0.004244 | 0.0042439 | 0.004244 | 0.98187 | -0.34685 | 0.98191 | -0.34618 | 1.1659
106 | -0.0058368 | -0.0014627 | 0.0058377 | 0.0014629 | 9.7996e-07 | 2.046e-07 | 0.0088452 | 0.008845 | 0.0088452 | 0.98191 | -0.34618 | 0.98209 | -0.34266 | 2.43
107 | -0.0058377 | -0.0014629 | 0.0058383 | 0.001463 | 5.9282e-07 | 1.2369e-07 | 0.008845 | 0.0088449 | 0.008845 | 0.98209 | -0.34266 | 0.9822 | -0.34053 | 2.43
108 | 0.0031978 | 0.0008011 | -0.0031975 | -0.00080136 | 3.2094e-07 | -2.5913e-07 | 0.0048365 | 0.0048366 | 0.0048366 | 0.98382 | -0.30987 | 0.98371 | -0.31198 | 1.3287
109 | 0.0066493 | 0.0016665 | -0.0066489 | -0.0016664 | 4.8713e-07 | 1.4877e-07 | 0.010058 | 0.010058 | 0.010058 | 0.9837 | -0.31231 | 0.98362 | -0.31385 | 2.7633
110 | 0.0032458 | 0.00081308 | -0.0032457 | -0.0008131 | 3.18e-08 | -2.4287e-08 | 0.0049103 | 0.0049103 | 0.0049103 | 0.98358 | -0.31363 | 0.98357 | -0.31384 | 1.349
111 | 0.0012975 | 0.00032482 | -0.0012974 | -0.00032517 | 4.2777e-08 | -3.4838e-07 | 0.0019628 | 0.0019629 | 0.0019629 | 0.98357 | -0.31384 | 0.98353 | -0.31453 | 0.53926
112 | 0.004225 | 0.0010585 | -0.0042242 | -0.0010586 | 7.5912e-07 | -1.3386e-07 | 0.0064149 | 0.0064151 | 0.0064151 | 0.98002 | -0.38431 | 0.97983 | -0.38808 | 1.7624
113 | 0.0021987 | 0.00054998 | -0.0021983 | -0.00055092 | 3.9361e-07 | -9.3468e-07 | 0.003338 | 0.0033384 | 0.0033384 | 0.98002 | -0.38431 | 0.97983 | -0.38807 | 0.91715
114 | 0.0021983 | 0.00055092 | -0.0021983 | -0.00055094 | 9.8478e-09 | -2.3375e-08 | 0.0033384 | 0.0033384 | 0.0033384 | 0.97983 | -0.38807 | 0.97982 | -0.38816 | 0.91716
115 | 0.0025405 | 0.00063661 | -0.0025405 | -0.00063664 | 1.8312e-08 | -2.9599e-08 | 0.0038581 | 0.0038581 | 0.0038581 | 0.97983 | -0.38808 | 0.97982 | -0.38823 | 1.0599
116 | 0.0010917 | 0.00027353 | -0.0010917 | -0.0002736 | 6.1479e-09 | -7.1191e-08 | 0.0016579 | 0.0016579 | 0.0016579 | 0.97982 | -0.38823 | 0.97981 | -0.38835 | 0.45546
117 | 0.0062806 | 0.0015741 | -0.0062799 | -0.0015739 | 7.2922e-07 | 2.0085e-07 | 0.0095679 | 0.009568 | 0.009568 | 0.97678 | -0.44625 | 0.97665 | -0.44868 | 2.6286
118 | 0.0036014 | 0.00090259 | -0.0036014 | -0.0009026 | 1.6742e-08 | -7.841e-09 | 0.0054871 | 0.0054871 | 0.0054871 | 0.97665 | -0.44868 | 0.97665 | -0.44878 | 1.5074

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34841 | 0.089042

## res_load
| p_mw | q_mvar
0 | 0.009251 | 0.0023185
1 | 0.0018146 | 0.00045479
2 | 0.0016722 | 0.00041911
3 | 0.0096657 | 0.0024224
4 | 0.0091473 | 0.0022925
5 | 0.0028204 | 0.00070685
6 | 0.0037887 | 0.00094953
7 | 0.0084867 | 0.002127
8 | 0.0089936 | 0.002254
9 | 0.0081153 | 0.0020339
10 | 0.0030377 | 0.00076132
11 | 0.002941 | 0.00073707
12 | 0.0046576 | 0.0011673
13 | 0.0014058 | 0.00035232
14 | 0.0015751 | 0.00039477
15 | 0.0074599 | 0.0018696
16 | 0.0082922 | 0.0020782
17 | 0.0016159 | 0.00040498
18 | 0.0035965 | 0.00090136
19 | 0.0040269 | 0.0010092
20 | 0.0050218 | 0.0012586
21 | 0.00081855 | 0.00020515
22 | 0.0012143 | 0.00030433
23 | 0.0024521 | 0.00061454
24 | 0.0035908 | 0.00089995
25 | 0.0050171 | 0.0012574
26 | 0.0011355 | 0.00028459
27 | 0.0040052 | 0.0010038
28 | 0.001016 | 0.00025464
29 | 0.00456 | 0.0011428
30 | 0.0043331 | 0.001086
31 | 0.0058219 | 0.0014591
32 | 0.0027306 | 0.00068436
33 | 0.0039312 | 0.00098526
34 | 0.0038953 | 0.00097624
35 | 0.0012446 | 0.00031192
36 | 0.0044667 | 0.0011195
37 | 0.0034636 | 0.00086807
38 | 0.0051056 | 0.0012796
39 | 0.0035263 | 0.00088377
40 | 0.0024511 | 0.00061431
41 | 0.0029944 | 0.00075047
42 | 0.0011355 | 0.00028459
43 | 0.00077463 | 0.00019414
44 | 0.0010838 | 0.00027163
45 | 0.001823 | 0.0004569
46 | 0.0012456 | 0.00031219
47 | 0.002035 | 0.00051002
48 | 0.0055232 | 0.0013842
49 | 0.0035608 | 0.00089242
50 | 0.0085049 | 0.0021315
51 | 0.0037081 | 0.00092935
52 | 0.014315 | 0.0035877
53 | 0.043307 | 0.010854
54 | 0.0051147 | 0.0012819
55 | 0.0047019 | 0.0011784
56 | 0.0020686 | 0.00051844
57 | 0.0043706 | 0.0010954
58 | 0.0049977 | 0.0012525
59 | 0.0028004 | 0.00070185
60 | 0.0030363 | 0.00076096
61 | 0.0028946 | 0.00072544
62 | 0.004071 | 0.0010203
63 | 0.0033935 | 0.0008505
64 | 0.0093425 | 0.0023415
65 | 0.0019483 | 0.00048828
66 | 0.0031975 | 0.00080136
67 | 0.0012974 | 0.00032517
68 | 0.0066489 | 0.0016664
69 | 0.0021769 | 0.00054559
70 | 0.0020125 | 0.00050437
71 | 0.0021983 | 0.00055094
72 | 0.0016837 | 0.00042198
73 | 0.0014488 | 0.00036311
74 | 0.0010917 | 0.0002736
75 | 0.0021615 | 0.00054174
76 | 0.0026785 | 0.00067129
77 | 0.0036014 | 0.0009026

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1