## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_138-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_138-1_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_138-1_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_138-1_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_138-1_0_4_node_61 | 0.4 | n |  | TRUE
5 | bus_LV_138-1_0_4_node_62 | 0.4 | n |  | TRUE
6 | bus_LV_138-1_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_138-1_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_138-1_0_4_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_138-1_0_4_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_138-1_0_4_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_138-1_0_4_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_138-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_138-1_0_4_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_138-1_0_4_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_138-1_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_138-1_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_138-1_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_138-1_0_4_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_138-1_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_138-1_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_138-1_0_4_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_138-1_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_138-1_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_138-1_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_138-1_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_138-1_0_4_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_138-1_0_4_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_138-1_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_138-1_0_4_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_138-1_0_4_node_41 | 0.4 | n |  | TRUE
31 | bus_LV_138-1_0_4_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_138-1_0_4_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_138-1_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_138-1_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_138-1_0_4_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_138-1_0_4_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_138-1_0_4_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_138-1_0_4_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_138-1_0_4_node_59 | 0.4 | n |  | TRUE
40 | bus_LV_138-1_0_4_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_138-1_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_138-1_0_4_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_138-1_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_138-1_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_138-1_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_138-1_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_138-1_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_138-1_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_138-1_0_4_node_57 | 0.4 | n |  | TRUE
50 | bus_LV_138-1_0_4_node_56 | 0.4 | n |  | TRUE
51 | bus_LV_138-1_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_138-1_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_138-1_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_138-1_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_138-1_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_138-1_0_4_node_51 | 0.4 | n |  | TRUE
57 | bus_MV_222_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_138-1_0_4_load_0 | 0 | 0.018784 | 0.0047077 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_138-1_0_4_load_61 | 4 | 0.017022 | 0.0042662 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_138-1_0_4_load_62 | 5 | 0.0077309 | 0.0019375 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_138-1_0_4_load_55 | 8 | 0.0076616 | 0.0019202 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_138-1_0_4_load_53 | 9 | 0.007896 | 0.0019789 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_138-1_0_4_load_47 | 10 | 0.012766 | 0.0031995 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_138-1_0_4_load_45 | 11 | 0.015992 | 0.004008 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_138-1_0_4_load_25 | 13 | 0.004788 | 0.0012 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_138-1_0_4_load_60 | 18 | 0.0085679 | 0.0021473 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_138-1_0_4_load_34 | 19 | 0.019443 | 0.0048729 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_138-1_0_4_load_39 | 21 | 0.0048554 | 0.0012169 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_138-1_0_4_load_20 | 24 | 0.011327 | 0.0028389 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_138-1_0_4_load_37 | 26 | 0.0062216 | 0.0015593 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_138-1_0_4_load_35 | 27 | 0.013823 | 0.0034644 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_138-1_0_4_load_44 | 29 | 0.0022405 | 0.00056152 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_138-1_0_4_load_41 | 30 | 0.0060814 | 0.0015241 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_138-1_0_4_load_58 | 31 | 0.0043438 | 0.0010887 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_138-1_0_4_load_54 | 32 | 0.011753 | 0.0029456 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_138-1_0_4_load_38 | 35 | 0.0076548 | 0.0019185 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_138-1_0_4_load_42 | 38 | 0.0043288 | 0.0010849 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_138-1_0_4_load_59 | 39 | 0.0032819 | 0.00082252 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_138-1_0_4_load_43 | 40 | 0.0085038 | 0.0021312 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_138-1_0_4_load_21 | 41 | 0.022715 | 0.005693 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_138-1_0_4_load_22 | 42 | 0.034185 | 0.0085675 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_138-1_0_4_load_26 | 44 | 0.010706 | 0.0026832 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_138-1_0_4_load_27 | 45 | 0.01426 | 0.003574 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_138-1_0_4_load_28 | 46 | 0.0092512 | 0.0023186 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_138-1_0_4_load_30 | 47 | 0.010541 | 0.0026417 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_138-1_0_4_load_31 | 48 | 0.005667 | 0.0014203 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_138-1_0_4_load_57 | 49 | 0.0042226 | 0.0010583 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_138-1_0_4_load_56 | 50 | 0.0021854 | 0.00054771 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_138-1_0_4_load_36 | 51 | 0.011756 | 0.0029464 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_138-1_0_4_load_40 | 52 | 0.0014302 | 0.00035843 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_138-1_0_4_load_52 | 53 | 0.025375 | 0.0063595 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_138-1_0_4_load_48 | 54 | 0.0064814 | 0.0016244 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_138-1_0_4_load_49 | 55 | 0.0033511 | 0.00083987 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_138-1_0_4_load_51 | 56 | 0.0042807 | 0.0010728 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 46 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_138-1_0_4_line_0 |  | 0 | 1 | 0.0033335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_138-1_0_4_line_1 |  | 1 | 2 | 0.018085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_138-1_0_4_line_2 |  | 2 | 3 | 0.049616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_138-1_0_4_line_3 |  | 2 | 4 | 0.015652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_138-1_0_4_line_4 |  | 3 | 5 | 0.010155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_138-1_0_4_line_5 |  | 3 | 6 | 0.073921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_138-1_0_4_line_6 |  | 6 | 10 | 0.0026742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_138-1_0_4_line_7 |  | 6 | 11 | 0.018588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_138-1_0_4_line_8 |  | 7 | 8 | 0.0080837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_138-1_0_4_line_9 |  | 7 | 9 | 0.012336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_138-1_0_4_line_10 |  | 9 | 10 | 0.022687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_138-1_0_4_line_11 |  | 11 | 14 | 0.017227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_138-1_0_4_line_12 |  | 12 | 13 | 0.0085143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_138-1_0_4_line_13 |  | 12 | 14 | 0.017638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_138-1_0_4_line_14 |  | 14 | 33 | 0.009115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_138-1_0_4_line_15 |  | 15 | 16 | 0.038252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_138-1_0_4_line_16 |  | 15 | 17 | 0.16826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_138-1_0_4_line_17 |  | 15 | 18 | 0.0088718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_138-1_0_4_line_18 |  | 16 | 19 | 0.025225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_138-1_0_4_line_19 |  | 17 | 20 | 0.063096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_138-1_0_4_line_20 |  | 17 | 21 | 0.048195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_138-1_0_4_line_21 |  | 19 | 34 | 0.0093886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_138-1_0_4_line_22 |  | 20 | 31 | 0.065469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_138-1_0_4_line_23 |  | 21 | 35 | 0.029939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_138-1_0_4_line_24 |  | 22 | 23 | 0.035291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_138-1_0_4_line_25 |  | 22 | 24 | 0.017226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_138-1_0_4_line_26 |  | 23 | 32 | 0.058679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_138-1_0_4_line_27 |  | 25 | 26 | 0.012612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_138-1_0_4_line_28 |  | 25 | 27 | 0.0021645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_138-1_0_4_line_29 |  | 27 | 36 | 0.017372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_138-1_0_4_line_30 |  | 28 | 29 | 0.031408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_138-1_0_4_line_31 |  | 28 | 30 | 0.032616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_138-1_0_4_line_32 |  | 29 | 37 | 0.0088499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_138-1_0_4_line_33 |  | 30 | 38 | 0.0047339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_138-1_0_4_line_34 |  | 31 | 39 | 0.045057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_138-1_0_4_line_35 |  | 32 | 40 | 0.013591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_138-1_0_4_line_36 |  | 33 | 49 | 0.0045013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_138-1_0_4_line_37 |  | 33 | 46 | 0.011931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_138-1_0_4_line_38 |  | 34 | 36 | 0.015142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_138-1_0_4_line_39 |  | 34 | 48 | 0.0082662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_138-1_0_4_line_40 |  | 35 | 52 | 0.019971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_138-1_0_4_line_41 |  | 36 | 51 | 0.038583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_138-1_0_4_line_42 |  | 37 | 53 | 0.035828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_138-1_0_4_line_43 |  | 37 | 54 | 0.009752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_138-1_0_4_line_44 |  | 38 | 40 | 0.0062095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_138-1_0_4_line_45 |  | 41 | 42 | 0.0018606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_138-1_0_4_line_46 |  | 42 | 43 | 0.013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_138-1_0_4_line_47 |  | 43 | 44 | 0.02102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_138-1_0_4_line_48 |  | 43 | 45 | 0.0077361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_138-1_0_4_line_49 |  | 44 | 46 | 0.003206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_138-1_0_4_line_50 |  | 45 | 47 | 0.025072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_138-1_0_4_line_51 |  | 47 | 48 | 0.0035586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_138-1_0_4_line_52 |  | 49 | 50 | 0.0094048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_138-1_0_4_line_53 |  | 50 | 56 | 0.0079248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_138-1_0_4_line_54 |  | 54 | 55 | 0.0035538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_138-1_0_4_line_55 |  | 55 | 56 | 0.013391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_138-1_0_4_trafo_28 | 0.63 MVA 20/0.4 kV | 57 | 46 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2696156.0833 | 1229324.6566 | 2696158.0772 | 1229321.9851
1 | 2696142.7366 | 1229326.7313 | 2696144.2401 | 1229325.1322 | 2696147.8487 | 1229321.2655 | 2696149.3677 | 1229319.6444 | 2696152.7218 | 1229322.1449 | 2696156.0833 | 1229324.6566
2 | 2696119.9866 | 1229365.3582 | 2696130.8485 | 1229354.348 | 2696128.8652 | 1229347.1996 | 2696130.5642 | 1229346.6267 | 2696132.3857 | 1229345.0327 | 2696138.0057 | 1229339.5529 | 2696142.9473 | 1229333.8509 | 2696142.7366 | 1229326.7313
3 | 2696142.7366 | 1229326.7313 | 2696142.6456 | 1229324.3948 | 2696142.1529 | 1229311.0897
4 | 2696116.0728 | 1229372.6335 | 2696114.482 | 1229371.2068 | 2696119.9866 | 1229365.3582
5 | 2696072.0013 | 1229370.0085 | 2696080.5405 | 1229377.5185 | 2696083.6112 | 1229380.2145 | 2696084.7024 | 1229381.1439 | 2696094.8828 | 1229389.7813 | 2696096.7949 | 1229391.4912 | 2696100.1464 | 1229379.6257 | 2696109.775 | 1229368.4954 | 2696116.6146 | 1229362.0902 | 2696119.9866 | 1229365.3582
6 | 2696072.0013 | 1229370.0085 | 2696073.6718 | 1229367.9203
7 | 2696072.0013 | 1229370.0085 | 2696058.3001 | 1229382.5695
8 | 2696088.1078 | 1229338.7572 | 2696089.3682 | 1229330.7723
9 | 2696088.1078 | 1229338.7572 | 2696085.826 | 1229340.2325 | 2696082.3019 | 1229349.1821 | 2696082.3019 | 1229349.1821
10 | 2696073.6718 | 1229367.9203 | 2696083.2766 | 1229355.9138 | 2696084.2084 | 1229354.0497 | 2696082.3019 | 1229349.1821
11 | 2696046.7697 | 1229395.3193 | 2696054.1119 | 1229386.4092 | 2696058.3001 | 1229382.5695
12 | 2696057.0778 | 1229409.6517 | 2696051.7474 | 1229416.291
13 | 2696046.7697 | 1229395.3193 | 2696057.0778 | 1229409.6517
14 | 2696046.7697 | 1229395.3193 | 2696040.1118 | 1229389.0739
15 | 2695996.7188 | 1229495.5059 | 2696016.1837 | 1229469.2567 | 2696011.683 | 1229465.9705
16 | 2695898.4509 | 1229580.1819 | 2695901.848 | 1229583.3056 | 2695914.24 | 1229592.4565 | 2695924.3931 | 1229599.959 | 2695964.5198 | 1229546.0006 | 2695972.0192 | 1229537.66 | 2695999.4877 | 1229506.5586 | 2695992.6848 | 1229501.3228 | 2695996.7188 | 1229495.5059
17 | 2695996.7188 | 1229495.5059 | 2695989.1017 | 1229490.9575
18 | 2696011.683 | 1229465.9705 | 2695991.3048 | 1229451.1044
19 | 2695851.9728 | 1229537.5352 | 2695874.1771 | 1229558.8974 | 2695898.4509 | 1229580.1819
20 | 2695898.4509 | 1229580.1819 | 2695929.1691 | 1229543.0452
21 | 2695983.72 | 1229445.5712 | 2695991.3048 | 1229451.1044
22 | 2695851.9728 | 1229537.5352 | 2695857.0053 | 1229532.2792 | 2695913.6805 | 1229519.0788
23 | 2695948.2517 | 1229519.9753 | 2695929.1691 | 1229543.0452
24 | 2696095.7341 | 1229244.3233 | 2696091.7668 | 1229240.8456 | 2696083.6933 | 1229237.3237 | 2696081.4997 | 1229239.9013 | 2696070.7486 | 1229252.4923 | 2696069.9298 | 1229253.4575
25 | 2696095.7341 | 1229244.3233 | 2696096.9627 | 1229243.3202 | 2696102.5809 | 1229240.7647 | 2696109.0724 | 1229247.6561
26 | 2696069.9298 | 1229253.4575 | 2696040.7881 | 1229282.9749 | 2696027.9599 | 1229294.4324
27 | 2695953.0993 | 1229429.2653 | 2695958.8818 | 1229418.0566
28 | 2695953.0993 | 1229429.2653 | 2695955.0398 | 1229430.2243
29 | 2695970.614 | 1229437.9208 | 2695955.0398 | 1229430.2243
30 | 2695980.8366 | 1229325.2377 | 2695984.5512 | 1229336.3835 | 2695989.3336 | 1229344.2886 | 2695996.5148 | 1229351.8391
31 | 2695980.8366 | 1229325.2377 | 2695992.4929 | 1229322.257 | 2695998.0909 | 1229318.1333 | 2696009.0365 | 1229310.0083
32 | 2696002.6874 | 1229358.1808 | 2695997.1418 | 1229352.4983 | 2695996.5148 | 1229351.8391
33 | 2696009.0365 | 1229310.0083 | 2696012.8376 | 1229307.1867
34 | 2695913.6805 | 1229519.0788 | 2695920.7165 | 1229517.44 | 2695953.317 | 1229498.2438
35 | 2696027.9599 | 1229294.4324 | 2696017.8236 | 1229303.4856
36 | 2696040.1118 | 1229389.0739 | 2696036.6405 | 1229386.2084
37 | 2696040.1118 | 1229389.0739 | 2696037.383 | 1229392.4212 | 2696032.479 | 1229398.243
38 | 2695983.72 | 1229445.5712 | 2695970.614 | 1229437.9208
39 | 2695983.72 | 1229445.5712 | 2695988.2219 | 1229438.6385
40 | 2695948.2517 | 1229519.9753 | 2695960.9804 | 1229504.5868
41 | 2695970.614 | 1229437.9208 | 2695964.5802 | 1229454.0351 | 2695964.1794 | 1229467.594 | 2695962.8032 | 1229475.2832
42 | 2696002.6874 | 1229358.1808 | 2695988.454 | 1229378.1099 | 2695994.7206 | 1229387.5584
43 | 2696002.6874 | 1229358.1808 | 2696010.2081 | 1229364.389
44 | 2696017.8236 | 1229303.4856 | 2696017.8236 | 1229303.4856 | 2696012.8376 | 1229307.1867
45 | 2696025.5203 | 1229424.98 | 2696024.0886 | 1229423.7917
46 | 2696014.2715 | 1229414.086 | 2696022.987 | 1229422.8774 | 2696024.0886 | 1229423.7917
47 | 2696014.2715 | 1229414.086 | 2696028.7616 | 1229402.6561 | 2696030.4136 | 1229400.695
48 | 2696014.2715 | 1229414.086 | 2696007.761 | 1229418.2646
49 | 2696032.479 | 1229398.243 | 2696030.4136 | 1229400.695
50 | 2696007.761 | 1229418.2646 | 2696002.4423 | 1229421.6783 | 2695997.8268 | 1229425.4954 | 2695993.8524 | 1229429.9679 | 2695990.16 | 1229435.654
51 | 2695988.2219 | 1229438.6385 | 2695990.16 | 1229435.654
52 | 2696029.3875 | 1229380.2213 | 2696036.6405 | 1229386.2084
53 | 2696029.3875 | 1229380.2213 | 2696023.276 | 1229375.1763
54 | 2696010.2081 | 1229364.389 | 2696012.9488 | 1229366.6514
55 | 2696023.276 | 1229375.1763 | 2696012.9488 | 1229366.6514

## bus_geodata
| x | y | coords
0 | 2696158.0772 | 1229321.9851
1 | 2696156.0833 | 1229324.6566
2 | 2696142.7366 | 1229326.7313
3 | 2696119.9866 | 1229365.3582
4 | 2696142.1529 | 1229311.0897
5 | 2696116.0728 | 1229372.6335
6 | 2696072.0013 | 1229370.0085
7 | 2696088.1078 | 1229338.7572
8 | 2696089.3682 | 1229330.7724
9 | 2696082.3019 | 1229349.1821
10 | 2696073.6718 | 1229367.9203
11 | 2696058.3001 | 1229382.5695
12 | 2696057.0778 | 1229409.6517
13 | 2696051.7474 | 1229416.291
14 | 2696046.7697 | 1229395.3193
15 | 2695996.7188 | 1229495.5059
16 | 2696011.683 | 1229465.9705
17 | 2695898.4509 | 1229580.1819
18 | 2695989.1017 | 1229490.9575
19 | 2695991.3048 | 1229451.1044
20 | 2695851.9728 | 1229537.5352
21 | 2695929.1691 | 1229543.0452
22 | 2696095.7341 | 1229244.3233
23 | 2696069.9298 | 1229253.4575
24 | 2696109.0724 | 1229247.6561
25 | 2695953.0993 | 1229429.2653
26 | 2695958.8818 | 1229418.0566
27 | 2695955.0398 | 1229430.2243
28 | 2695980.8366 | 1229325.2377
29 | 2695996.5148 | 1229351.8391
30 | 2696009.0365 | 1229310.0083
31 | 2695913.6805 | 1229519.0788
32 | 2696027.9599 | 1229294.4324
33 | 2696040.1118 | 1229389.0739
34 | 2695983.72 | 1229445.5712
35 | 2695948.2517 | 1229519.9753
36 | 2695970.614 | 1229437.9208
37 | 2696002.6874 | 1229358.1808
38 | 2696012.8376 | 1229307.1867
39 | 2695953.317 | 1229498.2438
40 | 2696017.8236 | 1229303.4856
41 | 2696025.5203 | 1229424.98
42 | 2696024.0886 | 1229423.7917
43 | 2696014.2715 | 1229414.086
44 | 2696030.4136 | 1229400.695
45 | 2696007.761 | 1229418.2646
46 | 2696032.479 | 1229398.243
47 | 2695990.16 | 1229435.654
48 | 2695988.2219 | 1229438.6385
49 | 2696036.6405 | 1229386.2084
50 | 2696029.3875 | 1229380.2213
51 | 2695962.8032 | 1229475.2832
52 | 2695960.9804 | 1229504.5868
53 | 2695994.7206 | 1229387.5584
54 | 2696010.2081 | 1229364.389
55 | 2696012.9488 | 1229366.6514
56 | 2696023.276 | 1229375.1763
57 | 2696040.1118 | 1229389.0739

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99069 | -0.17913 | 0.018784 | 0.0047077
1 | 0.99075 | -0.17802 | 0 | 0
2 | 0.99106 | -0.17199 | 0 | 0
3 | 0.99269 | -0.14051 | 0 | 0
4 | 0.99082 | -0.17672 | 0.017022 | 0.0042662
5 | 0.99262 | -0.1419 | 0.0077309 | 0.0019375
6 | 0.99563 | -0.083755 | 0 | 0
7 | 0.99516 | -0.092959 | 0 | 0
8 | 0.9951 | -0.094049 | 0.0076616 | 0.0019202
9 | 0.99524 | -0.091296 | 0.007896 | 0.0019789
10 | 0.99556 | -0.085087 | 0.012766 | 0.0031995
11 | 0.99685 | -0.060296 | 0.015992 | 0.004008
12 | 0.99816 | -0.035261 | 0 | 0
13 | 0.99812 | -0.035975 | 0.004788 | 0.0012
14 | 0.99823 | -0.033784 | 0 | 0
15 | 0.99202 | -0.15349 | 0 | 0
16 | 0.99307 | -0.13309 | 0 | 0
17 | 0.98869 | -0.21801 | 0 | 0
18 | 0.99195 | -0.15484 | 0.0085679 | 0.0021473
19 | 0.99377 | -0.11965 | 0.019443 | 0.0048729
20 | 0.98824 | -0.2266 | 0 | 0
21 | 0.98807 | -0.23 | 0.0048554 | 0.0012169
22 | 0.99104 | -0.17246 | 0 | 0
23 | 0.99141 | -0.16537 | 0 | 0
24 | 0.99086 | -0.17592 | 0.011327 | 0.0028389
25 | 0.99343 | -0.12632 | 0 | 0
26 | 0.99335 | -0.12771 | 0.0062216 | 0.0015593
27 | 0.99344 | -0.12608 | 0.013823 | 0.0034644
28 | 0.99389 | -0.11735 | 0 | 0
29 | 0.9951 | -0.094102 | 0.0022405 | 0.00056152
30 | 0.99264 | -0.14155 | 0.0060814 | 0.0015241
31 | 0.98779 | -0.23552 | 0.0043438 | 0.0010887
32 | 0.99202 | -0.15358 | 0.011753 | 0.0029456
33 | 0.999 | -0.019024 | 0 | 0
34 | 0.9942 | -0.11144 | 0 | 0
35 | 0.98782 | -0.23486 | 0.0076548 | 0.0019185
36 | 0.99376 | -0.11994 | 0 | 0
37 | 0.99545 | -0.087213 | 0 | 0
38 | 0.99248 | -0.14456 | 0.0043288 | 0.0010849
39 | 0.98765 | -0.23816 | 0.0032819 | 0.00082252
40 | 0.9923 | -0.14803 | 0.0085038 | 0.0021312
41 | 0.99737 | -0.050496 | 0.022715 | 0.005693
42 | 0.99741 | -0.049755 | 0.034185 | 0.0085675
43 | 0.99812 | -0.035997 | 0 | 0
44 | 0.99974 | -0.0050157 | 0.010706 | 0.0026832
45 | 0.99733 | -0.05115 | 0.01426 | 0.003574
46 | 1 | 0 | -0.36577 | -0.09198
47 | 0.99509 | -0.094128 | 0.010541 | 0.0026417
48 | 0.99481 | -0.099583 | 0.005667 | 0.0014203
49 | 0.99863 | -0.026113 | 0.0042226 | 0.0010583
50 | 0.9979 | -0.040245 | 0.0021854 | 0.00054771
51 | 0.99334 | -0.12795 | 0.011756 | 0.0029464
52 | 0.98779 | -0.23537 | 0.0014302 | 0.00035843
53 | 0.99462 | -0.10322 | 0.025375 | 0.0063595
54 | 0.99607 | -0.075279 | 0.0064814 | 0.0016244
55 | 0.99632 | -0.070529 | 0.0033511 | 0.00083987
56 | 0.99729 | -0.051867 | 0.0042807 | 0.0010728
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018784 | -0.0047077 | 0.018785 | 0.0047083 | 9.9504e-07 | 5.939e-07 | 0.028213 | 0.028213 | 0.028213 | 0.99069 | -0.17913 | 0.99075 | -0.17802 | 7.7509
1 | -0.018785 | -0.0047083 | 0.01879 | 0.0047115 | 5.3984e-06 | 3.222e-06 | 0.028213 | 0.028213 | 0.028213 | 0.99075 | -0.17802 | 0.99106 | -0.17199 | 7.7509
2 | -0.035817 | -0.00898 | 0.03587 | 0.0090138 | 5.3808e-05 | 3.3797e-05 | 0.053778 | 0.053777 | 0.053778 | 0.99106 | -0.17199 | 0.99269 | -0.14051 | 14.774
3 | 0.017026 | 0.0042685 | -0.017022 | -0.0042662 | 3.836e-06 | 2.2534e-06 | 0.025564 | 0.025564 | 0.025564 | 0.99106 | -0.17199 | 0.99082 | -0.17672 | 7.0232
4 | 0.0077314 | 0.0019377 | -0.0077309 | -0.0019375 | 5.1147e-07 | 1.9607e-07 | 0.011589 | 0.011589 | 0.011589 | 0.99269 | -0.14051 | 0.99262 | -0.1419 | 3.1839
5 | -0.043602 | -0.010952 | 0.04372 | 0.011026 | 0.00011844 | 7.4844e-05 | 0.065367 | 0.065366 | 0.065367 | 0.99269 | -0.14051 | 0.99563 | -0.083755 | 17.9578
6 | 0.028331 | 0.0071027 | -0.028329 | -0.0071016 | 1.798e-06 | 1.1159e-06 | 0.042343 | 0.042343 | 0.042343 | 0.99563 | -0.083755 | 0.99556 | -0.085087 | 11.6326
7 | -0.072051 | -0.018129 | 0.072132 | 0.018181 | 8.0865e-05 | 5.1511e-05 | 0.10771 | 0.10771 | 0.10771 | 0.99563 | -0.083755 | 0.99685 | -0.060296 | 29.5904
8 | 0.007662 | 0.0019203 | -0.0076616 | -0.0019202 | 3.9789e-07 | 1.4963e-07 | 0.011457 | 0.011457 | 0.011457 | 0.99516 | -0.092959 | 0.9951 | -0.094049 | 3.1475
9 | -0.007662 | -0.0019203 | 0.0076626 | 0.0019206 | 6.0717e-07 | 2.2831e-07 | 0.011457 | 0.011457 | 0.011457 | 0.99516 | -0.092959 | 0.99524 | -0.091296 | 3.1475
10 | -0.015559 | -0.0038995 | 0.015563 | 0.0039021 | 4.6038e-06 | 2.6515e-06 | 0.023262 | 0.023262 | 0.023262 | 0.99524 | -0.091296 | 0.99556 | -0.085087 | 6.3907
11 | -0.088124 | -0.022189 | 0.088236 | 0.02226 | 0.00011185 | 7.1359e-05 | 0.13158 | 0.13158 | 0.13158 | 0.99685 | -0.060296 | 0.99823 | -0.033784 | 36.1484
12 | 0.0047882 | 0.0012 | -0.004788 | -0.0012 | 1.6268e-07 | -7.1689e-09 | 0.0071381 | 0.0071381 | 0.0071381 | 0.99816 | -0.035261 | 0.99812 | -0.035975 | 1.961
13 | -0.0047882 | -0.0012 | 0.0047885 | 0.0012 | 3.37e-07 | -1.4881e-08 | 0.0071381 | 0.007138 | 0.0071381 | 0.99816 | -0.035261 | 0.99823 | -0.033784 | 1.961
14 | -0.093024 | -0.02346 | 0.09309 | 0.023502 | 6.5774e-05 | 4.1976e-05 | 0.13872 | 0.13872 | 0.13872 | 0.99823 | -0.033784 | 0.999 | -0.019024 | 38.1094
15 | -0.030218 | -0.0076003 | 0.030247 | 0.0076186 | 2.9483e-05 | 1.8375e-05 | 0.045336 | 0.045336 | 0.045336 | 0.99202 | -0.15349 | 0.99307 | -0.13309 | 12.455
16 | 0.021649 | 0.0054527 | -0.021583 | -0.0054123 | 6.6581e-05 | 4.0447e-05 | 0.032484 | 0.032484 | 0.032484 | 0.99202 | -0.15349 | 0.98869 | -0.21801 | 8.9243
17 | 0.0085684 | 0.0021475 | -0.0085679 | -0.0021473 | 5.4957e-07 | 2.3719e-07 | 0.012853 | 0.012853 | 0.012853 | 0.99202 | -0.15349 | 0.99195 | -0.15484 | 3.5309
18 | -0.030247 | -0.0076186 | 0.030267 | 0.0076308 | 1.9442e-05 | 1.2116e-05 | 0.045336 | 0.045336 | 0.045336 | 0.99307 | -0.13309 | 0.99377 | -0.11965 | 12.4549
19 | 0.0076325 | 0.0019133 | -0.0076293 | -0.0019121 | 3.1224e-06 | 1.1895e-06 | 0.011487 | 0.011488 | 0.011488 | 0.98869 | -0.21801 | 0.98824 | -0.2266 | 3.1559
20 | 0.01395 | 0.003499 | -0.013942 | -0.0034945 | 7.968e-06 | 4.4818e-06 | 0.020997 | 0.020997 | 0.020997 | 0.98869 | -0.21801 | 0.98807 | -0.23 | 5.7685
21 | -0.04971 | -0.012504 | 0.049729 | 0.012516 | 1.9514e-05 | 1.2367e-05 | 0.074449 | 0.074449 | 0.074449 | 0.99377 | -0.11965 | 0.9942 | -0.11144 | 20.4529
22 | 0.0076293 | 0.0019121 | -0.0076261 | -0.0019109 | 3.24e-06 | 1.2351e-06 | 0.011488 | 0.011488 | 0.011488 | 0.98824 | -0.2266 | 0.98779 | -0.23552 | 3.156
23 | 0.0090871 | 0.0022776 | -0.009085 | -0.0022767 | 2.1027e-06 | 9.6234e-07 | 0.013685 | 0.013685 | 0.013685 | 0.98807 | -0.23 | 0.98782 | -0.23486 | 3.7597
24 | -0.011329 | -0.0028399 | 0.011333 | 0.0028419 | 3.8294e-06 | 1.9959e-06 | 0.017011 | 0.01701 | 0.017011 | 0.99104 | -0.17246 | 0.99141 | -0.16537 | 4.6732
25 | 0.011329 | 0.0028399 | -0.011327 | -0.0028389 | 1.8691e-06 | 9.7434e-07 | 0.017011 | 0.017011 | 0.017011 | 0.99104 | -0.17246 | 0.99086 | -0.17592 | 4.6733
26 | -0.011333 | -0.0028419 | 0.011339 | 0.0028452 | 6.367e-06 | 3.3178e-06 | 0.01701 | 0.01701 | 0.01701 | 0.99141 | -0.16537 | 0.99202 | -0.15358 | 4.6732
27 | 0.006222 | 0.0015594 | -0.0062216 | -0.0015593 | 4.1081e-07 | 9.963e-08 | 0.0093197 | 0.0093198 | 0.0093198 | 0.99343 | -0.12632 | 0.99335 | -0.12771 | 2.5604
28 | -0.006222 | -0.0015594 | 0.0062221 | 0.0015594 | 7.0502e-08 | 1.7096e-08 | 0.0093197 | 0.0093197 | 0.0093197 | 0.99343 | -0.12632 | 0.99344 | -0.12608 | 2.5604
29 | -0.020045 | -0.0050238 | 0.020051 | 0.0050273 | 5.8727e-06 | 3.5335e-06 | 0.030025 | 0.030024 | 0.030025 | 0.99344 | -0.12608 | 0.99376 | -0.11994 | 8.2485
30 | -0.042072 | -0.010572 | 0.042118 | 0.010601 | 4.6743e-05 | 2.9508e-05 | 0.062998 | 0.062998 | 0.062998 | 0.99389 | -0.11735 | 0.9951 | -0.094102 | 17.3071
31 | 0.042072 | 0.010572 | -0.042023 | -0.010541 | 4.8542e-05 | 3.0645e-05 | 0.062998 | 0.062998 | 0.062998 | 0.99389 | -0.11735 | 0.99264 | -0.14155 | 17.3072
32 | -0.044359 | -0.011163 | 0.044373 | 0.011172 | 1.4609e-05 | 9.2349e-06 | 0.066348 | 0.066348 | 0.066348 | 0.9951 | -0.094102 | 0.99545 | -0.087213 | 18.2275
33 | 0.035942 | 0.0090172 | -0.035936 | -0.009014 | 5.1538e-06 | 3.2373e-06 | 0.053882 | 0.053882 | 0.053882 | 0.99264 | -0.14155 | 0.99248 | -0.14456 | 14.8027
34 | 0.0032823 | 0.00082221 | -0.0032819 | -0.00082252 | 4.1308e-07 | -3.1231e-07 | 0.0049444 | 0.0049446 | 0.0049446 | 0.98779 | -0.23552 | 0.98765 | -0.23816 | 1.3584
35 | -0.023093 | -0.0057908 | 0.023099 | 0.0057946 | 6.1154e-06 | 3.7383e-06 | 0.03464 | 0.03464 | 0.03464 | 0.99202 | -0.15358 | 0.9923 | -0.14803 | 9.5164
36 | 0.090553 | 0.022855 | -0.090522 | -0.022835 | 3.0734e-05 | 1.9611e-05 | 0.13493 | 0.13493 | 0.13493 | 0.999 | -0.019024 | 0.99863 | -0.026113 | 37.0699
37 | -0.18364 | -0.046357 | 0.18381 | 0.046464 | 0.00016752 | 0.0001069 | 0.27365 | 0.27365 | 0.27365 | 0.999 | -0.019024 | 1 | 0 | 37.5896
38 | 0.031825 | 0.0079842 | -0.031812 | -0.0079761 | 1.2885e-05 | 8.0499e-06 | 0.047635 | 0.047635 | 0.047635 | 0.9942 | -0.11144 | 0.99376 | -0.11994 | 13.0866
39 | -0.081554 | -0.0205 | 0.0816 | 0.02053 | 4.6201e-05 | 2.9461e-05 | 0.12208 | 0.12208 | 0.12208 | 0.9942 | -0.11144 | 0.99481 | -0.099583 | 33.5395
40 | 0.0014302 | 0.0003582 | -0.0014302 | -0.00035843 | 3.4758e-08 | -2.334e-07 | 0.0021543 | 0.0021544 | 0.0021544 | 0.98782 | -0.23486 | 0.98779 | -0.23537 | 0.59187
41 | 0.011761 | 0.0029488 | -0.011756 | -0.0029464 | 4.4873e-06 | 2.3722e-06 | 0.017611 | 0.017611 | 0.017611 | 0.99376 | -0.11994 | 0.99334 | -0.12795 | 4.8382
42 | 0.025394 | 0.0063714 | -0.025375 | -0.0063595 | 1.9362e-05 | 1.1926e-05 | 0.037962 | 0.037962 | 0.037962 | 0.99545 | -0.087213 | 0.99462 | -0.10322 | 10.4291
43 | -0.069767 | -0.017544 | 0.069807 | 0.017569 | 3.979e-05 | 2.5339e-05 | 0.10431 | 0.10431 | 0.10431 | 0.99545 | -0.087213 | 0.99607 | -0.075279 | 28.6565
44 | 0.031608 | 0.0079291 | -0.031602 | -0.0079258 | 5.2299e-06 | 3.2669e-06 | 0.047392 | 0.047392 | 0.047392 | 0.99248 | -0.14456 | 0.9923 | -0.14803 | 13.0197
45 | -0.022715 | -0.005693 | 0.022716 | 0.0056934 | 8.0133e-07 | 4.8857e-07 | 0.03389 | 0.03389 | 0.03389 | 0.99737 | -0.050496 | 0.99741 | -0.049755 | 9.3104
46 | -0.056901 | -0.014261 | 0.056938 | 0.014285 | 3.7322e-05 | 2.3706e-05 | 0.084889 | 0.084889 | 0.084889 | 0.99741 | -0.049755 | 0.99812 | -0.035997 | 23.3213
47 | -0.16931 | -0.042645 | 0.16956 | 0.042806 | 0.00025125 | 0.00016025 | 0.25249 | 0.25249 | 0.25249 | 0.99812 | -0.035997 | 0.99974 | -0.0050157 | 34.6824
48 | 0.11237 | 0.028361 | -0.11229 | -0.028309 | 8.1488e-05 | 5.2051e-05 | 0.1676 | 0.1676 | 0.1676 | 0.99812 | -0.035997 | 0.99733 | -0.05115 | 46.0435
49 | -0.18027 | -0.045489 | 0.18031 | 0.045516 | 4.3311e-05 | 2.7635e-05 | 0.26842 | 0.26842 | 0.26842 | 0.99974 | -0.0050157 | 1 | 0 | 36.8712
50 | 0.098032 | 0.024735 | -0.097831 | -0.024606 | 0.0002013 | 0.00012851 | 0.14632 | 0.14632 | 0.14632 | 0.99733 | -0.05115 | 0.99509 | -0.094128 | 40.1984
51 | 0.08729 | 0.021964 | -0.087267 | -0.02195 | 2.2747e-05 | 1.4512e-05 | 0.13056 | 0.13056 | 0.13056 | 0.99509 | -0.094128 | 0.99481 | -0.099583 | 35.8682
52 | 0.086299 | 0.021777 | -0.086241 | -0.02174 | 5.8365e-05 | 3.7231e-05 | 0.12864 | 0.12864 | 0.12864 | 0.99863 | -0.026113 | 0.9979 | -0.040245 | 35.3414
53 | 0.084055 | 0.021192 | -0.084009 | -0.021162 | 4.672e-05 | 2.9797e-05 | 0.12538 | 0.12538 | 0.12538 | 0.9979 | -0.040245 | 0.99729 | -0.051867 | 34.4461
54 | -0.076288 | -0.019193 | 0.076306 | 0.019204 | 1.7317e-05 | 1.1037e-05 | 0.11399 | 0.11399 | 0.11399 | 0.99607 | -0.075279 | 0.99632 | -0.070529 | 31.3165
55 | -0.079657 | -0.020044 | 0.079728 | 0.02009 | 7.1109e-05 | 4.5335e-05 | 0.119 | 0.119 | 0.119 | 0.99632 | -0.070529 | 0.99729 | -0.051867 | 32.6915

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37502 | 0.094299

## res_load
| p_mw | q_mvar
0 | 0.018784 | 0.0047077
1 | 0.017022 | 0.0042662
2 | 0.0077309 | 0.0019375
3 | 0.0076616 | 0.0019202
4 | 0.007896 | 0.0019789
5 | 0.012766 | 0.0031995
6 | 0.015992 | 0.004008
7 | 0.004788 | 0.0012
8 | 0.0085679 | 0.0021473
9 | 0.019443 | 0.0048729
10 | 0.0048554 | 0.0012169
11 | 0.011327 | 0.0028389
12 | 0.0062216 | 0.0015593
13 | 0.013823 | 0.0034644
14 | 0.0022405 | 0.00056152
15 | 0.0060814 | 0.0015241
16 | 0.0043438 | 0.0010887
17 | 0.011753 | 0.0029456
18 | 0.0076548 | 0.0019185
19 | 0.0043288 | 0.0010849
20 | 0.0032819 | 0.00082252
21 | 0.0085038 | 0.0021312
22 | 0.022715 | 0.005693
23 | 0.034185 | 0.0085675
24 | 0.010706 | 0.0026832
25 | 0.01426 | 0.003574
26 | 0.0092512 | 0.0023186
27 | 0.010541 | 0.0026417
28 | 0.005667 | 0.0014203
29 | 0.0042226 | 0.0010583
30 | 0.0021854 | 0.00054771
31 | 0.011756 | 0.0029464
32 | 0.0014302 | 0.00035843
33 | 0.025375 | 0.0063595
34 | 0.0064814 | 0.0016244
35 | 0.0033511 | 0.00083987
36 | 0.0042807 | 0.0010728

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1