## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_138-20_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_138-20_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_138-20_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_138-20_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_138-20_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_138-20_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_138-20_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_138-20_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_138-20_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_138-20_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_138-20_0_4_node_64 | 0.4 | n |  | TRUE
11 | bus_LV_138-20_0_4_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_138-20_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_138-20_0_4_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_138-20_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_138-20_0_4_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_138-20_0_4_node_125 | 0.4 | n |  | TRUE
17 | bus_LV_138-20_0_4_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_138-20_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_138-20_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_138-20_0_4_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_138-20_0_4_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_138-20_0_4_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_138-20_0_4_node_97 | 0.4 | n |  | TRUE
24 | bus_LV_138-20_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_138-20_0_4_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_138-20_0_4_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_138-20_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_138-20_0_4_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_138-20_0_4_node_96 | 0.4 | n |  | TRUE
30 | bus_LV_138-20_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_138-20_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_138-20_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_138-20_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_138-20_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_138-20_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_138-20_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_138-20_0_4_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_138-20_0_4_node_92 | 0.4 | n |  | TRUE
39 | bus_LV_138-20_0_4_node_95 | 0.4 | n |  | TRUE
40 | bus_LV_138-20_0_4_node_94 | 0.4 | n |  | TRUE
41 | bus_LV_138-20_0_4_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_138-20_0_4_node_124 | 0.4 | n |  | TRUE
43 | bus_LV_138-20_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_138-20_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_138-20_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_138-20_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_138-20_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_138-20_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_138-20_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_138-20_0_4_node_100 | 0.4 | n |  | TRUE
51 | bus_LV_138-20_0_4_node_101 | 0.4 | n |  | TRUE
52 | bus_LV_138-20_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_138-20_0_4_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_138-20_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_138-20_0_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_138-20_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_138-20_0_4_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_138-20_0_4_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_138-20_0_4_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_138-20_0_4_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_138-20_0_4_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_138-20_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_138-20_0_4_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_138-20_0_4_node_103 | 0.4 | n |  | TRUE
65 | bus_LV_138-20_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_138-20_0_4_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_138-20_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_138-20_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_138-20_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_138-20_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_138-20_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_138-20_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_138-20_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_138-20_0_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_138-20_0_4_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_138-20_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_138-20_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_138-20_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_138-20_0_4_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_138-20_0_4_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_138-20_0_4_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_138-20_0_4_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_138-20_0_4_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_138-20_0_4_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_138-20_0_4_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_138-20_0_4_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_138-20_0_4_node_109 | 0.4 | n |  | TRUE
88 | bus_LV_138-20_0_4_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_138-20_0_4_node_107 | 0.4 | n |  | TRUE
90 | bus_LV_138-20_0_4_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_138-20_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_138-20_0_4_node_105 | 0.4 | n |  | TRUE
93 | bus_LV_138-20_0_4_node_110 | 0.4 | n |  | TRUE
94 | bus_LV_138-20_0_4_node_111 | 0.4 | n |  | TRUE
95 | bus_LV_138-20_0_4_node_112 | 0.4 | n |  | TRUE
96 | bus_LV_138-20_0_4_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_138-20_0_4_node_119 | 0.4 | n |  | TRUE
98 | bus_LV_138-20_0_4_node_120 | 0.4 | n |  | TRUE
99 | bus_LV_138-20_0_4_node_121 | 0.4 | n |  | TRUE
100 | bus_LV_138-20_0_4_node_118 | 0.4 | n |  | TRUE
101 | bus_LV_138-20_0_4_node_79 | 0.4 | n |  | TRUE
102 | bus_LV_138-20_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_138-20_0_4_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_138-20_0_4_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_138-20_0_4_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_138-20_0_4_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_138-20_0_4_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_138-20_0_4_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_138-20_0_4_node_87 | 0.4 | n |  | TRUE
110 | bus_LV_138-20_0_4_node_88 | 0.4 | n |  | TRUE
111 | bus_LV_138-20_0_4_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_138-20_0_4_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_138-20_0_4_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_138-20_0_4_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_138-20_0_4_node_104 | 0.4 | n |  | TRUE
116 | bus_LV_138-20_0_4_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_138-20_0_4_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_138-20_0_4_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_138-20_0_4_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_138-20_0_4_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_138-20_0_4_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_138-20_0_4_node_122 | 0.4 | n |  | TRUE
123 | bus_MV_222_0_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_138-20_0_4_load_0 | 0 | 0.0082458 | 0.0020666 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_138-20_0_4_load_4 | 3 | 0.0057211 | 0.0014338 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_138-20_0_4_load_7 | 4 | 0.015365 | 0.0038508 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_138-20_0_4_load_9 | 5 | 0.010233 | 0.0025645 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_138-20_0_4_load_64 | 10 | 0.012029 | 0.0030147 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_138-20_0_4_load_76 | 11 | 0.0045643 | 0.0011439 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_138-20_0_4_load_24 | 13 | 0.0053758 | 0.0013473 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_138-20_0_4_load_72 | 15 | 0.0013059 | 0.0003273 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_138-20_0_4_load_125 | 16 | 0.0055908 | 0.0014012 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_138-20_0_4_load_35 | 18 | 0.0050979 | 0.0012776 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_138-20_0_4_load_74 | 20 | 0.00078122 | 0.00019579 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_138-20_0_4_load_70 | 21 | 0.0069625 | 0.001745 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_138-20_0_4_load_97 | 23 | 0.0034693 | 0.00086949 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_138-20_0_4_load_99 | 25 | 0.0016481 | 0.00041305 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_138-20_0_4_load_98 | 26 | 0.002839 | 0.00071152 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_138-20_0_4_load_96 | 29 | 0.0014629 | 0.00036664 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_138-20_0_4_load_15 | 30 | 0.001036 | 0.00025965 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_138-20_0_4_load_21 | 34 | 0.00053577 | 0.00013428 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_138-20_0_4_load_22 | 35 | 0.00095741 | 0.00023995 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_138-20_0_4_load_23 | 36 | 0.0022969 | 0.00057565 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_138-20_0_4_load_20 | 37 | 0.012877 | 0.0032272 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_138-20_0_4_load_92 | 38 | 0.0051084 | 0.0012803 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_138-20_0_4_load_95 | 39 | 0.00053567 | 0.00013425 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_138-20_0_4_load_94 | 40 | 0.0013052 | 0.00032712 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_138-20_0_4_load_90 | 41 | 0.0039003 | 0.00097752 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_138-20_0_4_load_124 | 42 | 0.00053589 | 0.00013431 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_138-20_0_4_load_25 | 43 | 0.00080751 | 0.00020238 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_138-20_0_4_load_26 | 44 | 0.0040641 | 0.0010186 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_138-20_0_4_load_27 | 45 | 0.00064047 | 0.00016052 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_138-20_0_4_load_29 | 47 | 0.00038614 | 9.6776e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_138-20_0_4_load_31 | 49 | 0.00017362 | 4.3514e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_138-20_0_4_load_100 | 50 | 0.00072427 | 0.00018152 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_138-20_0_4_load_101 | 51 | 0.00025292 | 6.3389e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_138-20_0_4_load_33 | 52 | 0.0015744 | 0.00039458 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_138-20_0_4_load_37 | 53 | 0.00063048 | 0.00015801 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_138-20_0_4_load_38 | 54 | 0.0012055 | 0.00030213 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_138-20_0_4_load_43 | 59 | 0.00019432 | 4.87e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_138-20_0_4_load_44 | 60 | 0.00083922 | 0.00021033 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_138-20_0_4_load_45 | 61 | 0.00046088 | 0.00011551 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_138-20_0_4_load_48 | 62 | 0.00075436 | 0.00018906 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_138-20_0_4_load_46 | 63 | 0.0010086 | 0.00025277 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_138-20_0_4_load_103 | 64 | 0.00049312 | 0.00012359 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_138-20_0_4_load_47 | 65 | 0.0011412 | 0.00028601 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_138-20_0_4_load_93 | 66 | 0.00070535 | 0.00017678 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_138-20_0_4_load_49 | 67 | 0.0012423 | 0.00031135 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_138-20_0_4_load_50 | 68 | 0.00088078 | 0.00022075 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_138-20_0_4_load_51 | 69 | 0.0012423 | 0.00031135 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_138-20_0_4_load_52 | 70 | 0.00088005 | 0.00022056 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_138-20_0_4_load_53 | 71 | 0.0023048 | 0.00057765 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_138-20_0_4_load_54 | 72 | 0.00088116 | 0.00022084 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_138-20_0_4_load_66 | 74 | 0.001533 | 0.0003842 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_138-20_0_4_load_67 | 75 | 0.0012438 | 0.00031172 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_138-20_0_4_load_73 | 76 | 0.0016452 | 0.00041233 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_138-20_0_4_load_68 | 77 | 0.0015321 | 0.00038397 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_138-20_0_4_load_69 | 78 | 0.0015321 | 0.00038397 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_138-20_0_4_load_56 | 79 | 0.0028008 | 0.00070195 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_138-20_0_4_load_57 | 80 | 0.0028024 | 0.00070236 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_138-20_0_4_load_59 | 82 | 0.0028008 | 0.00070195 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_138-20_0_4_load_61 | 83 | 0.002801 | 0.00070199 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_138-20_0_4_load_62 | 84 | 0.0028008 | 0.00070195 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_138-20_0_4_load_63 | 85 | 0.0030089 | 0.0007541 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_138-20_0_4_load_65 | 86 | 0.0028023 | 0.00070233 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_138-20_0_4_load_109 | 87 | 0.001533 | 0.0003842 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_138-20_0_4_load_77 | 88 | 0.0030543 | 0.00076547 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_138-20_0_4_load_107 | 89 | 0.0028019 | 0.00070222 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_138-20_0_4_load_108 | 90 | 0.0015321 | 0.00038397 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_138-20_0_4_load_78 | 91 | 0.010226 | 0.0025629 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_138-20_0_4_load_105 | 92 | 0.002801 | 0.00070199 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_138-20_0_4_load_111 | 94 | 0.0015395 | 0.00038583 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_138-20_0_4_load_112 | 95 | 0.0018623 | 0.00046675 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_138-20_0_4_load_119 | 97 | 0.0026082 | 0.00065367 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_138-20_0_4_load_121 | 99 | 0.0026092 | 0.00065394 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_138-20_0_4_load_79 | 101 | 0.0037361 | 0.00093636 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_138-20_0_4_load_80 | 102 | 0.012701 | 0.0031831 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_138-20_0_4_load_84 | 106 | 0.0011422 | 0.00028626 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_138-20_0_4_load_85 | 107 | 0.0050791 | 0.0012729 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_138-20_0_4_load_86 | 108 | 0.0083707 | 0.0020979 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_138-20_0_4_load_87 | 109 | 0.0061044 | 0.0015299 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_138-20_0_4_load_88 | 110 | 0.0026634 | 0.00066752 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_138-20_0_4_load_91 | 112 | 0.010794 | 0.0027052 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_138-20_0_4_load_102 | 114 | 0.00022504 | 5.64e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_138-20_0_4_load_104 | 115 | 0.002801 | 0.00070199 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_138-20_0_4_load_106 | 116 | 0.0055913 | 0.0014013 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_138-20_0_4_load_114 | 118 | 0.012349 | 0.0030949 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_138-20_0_4_load_115 | 119 | 0.0018622 | 0.00046671 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_138-20_0_4_load_116 | 120 | 0.0018608 | 0.00046637 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_138-20_0_4_load_117 | 121 | 0.0016195 | 0.00040588 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_138-20_0_4_load_122 | 122 | 0.0016195 | 0.00040588 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_138-20_0_4_line_0 |  | 0 | 1 | 0.021664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_138-20_0_4_line_1 |  | 1 | 2 | 0.040648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_138-20_0_4_line_2 |  | 1 | 3 | 0.012154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_138-20_0_4_line_3 |  | 2 | 4 | 0.025503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_138-20_0_4_line_4 |  | 3 | 5 | 0.0085545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_138-20_0_4_line_5 |  | 4 | 6 | 0.080917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_138-20_0_4_line_6 |  | 5 | 12 | 0.060266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_138-20_0_4_line_7 |  | 6 | 7 | 0.066415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_138-20_0_4_line_8 |  | 6 | 8 | 0.14313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_138-20_0_4_line_9 |  | 7 | 15 | 0.023053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_138-20_0_4_line_10 |  | 8 | 16 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_138-20_0_4_line_11 |  | 9 | 10 | 0.044132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_138-20_0_4_line_12 |  | 9 | 11 | 0.01727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_138-20_0_4_line_13 |  | 10 | 17 | 0.0098018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_138-20_0_4_line_14 |  | 11 | 18 | 0.018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_138-20_0_4_line_15 |  | 12 | 14 | 0.004846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_138-20_0_4_line_16 |  | 12 | 19 | 0.006459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_138-20_0_4_line_17 |  | 13 | 14 | 0.016665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_138-20_0_4_line_18 |  | 15 | 20 | 0.020236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_138-20_0_4_line_19 |  | 17 | 85 | 0.010842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_138-20_0_4_line_20 |  | 17 | 81 | 0.011815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_138-20_0_4_line_21 |  | 18 | 27 | 0.0083161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_138-20_0_4_line_22 |  | 19 | 23 | 0.038078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_138-20_0_4_line_23 |  | 20 | 40 | 0.0071057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_138-20_0_4_line_24 |  | 21 | 22 | 0.017889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_138-20_0_4_line_25 |  | 22 | 76 | 0.017463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_138-20_0_4_line_26 |  | 22 | 72 | 0.0097732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_138-20_0_4_line_27 |  | 23 | 29 | 0.0026845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_138-20_0_4_line_28 |  | 24 | 25 | 0.0045537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_138-20_0_4_line_29 |  | 24 | 26 | 0.010728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_138-20_0_4_line_30 |  | 26 | 29 | 0.0054211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_138-20_0_4_line_31 |  | 27 | 28 | 0.026966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_138-20_0_4_line_32 |  | 28 | 52 | 0.011859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_138-20_0_4_line_33 |  | 28 | 49 | 0.14306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_138-20_0_4_line_34 |  | 30 | 31 | 0.11621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_138-20_0_4_line_35 |  | 31 | 32 | 0.010407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_138-20_0_4_line_36 |  | 31 | 33 | 0.17542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_138-20_0_4_line_37 |  | 32 | 34 | 0.0075331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_138-20_0_4_line_38 |  | 32 | 35 | 0.0062118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_138-20_0_4_line_39 |  | 33 | 36 | 0.1156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_138-20_0_4_line_40 |  | 34 | 39 | 0.021246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_138-20_0_4_line_41 |  | 35 | 40 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_138-20_0_4_line_42 |  | 37 | 38 | 0.038363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_138-20_0_4_line_43 |  | 38 | 41 | 0.0047927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_138-20_0_4_line_44 |  | 39 | 42 | 0.006973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_138-20_0_4_line_45 |  | 41 | 111 | 0.020104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_138-20_0_4_line_46 |  | 42 | 113 | 0.013276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_138-20_0_4_line_47 |  | 43 | 44 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_138-20_0_4_line_48 |  | 43 | 45 | 0.031403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_138-20_0_4_line_49 |  | 44 | 46 | 0.18376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_138-20_0_4_line_50 |  | 45 | 47 | 0.025892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_138-20_0_4_line_51 |  | 46 | 48 | 0.17391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_138-20_0_4_line_52 |  | 47 | 49 | 0.00019954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_138-20_0_4_line_53 |  | 48 | 50 | 0.098978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_138-20_0_4_line_54 |  | 50 | 51 | 0.0086799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_138-20_0_4_line_55 |  | 51 | 114 | 0.01962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_138-20_0_4_line_56 |  | 53 | 54 | 0.0023933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_138-20_0_4_line_57 |  | 53 | 55 | 0.037628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_138-20_0_4_line_58 |  | 55 | 56 | 0.007215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_138-20_0_4_line_59 |  | 55 | 57 | 0.10207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_138-20_0_4_line_60 |  | 56 | 58 | 0.062396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_138-20_0_4_line_61 |  | 56 | 59 | 0.078479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_138-20_0_4_line_62 |  | 57 | 60 | 0.098035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_138-20_0_4_line_63 |  | 57 | 61 | 0.037627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_138-20_0_4_line_64 |  | 58 | 62 | 0.057551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_138-20_0_4_line_65 |  | 59 | 63 | 0.0039561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_138-20_0_4_line_66 |  | 62 | 64 | 0.026299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_138-20_0_4_line_67 |  | 63 | 65 | 0.0047511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_138-20_0_4_line_68 |  | 64 | 66 | 0.015214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_138-20_0_4_line_69 |  | 66 | 106 | 0.040764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_138-20_0_4_line_70 |  | 67 | 68 | 0.0073393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_138-20_0_4_line_71 |  | 67 | 69 | 0.0036282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_138-20_0_4_line_72 |  | 68 | 70 | 0.018768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_138-20_0_4_line_73 |  | 69 | 71 | 0.011751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_138-20_0_4_line_74 |  | 70 | 72 | 0.0073412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_138-20_0_4_line_75 |  | 71 | 73 | 0.0038198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_138-20_0_4_line_76 |  | 73 | 74 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_138-20_0_4_line_77 |  | 73 | 75 | 0.012938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_138-20_0_4_line_78 |  | 74 | 77 | 0.0051087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_138-20_0_4_line_79 |  | 75 | 78 | 0.0050735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_138-20_0_4_line_80 |  | 76 | 96 | 0.0049376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_138-20_0_4_line_81 |  | 77 | 90 | 0.019035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_138-20_0_4_line_82 |  | 79 | 80 | 0.0053485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_138-20_0_4_line_83 |  | 79 | 81 | 0.0099698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_138-20_0_4_line_84 |  | 80 | 82 | 0.0053485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_138-20_0_4_line_85 |  | 81 | 83 | 0.057338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_138-20_0_4_line_86 |  | 82 | 84 | 0.020444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_138-20_0_4_line_87 |  | 83 | 86 | 0.0054888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_138-20_0_4_line_88 |  | 84 | 87 | 0.0053485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_138-20_0_4_line_89 |  | 85 | 88 | 0.015467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_138-20_0_4_line_90 |  | 86 | 89 | 0.0074172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_138-20_0_4_line_91 |  | 87 | 90 | 0.0053485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_138-20_0_4_line_92 |  | 88 | 91 | 0.011459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_138-20_0_4_line_93 |  | 89 | 92 | 0.0054867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_138-20_0_4_line_94 |  | 91 | 101 | 0.010287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_138-20_0_4_line_95 |  | 92 | 115 | 0.0054875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_138-20_0_4_line_96 |  | 93 | 94 | 0.015731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_138-20_0_4_line_97 |  | 93 | 95 | 0.039333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_138-20_0_4_line_98 |  | 94 | 117 | 0.0075875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_138-20_0_4_line_99 |  | 95 | 118 | 0.010335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_138-20_0_4_line_100 |  | 96 | 97 | 0.005837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_138-20_0_4_line_101 |  | 96 | 98 | 0.027552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_138-20_0_4_line_102 |  | 98 | 99 | 0.005246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_138-20_0_4_line_103 |  | 98 | 100 | 0.002939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_138-20_0_4_line_104 |  | 100 | 120 | 0.018664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_138-20_0_4_line_105 |  | 101 | 102 | 0.048951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_138-20_0_4_line_106 |  | 102 | 103 | 0.023461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_138-20_0_4_line_107 |  | 103 | 104 | 0.038754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_138-20_0_4_line_108 |  | 104 | 108 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_138-20_0_4_line_109 |  | 104 | 109 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_138-20_0_4_line_110 |  | 105 | 106 | 0.14353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_138-20_0_4_line_111 |  | 105 | 107 | 0.03908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_138-20_0_4_line_112 |  | 107 | 109 | 0.0011134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_138-20_0_4_line_113 |  | 108 | 110 | 0.037916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_138-20_0_4_line_114 |  | 110 | 111 | 0.031058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_138-20_0_4_line_115 |  | 111 | 112 | 0.011598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_138-20_0_4_line_116 |  | 113 | 122 | 0.0029428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_138-20_0_4_line_117 |  | 115 | 116 | 0.0010782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_138-20_0_4_line_118 |  | 117 | 119 | 0.018538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_138-20_0_4_line_119 |  | 117 | 120 | 0.011884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_138-20_0_4_line_120 |  | 119 | 121 | 0.013036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_138-20_0_4_line_121 |  | 121 | 122 | 0.010099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_138-20_0_4_trafo_68 | 0.63 MVA 20/0.4 kV | 123 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2693826.6253 | 1227642.5427 | 2693843.8382 | 1227655.6975
1 | 2693826.6253 | 1227642.5427 | 2693815.8165 | 1227652.6795 | 2693810.3509 | 1227651.3034 | 2693801.3148 | 1227658.1325 | 2693800.2201 | 1227666.9882
2 | 2693826.6253 | 1227642.5427 | 2693821.1041 | 1227631.7146
3 | 2693800.2201 | 1227666.9882 | 2693810.8822 | 1227675.2733 | 2693821.2046 | 1227681.3938
4 | 2693821.1041 | 1227631.7146 | 2693821.1041 | 1227631.7146 | 2693814.7108 | 1227626.0308
5 | 2693897.9213 | 1227704.5672 | 2693888.5532 | 1227699.7826 | 2693862.9649 | 1227694.0859 | 2693845.3903 | 1227691.5958 | 2693830.976 | 1227687.1875 | 2693821.2046 | 1227681.3938
6 | 2693828.7067 | 1227575.0052 | 2693815.5362 | 1227598.3919 | 2693806.3411 | 1227613.858 | 2693807.8744 | 1227619.9532 | 2693814.7108 | 1227626.0308
7 | 2693877.8423 | 1227759.4005 | 2693893.4945 | 1227741.557 | 2693897.2479 | 1227737.1242 | 2693901.2019 | 1227732.4722 | 2693896.3169 | 1227729.3706 | 2693896.3067 | 1227721.3759 | 2693896.289 | 1227713.8592 | 2693896.9435 | 1227707.9319 | 2693897.9213 | 1227704.5672
8 | 2693897.9213 | 1227704.5672 | 2693896.9435 | 1227707.9319 | 2693896.289 | 1227713.8592 | 2693896.3067 | 1227721.3759 | 2693896.3169 | 1227729.3706 | 2693901.2019 | 1227732.4722 | 2693911.7164 | 1227740.4883 | 2693952.9505 | 1227775.2641 | 2693948.9451 | 1227780.7714 | 2693943.5757 | 1227788.1808 | 2693934.9901 | 1227781.8518 | 2693923.2276 | 1227796.232
9 | 2693877.8423 | 1227759.4005 | 2693862.6059 | 1227776.7
10 | 2693923.2276 | 1227796.232 | 2693916.1264 | 1227805.8045
11 | 2693733.9625 | 1227613.6394 | 2693702.3381 | 1227644.4207
12 | 2693733.9625 | 1227613.6394 | 2693730.6113 | 1227598.8093 | 2693730.3592 | 1227596.7587
13 | 2693695.3142 | 1227651.2574 | 2693702.3381 | 1227644.4207
14 | 2693730.3592 | 1227596.7587 | 2693729.4827 | 1227589.6295 | 2693729.2867 | 1227585.2344 | 2693729.346 | 1227581.4771 | 2693729.6613 | 1227578.8361
15 | 2693831.9006 | 1227578.6581 | 2693828.7067 | 1227575.0052
16 | 2693828.7067 | 1227575.0052 | 2693824.5941 | 1227570.0145
17 | 2693831.9006 | 1227578.6581 | 2693843.1168 | 1227590.2544 | 2693843.5278 | 1227590.5926
18 | 2693849.2313 | 1227791.8856 | 2693862.6059 | 1227776.7
19 | 2693695.3142 | 1227651.2574 | 2693688.1152 | 1227659.3643
20 | 2693703.9329 | 1227659.3656 | 2693695.3142 | 1227651.2574
21 | 2693730.6471 | 1227570.5787 | 2693729.6613 | 1227578.8361
22 | 2693824.5941 | 1227570.0145 | 2693817.7675 | 1227574.1876 | 2693808.3525 | 1227575.24 | 2693791.1633 | 1227569.4315 | 2693788.7863 | 1227568.802
23 | 2693849.2313 | 1227791.8856 | 2693844.5348 | 1227797.218
24 | 2693830.63 | 1227742.7328 | 2693840.8278 | 1227746.8076 | 2693847.3571 | 1227749.061
25 | 2693830.63 | 1227742.7328 | 2693827.7581 | 1227748.9364 | 2693821.3264 | 1227757.3965
26 | 2693830.63 | 1227742.7328 | 2693821.556 | 1227739.1026
27 | 2693786.1913 | 1227568.1149 | 2693788.7863 | 1227568.802
28 | 2693770.5805 | 1227563.981 | 2693766.2112 | 1227562.6981
29 | 2693770.5805 | 1227563.981 | 2693780.9508 | 1227566.7271
30 | 2693786.1913 | 1227568.1149 | 2693780.9508 | 1227566.7271
31 | 2693730.6471 | 1227570.5787 | 2693724.8359 | 1227569.9645 | 2693718.336 | 1227569.2838 | 2693710.6255 | 1227569.4292 | 2693703.743 | 1227570.4215
32 | 2693703.743 | 1227570.4215 | 2693703.5742 | 1227558.5632
33 | 2693703.743 | 1227570.4215 | 2693684.6987 | 1227575.0693 | 2693660.9379 | 1227580.8216 | 2693626.4212 | 1227588.5616 | 2693605.2943 | 1227591.1866 | 2693582.9005 | 1227591.9571 | 2693563.0785 | 1227589.8151
34 | 2693819.8528 | 1227825.3217 | 2693895.7428 | 1227900.5725 | 2693904.8335 | 1227902.6871
35 | 2693819.8528 | 1227825.3217 | 2693826.6993 | 1227817.4685
36 | 2693819.8528 | 1227825.3217 | 2693821.3631 | 1227834.7967 | 2693710.834 | 1227958.6764
37 | 2693826.6993 | 1227817.4685 | 2693821.3449 | 1227814.3374 | 2693820.1323 | 1227814.8846
38 | 2693826.6993 | 1227817.4685 | 2693830.805 | 1227812.807
39 | 2693710.834 | 1227958.6764 | 2693760.1986 | 1228008.9011 | 2693793.2491 | 1228039.7015
40 | 2693820.1323 | 1227814.8846 | 2693810.7269 | 1227819.1289 | 2693802.4844 | 1227811.9547
41 | 2693830.805 | 1227812.807 | 2693844.5348 | 1227797.218
42 | 2693742.8468 | 1227836.3632 | 2693743.5741 | 1227836.6163 | 2693750.6158 | 1227838.006 | 2693763.5546 | 1227837.4317 | 2693775.4565 | 1227834.8397 | 2693780.4897 | 1227833.2351
43 | 2693742.8468 | 1227836.3632 | 2693738.3203 | 1227834.7878
44 | 2693802.4844 | 1227811.9547 | 2693797.2247 | 1227807.3766
45 | 2693723.1966 | 1227822.5185 | 2693733.6103 | 1227827.7975 | 2693738.3203 | 1227834.7878
46 | 2693788.1589 | 1227799.7705 | 2693787.5415 | 1227801.4286 | 2693793.0977 | 1227803.7845 | 2693797.2247 | 1227807.3766
47 | 2693506.1753 | 1227581.6023 | 2693488.7631 | 1227579.0488
48 | 2693506.1753 | 1227581.6023 | 2693537.2462 | 1227586.1589
49 | 2693309.6745 | 1227540.3182 | 2693345.945 | 1227553.6188 | 2693392.0045 | 1227563.7599 | 2693474.8125 | 1227577.003 | 2693488.7631 | 1227579.0488
50 | 2693537.2462 | 1227586.1589 | 2693559.6565 | 1227589.4454 | 2693562.8801 | 1227589.7937
51 | 2693285.3304 | 1227702.5851 | 2693289.8194 | 1227661.871 | 2693288.4916 | 1227594.3355 | 2693286.5137 | 1227570.6432 | 2693287.4498 | 1227557.8377 | 2693292.6179 | 1227551.6254 | 2693295.4761 | 1227548.19 | 2693309.6745 | 1227540.3182
52 | 2693562.8801 | 1227589.7937 | 2693563.0785 | 1227589.8151
53 | 2693285.3304 | 1227702.5851 | 2693287.7824 | 1227711.5077 | 2693300.8627 | 1227759.4024 | 2693309.3503 | 1227798.5689
54 | 2693309.3503 | 1227798.5689 | 2693311.1887 | 1227807.0519
55 | 2693311.1887 | 1227807.0519 | 2693315.3441 | 1227826.2271
56 | 2693358.4065 | 1228055.7606 | 2693356.038 | 1228056.1039
57 | 2693387.1644 | 1228075.0255 | 2693376.5586 | 1228064.6183 | 2693367.404 | 1228054.4563 | 2693358.4065 | 1228055.7606
58 | 2693391.8644 | 1228069.6399 | 2693391.1825 | 1228071.0747 | 2693387.1644 | 1228075.0255
59 | 2693330.6908 | 1228158.3765 | 2693356.166 | 1228105.5386 | 2693387.1644 | 1228075.0255
60 | 2693431.5764 | 1228021.4291 | 2693391.8644 | 1228069.6399
61 | 2693391.8644 | 1228069.6399 | 2693398.8017 | 1228075.7309 | 2693425.6015 | 1228100.7029 | 2693435.3731 | 1228107.7613 | 2693442.8758 | 1228102.9535 | 2693452.45 | 1228100.391 | 2693454.0549 | 1228101.0614
62 | 2693407.2296 | 1228184.7187 | 2693398.3245 | 1228185.2237 | 2693389.5409 | 1228190.534 | 2693375.4879 | 1228199.3753 | 2693371.2647 | 1228199.9872 | 2693364.575 | 1228194.0558 | 2693346.3135 | 1228174.0995 | 2693330.6908 | 1228158.3765
63 | 2693330.6908 | 1228158.3765 | 2693323.4509 | 1228179.2889 | 2693318.7034 | 1228194.0405
64 | 2693431.5764 | 1228021.4291 | 2693473.0519 | 1227981.53
65 | 2693457.7053 | 1228102.5862 | 2693454.0549 | 1228101.0614
66 | 2693489.577 | 1227961.1528 | 2693489.577 | 1227961.1528 | 2693477.601 | 1227977.1538 | 2693473.0519 | 1227981.53
67 | 2693457.7053 | 1228102.5862 | 2693457.7053 | 1228102.5862 | 2693462.3835 | 1228103.4158
68 | 2693489.577 | 1227961.1528 | 2693495.1552 | 1227946.9983
69 | 2693495.1552 | 1227946.9983 | 2693504.6147 | 1227922.9953 | 2693513.6092 | 1227911.0358
70 | 2693790.5002 | 1227726.6784 | 2693797.3144 | 1227729.4045
71 | 2693790.5002 | 1227726.6784 | 2693787.1315 | 1227725.3307
72 | 2693797.3144 | 1227729.4045 | 2693814.74 | 1227736.3758
73 | 2693776.221 | 1227720.9658 | 2693787.1315 | 1227725.3307
74 | 2693814.74 | 1227736.3758 | 2693821.556 | 1227739.1026
75 | 2693772.6745 | 1227719.547 | 2693776.221 | 1227720.9658
76 | 2693772.6745 | 1227719.547 | 2693760.3561 | 1227710.1091
77 | 2693772.6745 | 1227719.547 | 2693767.5592 | 1227731.4313
78 | 2693756.3008 | 1227707.0021 | 2693760.3561 | 1227710.1091
79 | 2693765.5533 | 1227736.0914 | 2693767.5592 | 1227731.4313
80 | 2693824.8722 | 1227760.8327 | 2693821.3264 | 1227757.3965
81 | 2693741.6668 | 1227694.8648 | 2693746.9659 | 1227699.8501 | 2693756.3008 | 1227707.0021
82 | 2693711.1944 | 1227666.197 | 2693715.0899 | 1227669.8619
83 | 2693703.9329 | 1227659.3656 | 2693711.1944 | 1227666.197
84 | 2693715.0899 | 1227669.8619 | 2693718.9855 | 1227673.5267
85 | 2693703.9329 | 1227659.3656 | 2693708.7913 | 1227654.5498 | 2693708.5022 | 1227650.2866 | 2693731.9189 | 1227638.9474 | 2693739.4219 | 1227651.9526 | 2693742.9368 | 1227655.7747
86 | 2693718.9855 | 1227673.5267 | 2693733.8757 | 1227687.5351
87 | 2693742.9368 | 1227655.7747 | 2693746.6522 | 1227659.8148
88 | 2693733.8757 | 1227687.5351 | 2693737.7712 | 1227691.1999
89 | 2693688.1152 | 1227659.3643 | 2693677.845 | 1227670.9297
90 | 2693746.6522 | 1227659.8148 | 2693751.673 | 1227665.2743
91 | 2693741.6668 | 1227694.8648 | 2693737.7712 | 1227691.1999
92 | 2693677.845 | 1227670.9297 | 2693677.845 | 1227670.9297 | 2693673.0862 | 1227681.3544
93 | 2693751.673 | 1227665.2743 | 2693755.387 | 1227669.3128
94 | 2693668.8143 | 1227690.7128 | 2693673.0862 | 1227681.3544
95 | 2693759.1016 | 1227673.352 | 2693755.387 | 1227669.3128
96 | 2693754.1907 | 1227762.6976 | 2693768.9156 | 1227768.233
97 | 2693754.1907 | 1227762.6976 | 2693748.9873 | 1227760.5585 | 2693732.3435 | 1227768.2573 | 2693737.4178 | 1227782.7643
98 | 2693776.0178 | 1227770.903 | 2693768.9156 | 1227768.233
99 | 2693741.9597 | 1227791.9146 | 2693739.4651 | 1227788.6174 | 2693737.4178 | 1227782.7643
100 | 2693824.8722 | 1227760.8327 | 2693829.0366 | 1227764.9346
101 | 2693824.8722 | 1227760.8327 | 2693805.9713 | 1227780.9267
102 | 2693809.9415 | 1227784.3696 | 2693805.9713 | 1227780.9267
103 | 2693803.9593 | 1227783.0743 | 2693805.9713 | 1227780.9267
104 | 2693803.9593 | 1227783.0743 | 2693799.6063 | 1227780.3593 | 2693791.5214 | 1227777.3519 | 2693786.9983 | 1227775.4468
105 | 2693668.8143 | 1227690.7128 | 2693648.4866 | 1227735.2436
106 | 2693638.744 | 1227756.5863 | 2693648.4866 | 1227735.2436
107 | 2693638.744 | 1227756.5863 | 2693645.3167 | 1227768.5093 | 2693647.7136 | 1227787.6385 | 2693650.8642 | 1227792.5916
108 | 2693650.8642 | 1227792.5916 | 2693657.3104 | 1227795.7064 | 2693664.7801 | 1227794.3951
109 | 2693650.8642 | 1227792.5916 | 2693639.5324 | 1227793.6251 | 2693636.4868 | 1227794.033 | 2693631.4301 | 1227794.601
110 | 2693591.8054 | 1227796.1537 | 2693555.6974 | 1227826.5964 | 2693542.4076 | 1227845.1451 | 2693533.1937 | 1227884.9953 | 2693513.6092 | 1227911.0358
111 | 2693591.8054 | 1227796.1537 | 2693595.2354 | 1227797.8088 | 2693601.5008 | 1227797.9631 | 2693630.3236 | 1227794.7253
112 | 2693630.3236 | 1227794.7253 | 2693631.4301 | 1227794.601
113 | 2693700.6938 | 1227801.7354 | 2693690.2033 | 1227796.1913 | 2693675.6189 | 1227792.4923 | 2693664.7801 | 1227794.3951
114 | 2693723.1966 | 1227822.5185 | 2693708.7012 | 1227805.9673 | 2693700.6938 | 1227801.7354
115 | 2693722.9381 | 1227834.1116 | 2693723.1966 | 1227822.5185
116 | 2693788.1589 | 1227799.7705 | 2693785.4113 | 1227798.7163
117 | 2693759.8314 | 1227674.1456 | 2693759.1016 | 1227673.352
118 | 2693776.0178 | 1227770.903 | 2693769.1206 | 1227788.1106
119 | 2693776.0178 | 1227770.903 | 2693781.6207 | 1227773.1818 | 2693786.9983 | 1227775.4468
120 | 2693769.1206 | 1227788.1106 | 2693767.6076 | 1227791.8854 | 2693775.9822 | 1227795.0985
121 | 2693775.9822 | 1227795.0985 | 2693785.4113 | 1227798.7163

## bus_geodata
| x | y | coords
0 | 2693843.8382 | 1227655.6975
1 | 2693826.6253 | 1227642.5427
2 | 2693800.2201 | 1227666.9882
3 | 2693821.1041 | 1227631.7146
4 | 2693821.2046 | 1227681.3938
5 | 2693814.7108 | 1227626.0308
6 | 2693897.9213 | 1227704.5672
7 | 2693877.8423 | 1227759.4005
8 | 2693923.2276 | 1227796.232
9 | 2693733.9625 | 1227613.6394
10 | 2693702.3381 | 1227644.4207
11 | 2693730.3592 | 1227596.7587
12 | 2693828.7067 | 1227575.0052
13 | 2693843.5278 | 1227590.5926
14 | 2693831.9006 | 1227578.6581
15 | 2693862.6059 | 1227776.7
16 | 2693916.1264 | 1227805.8045
17 | 2693695.3142 | 1227651.2574
18 | 2693729.6613 | 1227578.8361
19 | 2693824.5941 | 1227570.0145
20 | 2693849.2313 | 1227791.8856
21 | 2693847.3571 | 1227749.061
22 | 2693830.63 | 1227742.7328
23 | 2693788.7863 | 1227568.802
24 | 2693770.5805 | 1227563.981
25 | 2693766.2112 | 1227562.6981
26 | 2693780.9508 | 1227566.7271
27 | 2693730.6471 | 1227570.5787
28 | 2693703.743 | 1227570.4215
29 | 2693786.1913 | 1227568.1149
30 | 2693904.8335 | 1227902.6871
31 | 2693819.8528 | 1227825.3217
32 | 2693826.6993 | 1227817.4685
33 | 2693710.834 | 1227958.6764
34 | 2693820.1323 | 1227814.8846
35 | 2693830.805 | 1227812.807
36 | 2693793.2491 | 1228039.7015
37 | 2693780.4897 | 1227833.2351
38 | 2693742.8468 | 1227836.3632
39 | 2693802.4844 | 1227811.9547
40 | 2693844.5348 | 1227797.218
41 | 2693738.3203 | 1227834.7878
42 | 2693797.2247 | 1227807.3766
43 | 2693506.1753 | 1227581.6023
44 | 2693488.7631 | 1227579.0488
45 | 2693537.2462 | 1227586.1589
46 | 2693309.6745 | 1227540.3182
47 | 2693562.8801 | 1227589.7937
48 | 2693285.3304 | 1227702.5851
49 | 2693563.0785 | 1227589.8151
50 | 2693309.3503 | 1227798.5689
51 | 2693311.1887 | 1227807.0519
52 | 2693703.5742 | 1227558.5632
53 | 2693358.4065 | 1228055.7606
54 | 2693356.038 | 1228056.1039
55 | 2693387.1644 | 1228075.0255
56 | 2693391.8644 | 1228069.6399
57 | 2693330.6908 | 1228158.3765
58 | 2693431.5764 | 1228021.4291
59 | 2693454.0549 | 1228101.0614
60 | 2693407.2296 | 1228184.7187
61 | 2693318.7034 | 1228194.0405
62 | 2693473.0519 | 1227981.53
63 | 2693457.7053 | 1228102.5862
64 | 2693489.577 | 1227961.1528
65 | 2693462.3835 | 1228103.4158
66 | 2693495.1552 | 1227946.9983
67 | 2693790.5002 | 1227726.6784
68 | 2693797.3144 | 1227729.4045
69 | 2693787.1315 | 1227725.3307
70 | 2693814.74 | 1227736.3758
71 | 2693776.221 | 1227720.9658
72 | 2693821.556 | 1227739.1026
73 | 2693772.6745 | 1227719.547
74 | 2693760.3561 | 1227710.1091
75 | 2693767.5592 | 1227731.4313
76 | 2693821.3264 | 1227757.3965
77 | 2693756.3008 | 1227707.0021
78 | 2693765.5533 | 1227736.0914
79 | 2693711.1944 | 1227666.197
80 | 2693715.0899 | 1227669.8619
81 | 2693703.9329 | 1227659.3656
82 | 2693718.9855 | 1227673.5267
83 | 2693742.9368 | 1227655.7747
84 | 2693733.8757 | 1227687.5351
85 | 2693688.1152 | 1227659.3643
86 | 2693746.6522 | 1227659.8148
87 | 2693737.7712 | 1227691.1999
88 | 2693677.845 | 1227670.9297
89 | 2693751.673 | 1227665.2743
90 | 2693741.6668 | 1227694.8648
91 | 2693673.0862 | 1227681.3544
92 | 2693755.387 | 1227669.3128
93 | 2693754.1907 | 1227762.6976
94 | 2693768.9156 | 1227768.233
95 | 2693737.4178 | 1227782.7643
96 | 2693824.8722 | 1227760.8327
97 | 2693829.0366 | 1227764.9346
98 | 2693805.9713 | 1227780.9267
99 | 2693809.9415 | 1227784.3696
100 | 2693803.9593 | 1227783.0743
101 | 2693668.8143 | 1227690.7128
102 | 2693648.4866 | 1227735.2436
103 | 2693638.744 | 1227756.5863
104 | 2693650.8642 | 1227792.5916
105 | 2693591.8054 | 1227796.1537
106 | 2693513.6092 | 1227911.0358
107 | 2693630.3236 | 1227794.7253
108 | 2693664.7801 | 1227794.3951
109 | 2693631.4301 | 1227794.601
110 | 2693700.6938 | 1227801.7354
111 | 2693723.1966 | 1227822.5185
112 | 2693722.9381 | 1227834.1116
113 | 2693788.1589 | 1227799.7705
114 | 2693315.3441 | 1227826.2271
115 | 2693759.1016 | 1227673.352
116 | 2693759.8314 | 1227674.1456
117 | 2693776.0178 | 1227770.903
118 | 2693741.9597 | 1227791.9146
119 | 2693769.1206 | 1227788.1106
120 | 2693786.9983 | 1227775.4468
121 | 2693775.9822 | 1227795.0985
122 | 2693785.4113 | 1227798.7163
123 | 2693772.6745 | 1227719.547

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97175 | -0.54438 | 0.0082458 | 0.0020666
1 | 0.97192 | -0.54108 | 0 | 0
2 | 0.9734 | -0.51188 | 0 | 0
3 | 0.97157 | -0.54798 | 0.0057211 | 0.0014338
4 | 0.97433 | -0.4936 | 0.015365 | 0.0038508
5 | 0.97137 | -0.55194 | 0.010233 | 0.0025645
6 | 0.97843 | -0.41316 | 0 | 0
7 | 0.98215 | -0.34093 | 0 | 0
8 | 0.97769 | -0.42775 | 0 | 0
9 | 0.99255 | -0.14241 | 0 | 0
10 | 0.9933 | -0.12795 | 0.012029 | 0.0030147
11 | 0.99226 | -0.14808 | 0.0045643 | 0.0011439
12 | 0.97054 | -0.56843 | 0 | 0
13 | 0.97043 | -0.57057 | 0.0053758 | 0.0013473
14 | 0.97051 | -0.56891 | 0 | 0
15 | 0.98344 | -0.31598 | 0.0013059 | 0.0003273
16 | 0.97763 | -0.42896 | 0.0055908 | 0.0014012
17 | 0.99357 | -0.12266 | 0 | 0
18 | 0.99203 | -0.15253 | 0.0050979 | 0.0012776
19 | 0.97048 | -0.56955 | 0 | 0
20 | 0.98459 | -0.29366 | 0.00078122 | 0.00019579
21 | 0.99565 | -0.082434 | 0.0069625 | 0.001745
22 | 0.99576 | -0.080244 | 0 | 0
23 | 0.97014 | -0.57619 | 0.0034693 | 0.00086949
24 | 0.97009 | -0.57727 | 0 | 0
25 | 0.97008 | -0.57741 | 0.0016481 | 0.00041305
26 | 0.97011 | -0.57694 | 0.002839 | 0.00071152
27 | 0.99196 | -0.15384 | 0 | 0
28 | 0.99174 | -0.15808 | 0 | 0
29 | 0.97013 | -0.57649 | 0.0014629 | 0.00036664
30 | 0.98646 | -0.25775 | 0.001036 | 0.00025965
31 | 0.98657 | -0.25559 | 0 | 0
32 | 0.9866 | -0.25496 | 0 | 0
33 | 0.9862 | -0.26283 | 0 | 0
34 | 0.98708 | -0.24584 | 0.00053577 | 0.00013428
35 | 0.98623 | -0.26212 | 0.00095741 | 0.00023995
36 | 0.98596 | -0.26759 | 0.0022969 | 0.00057565
37 | 0.97874 | -0.41019 | 0.012877 | 0.0032272
38 | 0.9792 | -0.4012 | 0.0051084 | 0.0012803
39 | 0.98843 | -0.21995 | 0.00053567 | 0.00013425
40 | 0.985 | -0.28574 | 0.0013052 | 0.00032712
41 | 0.97928 | -0.39964 | 0.0039003 | 0.00097752
42 | 0.98887 | -0.21141 | 0.00053589 | 0.00013431
43 | 0.99046 | -0.18311 | 0.00080751 | 0.00020238
44 | 0.99037 | -0.18476 | 0.0040641 | 0.0010186
45 | 0.99063 | -0.17971 | 0.00064047 | 0.00016052
46 | 0.99017 | -0.18873 | 0 | 0
47 | 0.99079 | -0.17661 | 0.00038614 | 9.6776e-05
48 | 0.98998 | -0.19247 | 0 | 0
49 | 0.99079 | -0.17659 | 0.00017362 | 4.3514e-05
50 | 0.98987 | -0.19459 | 0.00072427 | 0.00018152
51 | 0.98987 | -0.19466 | 0.00025292 | 6.3389e-05
52 | 0.99173 | -0.15841 | 0.0015744 | 0.00039458
53 | 0.97942 | -0.39697 | 0.00063048 | 0.00015801
54 | 0.97942 | -0.39702 | 0.0012055 | 0.00030213
55 | 0.97949 | -0.39572 | 0 | 0
56 | 0.97951 | -0.3953 | 0 | 0
57 | 0.97936 | -0.39814 | 0 | 0
58 | 0.97982 | -0.38908 | 0 | 0
59 | 0.97934 | -0.39865 | 0.00019432 | 4.87e-05
60 | 0.97929 | -0.39964 | 0.00083922 | 0.00021033
61 | 0.97935 | -0.39845 | 0.00046088 | 0.00011551
62 | 0.98012 | -0.38334 | 0.00075436 | 0.00018906
63 | 0.97933 | -0.3988 | 0.0010086 | 0.00025277
64 | 0.98027 | -0.38036 | 0.00049312 | 0.00012359
65 | 0.97933 | -0.3989 | 0.0011412 | 0.00028601
66 | 0.98036 | -0.3785 | 0.00070535 | 0.00017678
67 | 0.9979 | -0.039612 | 0.0012423 | 0.00031135
68 | 0.99753 | -0.046582 | 0.00088078 | 0.00022075
69 | 0.99809 | -0.036129 | 0.0012423 | 0.00031135
70 | 0.9966 | -0.064282 | 0.00088005 | 0.00022056
71 | 0.99869 | -0.02473 | 0.0023048 | 0.00057765
72 | 0.99624 | -0.071158 | 0.00088116 | 0.00022084
73 | 0.99889 | -0.02095 | 0 | 0
74 | 0.99972 | -0.0052358 | 0.001533 | 0.0003842
75 | 0.99886 | -0.021578 | 0.0012438 | 0.00031172
76 | 0.99496 | -0.09543 | 0.0016452 | 0.00041233
77 | 1 | 0 | -0.2836 | -0.072105
78 | 0.99885 | -0.021713 | 0.0015321 | 0.00038397
79 | 0.99562 | -0.083404 | 0.0028008 | 0.00070195
80 | 0.99599 | -0.076391 | 0.0028024 | 0.00070236
81 | 0.99495 | -0.096245 | 0 | 0
82 | 0.99636 | -0.069251 | 0.0028008 | 0.00070195
83 | 0.99392 | -0.11605 | 0.002801 | 0.00070199
84 | 0.99782 | -0.041509 | 0.0028008 | 0.00070195
85 | 0.99261 | -0.1411 | 0.0030089 | 0.0007541
86 | 0.99384 | -0.11768 | 0.0028023 | 0.00070233
87 | 0.9982 | -0.034133 | 0.001533 | 0.0003842
88 | 0.99128 | -0.16664 | 0.0030543 | 0.00076547
89 | 0.99375 | -0.11951 | 0.0028019 | 0.00070222
90 | 0.99859 | -0.026692 | 0.0015321 | 0.00038397
91 | 0.99032 | -0.18499 | 0.010226 | 0.0025629
92 | 0.99369 | -0.1206 | 0.002801 | 0.00070199
93 | 0.9918 | -0.15576 | 0 | 0
94 | 0.992 | -0.1518 | 0.0015395 | 0.00038583
95 | 0.99128 | -0.16567 | 0.0018623 | 0.00046675
96 | 0.99474 | -0.099657 | 0 | 0
97 | 0.99472 | -0.099925 | 0.0026082 | 0.00065367
98 | 0.99353 | -0.12264 | 0 | 0
99 | 0.99352 | -0.12288 | 0.0026092 | 0.00065394
100 | 0.9934 | -0.12503 | 0 | 0
101 | 0.98956 | -0.19961 | 0.0037361 | 0.00093636
102 | 0.98612 | -0.26624 | 0.012701 | 0.0031831
103 | 0.98474 | -0.29298 | 0 | 0
104 | 0.98246 | -0.33732 | 0 | 0
105 | 0.98178 | -0.35065 | 0 | 0
106 | 0.98064 | -0.37299 | 0.0011422 | 0.00028626
107 | 0.98209 | -0.34458 | 0.0050791 | 0.0012729
108 | 0.98187 | -0.34897 | 0.0083707 | 0.0020979
109 | 0.98211 | -0.3443 | 0.0061044 | 0.0015299
110 | 0.98063 | -0.37323 | 0.0026634 | 0.00066752
111 | 0.97969 | -0.39164 | 0 | 0
112 | 0.97957 | -0.39392 | 0.010794 | 0.0027052
113 | 0.98973 | -0.19503 | 0 | 0
114 | 0.98986 | -0.19474 | 0.00022504 | 5.64e-05
115 | 0.99365 | -0.12141 | 0.002801 | 0.00070199
116 | 0.99364 | -0.12152 | 0.0055913 | 0.0014013
117 | 0.99211 | -0.14968 | 0 | 0
118 | 0.99117 | -0.16793 | 0.012349 | 0.0030949
119 | 0.99147 | -0.1619 | 0.0018622 | 0.00046671
120 | 0.99261 | -0.1402 | 0.0018608 | 0.00046637
121 | 0.99059 | -0.17868 | 0.0016195 | 0.00040588
122 | 0.98992 | -0.1914 | 0.0016195 | 0.00040588
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0082458 | -0.0020666 | 0.0082471 | 0.0020672 | 1.2952e-06 | 5.605e-07 | 0.012627 | 0.012627 | 0.012627 | 0.97175 | -0.54438 | 0.97192 | -0.54108 | 3.4688
1 | -0.039027 | -0.0097911 | 0.039081 | 0.0098254 | 5.4425e-05 | 3.4328e-05 | 0.059754 | 0.059754 | 0.059754 | 0.97192 | -0.54108 | 0.9734 | -0.51188 | 16.4159
2 | 0.03078 | 0.0077239 | -0.030769 | -0.0077176 | 1.0123e-05 | 6.3282e-06 | 0.047127 | 0.047127 | 0.047127 | 0.97192 | -0.54108 | 0.97157 | -0.54798 | 12.9471
3 | -0.039081 | -0.0098254 | 0.039115 | 0.009847 | 3.4147e-05 | 2.1537e-05 | 0.059754 | 0.059754 | 0.059754 | 0.9734 | -0.51188 | 0.97433 | -0.4936 | 16.4159
4 | 0.025048 | 0.0062838 | -0.025044 | -0.0062809 | 4.7218e-06 | 2.916e-06 | 0.038365 | 0.038365 | 0.038365 | 0.97157 | -0.54798 | 0.97137 | -0.55194 | 10.5399
5 | -0.05448 | -0.013698 | 0.05469 | 0.013831 | 0.00021015 | 0.00013348 | 0.083219 | 0.083219 | 0.083219 | 0.97433 | -0.4936 | 0.97843 | -0.41316 | 22.8625
6 | 0.014811 | 0.0037163 | -0.014799 | -0.0037096 | 1.1635e-05 | 6.7013e-06 | 0.02269 | 0.02269 | 0.02269 | 0.97137 | -0.55194 | 0.97054 | -0.56843 | 6.2336
7 | -0.060285 | -0.015233 | 0.060495 | 0.015366 | 0.00020955 | 0.00013328 | 0.091728 | 0.091728 | 0.091728 | 0.97843 | -0.41316 | 0.98215 | -0.34093 | 25.2
8 | 0.005595 | 0.0014019 | -0.0055911 | -0.0014012 | 3.8863e-06 | 6.9095e-07 | 0.0085088 | 0.0085095 | 0.0085095 | 0.97843 | -0.41316 | 0.97769 | -0.42775 | 2.3378
9 | -0.060495 | -0.015366 | 0.060568 | 0.015413 | 7.2736e-05 | 4.6259e-05 | 0.091728 | 0.091728 | 0.091728 | 0.98215 | -0.34093 | 0.98344 | -0.31598 | 25.1999
10 | 0.0055911 | 0.0014012 | -0.0055908 | -0.0014012 | 3.2335e-07 | 5.7624e-08 | 0.0085095 | 0.0085095 | 0.0085095 | 0.97769 | -0.42775 | 0.97763 | -0.42896 | 2.3378
11 | -0.01853 | -0.0046417 | 0.018543 | 0.0046493 | 1.2771e-05 | 7.6027e-06 | 0.02778 | 0.027779 | 0.02778 | 0.99255 | -0.14241 | 0.9933 | -0.12795 | 7.6317
12 | 0.01853 | 0.0046417 | -0.018525 | -0.0046387 | 4.9978e-06 | 2.9754e-06 | 0.02778 | 0.02778 | 0.02778 | 0.99255 | -0.14241 | 0.99226 | -0.14808 | 7.6318
13 | -0.030572 | -0.007664 | 0.03058 | 0.0076688 | 7.7099e-06 | 4.8074e-06 | 0.045799 | 0.045799 | 0.045799 | 0.9933 | -0.12795 | 0.99357 | -0.12266 | 12.5822
14 | 0.013961 | 0.0034948 | -0.013958 | -0.0034931 | 2.9583e-06 | 1.6609e-06 | 0.020935 | 0.020935 | 0.020935 | 0.99226 | -0.14808 | 0.99203 | -0.15253 | 5.7514
15 | 0.0053764 | 0.0013474 | -0.0053762 | -0.0013474 | 1.2348e-07 | 1.9141e-08 | 0.008243 | 0.008243 | 0.008243 | 0.97054 | -0.56843 | 0.97051 | -0.56891 | 2.2646
16 | 0.009423 | 0.0023622 | -0.0094225 | -0.002362 | 5.0557e-07 | 2.4375e-07 | 0.014447 | 0.014447 | 0.014447 | 0.97054 | -0.56843 | 0.97048 | -0.56955 | 3.9691
17 | -0.0053758 | -0.0013473 | 0.0053762 | 0.0013474 | 4.2464e-07 | 6.5853e-08 | 0.0082431 | 0.008243 | 0.0082431 | 0.97043 | -0.57057 | 0.97051 | -0.56891 | 2.2646
18 | -0.061874 | -0.01574 | 0.06194 | 0.015782 | 6.6629e-05 | 4.2385e-05 | 0.093703 | 0.093703 | 0.093703 | 0.98344 | -0.31598 | 0.98459 | -0.29366 | 25.7427
19 | 0.097135 | 0.024695 | -0.097049 | -0.02464 | 8.6189e-05 | 5.5021e-05 | 0.1456 | 0.1456 | 0.1456 | 0.99357 | -0.12266 | 0.99261 | -0.1411 | 39.9995
20 | -0.12771 | -0.032364 | 0.12788 | 0.032467 | 0.00016231 | 0.00010372 | 0.1914 | 0.1914 | 0.1914 | 0.99357 | -0.12266 | 0.99495 | -0.096245 | 52.5816
21 | 0.0088602 | 0.0022155 | -0.0088597 | -0.0022152 | 5.5067e-07 | 2.4507e-07 | 0.013288 | 0.013288 | 0.013288 | 0.99203 | -0.15253 | 0.99196 | -0.15384 | 3.6506
22 | 0.0094225 | 0.002362 | -0.0094195 | -0.0023605 | 2.9805e-06 | 1.4372e-06 | 0.014447 | 0.014448 | 0.014448 | 0.97048 | -0.56955 | 0.97014 | -0.57619 | 3.9691
23 | -0.062721 | -0.015978 | 0.062745 | 0.015993 | 2.399e-05 | 1.5263e-05 | 0.094884 | 0.094884 | 0.094884 | 0.98459 | -0.29366 | 0.985 | -0.28574 | 26.067
24 | -0.0069625 | -0.001745 | 0.0069632 | 0.0017452 | 7.2636e-07 | 2.3219e-07 | 0.010406 | 0.010406 | 0.010406 | 0.99565 | -0.082434 | 0.99576 | -0.080244 | 2.8587
25 | 0.10032 | 0.025708 | -0.10024 | -0.025662 | 7.3783e-05 | 4.6767e-05 | 0.15011 | 0.15011 | 0.15011 | 0.99576 | -0.080244 | 0.99496 | -0.09543 | 20.6197
26 | -0.10728 | -0.027454 | 0.10733 | 0.027484 | 4.7215e-05 | 2.9963e-05 | 0.16052 | 0.16052 | 0.16052 | 0.99576 | -0.080244 | 0.99624 | -0.071158 | 22.049
27 | 0.0059502 | 0.0014911 | -0.0059501 | -0.001491 | 8.3848e-08 | 2.0517e-08 | 0.0091264 | 0.0091264 | 0.0091264 | 0.97014 | -0.57619 | 0.97013 | -0.57649 | 2.5073
28 | 0.0016481 | 0.000413 | -0.0016481 | -0.00041305 | 1.0913e-08 | -4.9236e-08 | 0.002528 | 0.002528 | 0.002528 | 0.97009 | -0.57727 | 0.97008 | -0.57741 | 0.69451
29 | -0.0016481 | -0.000413 | 0.0016481 | 0.00041289 | 2.5709e-08 | -1.16e-07 | 0.002528 | 0.002528 | 0.002528 | 0.97009 | -0.57727 | 0.97011 | -0.57694 | 0.69451
30 | -0.0044871 | -0.0011244 | 0.0044872 | 0.0011244 | 9.6299e-08 | -5.3024e-09 | 0.0068826 | 0.0068826 | 0.0068826 | 0.97011 | -0.57694 | 0.97013 | -0.57649 | 1.8908
31 | 0.0088597 | 0.0022152 | -0.0088579 | -0.0022145 | 1.7856e-06 | 7.9478e-07 | 0.013288 | 0.013288 | 0.013288 | 0.99196 | -0.15384 | 0.99174 | -0.15808 | 3.6507
32 | 0.0015744 | 0.00039445 | -0.0015744 | -0.00039458 | 2.4817e-08 | -1.3714e-07 | 0.0023622 | 0.0023623 | 0.0023623 | 0.99174 | -0.15808 | 0.99173 | -0.15841 | 0.64898
33 | 0.0072835 | 0.00182 | -0.0072771 | -0.0018177 | 6.4049e-06 | 2.2549e-06 | 0.010926 | 0.010927 | 0.010927 | 0.99174 | -0.15808 | 0.99079 | -0.17659 | 3.0019
34 | -0.001036 | -0.00025965 | 0.0010361 | 0.00025824 | 1.064e-07 | -1.4156e-06 | 0.0015628 | 0.0015623 | 0.0015628 | 0.98646 | -0.25775 | 0.98657 | -0.25559 | 0.42934
35 | -0.0033343 | -0.00083101 | 0.0033344 | 0.00083094 | 9.8636e-08 | -6.9767e-08 | 0.0050274 | 0.0050273 | 0.0050274 | 0.98657 | -0.25559 | 0.9866 | -0.25496 | 1.3811
36 | 0.0022982 | 0.00057277 | -0.0022974 | -0.0005745 | 7.9005e-07 | -1.7336e-06 | 0.0034651 | 0.0034659 | 0.0034659 | 0.98657 | -0.25559 | 0.9862 | -0.26283 | 0.95217
37 | -0.068438 | -0.017452 | 0.068468 | 0.017472 | 3.016e-05 | 1.9206e-05 | 0.10333 | 0.10333 | 0.10333 | 0.9866 | -0.25496 | 0.98708 | -0.24584 | 28.3867
38 | 0.065104 | 0.016621 | -0.065081 | -0.016607 | 2.2509e-05 | 1.4326e-05 | 0.0983 | 0.0983 | 0.0983 | 0.9866 | -0.25496 | 0.98623 | -0.26212 | 27.0055
39 | 0.0022974 | 0.0005745 | -0.0022969 | -0.00057565 | 5.2082e-07 | -1.1413e-06 | 0.0034659 | 0.0034664 | 0.0034664 | 0.9862 | -0.26283 | 0.98596 | -0.26759 | 0.95232
40 | -0.069004 | -0.017606 | 0.06909 | 0.017661 | 8.6398e-05 | 5.5023e-05 | 0.10414 | 0.10413 | 0.10414 | 0.98708 | -0.24584 | 0.98843 | -0.21995 | 28.6085
41 | 0.064124 | 0.016367 | -0.064051 | -0.016321 | 7.3078e-05 | 4.6505e-05 | 0.096856 | 0.096856 | 0.096856 | 0.98623 | -0.26212 | 0.985 | -0.28574 | 26.6087
42 | -0.012877 | -0.0032272 | 0.012882 | 0.0032303 | 5.5136e-06 | 3.0464e-06 | 0.019577 | 0.019577 | 0.019577 | 0.97874 | -0.41019 | 0.9792 | -0.4012 | 5.3783
43 | -0.017991 | -0.0045106 | 0.017992 | 0.0045114 | 1.3434e-06 | 7.9949e-07 | 0.02734 | 0.02734 | 0.02734 | 0.9792 | -0.4012 | 0.97928 | -0.39964 | 7.511
44 | -0.069626 | -0.017795 | 0.069655 | 0.017813 | 2.8797e-05 | 1.8341e-05 | 0.10494 | 0.10494 | 0.10494 | 0.98843 | -0.21995 | 0.98887 | -0.21141 | 28.83
45 | -0.021892 | -0.0054889 | 0.021901 | 0.005494 | 8.3432e-06 | 5.0866e-06 | 0.033266 | 0.033266 | 0.033266 | 0.97928 | -0.39964 | 0.97969 | -0.39164 | 9.1391
46 | -0.070191 | -0.017948 | 0.070246 | 0.017983 | 5.5671e-05 | 3.5459e-05 | 0.10575 | 0.10575 | 0.10575 | 0.98887 | -0.21141 | 0.98973 | -0.19503 | 29.0516
47 | 0.0052673 | 0.001314 | -0.0052669 | -0.001314 | 4.1305e-07 | 3.7876e-08 | 0.0079112 | 0.0079113 | 0.0079113 | 0.99046 | -0.18311 | 0.99037 | -0.18476 | 2.1734
48 | -0.0060748 | -0.0015164 | 0.0060758 | 0.0015166 | 9.8041e-07 | 2.2323e-07 | 0.0091244 | 0.0091243 | 0.0091244 | 0.99046 | -0.18311 | 0.99063 | -0.17971 | 2.5067
49 | 0.0012028 | 0.00029543 | -0.0012026 | -0.00029765 | 2.2462e-07 | -2.2203e-06 | 0.0018051 | 0.0018059 | 0.0018059 | 0.99037 | -0.18476 | 0.99017 | -0.18873 | 0.49613
50 | -0.0067163 | -0.0016772 | 0.0067173 | 0.0016775 | 9.8779e-07 | 2.9878e-07 | 0.010086 | 0.010086 | 0.010086 | 0.99063 | -0.17971 | 0.99079 | -0.17661 | 2.771
51 | 0.0012026 | 0.00029765 | -0.0012024 | -0.00029975 | 2.1278e-07 | -2.1003e-06 | 0.0018059 | 0.0018067 | 0.0018067 | 0.99017 | -0.18873 | 0.98998 | -0.19247 | 0.49634
52 | -0.0071034 | -0.0017742 | 0.0071034 | 0.0017742 | 8.5131e-09 | 2.8791e-09 | 0.010666 | 0.010666 | 0.010666 | 0.99079 | -0.17661 | 0.99079 | -0.17659 | 2.9303
53 | 0.0012024 | 0.00029975 | -0.0012022 | -0.00030095 | 1.2118e-07 | -1.1949e-06 | 0.0018067 | 0.0018071 | 0.0018071 | 0.98998 | -0.19247 | 0.98987 | -0.19459 | 0.49646
54 | 0.00047796 | 0.00011943 | -0.00047796 | -0.00011954 | 1.6798e-09 | -1.105e-07 | 0.00071837 | 0.00071841 | 0.00071841 | 0.98987 | -0.19459 | 0.98987 | -0.19466 | 0.19736
55 | 0.00022504 | 5.6148e-05 | -0.00022504 | -5.64e-05 | 8.4178e-10 | -2.5167e-07 | 0.0003382 | 0.00033829 | 0.00033829 | 0.98987 | -0.19466 | 0.98986 | -0.19474 | 0.092937
56 | 0.0012055 | 0.00030211 | -0.0012055 | -0.00030213 | 3.0106e-09 | -2.8192e-08 | 0.0018315 | 0.0018315 | 0.0018315 | 0.97942 | -0.39697 | 0.97942 | -0.39702 | 0.50317
57 | -0.001836 | -0.00046012 | 0.0018361 | 0.00045972 | 1.0978e-07 | -4.0332e-07 | 0.0027894 | 0.0027892 | 0.0027894 | 0.97942 | -0.39697 | 0.97949 | -0.39572 | 0.76632
58 | -0.0031364 | -0.0007827 | 0.0031365 | 0.00078265 | 6.1396e-08 | -5.1521e-08 | 0.0047636 | 0.0047636 | 0.0047636 | 0.97949 | -0.39572 | 0.97951 | -0.3953 | 1.3087
59 | 0.0013003 | 0.00032298 | -0.0013002 | -0.00032417 | 1.4925e-07 | -1.1891e-06 | 0.0019744 | 0.0019748 | 0.0019748 | 0.97949 | -0.39572 | 0.97936 | -0.39814 | 0.54254
60 | -0.005481 | -0.0013693 | 0.0054826 | 0.0013695 | 1.6215e-06 | 2.5213e-07 | 0.0083248 | 0.0083245 | 0.0083248 | 0.97951 | -0.3953 | 0.97982 | -0.38908 | 2.287
61 | 0.0023445 | 0.00058663 | -0.0023441 | -0.00058738 | 3.7327e-07 | -7.4875e-07 | 0.0035612 | 0.0035616 | 0.0035616 | 0.97951 | -0.3953 | 0.97934 | -0.39865 | 0.97846
62 | 0.00083928 | 0.00020913 | -0.00083922 | -0.00021033 | 5.976e-08 | -1.1953e-06 | 0.0012748 | 0.0012752 | 0.0012752 | 0.97936 | -0.39814 | 0.97929 | -0.39964 | 0.35033
63 | 0.00046089 | 0.00011504 | -0.00046088 | -0.00011551 | 6.9174e-09 | -4.6904e-07 | 0.00070009 | 0.00070026 | 0.00070026 | 0.97936 | -0.39814 | 0.97935 | -0.39845 | 0.19238
64 | -0.0054826 | -0.0013695 | 0.0054841 | 0.0013698 | 1.4955e-06 | 2.3204e-07 | 0.0083245 | 0.0083243 | 0.0083245 | 0.97982 | -0.38908 | 0.98012 | -0.38334 | 2.287
65 | 0.0021498 | 0.00053868 | -0.0021497 | -0.00053872 | 1.5828e-08 | -3.9648e-08 | 0.0032663 | 0.0032664 | 0.0032664 | 0.97934 | -0.39865 | 0.97933 | -0.3988 | 0.89735
66 | -0.0062384 | -0.0015588 | 0.0062393 | 0.0015591 | 8.8434e-07 | 2.3449e-07 | 0.0094695 | 0.0094694 | 0.0094695 | 0.98012 | -0.38334 | 0.98027 | -0.38036 | 2.6015
67 | 0.0011412 | 0.00028595 | -0.0011412 | -0.00028601 | 5.3567e-09 | -5.6353e-08 | 0.0017339 | 0.001734 | 0.001734 | 0.97933 | -0.3988 | 0.97933 | -0.3989 | 0.47636
68 | -0.0067324 | -0.0016826 | 0.006733 | 0.0016828 | 5.9567e-07 | 1.8941e-07 | 0.010218 | 0.010218 | 0.010218 | 0.98027 | -0.38036 | 0.98036 | -0.3785 | 2.8071
69 | -0.0074384 | -0.0018596 | 0.0074403 | 0.0018603 | 1.9479e-06 | 7.3253e-07 | 0.011288 | 0.011288 | 0.011288 | 0.98036 | -0.3785 | 0.98064 | -0.37299 | 3.1012
70 | 0.11014 | 0.028252 | -0.1101 | -0.028228 | 3.722e-05 | 2.3629e-05 | 0.16446 | 0.16446 | 0.16446 | 0.9979 | -0.039612 | 0.99753 | -0.046582 | 22.5907
71 | -0.11138 | -0.028563 | 0.1114 | 0.028575 | 1.8817e-05 | 1.1948e-05 | 0.16631 | 0.16631 | 0.16631 | 0.9979 | -0.039612 | 0.99809 | -0.036129 | 22.8451
72 | 0.10922 | 0.028007 | -0.10912 | -0.027948 | 9.3666e-05 | 5.9457e-05 | 0.16315 | 0.16315 | 0.16315 | 0.99753 | -0.046582 | 0.9966 | -0.064282 | 22.4102
73 | -0.11264 | -0.028886 | 0.1127 | 0.028926 | 6.231e-05 | 3.9571e-05 | 0.16816 | 0.16816 | 0.16816 | 0.99809 | -0.036129 | 0.99869 | -0.02473 | 23.0995
74 | 0.10824 | 0.027727 | -0.10821 | -0.027704 | 3.6049e-05 | 2.288e-05 | 0.16183 | 0.16183 | 0.16183 | 0.9966 | -0.064282 | 0.99624 | -0.071158 | 22.2297
75 | -0.11501 | -0.029504 | 0.11503 | 0.029517 | 2.1089e-05 | 1.3397e-05 | 0.1716 | 0.1716 | 0.1716 | 0.99869 | -0.02473 | 0.99889 | -0.02095 | 23.5712
76 | -0.1178 | -0.030213 | 0.11789 | 0.03027 | 8.9858e-05 | 5.7102e-05 | 0.17573 | 0.17573 | 0.17573 | 0.99889 | -0.02095 | 0.99972 | -0.0052358 | 24.1392
77 | 0.0027759 | 0.00069551 | -0.0027758 | -0.00069563 | 8.2965e-08 | -1.1626e-07 | 0.0041351 | 0.0041352 | 0.0041352 | 0.99889 | -0.02095 | 0.99886 | -0.021578 | 1.136
78 | -0.11943 | -0.030654 | 0.11946 | 0.030673 | 3.0354e-05 | 1.9293e-05 | 0.17802 | 0.17802 | 0.17802 | 0.99972 | -0.0052358 | 1 | 0 | 24.4526
79 | 0.0015321 | 0.00038391 | -0.0015321 | -0.00038397 | 9.9107e-09 | -6.0065e-08 | 0.0022823 | 0.0022824 | 0.0022824 | 0.99886 | -0.021578 | 0.99885 | -0.021713 | 0.62702
80 | 0.098598 | 0.025249 | -0.098578 | -0.025237 | 2.0183e-05 | 1.2789e-05 | 0.14765 | 0.14765 | 0.14765 | 0.99496 | -0.09543 | 0.99474 | -0.099657 | 20.2817
81 | 0.16249 | 0.041432 | -0.16228 | -0.041298 | 0.0002091 | 0.00013332 | 0.24204 | 0.24204 | 0.24204 | 1 | 0 | 0.99859 | -0.026692 | 33.2477
82 | -0.15039 | -0.038152 | 0.15044 | 0.038185 | 5.0737e-05 | 3.2333e-05 | 0.22493 | 0.22493 | 0.22493 | 0.99562 | -0.083404 | 0.99599 | -0.076391 | 30.8968
83 | 0.14759 | 0.03745 | -0.1475 | -0.037392 | 9.1089e-05 | 5.8038e-05 | 0.22074 | 0.22074 | 0.22074 | 0.99562 | -0.083404 | 0.99495 | -0.096245 | 30.3219
84 | -0.15324 | -0.038887 | 0.15329 | 0.038921 | 5.2643e-05 | 3.3553e-05 | 0.22912 | 0.22912 | 0.22912 | 0.99599 | -0.076391 | 0.99636 | -0.069251 | 31.472
85 | 0.01962 | 0.0049248 | -0.019602 | -0.0049137 | 1.8518e-05 | 1.1107e-05 | 0.029346 | 0.029347 | 0.029347 | 0.99495 | -0.096245 | 0.99392 | -0.11605 | 8.0623
86 | -0.1561 | -0.039622 | 0.1563 | 0.039755 | 0.00020864 | 0.00013299 | 0.2333 | 0.2333 | 0.2333 | 0.99636 | -0.069251 | 0.99782 | -0.041509 | 32.0465
87 | 0.016801 | 0.0042117 | -0.0168 | -0.004211 | 1.3023e-06 | 7.6232e-07 | 0.025153 | 0.025153 | 0.025153 | 0.99392 | -0.11605 | 0.99384 | -0.11768 | 6.9103
88 | -0.15911 | -0.040457 | 0.15916 | 0.040493 | 5.6555e-05 | 3.6055e-05 | 0.23748 | 0.23748 | 0.23748 | 0.99782 | -0.041509 | 0.9982 | -0.034133 | 32.6202
89 | 0.09404 | 0.023886 | -0.093924 | -0.023812 | 0.00011546 | 7.3693e-05 | 0.14109 | 0.14109 | 0.14109 | 0.99261 | -0.1411 | 0.99128 | -0.16664 | 38.7603
90 | 0.013997 | 0.0035086 | -0.013996 | -0.003508 | 1.2217e-06 | 6.8576e-07 | 0.020958 | 0.020958 | 0.020958 | 0.99384 | -0.11768 | 0.99375 | -0.11951 | 5.7576
91 | -0.16069 | -0.040878 | 0.16075 | 0.040914 | 5.7648e-05 | 3.6755e-05 | 0.23976 | 0.23976 | 0.23976 | 0.9982 | -0.034133 | 0.99859 | -0.026692 | 32.9341
92 | 0.09087 | 0.023047 | -0.09079 | -0.022996 | 8.0072e-05 | 5.1098e-05 | 0.1365 | 0.1365 | 0.1365 | 0.99128 | -0.16664 | 0.99032 | -0.18499 | 37.5008
93 | 0.011194 | 0.0028057 | -0.011194 | -0.0028054 | 5.7809e-07 | 2.989e-07 | 0.016762 | 0.016762 | 0.016762 | 0.99375 | -0.11951 | 0.99369 | -0.1206 | 4.605
94 | 0.080564 | 0.020433 | -0.080507 | -0.020397 | 5.661e-05 | 3.6098e-05 | 0.12114 | 0.12114 | 0.12114 | 0.99032 | -0.18499 | 0.98956 | -0.19961 | 33.2796
95 | 0.0083926 | 0.0021034 | -0.0083923 | -0.0021033 | 3.2503e-07 | 1.3693e-07 | 0.012568 | 0.012568 | 0.012568 | 0.99369 | -0.1206 | 0.99365 | -0.12141 | 3.4527
96 | -0.014219 | -0.0035662 | 0.014222 | 0.0035677 | 2.685e-06 | 1.5154e-06 | 0.021335 | 0.021334 | 0.021335 | 0.9918 | -0.15576 | 0.992 | -0.1518 | 5.8611
97 | 0.014219 | 0.0035662 | -0.014213 | -0.0035624 | 6.7136e-06 | 3.7894e-06 | 0.021335 | 0.021335 | 0.021335 | 0.9918 | -0.15576 | 0.99128 | -0.16567 | 5.8612
98 | -0.015762 | -0.0039535 | 0.015763 | 0.0039545 | 1.5906e-06 | 9.2002e-07 | 0.023644 | 0.023644 | 0.023644 | 0.992 | -0.1518 | 0.99211 | -0.14968 | 6.4955
99 | 0.01235 | 0.0030957 | -0.012349 | -0.0030949 | 1.3321e-06 | 7.1932e-07 | 0.018539 | 0.018539 | 0.018539 | 0.99128 | -0.16567 | 0.99117 | -0.16793 | 5.0932
100 | 0.0026082 | 0.00065361 | -0.0026082 | -0.00065367 | 3.332e-08 | -5.4448e-08 | 0.0039016 | 0.0039016 | 0.0039016 | 0.99474 | -0.099657 | 0.99472 | -0.099925 | 1.0719
101 | 0.09597 | 0.024583 | -0.095863 | -0.024515 | 0.00010675 | 6.7605e-05 | 0.14375 | 0.14375 | 0.14375 | 0.99474 | -0.099657 | 0.99353 | -0.12264 | 19.7458
102 | 0.0026093 | 0.00065389 | -0.0026092 | -0.00065394 | 3.0043e-08 | -4.8707e-08 | 0.0039079 | 0.0039079 | 0.0039079 | 0.99353 | -0.12264 | 0.99352 | -0.12288 | 1.0736
103 | 0.093254 | 0.023861 | -0.093243 | -0.023855 | 1.0776e-05 | 6.8208e-06 | 0.13984 | 0.13984 | 0.13984 | 0.99353 | -0.12264 | 0.9934 | -0.12503 | 19.209
104 | 0.093243 | 0.023855 | -0.093175 | -0.023811 | 6.8437e-05 | 4.3316e-05 | 0.13984 | 0.13984 | 0.13984 | 0.9934 | -0.12503 | 0.99261 | -0.1402 | 19.2091
105 | 0.076771 | 0.01946 | -0.076526 | -0.019304 | 0.00024497 | 0.00015615 | 0.11552 | 0.11552 | 0.11552 | 0.98956 | -0.19961 | 0.98612 | -0.26624 | 31.7362
106 | 0.063825 | 0.016121 | -0.063744 | -0.016069 | 8.1682e-05 | 5.1978e-05 | 0.096355 | 0.096355 | 0.096355 | 0.98612 | -0.26624 | 0.98474 | -0.29298 | 26.4711
107 | 0.063744 | 0.016069 | -0.063609 | -0.015983 | 0.00013493 | 8.5861e-05 | 0.096355 | 0.096355 | 0.096355 | 0.98474 | -0.29298 | 0.98246 | -0.33732 | 26.4712
108 | 0.043824 | 0.011024 | -0.0438 | -0.011009 | 2.4368e-05 | 1.5409e-05 | 0.06639 | 0.06639 | 0.06639 | 0.98246 | -0.33732 | 0.98187 | -0.34897 | 18.239
109 | 0.019784 | 0.0049586 | -0.019778 | -0.0049547 | 6.5795e-06 | 3.9635e-06 | 0.029965 | 0.029965 | 0.029965 | 0.98246 | -0.33732 | 0.98211 | -0.3443 | 8.2322
110 | 0.0085917 | 0.0021506 | -0.0085825 | -0.0021466 | 9.1259e-06 | 4.0276e-06 | 0.013021 | 0.013021 | 0.013021 | 0.98178 | -0.35065 | 0.98064 | -0.37299 | 3.5773
111 | -0.0085917 | -0.0021506 | 0.0085941 | 0.0021517 | 2.4846e-06 | 1.0958e-06 | 0.013021 | 0.013021 | 0.013021 | 0.98178 | -0.35065 | 0.98209 | -0.34458 | 3.5771
112 | -0.013673 | -0.0034247 | 0.013673 | 0.0034248 | 1.7919e-07 | 1.0059e-07 | 0.020716 | 0.020716 | 0.020716 | 0.98209 | -0.34458 | 0.98211 | -0.3443 | 5.6913
113 | 0.035429 | 0.0089111 | -0.035388 | -0.0088853 | 4.1008e-05 | 2.5766e-05 | 0.053704 | 0.053704 | 0.053704 | 0.98187 | -0.34897 | 0.98063 | -0.37323 | 14.7539
114 | 0.032725 | 0.0082178 | -0.032696 | -0.0081998 | 2.8726e-05 | 1.7993e-05 | 0.049663 | 0.049663 | 0.049663 | 0.98063 | -0.37323 | 0.97969 | -0.39164 | 13.6437
115 | 0.010795 | 0.0027058 | -0.010794 | -0.0027052 | 1.1693e-06 | 6.0232e-07 | 0.016397 | 0.016397 | 0.016397 | 0.97969 | -0.39164 | 0.97957 | -0.39392 | 4.5046
116 | -0.070246 | -0.017983 | 0.070259 | 0.017991 | 1.2341e-05 | 7.8602e-06 | 0.10575 | 0.10575 | 0.10575 | 0.98973 | -0.19503 | 0.98992 | -0.1914 | 29.0516
117 | 0.0055913 | 0.0014013 | -0.0055913 | -0.0014013 | 2.8347e-08 | 4.1763e-09 | 0.0083732 | 0.0083732 | 0.0083732 | 0.99365 | -0.12141 | 0.99364 | -0.12152 | 2.3003
118 | 0.075509 | 0.019364 | -0.075464 | -0.019336 | 4.4707e-05 | 2.8134e-05 | 0.11341 | 0.11341 | 0.11341 | 0.99211 | -0.14968 | 0.99147 | -0.1619 | 15.5782
119 | -0.091272 | -0.023318 | 0.091314 | 0.023345 | 4.1853e-05 | 2.6479e-05 | 0.13705 | 0.13705 | 0.13705 | 0.99211 | -0.14968 | 0.99261 | -0.1402 | 18.8259
120 | 0.073602 | 0.018869 | -0.073542 | -0.018831 | 5.9816e-05 | 3.8114e-05 | 0.11061 | 0.11061 | 0.11061 | 0.99147 | -0.1619 | 0.99059 | -0.17868 | 30.3886
121 | 0.071923 | 0.018425 | -0.071878 | -0.018397 | 4.4324e-05 | 2.8237e-05 | 0.10818 | 0.10818 | 0.10818 | 0.99059 | -0.17868 | 0.98992 | -0.1914 | 29.7203

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28513 | 0.072489

## res_load
| p_mw | q_mvar
0 | 0.0082458 | 0.0020666
1 | 0.0057211 | 0.0014338
2 | 0.015365 | 0.0038508
3 | 0.010233 | 0.0025645
4 | 0.012029 | 0.0030147
5 | 0.0045643 | 0.0011439
6 | 0.0053758 | 0.0013473
7 | 0.0013059 | 0.0003273
8 | 0.0055908 | 0.0014012
9 | 0.0050979 | 0.0012776
10 | 0.00078122 | 0.00019579
11 | 0.0069625 | 0.001745
12 | 0.0034693 | 0.00086949
13 | 0.0016481 | 0.00041305
14 | 0.002839 | 0.00071152
15 | 0.0014629 | 0.00036664
16 | 0.001036 | 0.00025965
17 | 0.00053577 | 0.00013428
18 | 0.00095741 | 0.00023995
19 | 0.0022969 | 0.00057565
20 | 0.012877 | 0.0032272
21 | 0.0051084 | 0.0012803
22 | 0.00053567 | 0.00013425
23 | 0.0013052 | 0.00032712
24 | 0.0039003 | 0.00097752
25 | 0.00053589 | 0.00013431
26 | 0.00080751 | 0.00020238
27 | 0.0040641 | 0.0010186
28 | 0.00064047 | 0.00016052
29 | 0.00038614 | 9.6776e-05
30 | 0.00017362 | 4.3514e-05
31 | 0.00072427 | 0.00018152
32 | 0.00025292 | 6.3389e-05
33 | 0.0015744 | 0.00039458
34 | 0.00063048 | 0.00015801
35 | 0.0012055 | 0.00030213
36 | 0.00019432 | 4.87e-05
37 | 0.00083922 | 0.00021033
38 | 0.00046088 | 0.00011551
39 | 0.00075436 | 0.00018906
40 | 0.0010086 | 0.00025277
41 | 0.00049312 | 0.00012359
42 | 0.0011412 | 0.00028601
43 | 0.00070535 | 0.00017678
44 | 0.0012423 | 0.00031135
45 | 0.00088078 | 0.00022075
46 | 0.0012423 | 0.00031135
47 | 0.00088005 | 0.00022056
48 | 0.0023048 | 0.00057765
49 | 0.00088116 | 0.00022084
50 | 0.001533 | 0.0003842
51 | 0.0012438 | 0.00031172
52 | 0.0016452 | 0.00041233
53 | 0.0015321 | 0.00038397
54 | 0.0015321 | 0.00038397
55 | 0.0028008 | 0.00070195
56 | 0.0028024 | 0.00070236
57 | 0.0028008 | 0.00070195
58 | 0.002801 | 0.00070199
59 | 0.0028008 | 0.00070195
60 | 0.0030089 | 0.0007541
61 | 0.0028023 | 0.00070233
62 | 0.001533 | 0.0003842
63 | 0.0030543 | 0.00076547
64 | 0.0028019 | 0.00070222
65 | 0.0015321 | 0.00038397
66 | 0.010226 | 0.0025629
67 | 0.002801 | 0.00070199
68 | 0.0015395 | 0.00038583
69 | 0.0018623 | 0.00046675
70 | 0.0026082 | 0.00065367
71 | 0.0026092 | 0.00065394
72 | 0.0037361 | 0.00093636
73 | 0.012701 | 0.0031831
74 | 0.0011422 | 0.00028626
75 | 0.0050791 | 0.0012729
76 | 0.0083707 | 0.0020979
77 | 0.0061044 | 0.0015299
78 | 0.0026634 | 0.00066752
79 | 0.010794 | 0.0027052
80 | 0.00022504 | 5.64e-05
81 | 0.002801 | 0.00070199
82 | 0.0055913 | 0.0014013
83 | 0.012349 | 0.0030949
84 | 0.0018622 | 0.00046671
85 | 0.0018608 | 0.00046637
86 | 0.0016195 | 0.00040588
87 | 0.0016195 | 0.00040588

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1