## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_138-22_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_138-22_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_138-22_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_138-22_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_138-22_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_138-22_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_138-22_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_138-22_0_5_node_72 | 0.4 | n |  | TRUE
8 | bus_LV_138-22_0_5_node_70 | 0.4 | n |  | TRUE
9 | bus_LV_138-22_0_5_node_125 | 0.4 | n |  | TRUE
10 | bus_LV_138-22_0_5_node_69 | 0.4 | n |  | TRUE
11 | bus_LV_138-22_0_5_node_126 | 0.4 | n |  | TRUE
12 | bus_LV_138-22_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_138-22_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_138-22_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_138-22_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_138-22_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_138-22_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_138-22_0_5_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_138-22_0_5_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_138-22_0_5_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_138-22_0_5_node_62 | 0.4 | n |  | TRUE
22 | bus_LV_138-22_0_5_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_138-22_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_138-22_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_138-22_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_138-22_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_138-22_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_138-22_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_138-22_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_138-22_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_138-22_0_5_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_138-22_0_5_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_138-22_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_138-22_0_5_node_120 | 0.4 | n |  | TRUE
35 | bus_LV_138-22_0_5_node_74 | 0.4 | n |  | TRUE
36 | bus_LV_138-22_0_5_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_138-22_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_138-22_0_5_node_118 | 0.4 | n |  | TRUE
39 | bus_LV_138-22_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_138-22_0_5_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_138-22_0_5_node_127 | 0.4 | n |  | TRUE
42 | bus_LV_138-22_0_5_node_128 | 0.4 | n |  | TRUE
43 | bus_LV_138-22_0_5_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_138-22_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_138-22_0_5_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_138-22_0_5_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_138-22_0_5_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_138-22_0_5_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_138-22_0_5_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_138-22_0_5_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_138-22_0_5_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_138-22_0_5_node_96 | 0.4 | n |  | TRUE
53 | bus_LV_138-22_0_5_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_138-22_0_5_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_138-22_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_138-22_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_138-22_0_5_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_138-22_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_138-22_0_5_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_138-22_0_5_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_138-22_0_5_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_138-22_0_5_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_138-22_0_5_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_138-22_0_5_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_138-22_0_5_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_138-22_0_5_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_138-22_0_5_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_138-22_0_5_node_90 | 0.4 | n |  | TRUE
69 | bus_LV_138-22_0_5_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_138-22_0_5_node_91 | 0.4 | n |  | TRUE
71 | bus_LV_138-22_0_5_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_138-22_0_5_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_138-22_0_5_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_138-22_0_5_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_138-22_0_5_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_138-22_0_5_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_138-22_0_5_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_138-22_0_5_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_138-22_0_5_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_138-22_0_5_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_138-22_0_5_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_138-22_0_5_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_138-22_0_5_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_138-22_0_5_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_138-22_0_5_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_138-22_0_5_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_138-22_0_5_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_138-22_0_5_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_138-22_0_5_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_138-22_0_5_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_138-22_0_5_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_138-22_0_5_node_112 | 0.4 | n |  | TRUE
93 | bus_LV_138-22_0_5_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_138-22_0_5_node_100 | 0.4 | n |  | TRUE
95 | bus_LV_138-22_0_5_node_108 | 0.4 | n |  | TRUE
96 | bus_LV_138-22_0_5_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_138-22_0_5_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_138-22_0_5_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_138-22_0_5_node_106 | 0.4 | n |  | TRUE
100 | bus_LV_138-22_0_5_node_109 | 0.4 | n |  | TRUE
101 | bus_LV_138-22_0_5_node_103 | 0.4 | n |  | TRUE
102 | bus_LV_138-22_0_5_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_138-22_0_5_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_138-22_0_5_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_138-22_0_5_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_138-22_0_5_node_114 | 0.4 | n |  | TRUE
107 | bus_LV_138-22_0_5_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_138-22_0_5_node_122 | 0.4 | n |  | TRUE
109 | bus_LV_138-22_0_5_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_138-22_0_5_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_138-22_0_5_node_124 | 0.4 | n |  | TRUE
112 | bus_LV_138-22_0_5_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_138-22_0_5_node_92 | 0.4 | n |  | TRUE
114 | bus_LV_138-22_0_5_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_138-22_0_5_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_138-22_0_5_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_138-22_0_5_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_138-22_0_5_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_138-22_0_5_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_138-22_0_5_node_131 | 0.4 | n |  | TRUE
121 | bus_LV_138-22_0_5_node_130 | 0.4 | n |  | TRUE
122 | bus_LV_138-22_0_5_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_138-22_0_5_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_138-22_0_5_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_138-22_0_5_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_138-22_0_5_node_129 | 0.4 | n |  | TRUE
127 | bus_LV_138-22_0_5_node_132 | 0.4 | n |  | TRUE
128 | bus_MV_222_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_138-22_0_5_load_0 | 0 | 0.015532 | 0.0038926 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_138-22_0_5_load_1 | 1 | 0.0045912 | 0.0011507 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_138-22_0_5_load_2 | 2 | 0.0045926 | 0.001151 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_138-22_0_5_load_3 | 3 | 0.0045912 | 0.0011507 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_138-22_0_5_load_4 | 4 | 0.0045913 | 0.0011507 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_138-22_0_5_load_5 | 5 | 0.0128 | 0.003208 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_138-22_0_5_load_72 | 7 | 0.0072045 | 0.0018056 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_138-22_0_5_load_70 | 8 | 0.001749 | 0.00043834 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_138-22_0_5_load_125 | 9 | 0.001746 | 0.0004376 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_138-22_0_5_load_69 | 10 | 0.0035559 | 0.00089119 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_138-22_0_5_load_126 | 11 | 0.0017467 | 0.00043775 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_138-22_0_5_load_7 | 12 | 0.0034426 | 0.00086279 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_138-22_0_5_load_8 | 13 | 0.0015593 | 0.0003908 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_138-22_0_5_load_10 | 15 | 0.0016416 | 0.00041141 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_138-22_0_5_load_11 | 16 | 0.0027291 | 0.00068397 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_138-22_0_5_load_12 | 17 | 0.0066272 | 0.0016609 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_138-22_0_5_load_13 | 18 | 0.0017591 | 0.00044088 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_138-22_0_5_load_61 | 19 | 0.0066279 | 0.0016611 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_138-22_0_5_load_60 | 20 | 0.0020306 | 0.00050891 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_138-22_0_5_load_62 | 21 | 0.0066289 | 0.0016614 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_138-22_0_5_load_43 | 22 | 0.0028305 | 0.00070938 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_138-22_0_5_load_14 | 23 | 0.0060093 | 0.0015061 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_138-22_0_5_load_15 | 24 | 0.0042608 | 0.0010679 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_138-22_0_5_load_16 | 25 | 0.0020287 | 0.00050843 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_138-22_0_5_load_17 | 26 | 0.0018446 | 0.00046229 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_138-22_0_5_load_19 | 28 | 0.0060106 | 0.0015064 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_138-22_0_5_load_21 | 30 | 0.0034514 | 0.00086499 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_138-22_0_5_load_73 | 31 | 0.0036543 | 0.00091586 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_138-22_0_5_load_24 | 32 | 0.0055985 | 0.0014031 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_138-22_0_5_load_22 | 33 | 0.0058784 | 0.0014733 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_138-22_0_5_load_120 | 34 | 0.0020296 | 0.00050867 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_138-22_0_5_load_74 | 35 | 0.0034583 | 0.00086674 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_138-22_0_5_load_26 | 36 | 0.0058529 | 0.0014669 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_138-22_0_5_load_118 | 38 | 0.0020296 | 0.00050867 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_138-22_0_5_load_27 | 40 | 0.0039191 | 0.00098223 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_138-22_0_5_load_127 | 41 | 0.0055996 | 0.0014034 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_138-22_0_5_load_128 | 42 | 0.0058522 | 0.0014667 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_138-22_0_5_load_28 | 43 | 0.0038041 | 0.0009534 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_138-22_0_5_load_29 | 44 | 0.0034357 | 0.00086107 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_138-22_0_5_load_31 | 45 | 0.0031819 | 0.00079747 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_138-22_0_5_load_32 | 46 | 0.0030576 | 0.00076632 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_138-22_0_5_load_33 | 47 | 0.001159 | 0.00029047 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_138-22_0_5_load_52 | 50 | 0.0041123 | 0.0010306 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_138-22_0_5_load_51 | 51 | 0.004113 | 0.0010308 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_138-22_0_5_load_96 | 52 | 0.0045284 | 0.0011349 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_138-22_0_5_load_48 | 53 | 0.0025383 | 0.00063615 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_138-22_0_5_load_36 | 54 | 0.0027291 | 0.00068397 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_138-22_0_5_load_37 | 55 | 0.0027285 | 0.00068382 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_138-22_0_5_load_38 | 56 | 0.0022363 | 0.00056046 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_138-22_0_5_load_39 | 57 | 0.0018078 | 0.00045309 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_138-22_0_5_load_40 | 58 | 0.0035214 | 0.00088255 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_138-22_0_5_load_41 | 59 | 0.0026097 | 0.00065404 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_138-22_0_5_load_42 | 60 | 0.0022377 | 0.00056082 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_138-22_0_5_load_45 | 62 | 0.0022636 | 0.00056732 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_138-22_0_5_load_46 | 63 | 0.0021147 | 0.00053 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_138-22_0_5_load_49 | 64 | 0.0021585 | 0.00054098 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_138-22_0_5_load_47 | 65 | 0.002389 | 0.00059874 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_138-22_0_5_load_50 | 66 | 0.0042211 | 0.0010579 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_138-22_0_5_load_65 | 67 | 0.0022105 | 0.00055401 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_138-22_0_5_load_90 | 68 | 0.0023295 | 0.00058383 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_138-22_0_5_load_63 | 69 | 0.0047517 | 0.0011909 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_138-22_0_5_load_91 | 70 | 0.0018369 | 0.00046036 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_138-22_0_5_load_95 | 71 | 0.0084915 | 0.0021282 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_138-22_0_5_load_53 | 72 | 0.0041562 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_138-22_0_5_load_54 | 73 | 0.0016152 | 0.0004048 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_138-22_0_5_load_55 | 74 | 0.0020285 | 0.00050838 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_138-22_0_5_load_56 | 75 | 0.0016156 | 0.00040491 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_138-22_0_5_load_57 | 76 | 0.002176 | 0.00054536 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_138-22_0_5_load_58 | 77 | 0.0041532 | 0.0010409 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_138-22_0_5_load_59 | 78 | 0.0013839 | 0.00034684 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_138-22_0_5_load_66 | 79 | 0.0035805 | 0.00089735 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_138-22_0_5_load_64 | 80 | 0.0015784 | 0.00039558 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_138-22_0_5_load_67 | 81 | 0.0035805 | 0.00089736 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_138-22_0_5_load_75 | 83 | 0.0024708 | 0.00061924 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_138-22_0_5_load_76 | 84 | 0.0025283 | 0.00063366 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_138-22_0_5_load_78 | 85 | 0.0026173 | 0.00065595 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_138-22_0_5_load_77 | 86 | 0.0024386 | 0.00061117 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_138-22_0_5_load_80 | 88 | 0.0040844 | 0.0010236 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_138-22_0_5_load_81 | 89 | 0.0040831 | 0.0010233 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_138-22_0_5_load_82 | 90 | 0.001793 | 0.00044937 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_138-22_0_5_load_112 | 92 | 0.0040844 | 0.0010236 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_138-22_0_5_load_100 | 94 | 0.0024595 | 0.00061641 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_138-22_0_5_load_108 | 95 | 0.0040851 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_138-22_0_5_load_84 | 96 | 0.002596 | 0.00065063 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_138-22_0_5_load_85 | 97 | 0.0017493 | 0.00043842 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_138-22_0_5_load_86 | 98 | 0.0020527 | 0.00051446 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_138-22_0_5_load_106 | 99 | 0.0082025 | 0.0020557 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_138-22_0_5_load_109 | 100 | 0.0066306 | 0.0016618 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_138-22_0_5_load_101 | 104 | 0.0085286 | 0.0021375 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_138-22_0_5_load_115 | 105 | 0.0020824 | 0.0005219 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_138-22_0_5_load_114 | 106 | 0.0017698 | 0.00044355 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_138-22_0_5_load_113 | 107 | 0.0022441 | 0.00056244 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_138-22_0_5_load_122 | 108 | 0.0021593 | 0.00054118 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_138-22_0_5_load_88 | 109 | 0.00096607 | 0.00024212 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_138-22_0_5_load_123 | 112 | 0.00069424 | 0.00017399 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_138-22_0_5_load_92 | 113 | 0.0022985 | 0.00057607 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_138-22_0_5_load_93 | 114 | 0.0022107 | 0.00055404 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_138-22_0_5_load_97 | 115 | 0.0018051 | 0.00045241 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_138-22_0_5_load_98 | 116 | 0.0025237 | 0.00063251 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_138-22_0_5_load_94 | 117 | 0.011978 | 0.0030021 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_138-22_0_5_load_99 | 118 | 0.0031424 | 0.00078757 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_138-22_0_5_load_110 | 119 | 0.0040824 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_138-22_0_5_load_131 | 120 | 0.0040851 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_138-22_0_5_load_130 | 121 | 0.004085 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_138-22_0_5_load_116 | 122 | 0.0020279 | 0.00050825 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_138-22_0_5_load_117 | 123 | 0.0056781 | 0.0014231 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_138-22_0_5_load_119 | 124 | 0.0017445 | 0.00043722 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_138-22_0_5_load_121 | 125 | 0.0056782 | 0.0014231 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_138-22_0_5_load_129 | 126 | 0.016806 | 0.004212 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_138-22_0_5_load_132 | 127 | 0.0018766 | 0.00047032 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_138-22_0_5_line_0 |  | 0 | 1 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_138-22_0_5_line_1 |  | 0 | 2 | 0.012343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_138-22_0_5_line_2 |  | 1 | 3 | 0.0027013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_138-22_0_5_line_3 |  | 2 | 4 | 0.0067796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_138-22_0_5_line_4 |  | 3 | 5 | 0.025756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_138-22_0_5_line_5 |  | 4 | 6 | 0.038026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_138-22_0_5_line_6 |  | 5 | 7 | 0.0084017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_138-22_0_5_line_7 |  | 6 | 8 | 0.0068426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_138-22_0_5_line_8 |  | 6 | 9 | 0.0025037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_138-22_0_5_line_9 |  | 8 | 10 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_138-22_0_5_line_10 |  | 9 | 11 | 0.0083432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_138-22_0_5_line_11 |  | 10 | 82 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_138-22_0_5_line_12 |  | 11 | 125 | 0.00031444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_138-22_0_5_line_13 |  | 12 | 13 | 0.0052226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_138-22_0_5_line_14 |  | 12 | 14 | 0.012856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_138-22_0_5_line_15 |  | 13 | 15 | 0.019898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_138-22_0_5_line_16 |  | 14 | 16 | 0.015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_138-22_0_5_line_17 |  | 15 | 17 | 0.0048432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_138-22_0_5_line_18 |  | 16 | 18 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_138-22_0_5_line_19 |  | 17 | 19 | 0.0073585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_138-22_0_5_line_20 |  | 18 | 20 | 0.013569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_138-22_0_5_line_21 |  | 19 | 21 | 0.014945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_138-22_0_5_line_22 |  | 20 | 22 | 0.017192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_138-22_0_5_line_23 |  | 21 | 82 | 0.022253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_138-22_0_5_line_24 |  | 22 | 59 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_138-22_0_5_line_25 |  | 23 | 24 | 0.013156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_138-22_0_5_line_26 |  | 23 | 25 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_138-22_0_5_line_27 |  | 24 | 26 | 0.012012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_138-22_0_5_line_28 |  | 25 | 27 | 0.02029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_138-22_0_5_line_29 |  | 26 | 28 | 0.0025709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_138-22_0_5_line_30 |  | 27 | 29 | 0.012418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_138-22_0_5_line_31 |  | 27 | 30 | 0.012993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_138-22_0_5_line_32 |  | 28 | 31 | 0.014491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_138-22_0_5_line_33 |  | 29 | 32 | 0.012874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_138-22_0_5_line_34 |  | 29 | 33 | 0.035746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_138-22_0_5_line_35 |  | 30 | 34 | 0.019254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_138-22_0_5_line_36 |  | 31 | 35 | 0.010255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_138-22_0_5_line_37 |  | 32 | 36 | 0.021079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_138-22_0_5_line_38 |  | 33 | 37 | 0.012882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_138-22_0_5_line_39 |  | 34 | 38 | 0.0027138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_138-22_0_5_line_40 |  | 35 | 83 | 0.017578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_138-22_0_5_line_41 |  | 36 | 41 | 0.03051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_138-22_0_5_line_42 |  | 37 | 39 | 0.026526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_138-22_0_5_line_43 |  | 38 | 122 | 0.0088239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_138-22_0_5_line_44 |  | 39 | 40 | 0.0025058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_138-22_0_5_line_45 |  | 41 | 42 | 0.024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_138-22_0_5_line_46 |  | 42 | 126 | 0.023748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_138-22_0_5_line_47 |  | 43 | 44 | 0.030411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_138-22_0_5_line_48 |  | 44 | 45 | 0.030586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_138-22_0_5_line_49 |  | 45 | 46 | 0.033427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_138-22_0_5_line_50 |  | 46 | 47 | 0.030276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_138-22_0_5_line_51 |  | 47 | 48 | 0.045451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_138-22_0_5_line_52 |  | 48 | 49 | 0.02555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_138-22_0_5_line_53 |  | 49 | 50 | 0.023295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_138-22_0_5_line_54 |  | 49 | 51 | 0.033696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_138-22_0_5_line_55 |  | 50 | 52 | 0.033387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_138-22_0_5_line_56 |  | 51 | 53 | 0.0041223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_138-22_0_5_line_57 |  | 52 | 71 | 0.0082057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_138-22_0_5_line_58 |  | 53 | 62 | 0.01752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_138-22_0_5_line_59 |  | 54 | 55 | 0.0092153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_138-22_0_5_line_60 |  | 54 | 56 | 0.014415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_138-22_0_5_line_61 |  | 55 | 57 | 0.014397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_138-22_0_5_line_62 |  | 56 | 58 | 0.0095564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_138-22_0_5_line_63 |  | 57 | 59 | 0.009795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_138-22_0_5_line_64 |  | 58 | 60 | 0.015535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_138-22_0_5_line_65 |  | 60 | 61 | 0.023124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_138-22_0_5_line_66 |  | 61 | 62 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_138-22_0_5_line_67 |  | 63 | 64 | 0.0069817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_138-22_0_5_line_68 |  | 64 | 67 | 0.010051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_138-22_0_5_line_69 |  | 65 | 66 | 0.00018738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_138-22_0_5_line_70 |  | 66 | 68 | 0.020804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_138-22_0_5_line_71 |  | 67 | 69 | 0.0092369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_138-22_0_5_line_72 |  | 68 | 70 | 0.019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_138-22_0_5_line_73 |  | 69 | 80 | 0.0060604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_138-22_0_5_line_74 |  | 70 | 113 | 0.0023667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_138-22_0_5_line_75 |  | 71 | 117 | 0.025596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_138-22_0_5_line_76 |  | 72 | 73 | 0.0026618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_138-22_0_5_line_77 |  | 72 | 74 | 0.0042401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_138-22_0_5_line_78 |  | 73 | 75 | 0.0057889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_138-22_0_5_line_79 |  | 74 | 76 | 0.018785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_138-22_0_5_line_80 |  | 75 | 77 | 0.027073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_138-22_0_5_line_81 |  | 76 | 78 | 0.0036475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_138-22_0_5_line_82 |  | 77 | 79 | 0.016754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_138-22_0_5_line_83 |  | 78 | 80 | 0.0050295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_138-22_0_5_line_84 |  | 79 | 81 | 0.014723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_138-22_0_5_line_85 |  | 81 | 82 | 0.014029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_138-22_0_5_line_86 |  | 83 | 84 | 0.0173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_138-22_0_5_line_87 |  | 84 | 85 | 0.0064322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_138-22_0_5_line_88 |  | 85 | 86 | 0.010785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_138-22_0_5_line_89 |  | 86 | 87 | 0.017164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_138-22_0_5_line_90 |  | 87 | 88 | 0.023373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_138-22_0_5_line_91 |  | 87 | 89 | 0.010298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_138-22_0_5_line_92 |  | 88 | 90 | 0.021322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_138-22_0_5_line_93 |  | 89 | 91 | 0.023455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_138-22_0_5_line_94 |  | 90 | 92 | 0.001931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_138-22_0_5_line_95 |  | 91 | 93 | 0.037758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_138-22_0_5_line_96 |  | 92 | 94 | 0.015896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_138-22_0_5_line_97 |  | 93 | 95 | 0.059065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_138-22_0_5_line_98 |  | 94 | 118 | 0.005508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_138-22_0_5_line_99 |  | 95 | 103 | 0.020555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_138-22_0_5_line_100 |  | 96 | 97 | 0.027409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_138-22_0_5_line_101 |  | 97 | 98 | 0.013502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_138-22_0_5_line_102 |  | 98 | 102 | 0.032954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_138-22_0_5_line_103 |  | 99 | 100 | 0.058413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_138-22_0_5_line_104 |  | 99 | 101 | 0.031214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_138-22_0_5_line_105 |  | 101 | 103 | 0.019521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_138-22_0_5_line_106 |  | 101 | 104 | 0.012808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_138-22_0_5_line_107 |  | 102 | 105 | 0.0099056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_138-22_0_5_line_108 |  | 102 | 106 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_138-22_0_5_line_109 |  | 103 | 119 | 0.0032696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_138-22_0_5_line_110 |  | 104 | 107 | 0.053915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_138-22_0_5_line_111 |  | 105 | 108 | 0.037078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_138-22_0_5_line_112 |  | 106 | 107 | 0.0012422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_138-22_0_5_line_113 |  | 108 | 112 | 0.022381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_138-22_0_5_line_114 |  | 109 | 110 | 0.060915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_138-22_0_5_line_115 |  | 110 | 111 | 0.003394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_138-22_0_5_line_116 |  | 111 | 112 | 0.023229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_138-22_0_5_line_117 |  | 113 | 114 | 0.0082524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_138-22_0_5_line_118 |  | 114 | 115 | 0.0078753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_138-22_0_5_line_119 |  | 115 | 116 | 0.0020759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_138-22_0_5_line_120 |  | 116 | 118 | 0.0025002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_138-22_0_5_line_121 |  | 119 | 120 | 0.029172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_138-22_0_5_line_122 |  | 120 | 121 | 0.022396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_138-22_0_5_line_123 |  | 122 | 123 | 0.011279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_138-22_0_5_line_124 |  | 123 | 124 | 0.013323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_138-22_0_5_line_125 |  | 124 | 125 | 0.0077151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_138-22_0_5_line_126 |  | 126 | 127 | 0.19507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_138-22_0_5_trafo_57 | 0.63 MVA 20/0.4 kV | 128 | 76 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2695628.3027 | 1228987.4774 | 2695614.0213 | 1228992.7038
1 | 2695628.3027 | 1228987.4774 | 2695629.278 | 1228987.1205 | 2695640.1099 | 1228983.8866
2 | 2695614.0213 | 1228992.7038 | 2695612.3104 | 1228993.33 | 2695611.6056 | 1228993.856
3 | 2695640.1099 | 1228983.8866 | 2695646.6061 | 1228981.9471
4 | 2695592.6184 | 1229011.1041 | 2695601.9717 | 1229001.0471 | 2695611.6056 | 1228993.856
5 | 2695683.2779 | 1228971.9334 | 2695665.3235 | 1228976.359 | 2695646.6061 | 1228981.9471
6 | 2695592.6184 | 1229011.1041 | 2695592.6184 | 1229011.1041 | 2695590.2592 | 1229019.1677
7 | 2695683.2779 | 1228971.9334 | 2695682.6447 | 1228978.7467
8 | 2695683.2779 | 1228971.9334 | 2695683.7506 | 1228969.4747
9 | 2695680.8739 | 1228997.8 | 2695682.6447 | 1228978.7467
10 | 2695685.326 | 1228961.2816 | 2695683.7506 | 1228969.4747
11 | 2695679.392 | 1229013.7455 | 2695680.8739 | 1228997.8
12 | 2695685.3853 | 1228960.9728 | 2695685.326 | 1228961.2816
13 | 2695714.7791 | 1229076.6294 | 2695712.505 | 1229071.928
14 | 2695720.3772 | 1229088.203 | 2695714.7791 | 1229076.6294
15 | 2695712.505 | 1229071.928 | 2695711.6285 | 1229070.1158 | 2695703.6419 | 1229065.4062 | 2695698.1675 | 1229058.7564
16 | 2695720.3772 | 1229088.203 | 2695732.0936 | 1229077.6261
17 | 2695695.0894 | 1229055.0172 | 2695698.1675 | 1229058.7564
18 | 2695732.0936 | 1229077.6261 | 2695739.5353 | 1229070.9083
19 | 2695695.0894 | 1229055.0172 | 2695690.9329 | 1229049.9684 | 2695690.6843 | 1229049.1881
20 | 2695748.3563 | 1229060.6214 | 2695740.9614 | 1229069.6209 | 2695739.5353 | 1229070.9083
21 | 2695690.6843 | 1229049.1881 | 2695686.1475 | 1229034.9485
22 | 2695748.3563 | 1229060.6214 | 2695759.2708 | 1229047.3384
23 | 2695679.392 | 1229013.7455 | 2695686.1475 | 1229034.9485
24 | 2695771.0527 | 1229033.9796 | 2695768.8246 | 1229035.7116 | 2695759.2708 | 1229047.3384
25 | 2695736.0046 | 1228875.374 | 2695748.1504 | 1228870.3177
26 | 2695736.0046 | 1228875.374 | 2695722.2048 | 1228881.1188
27 | 2695748.1504 | 1228870.3177 | 2695759.2402 | 1228865.701
28 | 2695702.874 | 1228887.1876 | 2695717.2986 | 1228883.1613 | 2695722.2048 | 1228881.1188
29 | 2695759.2402 | 1228865.701 | 2695761.6137 | 1228864.7129
30 | 2695690.4441 | 1228886.3982 | 2695702.874 | 1228887.1876
31 | 2695702.874 | 1228887.1876 | 2695697.8163 | 1228899.1557
32 | 2695773.5659 | 1228856.6018 | 2695763.4305 | 1228863.9566 | 2695761.6137 | 1228864.7129
33 | 2695690.4441 | 1228886.3982 | 2695677.5872 | 1228887.0638
34 | 2695690.4441 | 1228886.3982 | 2695684.1777 | 1228883.5509 | 2695680.197 | 1228877.5826 | 2695679.2514 | 1228866.1814 | 2695683.2911 | 1228856.7625
35 | 2695697.8163 | 1228899.1557 | 2695696.816 | 1228901.5227 | 2695693.6657 | 1228917.9072
36 | 2695773.5659 | 1228856.6018 | 2695781.8658 | 1228850.5789
37 | 2695677.5872 | 1228887.0638 | 2695656.5363 | 1228888.1537
38 | 2695688.3686 | 1228844.9238 | 2695683.2911 | 1228856.7625
39 | 2695693.6657 | 1228917.9072 | 2695693.1533 | 1228920.5722
40 | 2695796.0927 | 1228840.2552 | 2695781.8658 | 1228850.5789
41 | 2695656.5363 | 1228888.1537 | 2695626.0666 | 1228889.7311
42 | 2695688.3686 | 1228844.9238 | 2695703.1014 | 1228843.8823 | 2695714.5324 | 1228840.8307
43 | 2695691.4872 | 1228929.2374 | 2695693.1533 | 1228920.5722
44 | 2695714.5324 | 1228840.8307 | 2695716.8565 | 1228839.894
45 | 2695626.0666 | 1228889.7311 | 2695618.0242 | 1228890.1475 | 2695601.8282 | 1228893.879
46 | 2695578.6865 | 1228899.2107 | 2695601.8282 | 1228893.879
47 | 2695788.8128 | 1229096.531 | 2695789.1548 | 1229095.9157 | 2695810.4978 | 1229075.2528
48 | 2695835.0016 | 1229057.0836 | 2695815.6576 | 1229070.2574 | 2695810.4978 | 1229075.2528
49 | 2695863.3445 | 1229039.3962 | 2695846.2964 | 1229049.3915 | 2695835.0016 | 1229057.0836
50 | 2695889.4621 | 1229024.0835 | 2695863.3445 | 1229039.3962
51 | 2695928.6706 | 1229001.0956 | 2695889.4621 | 1229024.0835
52 | 2695913.308 | 1228989.5285 | 2695929.6411 | 1228992.1382 | 2695928.6706 | 1229001.0956
53 | 2695913.308 | 1228989.5285 | 2695909.7158 | 1228966.5124
54 | 2695913.308 | 1228989.5285 | 2695903.9704 | 1228987.7766 | 2695880.2749 | 1228982.8817
55 | 2695909.7158 | 1228966.5124 | 2695904.5673 | 1228933.5251
56 | 2695876.2378 | 1228982.0477 | 2695876.2378 | 1228982.0477 | 2695880.2749 | 1228982.8817
57 | 2695904.5673 | 1228933.5251 | 2695903.3019 | 1228925.4176
58 | 2695876.2378 | 1228982.0477 | 2695859.3376 | 1228977.4271
59 | 2695797.428 | 1229013.4763 | 2695790.1524 | 1229019.1321
60 | 2695808.8086 | 1229004.6295 | 2695797.428 | 1229013.4763
61 | 2695778.7859 | 1229027.968 | 2695790.1524 | 1229019.1321
62 | 2695808.8086 | 1229004.6295 | 2695816.3535 | 1228998.7643
63 | 2695771.0527 | 1229033.9796 | 2695778.7859 | 1229027.968
64 | 2695816.3535 | 1228998.7643 | 2695818.0666 | 1228997.4326 | 2695828.8076 | 1228989.4788
65 | 2695845.5097 | 1228973.6464 | 2695836.1275 | 1228984.0583 | 2695828.8076 | 1228989.4788
66 | 2695845.5097 | 1228973.6464 | 2695859.3376 | 1228977.4271
67 | 2695800.0939 | 1228959.2712 | 2695806.6774 | 1228961.5952
68 | 2695800.0939 | 1228959.2712 | 2695800.0939 | 1228959.2712 | 2695790.1701 | 1228957.6769
69 | 2695847.676 | 1228949.9208 | 2695847.6637 | 1228949.7338
70 | 2695846.2634 | 1228928.9775 | 2695846.3664 | 1228929.9176 | 2695847.6637 | 1228949.7338
71 | 2695780.9343 | 1228957.5347 | 2695790.1701 | 1228957.6769
72 | 2695846.2634 | 1228928.9775 | 2695844.1301 | 1228909.4957
73 | 2695780.9343 | 1228957.5347 | 2695774.8747 | 1228957.4415 | 2695774.8747 | 1228957.4415
74 | 2695843.8725 | 1228907.1431 | 2695844.1301 | 1228909.4957
75 | 2695899.3548 | 1228900.1277 | 2695903.3019 | 1228925.4176
76 | 2695744.557 | 1228966.2701 | 2695742.1164 | 1228967.3324 | 2695742.1164 | 1228967.3324
77 | 2695744.557 | 1228966.2701 | 2695748.4448 | 1228964.5779
78 | 2695737.0968 | 1228970.2159 | 2695742.1164 | 1228967.3324
79 | 2695766.37 | 1228959.1624 | 2695758.6891 | 1228960.7166 | 2695748.5952 | 1228964.5124 | 2695748.4448 | 1228964.5779
80 | 2695716.3817 | 1228987.6061 | 2695735.7147 | 1228971.0098 | 2695737.0968 | 1228970.2159
81 | 2695769.9451 | 1228958.439 | 2695766.37 | 1228959.1624
82 | 2695703.6692 | 1228998.519 | 2695716.3817 | 1228987.6061
83 | 2695769.9451 | 1228958.439 | 2695774.8747 | 1228957.4415
84 | 2695703.6692 | 1228998.519 | 2695701.806 | 1229000.1185 | 2695691.7282 | 1229007.1141
85 | 2695679.392 | 1229013.7455 | 2695689.3916 | 1229008.7361 | 2695691.7282 | 1229007.1141
86 | 2695810.0945 | 1228830.0947 | 2695810.0945 | 1228830.0947 | 2695796.0927 | 1228840.2552
87 | 2695810.0945 | 1228830.0947 | 2695816.0365 | 1228827.6316
88 | 2695826.1412 | 1228823.9708 | 2695823.7271 | 1228824.4435 | 2695816.0365 | 1228827.6316
89 | 2695842.3043 | 1228818.5608 | 2695833.7995 | 1228822.471 | 2695826.1412 | 1228823.9708
90 | 2695842.3043 | 1228818.5608 | 2695842.8788 | 1228841.6756 | 2695842.8715 | 1228841.9264
91 | 2695842.3043 | 1228818.5608 | 2695848.8284 | 1228810.5935
92 | 2695842.8715 | 1228841.9264 | 2695842.2484 | 1228863.2396
93 | 2695852.9215 | 1228787.4984 | 2695848.8284 | 1228810.5935
94 | 2695842.192 | 1228865.1698 | 2695842.2484 | 1228863.2396
95 | 2695852.9215 | 1228787.4984 | 2695856.1345 | 1228772.4615 | 2695860.7836 | 1228758.5931 | 2695864.8083 | 1228751.9643
96 | 2695842.192 | 1228865.1698 | 2695841.7275 | 1228881.0588
97 | 2695864.8083 | 1228751.9643 | 2695875.627 | 1228751.1826 | 2695880.2 | 1228752.8464 | 2695882.43 | 1228756.9408 | 2695895.3617 | 1228793.4055
98 | 2695841.6188 | 1228886.5623 | 2695841.5776 | 1228886.1867 | 2695841.7275 | 1228881.0588
99 | 2695902.232 | 1228812.778 | 2695895.3617 | 1228793.4055
100 | 2695995.1085 | 1228805.7731 | 2695981.6891 | 1228781.8741
101 | 2695981.6891 | 1228781.8741 | 2695975.0784 | 1228770.1011
102 | 2695958.2492 | 1228741.7747 | 2695962.4093 | 1228748.3576 | 2695970.8563 | 1228762.5819 | 2695975.0784 | 1228770.1011
103 | 2695933.2821 | 1228832.746 | 2695958.1966 | 1228885.5791
104 | 2695919.9686 | 1228804.5136 | 2695933.2821 | 1228832.746
105 | 2695902.232 | 1228812.778 | 2695911.1803 | 1228808.6193 | 2695919.9686 | 1228804.5136
106 | 2695919.9686 | 1228804.5136 | 2695916.7593 | 1228797.7125 | 2695914.6454 | 1228792.8654
107 | 2695958.2492 | 1228741.7747 | 2695959.0003 | 1228735.1487 | 2695960.2131 | 1228732.1473
108 | 2695958.2492 | 1228741.7747 | 2695947.417 | 1228748.0823 | 2695947.0092 | 1228748.3263
109 | 2695902.232 | 1228812.778 | 2695903.0057 | 1228815.9548
110 | 2695914.6454 | 1228792.8654 | 2695945.9433 | 1228748.9642
111 | 2695960.2131 | 1228732.1473 | 2695962.8127 | 1228725.7145 | 2695979.6555 | 1228719.793 | 2695991.5246 | 1228716.62
112 | 2695945.9433 | 1228748.9642 | 2695947.0092 | 1228748.3263
113 | 2696013.1462 | 1228710.8398 | 2695991.5246 | 1228716.62
114 | 2696038.3846 | 1228702.9065 | 2696046.764 | 1228763.2419
115 | 2696038.3846 | 1228702.9065 | 2696035.5874 | 1228704.8405
116 | 2696035.5874 | 1228704.8405 | 2696013.1462 | 1228710.8398
117 | 2695843.8725 | 1228907.1431 | 2695842.9742 | 1228898.9397
118 | 2695842.1169 | 1228891.1113 | 2695842.9742 | 1228898.9397
119 | 2695842.1169 | 1228891.1113 | 2695841.8909 | 1228889.0477
120 | 2695841.6188 | 1228886.5623 | 2695841.8909 | 1228889.0477
121 | 2695907.7808 | 1228844.282 | 2695908.8771 | 1228840.0604 | 2695903.0057 | 1228815.9548
122 | 2695902.1518 | 1228865.959 | 2695907.7808 | 1228844.282
123 | 2695691.4872 | 1228929.2374 | 2695689.3576 | 1228940.3134
124 | 2695689.3576 | 1228940.3134 | 2695686.842 | 1228953.3966
125 | 2695685.3853 | 1228960.9728 | 2695686.842 | 1228953.3966
126 | 2695578.6865 | 1228899.2107 | 2695391.4718 | 1228954.0006

## bus_geodata
| x | y | coords
0 | 2695628.3027 | 1228987.4774
1 | 2695614.0213 | 1228992.7038
2 | 2695640.1099 | 1228983.8866
3 | 2695611.6056 | 1228993.856
4 | 2695646.6061 | 1228981.9471
5 | 2695592.6184 | 1229011.1041
6 | 2695683.2779 | 1228971.9334
7 | 2695590.2592 | 1229019.1677
8 | 2695682.6447 | 1228978.7467
9 | 2695683.7506 | 1228969.4747
10 | 2695680.8739 | 1228997.8
11 | 2695685.326 | 1228961.2816
12 | 2695714.7791 | 1229076.6294
13 | 2695712.505 | 1229071.928
14 | 2695720.3772 | 1229088.203
15 | 2695698.1675 | 1229058.7564
16 | 2695732.0936 | 1229077.6261
17 | 2695695.0894 | 1229055.0172
18 | 2695739.5353 | 1229070.9083
19 | 2695690.6843 | 1229049.1881
20 | 2695748.3563 | 1229060.6214
21 | 2695686.1475 | 1229034.9485
22 | 2695759.2708 | 1229047.3384
23 | 2695736.0046 | 1228875.374
24 | 2695748.1504 | 1228870.3177
25 | 2695722.2048 | 1228881.1188
26 | 2695759.2402 | 1228865.701
27 | 2695702.874 | 1228887.1876
28 | 2695761.6137 | 1228864.7129
29 | 2695690.4441 | 1228886.3982
30 | 2695697.8163 | 1228899.1557
31 | 2695773.5659 | 1228856.6018
32 | 2695677.5872 | 1228887.0638
33 | 2695683.2911 | 1228856.7625
34 | 2695693.6657 | 1228917.9072
35 | 2695781.8658 | 1228850.5789
36 | 2695656.5363 | 1228888.1537
37 | 2695688.3686 | 1228844.9238
38 | 2695693.1533 | 1228920.5722
39 | 2695714.5324 | 1228840.8307
40 | 2695716.8565 | 1228839.894
41 | 2695626.0666 | 1228889.7311
42 | 2695601.8282 | 1228893.879
43 | 2695788.8128 | 1229096.531
44 | 2695810.4978 | 1229075.2528
45 | 2695835.0016 | 1229057.0836
46 | 2695863.3445 | 1229039.3962
47 | 2695889.4621 | 1229024.0835
48 | 2695928.6706 | 1229001.0956
49 | 2695913.308 | 1228989.5285
50 | 2695909.7158 | 1228966.5124
51 | 2695880.2749 | 1228982.8817
52 | 2695904.5673 | 1228933.5251
53 | 2695876.2378 | 1228982.0477
54 | 2695797.428 | 1229013.4763
55 | 2695790.1524 | 1229019.1321
56 | 2695808.8086 | 1229004.6295
57 | 2695778.786 | 1229027.968
58 | 2695816.3535 | 1228998.7643
59 | 2695771.0527 | 1229033.9796
60 | 2695828.8076 | 1228989.4788
61 | 2695845.5097 | 1228973.6464
62 | 2695859.3376 | 1228977.4271
63 | 2695806.6774 | 1228961.5952
64 | 2695800.0939 | 1228959.2712
65 | 2695847.676 | 1228949.9208
66 | 2695847.6637 | 1228949.7338
67 | 2695790.1701 | 1228957.6769
68 | 2695846.2634 | 1228928.9775
69 | 2695780.9343 | 1228957.5347
70 | 2695844.1301 | 1228909.4957
71 | 2695903.3019 | 1228925.4176
72 | 2695744.557 | 1228966.2701
73 | 2695742.1164 | 1228967.3324
74 | 2695748.4448 | 1228964.5779
75 | 2695737.0968 | 1228970.2159
76 | 2695766.37 | 1228959.1624
77 | 2695716.3817 | 1228987.6061
78 | 2695769.9451 | 1228958.439
79 | 2695703.6692 | 1228998.519
80 | 2695774.8747 | 1228957.4415
81 | 2695691.7282 | 1229007.1141
82 | 2695679.392 | 1229013.7455
83 | 2695796.0927 | 1228840.2552
84 | 2695810.0945 | 1228830.0947
85 | 2695816.0365 | 1228827.6316
86 | 2695826.1412 | 1228823.9708
87 | 2695842.3043 | 1228818.5608
88 | 2695842.8715 | 1228841.9264
89 | 2695848.8284 | 1228810.5935
90 | 2695842.2484 | 1228863.2396
91 | 2695852.9215 | 1228787.4984
92 | 2695842.192 | 1228865.1698
93 | 2695864.8083 | 1228751.9643
94 | 2695841.7275 | 1228881.0588
95 | 2695895.3617 | 1228793.4055
96 | 2695995.1085 | 1228805.7731
97 | 2695981.6891 | 1228781.8741
98 | 2695975.0784 | 1228770.1011
99 | 2695933.2821 | 1228832.746
100 | 2695958.1966 | 1228885.5791
101 | 2695919.9686 | 1228804.5136
102 | 2695958.2492 | 1228741.7747
103 | 2695902.232 | 1228812.778
104 | 2695914.6454 | 1228792.8654
105 | 2695960.2131 | 1228732.1473
106 | 2695947.0092 | 1228748.3263
107 | 2695945.9433 | 1228748.9642
108 | 2695991.5246 | 1228716.62
109 | 2696046.764 | 1228763.2419
110 | 2696038.3846 | 1228702.9065
111 | 2696035.5874 | 1228704.8405
112 | 2696013.1462 | 1228710.8398
113 | 2695843.8725 | 1228907.1431
114 | 2695842.9742 | 1228898.9397
115 | 2695842.1169 | 1228891.1113
116 | 2695841.8909 | 1228889.0477
117 | 2695899.3548 | 1228900.1277
118 | 2695841.6188 | 1228886.5623
119 | 2695903.0057 | 1228815.9548
120 | 2695907.7808 | 1228844.282
121 | 2695902.1518 | 1228865.959
122 | 2695691.4872 | 1228929.2374
123 | 2695689.3576 | 1228940.3134
124 | 2695686.842 | 1228953.3966
125 | 2695685.3853 | 1228960.9728
126 | 2695578.6865 | 1228899.2107
127 | 2695391.4717 | 1228954.0006
128 | 2695845.5097 | 1228973.6464

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9854 | -0.27912 | 0.015532 | 0.0038926
1 | 0.985 | -0.28709 | 0.0045912 | 0.0011507
2 | 0.98591 | -0.26922 | 0.0045926 | 0.001151
3 | 0.98493 | -0.28829 | 0.0045912 | 0.0011507
4 | 0.98622 | -0.26323 | 0.0045913 | 0.0011507
5 | 0.98446 | -0.29755 | 0.0128 | 0.003208
6 | 0.98811 | -0.22656 | 0 | 0
7 | 0.9844 | -0.29864 | 0.0072045 | 0.0018056
8 | 0.98852 | -0.2185 | 0.001749 | 0.00043834
9 | 0.98798 | -0.22891 | 0.001746 | 0.0004376
10 | 0.9897 | -0.19585 | 0.0035559 | 0.00089119
11 | 0.98758 | -0.23668 | 0.0017467 | 0.00043775
12 | 0.98668 | -0.25368 | 0.0034426 | 0.00086279
13 | 0.98709 | -0.24589 | 0.0015593 | 0.0003908
14 | 0.98572 | -0.27209 | 0 | 0
15 | 0.98866 | -0.21572 | 0.0016416 | 0.00041141
16 | 0.98455 | -0.29474 | 0.0027291 | 0.00068397
17 | 0.98905 | -0.20825 | 0.0066272 | 0.0016609
18 | 0.98383 | -0.30866 | 0.0017591 | 0.00044088
19 | 0.98969 | -0.19604 | 0.0066279 | 0.0016611
20 | 0.98287 | -0.3271 | 0.0020306 | 0.00050891
21 | 0.99015 | -0.1872 | 0.0066289 | 0.0016614
22 | 0.9817 | -0.34989 | 0.0028305 | 0.00070938
23 | 0.98311 | -0.32331 | 0.0060093 | 0.0015061
24 | 0.98273 | -0.33071 | 0.0042608 | 0.0010679
25 | 0.98356 | -0.31451 | 0.0020287 | 0.00050843
26 | 0.98239 | -0.33723 | 0.0018446 | 0.00046229
27 | 0.98418 | -0.3024 | 0 | 0
28 | 0.98232 | -0.33861 | 0.0060106 | 0.0015064
29 | 0.9836 | -0.31389 | 0 | 0
30 | 0.98474 | -0.29165 | 0.0034514 | 0.00086499
31 | 0.98194 | -0.34597 | 0.0036543 | 0.00091586
32 | 0.9831 | -0.32354 | 0.0055985 | 0.0014031
33 | 0.98327 | -0.3202 | 0.0058784 | 0.0014733
34 | 0.98558 | -0.27544 | 0.0020296 | 0.00050867
35 | 0.98168 | -0.35101 | 0.0034583 | 0.00086674
36 | 0.9824 | -0.33724 | 0.0058529 | 0.0014669
37 | 0.98323 | -0.32111 | 0 | 0
38 | 0.98569 | -0.27313 | 0.0020296 | 0.00050867
39 | 0.98313 | -0.32299 | 0 | 0
40 | 0.98312 | -0.32317 | 0.0039191 | 0.00098223
41 | 0.98155 | -0.35386 | 0.0055996 | 0.0014034
42 | 0.98099 | -0.36482 | 0.0058522 | 0.0014667
43 | 0.97011 | -0.57702 | 0.0038041 | 0.0009534
44 | 0.97022 | -0.57488 | 0.0034357 | 0.00086107
45 | 0.97043 | -0.57078 | 0.0031819 | 0.00079747
46 | 0.97075 | -0.56433 | 0.0030576 | 0.00076632
47 | 0.97114 | -0.55678 | 0.001159 | 0.00029047
48 | 0.97176 | -0.54449 | 0 | 0
49 | 0.97211 | -0.53759 | 0 | 0
50 | 0.97147 | -0.5501 | 0.0041123 | 0.0010306
51 | 0.97348 | -0.51043 | 0.004113 | 0.0010308
52 | 0.97069 | -0.56553 | 0.0045284 | 0.0011349
53 | 0.97367 | -0.5068 | 0.0025383 | 0.00063615
54 | 0.97847 | -0.41272 | 0.0027291 | 0.00068397
55 | 0.97901 | -0.40209 | 0.0027285 | 0.00068382
56 | 0.97765 | -0.42865 | 0.0022363 | 0.00056046
57 | 0.9799 | -0.38479 | 0.0018078 | 0.00045309
58 | 0.97713 | -0.43884 | 0.0035214 | 0.00088255
59 | 0.98052 | -0.37272 | 0.0026097 | 0.00065404
60 | 0.97634 | -0.45443 | 0.0022377 | 0.00056082
61 | 0.9752 | -0.47673 | 0 | 0
62 | 0.97449 | -0.49058 | 0.0022636 | 0.00056732
63 | 0.99973 | -0.0052644 | 0.0021147 | 0.00053
64 | 0.99974 | -0.0050069 | 0.0021585 | 0.00054098
65 | 0.97754 | -0.43205 | 0.002389 | 0.00059874
66 | 0.97754 | -0.43204 | 0.0042211 | 0.0010579
67 | 0.99978 | -0.0042579 | 0.0022105 | 0.00055401
68 | 0.97767 | -0.42953 | 0.0023295 | 0.00058383
69 | 0.99983 | -0.0032135 | 0.0047517 | 0.0011909
70 | 0.97783 | -0.42634 | 0.0018369 | 0.00046036
71 | 0.97054 | -0.56864 | 0.0084915 | 0.0021282
72 | 0.99789 | -0.039834 | 0.0041562 | 0.0010416
73 | 0.99765 | -0.044382 | 0.0016152 | 0.0004048
74 | 0.99828 | -0.032516 | 0.0020285 | 0.00050838
75 | 0.99713 | -0.05424 | 0.0016156 | 0.00040491
76 | 1 | 0 | -0.4195 | -0.10748
77 | 0.9947 | -0.10029 | 0.0041532 | 0.0010409
78 | 0.99995 | -0.00090274 | 0.0013839 | 0.00034684
79 | 0.99321 | -0.12859 | 0.0035805 | 0.00089735
80 | 0.99989 | -0.0020263 | 0.0015784 | 0.00039558
81 | 0.99192 | -0.1533 | 0.0035805 | 0.00089736
82 | 0.9907 | -0.17667 | 0 | 0
83 | 0.98125 | -0.35939 | 0.0024708 | 0.00061924
84 | 0.98084 | -0.36745 | 0.0025283 | 0.00063366
85 | 0.98069 | -0.37037 | 0.0026173 | 0.00065595
86 | 0.98044 | -0.37515 | 0.0024386 | 0.00061117
87 | 0.98006 | -0.38257 | 0 | 0
88 | 0.9793 | -0.3975 | 0.0040844 | 0.0010236
89 | 0.97992 | -0.38538 | 0.0040831 | 0.0010233
90 | 0.97868 | -0.40956 | 0.001793 | 0.00044937
91 | 0.9793 | -0.39731 | 0 | 0
92 | 0.97863 | -0.41059 | 0.0040844 | 0.0010236
93 | 0.97733 | -0.43584 | 0 | 0
94 | 0.97826 | -0.41789 | 0.0024595 | 0.00061641
95 | 0.97424 | -0.49642 | 0.0040851 | 0.0010238
96 | 0.97092 | -0.562 | 0.002596 | 0.00065063
97 | 0.97099 | -0.56068 | 0.0017493 | 0.00043842
98 | 0.97105 | -0.5596 | 0.0020527 | 0.00051446
99 | 0.97209 | -0.53885 | 0.0082025 | 0.0020557
100 | 0.97173 | -0.546 | 0.0066306 | 0.0016618
101 | 0.97253 | -0.53031 | 0 | 0
102 | 0.97124 | -0.5557 | 0 | 0
103 | 0.97325 | -0.51605 | 0 | 0
104 | 0.97223 | -0.53618 | 0.0085286 | 0.0021375
105 | 0.97119 | -0.55678 | 0.0020824 | 0.0005219
106 | 0.97139 | -0.55274 | 0.0017698 | 0.00044355
107 | 0.97141 | -0.55242 | 0.0022441 | 0.00056244
108 | 0.97106 | -0.5594 | 0.0021593 | 0.00054118
109 | 0.97094 | -0.56166 | 0.00096607 | 0.00024212
110 | 0.971 | -0.56057 | 0 | 0
111 | 0.971 | -0.56051 | 0 | 0
112 | 0.97102 | -0.56009 | 0.00069424 | 0.00017399
113 | 0.97785 | -0.42587 | 0.0022985 | 0.00057607
114 | 0.97795 | -0.42391 | 0.0022107 | 0.00055404
115 | 0.97807 | -0.42171 | 0.0018051 | 0.00045241
116 | 0.9781 | -0.42106 | 0.0025237 | 0.00063251
117 | 0.97025 | -0.57431 | 0.011978 | 0.0030021
118 | 0.97814 | -0.42017 | 0.0031424 | 0.00078757
119 | 0.97321 | -0.51678 | 0.0040824 | 0.0010231
120 | 0.97299 | -0.52117 | 0.0040851 | 0.0010238
121 | 0.9729 | -0.52286 | 0.004085 | 0.0010238
122 | 0.98609 | -0.26556 | 0.0020279 | 0.00050825
123 | 0.98659 | -0.25578 | 0.0056781 | 0.0014231
124 | 0.98721 | -0.2439 | 0.0017445 | 0.00043722
125 | 0.98757 | -0.23697 | 0.0056782 | 0.0014231
126 | 0.98058 | -0.37286 | 0.016806 | 0.004212
127 | 0.98024 | -0.37951 | 0.0018766 | 0.00047032
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.029209 | 0.0073282 | -0.029198 | -0.0073213 | 1.1096e-05 | 6.9078e-06 | 0.04411 | 0.04411 | 0.04411 | 0.9854 | -0.27912 | 0.985 | -0.28709 | 12.1181
1 | -0.044741 | -0.011221 | 0.044762 | 0.011234 | 2.1129e-05 | 1.3365e-05 | 0.067564 | 0.067564 | 0.067564 | 0.9854 | -0.27912 | 0.98591 | -0.26922 | 18.5614
2 | 0.024607 | 0.0061706 | -0.024605 | -0.0061698 | 1.3999e-06 | 8.6153e-07 | 0.037174 | 0.037174 | 0.037174 | 0.985 | -0.28709 | 0.98493 | -0.28829 | 10.2127
3 | -0.049354 | -0.012385 | 0.049368 | 0.012394 | 1.4109e-05 | 8.9431e-06 | 0.074495 | 0.074495 | 0.074495 | 0.98591 | -0.26922 | 0.98622 | -0.26323 | 20.4657
4 | 0.020014 | 0.0050191 | -0.020005 | -0.0050138 | 8.831e-06 | 5.3242e-06 | 0.030238 | 0.030238 | 0.030238 | 0.98493 | -0.28829 | 0.98446 | -0.29755 | 8.3071
5 | -0.05396 | -0.013545 | 0.054054 | 0.013605 | 9.4535e-05 | 6.0016e-05 | 0.081422 | 0.081422 | 0.081422 | 0.98622 | -0.26323 | 0.98811 | -0.22656 | 22.3688
6 | 0.0072049 | 0.0018058 | -0.0072045 | -0.0018056 | 3.7366e-07 | 1.3232e-07 | 0.01089 | 0.01089 | 0.01089 | 0.98446 | -0.29755 | 0.9844 | -0.29864 | 2.9918
7 | -0.26592 | -0.067359 | 0.26602 | 0.067425 | 0.000103 | 6.5572e-05 | 0.40071 | 0.40071 | 0.40071 | 0.98811 | -0.22656 | 0.98852 | -0.2185 | 27.5214
8 | 0.21187 | 0.053754 | -0.21184 | -0.053739 | 2.3929e-05 | 1.5186e-05 | 0.31929 | 0.31929 | 0.31929 | 0.98811 | -0.22656 | 0.98798 | -0.22891 | 21.9292
9 | -0.26777 | -0.067863 | 0.26806 | 0.068049 | 0.00029185 | 0.0001858 | 0.40334 | 0.40334 | 0.40334 | 0.98852 | -0.2185 | 0.9897 | -0.19585 | 27.7022
10 | 0.2101 | 0.053301 | -0.21002 | -0.053252 | 7.8431e-05 | 4.9769e-05 | 0.31666 | 0.31666 | 0.31666 | 0.98798 | -0.22891 | 0.98758 | -0.23668 | 21.7486
11 | -0.27162 | -0.06894 | 0.27187 | 0.0691 | 0.00025076 | 0.00015966 | 0.40869 | 0.40869 | 0.40869 | 0.9897 | -0.19585 | 0.9907 | -0.17667 | 28.0693
12 | 0.20827 | 0.052814 | -0.20827 | -0.052812 | 2.907e-06 | 1.8444e-06 | 0.31403 | 0.31403 | 0.31403 | 0.98758 | -0.23668 | 0.98757 | -0.23697 | 21.5678
13 | -0.08427 | -0.021481 | 0.084302 | 0.021501 | 3.1696e-05 | 2.0219e-05 | 0.12722 | 0.12722 | 0.12722 | 0.98668 | -0.25368 | 0.98709 | -0.24589 | 34.9499
14 | 0.080828 | 0.020618 | -0.080756 | -0.020572 | 7.1788e-05 | 4.578e-05 | 0.12203 | 0.12203 | 0.12203 | 0.98668 | -0.25368 | 0.98572 | -0.27209 | 33.5236
15 | -0.085861 | -0.021892 | 0.085986 | 0.021972 | 0.00012527 | 7.9916e-05 | 0.12957 | 0.12957 | 0.12957 | 0.98709 | -0.24589 | 0.98866 | -0.21572 | 35.5956
16 | 0.080756 | 0.020572 | -0.080668 | -0.020516 | 8.8137e-05 | 5.6207e-05 | 0.12203 | 0.12203 | 0.12203 | 0.98572 | -0.27209 | 0.98455 | -0.29474 | 33.5236
17 | -0.087628 | -0.022383 | 0.08766 | 0.022404 | 3.1664e-05 | 2.0203e-05 | 0.13204 | 0.13204 | 0.13204 | 0.98866 | -0.21572 | 0.98905 | -0.20825 | 36.2743
18 | 0.077939 | 0.019832 | -0.077886 | -0.019799 | 5.226e-05 | 3.3319e-05 | 0.1179 | 0.1179 | 0.1179 | 0.98455 | -0.29474 | 0.98383 | -0.30866 | 32.3905
19 | -0.094287 | -0.024064 | 0.094343 | 0.0241 | 5.5649e-05 | 3.5521e-05 | 0.14201 | 0.14201 | 0.14201 | 0.98905 | -0.20825 | 0.98969 | -0.19604 | 39.0135
20 | 0.076127 | 0.019358 | -0.07606 | -0.019315 | 6.7577e-05 | 4.3077e-05 | 0.11524 | 0.11524 | 0.11524 | 0.98383 | -0.30866 | 0.98287 | -0.3271 | 31.6595
21 | -0.10097 | -0.025761 | 0.10101 | 0.025788 | 4.3146e-05 | 2.7037e-05 | 0.15197 | 0.15197 | 0.15197 | 0.98969 | -0.19604 | 0.99015 | -0.1872 | 13.917
22 | 0.074029 | 0.018806 | -0.073948 | -0.018754 | 8.1112e-05 | 5.1694e-05 | 0.11217 | 0.11217 | 0.11217 | 0.98287 | -0.3271 | 0.9817 | -0.34989 | 30.815
23 | -0.10764 | -0.027449 | 0.1077 | 0.027483 | 5.4708e-05 | 3.3867e-05 | 0.16194 | 0.16194 | 0.16194 | 0.99015 | -0.1872 | 0.9907 | -0.17667 | 11.122
24 | 0.071118 | 0.018045 | -0.07104 | -0.017995 | 7.7987e-05 | 4.9686e-05 | 0.10788 | 0.10788 | 0.10788 | 0.9817 | -0.34989 | 0.98052 | -0.37272 | 29.6364
25 | 0.12535 | 0.031707 | -0.1253 | -0.031679 | 4.4446e-05 | 2.7778e-05 | 0.18983 | 0.18983 | 0.18983 | 0.98311 | -0.32331 | 0.98273 | -0.33071 | 13.0378
26 | -0.13136 | -0.033213 | 0.13141 | 0.033247 | 5.5453e-05 | 3.4732e-05 | 0.19893 | 0.19892 | 0.19893 | 0.98311 | -0.32331 | 0.98356 | -0.31451 | 13.6624
27 | 0.12104 | 0.030611 | -0.12101 | -0.030587 | 3.787e-05 | 2.3628e-05 | 0.18338 | 0.18338 | 0.18338 | 0.98273 | -0.33071 | 0.98239 | -0.33723 | 12.5947
28 | -0.13344 | -0.033756 | 0.13352 | 0.033804 | 7.7613e-05 | 4.8642e-05 | 0.20199 | 0.20199 | 0.20199 | 0.98356 | -0.31451 | 0.98418 | -0.3024 | 13.8732
29 | 0.11916 | 0.030125 | -0.11915 | -0.03012 | 7.86e-06 | 4.9002e-06 | 0.18058 | 0.18058 | 0.18058 | 0.98239 | -0.33723 | 0.98232 | -0.33861 | 12.4028
30 | 0.051502 | 0.012949 | -0.051474 | -0.012931 | 2.8247e-05 | 1.792e-05 | 0.077883 | 0.077883 | 0.077883 | 0.98418 | -0.3024 | 0.9836 | -0.31389 | 21.3964
31 | -0.18502 | -0.046753 | 0.18512 | 0.046814 | 9.5413e-05 | 6.0404e-05 | 0.27988 | 0.27988 | 0.27988 | 0.98418 | -0.3024 | 0.98474 | -0.29165 | 19.2223
32 | 0.11314 | 0.028614 | -0.1131 | -0.028589 | 3.9947e-05 | 2.4833e-05 | 0.17148 | 0.17148 | 0.17148 | 0.98232 | -0.33861 | 0.98194 | -0.34597 | 11.7775
33 | 0.041673 | 0.010474 | -0.041654 | -0.010462 | 1.9195e-05 | 1.2122e-05 | 0.063055 | 0.063055 | 0.063055 | 0.9836 | -0.31389 | 0.9831 | -0.32354 | 17.3229
34 | 0.009801 | 0.0024568 | -0.0097981 | -0.0024553 | 2.9471e-06 | 1.4326e-06 | 0.014827 | 0.014828 | 0.014828 | 0.9836 | -0.31389 | 0.98327 | -0.3202 | 4.0735
35 | -0.18857 | -0.047679 | 0.18872 | 0.047772 | 0.00014671 | 9.2915e-05 | 0.28509 | 0.28509 | 0.28509 | 0.98474 | -0.29165 | 0.98558 | -0.27544 | 19.5805
36 | 0.10945 | 0.027673 | -0.10942 | -0.027657 | 2.6474e-05 | 1.6425e-05 | 0.16594 | 0.16594 | 0.16594 | 0.98194 | -0.34597 | 0.98168 | -0.35101 | 11.3972
37 | 0.036056 | 0.0090591 | -0.036032 | -0.0090443 | 2.3549e-05 | 1.4804e-05 | 0.054582 | 0.054582 | 0.054582 | 0.9831 | -0.32354 | 0.9824 | -0.33724 | 14.995
38 | 0.0039197 | 0.00098205 | -0.0039195 | -0.00098211 | 1.6996e-07 | -5.4605e-08 | 0.0059317 | 0.0059317 | 0.0059317 | 0.98327 | -0.3202 | 0.98323 | -0.32111 | 1.6296
39 | -0.19074 | -0.04828 | 0.19077 | 0.048294 | 2.1125e-05 | 1.3382e-05 | 0.28816 | 0.28816 | 0.28816 | 0.98558 | -0.27544 | 0.98569 | -0.27313 | 19.7909
40 | 0.10596 | 0.02679 | -0.10592 | -0.026763 | 4.2557e-05 | 2.6348e-05 | 0.1607 | 0.1607 | 0.1607 | 0.98168 | -0.35101 | 0.98125 | -0.35939 | 11.0371
41 | 0.030179 | 0.0075775 | -0.030155 | -0.0075625 | 2.3913e-05 | 1.4918e-05 | 0.045716 | 0.045717 | 0.045717 | 0.9824 | -0.33724 | 0.98155 | -0.35386 | 12.5595
42 | 0.0039195 | 0.00098211 | -0.0039192 | -0.00098222 | 3.5001e-07 | -1.1239e-07 | 0.0059317 | 0.0059319 | 0.0059319 | 0.98323 | -0.32111 | 0.98313 | -0.32299 | 1.6296
43 | -0.1928 | -0.048802 | 0.19287 | 0.048847 | 7.0157e-05 | 4.4451e-05 | 0.29122 | 0.29122 | 0.29122 | 0.98569 | -0.27313 | 0.98609 | -0.26556 | 20.0013
44 | 0.0039192 | 0.00098222 | -0.0039191 | -0.00098223 | 3.3064e-08 | -1.0613e-08 | 0.0059319 | 0.0059319 | 0.0059319 | 0.98313 | -0.32299 | 0.98312 | -0.32317 | 1.6296
45 | 0.024556 | 0.0061591 | -0.024543 | -0.0061513 | 1.2823e-05 | 7.8951e-06 | 0.037228 | 0.037228 | 0.037228 | 0.98155 | -0.35386 | 0.98099 | -0.36482 | 10.2274
46 | 0.018691 | 0.0046845 | -0.018683 | -0.0046803 | 7.158e-06 | 4.2814e-06 | 0.028351 | 0.028351 | 0.028351 | 0.98099 | -0.36482 | 0.98058 | -0.37286 | 7.7887
47 | -0.0038041 | -0.0009534 | 0.0038045 | 0.00095327 | 3.8826e-07 | -1.2703e-07 | 0.005835 | 0.0058348 | 0.005835 | 0.97011 | -0.57702 | 0.97022 | -0.57488 | 1.603
48 | -0.0072402 | -0.0018143 | 0.0072416 | 0.0018149 | 1.4142e-06 | 5.2729e-07 | 0.011104 | 0.011104 | 0.011104 | 0.97022 | -0.57488 | 0.97043 | -0.57078 | 3.0506
49 | -0.010424 | -0.0026123 | 0.010427 | 0.002614 | 3.2022e-06 | 1.6363e-06 | 0.015983 | 0.015983 | 0.015983 | 0.97043 | -0.57078 | 0.97075 | -0.56433 | 4.3909
50 | -0.013484 | -0.0033803 | 0.013489 | 0.003383 | 4.8506e-06 | 2.7299e-06 | 0.02067 | 0.02067 | 0.02067 | 0.97075 | -0.56433 | 0.97114 | -0.55678 | 5.6785
51 | -0.014648 | -0.0036735 | 0.014657 | 0.0036784 | 8.5867e-06 | 4.9327e-06 | 0.022445 | 0.022445 | 0.022445 | 0.97114 | -0.55678 | 0.97176 | -0.54449 | 6.1663
52 | -0.014657 | -0.0036784 | 0.014662 | 0.0036812 | 4.8269e-06 | 2.7726e-06 | 0.022445 | 0.022445 | 0.022445 | 0.97176 | -0.54449 | 0.97211 | -0.53759 | 6.1663
53 | 0.029153 | 0.0073216 | -0.029135 | -0.0073108 | 1.74e-05 | 1.0847e-05 | 0.04463 | 0.04463 | 0.04463 | 0.97211 | -0.53759 | 0.97147 | -0.5501 | 12.261
54 | -0.043814 | -0.011003 | 0.043871 | 0.011039 | 5.6851e-05 | 3.5966e-05 | 0.067075 | 0.067075 | 0.067075 | 0.97211 | -0.53759 | 0.97348 | -0.51043 | 18.4272
55 | 0.025023 | 0.0062801 | -0.025005 | -0.0062688 | 1.8395e-05 | 1.136e-05 | 0.038331 | 0.038331 | 0.038331 | 0.97147 | -0.5501 | 0.97069 | -0.56553 | 10.5306
56 | -0.047984 | -0.01207 | 0.047993 | 0.012075 | 8.3198e-06 | 5.2734e-06 | 0.073362 | 0.073362 | 0.073362 | 0.97348 | -0.51043 | 0.97367 | -0.5068 | 20.1544
57 | 0.020476 | 0.0051339 | -0.020473 | -0.005132 | 3.0319e-06 | 1.839e-06 | 0.03139 | 0.03139 | 0.03139 | 0.97069 | -0.56553 | 0.97054 | -0.56864 | 8.6235
58 | -0.050531 | -0.012711 | 0.05057 | 0.012736 | 3.9199e-05 | 2.4869e-05 | 0.077241 | 0.077241 | 0.077241 | 0.97367 | -0.5068 | 0.97449 | -0.49058 | 21.2201
59 | -0.063766 | -0.016123 | 0.063799 | 0.016144 | 3.2531e-05 | 2.0704e-05 | 0.097024 | 0.097024 | 0.097024 | 0.97847 | -0.41272 | 0.97901 | -0.40209 | 26.6549
60 | 0.061037 | 0.015439 | -0.06099 | -0.01541 | 4.6626e-05 | 2.9659e-05 | 0.092874 | 0.092874 | 0.092874 | 0.97847 | -0.41272 | 0.97765 | -0.42865 | 25.5148
61 | -0.066527 | -0.016828 | 0.066582 | 0.016863 | 5.526e-05 | 3.5185e-05 | 0.10117 | 0.10117 | 0.10117 | 0.97901 | -0.40209 | 0.9799 | -0.38479 | 27.7942
62 | 0.058754 | 0.014849 | -0.058725 | -0.014831 | 2.8687e-05 | 1.824e-05 | 0.08947 | 0.08947 | 0.08947 | 0.97765 | -0.42865 | 0.97713 | -0.43884 | 24.5797
63 | -0.06839 | -0.017316 | 0.06843 | 0.017341 | 3.9665e-05 | 2.5262e-05 | 0.10392 | 0.10392 | 0.10392 | 0.9799 | -0.38479 | 0.98052 | -0.37272 | 28.5484
64 | 0.055204 | 0.013948 | -0.055163 | -0.013922 | 4.1211e-05 | 2.6181e-05 | 0.084108 | 0.084108 | 0.084108 | 0.97713 | -0.43884 | 0.97634 | -0.45443 | 23.1065
65 | 0.052925 | 0.013361 | -0.052869 | -0.013325 | 5.6469e-05 | 3.5851e-05 | 0.080697 | 0.080697 | 0.080697 | 0.97634 | -0.45443 | 0.9752 | -0.47673 | 22.1696
66 | 0.052869 | 0.013325 | -0.052834 | -0.013303 | 3.5007e-05 | 2.2226e-05 | 0.080697 | 0.080697 | 0.080697 | 0.9752 | -0.47673 | 0.97449 | -0.49058 | 22.1696
67 | -0.0021147 | -0.00053 | 0.0021148 | 0.00052993 | 2.5939e-08 | -7.4945e-08 | 0.0031476 | 0.0031476 | 0.0031476 | 0.99973 | -0.0052644 | 0.99974 | -0.0050069 | 0.86473
68 | -0.0042733 | -0.0010709 | 0.0042734 | 0.0010709 | 1.5248e-07 | -3.4214e-08 | 0.0063604 | 0.0063603 | 0.0063604 | 0.99974 | -0.0050069 | 0.99978 | -0.0042579 | 1.7473
69 | -0.002389 | -0.00059874 | 0.002389 | 0.00059874 | 9.2935e-10 | -1.7547e-09 | 0.0036366 | 0.0036366 | 0.0036366 | 0.97754 | -0.43205 | 0.97754 | -0.43204 | 0.99906
70 | -0.0066102 | -0.0016567 | 0.0066109 | 0.0016569 | 7.8986e-07 | 2.4466e-07 | 0.010062 | 0.010062 | 0.010062 | 0.97754 | -0.43204 | 0.97767 | -0.42953 | 2.7643
71 | -0.006484 | -0.0016249 | 0.0064843 | 0.001625 | 3.2258e-07 | 8.5318e-08 | 0.0096503 | 0.0096503 | 0.0096503 | 0.99978 | -0.0042579 | 0.99983 | -0.0032135 | 2.6512
72 | -0.0089405 | -0.0022407 | 0.0089418 | 0.0022414 | 1.3608e-06 | 6.2512e-07 | 0.013607 | 0.013607 | 0.013607 | 0.97767 | -0.42953 | 0.97783 | -0.42634 | 3.7383
73 | -0.011236 | -0.0028159 | 0.011237 | 0.0028162 | 6.355e-07 | 3.2723e-07 | 0.016722 | 0.016722 | 0.016722 | 0.99983 | -0.0032135 | 0.99989 | -0.0020263 | 4.594
74 | -0.010779 | -0.0027017 | 0.010779 | 0.0027018 | 2.3878e-07 | 1.2313e-07 | 0.016403 | 0.016403 | 0.016403 | 0.97783 | -0.42634 | 0.97785 | -0.42587 | 4.5062
75 | 0.011982 | 0.0030038 | -0.011978 | -0.0030021 | 3.2393e-06 | 1.7569e-06 | 0.018371 | 0.018371 | 0.018371 | 0.97054 | -0.56864 | 0.97025 | -0.57431 | 5.0469
76 | 0.39668 | 0.10187 | -0.3966 | -0.10181 | 8.7573e-05 | 5.5908e-05 | 0.59239 | 0.59239 | 0.59239 | 0.99789 | -0.039834 | 0.99765 | -0.044382 | 40.6862
77 | -0.40084 | -0.10291 | 0.40098 | 0.103 | 0.00014243 | 9.0934e-05 | 0.59859 | 0.59859 | 0.59859 | 0.99789 | -0.039834 | 0.99828 | -0.032516 | 41.1119
78 | 0.39498 | 0.10141 | -0.39479 | -0.10129 | 0.00018891 | 0.0001206 | 0.58998 | 0.58998 | 0.58998 | 0.99765 | -0.044382 | 0.99713 | -0.05424 | 40.5208
79 | -0.40301 | -0.10351 | 0.40365 | 0.10392 | 0.00063739 | 0.00040695 | 0.60161 | 0.60161 | 0.60161 | 0.99828 | -0.032516 | 1 | 0 | 41.3195
80 | 0.39318 | 0.10088 | -0.3923 | -0.10032 | 0.00087626 | 0.0005594 | 0.58757 | 0.58757 | 0.58757 | 0.99713 | -0.05424 | 0.9947 | -0.10029 | 40.3552
81 | 0.0142 | 0.0035593 | -0.0142 | -0.003559 | 6.1072e-07 | 3.4301e-07 | 0.02113 | 0.02113 | 0.02113 | 1 | 0 | 0.99995 | -0.00090274 | 5.805
82 | 0.38815 | 0.099282 | -0.38762 | -0.098943 | 0.00053086 | 0.00033888 | 0.58136 | 0.58136 | 0.58136 | 0.9947 | -0.10029 | 0.99321 | -0.12859 | 39.9285
83 | 0.012816 | 0.0032121 | -0.012815 | -0.0032118 | 6.8597e-07 | 3.7305e-07 | 0.019071 | 0.019071 | 0.019071 | 0.99995 | -0.00090274 | 0.99989 | -0.0020263 | 5.2393
84 | 0.38403 | 0.098046 | -0.38358 | -0.097754 | 0.00045795 | 0.00029233 | 0.576 | 0.576 | 0.576 | 0.99321 | -0.12859 | 0.99192 | -0.1533 | 39.5601
85 | 0.38 | 0.096856 | -0.37957 | -0.096583 | 0.00042824 | 0.00027335 | 0.57062 | 0.57062 | 0.57062 | 0.99192 | -0.1533 | 0.9907 | -0.17667 | 39.1912
86 | 0.10345 | 0.026144 | -0.10341 | -0.02612 | 3.9954e-05 | 2.4697e-05 | 0.15695 | 0.15695 | 0.15695 | 0.98125 | -0.35939 | 0.98084 | -0.36745 | 10.7798
87 | 0.10088 | 0.025486 | -0.10087 | -0.025477 | 1.4138e-05 | 8.7237e-06 | 0.15312 | 0.15312 | 0.15312 | 0.98084 | -0.36745 | 0.98069 | -0.37037 | 10.5164
88 | 0.09825 | 0.024821 | -0.098227 | -0.024807 | 2.2492e-05 | 1.3851e-05 | 0.14915 | 0.14915 | 0.14915 | 0.98069 | -0.37037 | 0.98044 | -0.37515 | 10.2437
89 | 0.095789 | 0.024196 | -0.095755 | -0.024175 | 3.4041e-05 | 2.0921e-05 | 0.14545 | 0.14545 | 0.14545 | 0.98044 | -0.37515 | 0.98006 | -0.38257 | 9.9895
90 | 0.035241 | 0.0088547 | -0.035215 | -0.0088389 | 2.51e-05 | 1.577e-05 | 0.053513 | 0.053513 | 0.053513 | 0.98006 | -0.38257 | 0.9793 | -0.3975 | 14.7015
91 | 0.060514 | 0.015321 | -0.060506 | -0.015316 | 8.1594e-06 | 4.7031e-06 | 0.091934 | 0.091934 | 0.091934 | 0.98006 | -0.38257 | 0.97992 | -0.38538 | 6.3141
92 | 0.031131 | 0.0078153 | -0.031113 | -0.0078041 | 1.7895e-05 | 1.1184e-05 | 0.047307 | 0.047307 | 0.047307 | 0.9793 | -0.3975 | 0.97868 | -0.40956 | 12.9966
93 | 0.056423 | 0.014293 | -0.056391 | -0.014272 | 3.2325e-05 | 2.0097e-05 | 0.085734 | 0.085734 | 0.085734 | 0.97992 | -0.38538 | 0.9793 | -0.39731 | 11.7766
94 | 0.02932 | 0.0073547 | -0.029319 | -0.0073538 | 1.4392e-06 | 8.9682e-07 | 0.044581 | 0.044581 | 0.044581 | 0.97868 | -0.40956 | 0.97863 | -0.41059 | 12.2476
95 | 0.056391 | 0.014272 | -0.056287 | -0.014206 | 0.00010407 | 6.6134e-05 | 0.085734 | 0.085734 | 0.085734 | 0.9793 | -0.39731 | 0.97733 | -0.43584 | 23.5533
96 | 0.025234 | 0.0063302 | -0.025226 | -0.0063248 | 8.7765e-06 | 5.4173e-06 | 0.038371 | 0.038371 | 0.038371 | 0.97863 | -0.41059 | 0.97826 | -0.41789 | 10.5415
97 | 0.056287 | 0.014206 | -0.056124 | -0.014103 | 0.00016281 | 0.00010346 | 0.085734 | 0.085734 | 0.085734 | 0.97733 | -0.43584 | 0.97424 | -0.49642 | 23.5533
98 | 0.022766 | 0.0057084 | -0.022764 | -0.0057069 | 2.477e-06 | 1.5162e-06 | 0.03463 | 0.03463 | 0.03463 | 0.97826 | -0.41789 | 0.97814 | -0.42017 | 9.5138
99 | 0.052039 | 0.013079 | -0.05199 | -0.013048 | 4.871e-05 | 3.0919e-05 | 0.079495 | 0.079495 | 0.079495 | 0.97424 | -0.49642 | 0.97325 | -0.51605 | 21.8393
100 | -0.002596 | -0.00065063 | 0.0025962 | 0.00065039 | 1.6269e-07 | -2.3488e-07 | 0.0039786 | 0.0039785 | 0.0039786 | 0.97092 | -0.562 | 0.97099 | -0.56068 | 1.093
101 | -0.0043455 | -0.0010888 | 0.0043457 | 0.0010888 | 2.2453e-07 | -2.3319e-08 | 0.0066592 | 0.0066592 | 0.0066592 | 0.97099 | -0.56068 | 0.97105 | -0.5596 | 1.8295
102 | -0.0063984 | -0.0016032 | 0.0063996 | 0.0016036 | 1.188e-06 | 3.5256e-07 | 0.0098047 | 0.0098046 | 0.0098047 | 0.97105 | -0.5596 | 0.97124 | -0.5557 | 2.6936
103 | 0.0066329 | 0.0016625 | -0.0066306 | -0.0016618 | 2.2582e-06 | 7.2135e-07 | 0.010153 | 0.010153 | 0.010153 | 0.97209 | -0.53885 | 0.97173 | -0.546 | 2.7894
104 | -0.014835 | -0.0037183 | 0.014841 | 0.0037217 | 6.0364e-06 | 3.4762e-06 | 0.022709 | 0.022709 | 0.022709 | 0.97209 | -0.53885 | 0.97253 | -0.53031 | 6.2388
105 | -0.039708 | -0.0099594 | 0.039735 | 0.0099764 | 2.7023e-05 | 1.7053e-05 | 0.060758 | 0.060758 | 0.060758 | 0.97253 | -0.53031 | 0.97325 | -0.51605 | 16.6918
106 | 0.024867 | 0.0062376 | -0.02486 | -0.0062334 | 6.9536e-06 | 4.2914e-06 | 0.038049 | 0.038049 | 0.038049 | 0.97253 | -0.53031 | 0.97223 | -0.53618 | 10.4531
107 | 0.0059029 | 0.0014778 | -0.0059026 | -0.0014778 | 3.0378e-07 | 7.1837e-08 | 0.0090432 | 0.0090432 | 0.0090432 | 0.97124 | -0.5557 | 0.97119 | -0.55678 | 2.4844
108 | -0.012303 | -0.0030814 | 0.012304 | 0.0030824 | 1.7331e-06 | 9.4816e-07 | 0.018848 | 0.018848 | 0.018848 | 0.97124 | -0.5557 | 0.97139 | -0.55274 | 5.178
109 | 0.012255 | 0.0030717 | -0.012255 | -0.0030714 | 4.3045e-07 | 2.3486e-07 | 0.018737 | 0.018737 | 0.018737 | 0.97325 | -0.51605 | 0.97321 | -0.51678 | 5.1475
110 | 0.016331 | 0.0040959 | -0.016318 | -0.0040885 | 1.2633e-05 | 7.4168e-06 | 0.024996 | 0.024996 | 0.024996 | 0.97223 | -0.53618 | 0.97141 | -0.55242 | 6.8671
111 | 0.0038202 | 0.00095586 | -0.0038198 | -0.00095601 | 4.7628e-07 | -1.5392e-07 | 0.0058527 | 0.0058528 | 0.0058528 | 0.97119 | -0.55678 | 0.97106 | -0.5594 | 1.6079
112 | -0.014074 | -0.0035259 | 0.014074 | 0.003526 | 2.1651e-07 | 1.2319e-07 | 0.021559 | 0.021559 | 0.021559 | 0.97139 | -0.55274 | 0.97141 | -0.55242 | 5.9227
113 | 0.0016604 | 0.00041483 | -0.0016604 | -0.00041508 | 5.4317e-08 | -2.421e-07 | 0.0025439 | 0.002544 | 0.002544 | 0.97106 | -0.5594 | 0.97102 | -0.56009 | 0.69891
114 | -0.00096607 | -0.00024212 | 0.00096612 | 0.0002414 | 5.0064e-08 | -7.2139e-07 | 0.0014806 | 0.0014803 | 0.0014806 | 0.97094 | -0.56166 | 0.971 | -0.56057 | 0.40675
115 | -0.00096612 | -0.0002414 | 0.00096613 | 0.00024136 | 2.7889e-09 | -4.0197e-08 | 0.0014803 | 0.0014803 | 0.0014803 | 0.971 | -0.56057 | 0.971 | -0.56051 | 0.40667
116 | -0.00096613 | -0.00024136 | 0.00096615 | 0.00024108 | 1.9086e-08 | -2.7512e-07 | 0.0014803 | 0.0014802 | 0.0014803 | 0.971 | -0.56051 | 0.97102 | -0.56009 | 0.40667
117 | -0.013077 | -0.0032779 | 0.013079 | 0.0032786 | 1.2255e-06 | 6.8082e-07 | 0.0199 | 0.0199 | 0.0199 | 0.97785 | -0.42587 | 0.97795 | -0.42391 | 5.4671
118 | -0.015289 | -0.0038326 | 0.015291 | 0.0038336 | 1.5983e-06 | 9.2409e-07 | 0.023264 | 0.023264 | 0.023264 | 0.97795 | -0.42391 | 0.97807 | -0.42171 | 6.3912
119 | -0.017096 | -0.004286 | 0.017097 | 0.0042863 | 5.2665e-07 | 3.11e-07 | 0.02601 | 0.02601 | 0.02601 | 0.97807 | -0.42171 | 0.9781 | -0.42106 | 7.1457
120 | -0.01962 | -0.0049188 | 0.019621 | 0.0049193 | 8.3539e-07 | 5.0327e-07 | 0.02985 | 0.02985 | 0.02985 | 0.9781 | -0.42106 | 0.97814 | -0.42017 | 8.2004
121 | 0.0081721 | 0.0020483 | -0.0081704 | -0.0020476 | 1.708e-06 | 7.3069e-07 | 0.012495 | 0.012495 | 0.012495 | 0.97321 | -0.51678 | 0.97299 | -0.52117 | 3.4327
122 | 0.0040854 | 0.0010237 | -0.004085 | -0.0010238 | 3.2784e-07 | -6.8319e-08 | 0.0062478 | 0.0062479 | 0.0062479 | 0.97299 | -0.52117 | 0.9729 | -0.52286 | 1.7165
123 | -0.19489 | -0.049355 | 0.19499 | 0.049413 | 9.157e-05 | 5.8029e-05 | 0.29428 | 0.29428 | 0.29428 | 0.98609 | -0.26556 | 0.98659 | -0.25578 | 20.2115
124 | -0.20066 | -0.050836 | 0.20078 | 0.050909 | 0.00011455 | 7.2632e-05 | 0.30284 | 0.30284 | 0.30284 | 0.98659 | -0.25578 | 0.98721 | -0.2439 | 20.7996
125 | -0.20252 | -0.051346 | 0.20259 | 0.051389 | 6.7492e-05 | 4.28e-05 | 0.30547 | 0.30547 | 0.30547 | 0.98721 | -0.2439 | 0.98757 | -0.23697 | 20.9802
126 | 0.0018772 | 0.00046824 | -0.0018766 | -0.00047032 | 5.9344e-07 | -2.0801e-06 | 0.0028478 | 0.0028487 | 0.0028487 | 0.98058 | -0.37286 | 0.98024 | -0.37951 | 0.78261

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42167 | 0.10802

## res_load
| p_mw | q_mvar
0 | 0.015532 | 0.0038926
1 | 0.0045912 | 0.0011507
2 | 0.0045926 | 0.001151
3 | 0.0045912 | 0.0011507
4 | 0.0045913 | 0.0011507
5 | 0.0128 | 0.003208
6 | 0.0072045 | 0.0018056
7 | 0.001749 | 0.00043834
8 | 0.001746 | 0.0004376
9 | 0.0035559 | 0.00089119
10 | 0.0017467 | 0.00043775
11 | 0.0034426 | 0.00086279
12 | 0.0015593 | 0.0003908
13 | 0.0016416 | 0.00041141
14 | 0.0027291 | 0.00068397
15 | 0.0066272 | 0.0016609
16 | 0.0017591 | 0.00044088
17 | 0.0066279 | 0.0016611
18 | 0.0020306 | 0.00050891
19 | 0.0066289 | 0.0016614
20 | 0.0028305 | 0.00070938
21 | 0.0060093 | 0.0015061
22 | 0.0042608 | 0.0010679
23 | 0.0020287 | 0.00050843
24 | 0.0018446 | 0.00046229
25 | 0.0060106 | 0.0015064
26 | 0.0034514 | 0.00086499
27 | 0.0036543 | 0.00091586
28 | 0.0055985 | 0.0014031
29 | 0.0058784 | 0.0014733
30 | 0.0020296 | 0.00050867
31 | 0.0034583 | 0.00086674
32 | 0.0058529 | 0.0014669
33 | 0.0020296 | 0.00050867
34 | 0.0039191 | 0.00098223
35 | 0.0055996 | 0.0014034
36 | 0.0058522 | 0.0014667
37 | 0.0038041 | 0.0009534
38 | 0.0034357 | 0.00086107
39 | 0.0031819 | 0.00079747
40 | 0.0030576 | 0.00076632
41 | 0.001159 | 0.00029047
42 | 0.0041123 | 0.0010306
43 | 0.004113 | 0.0010308
44 | 0.0045284 | 0.0011349
45 | 0.0025383 | 0.00063615
46 | 0.0027291 | 0.00068397
47 | 0.0027285 | 0.00068382
48 | 0.0022363 | 0.00056046
49 | 0.0018078 | 0.00045309
50 | 0.0035214 | 0.00088255
51 | 0.0026097 | 0.00065404
52 | 0.0022377 | 0.00056082
53 | 0.0022636 | 0.00056732
54 | 0.0021147 | 0.00053
55 | 0.0021585 | 0.00054098
56 | 0.002389 | 0.00059874
57 | 0.0042211 | 0.0010579
58 | 0.0022105 | 0.00055401
59 | 0.0023295 | 0.00058383
60 | 0.0047517 | 0.0011909
61 | 0.0018369 | 0.00046036
62 | 0.0084915 | 0.0021282
63 | 0.0041562 | 0.0010416
64 | 0.0016152 | 0.0004048
65 | 0.0020285 | 0.00050838
66 | 0.0016156 | 0.00040491
67 | 0.002176 | 0.00054536
68 | 0.0041532 | 0.0010409
69 | 0.0013839 | 0.00034684
70 | 0.0035805 | 0.00089735
71 | 0.0015784 | 0.00039558
72 | 0.0035805 | 0.00089736
73 | 0.0024708 | 0.00061924
74 | 0.0025283 | 0.00063366
75 | 0.0026173 | 0.00065595
76 | 0.0024386 | 0.00061117
77 | 0.0040844 | 0.0010236
78 | 0.0040831 | 0.0010233
79 | 0.001793 | 0.00044937
80 | 0.0040844 | 0.0010236
81 | 0.0024595 | 0.00061641
82 | 0.0040851 | 0.0010238
83 | 0.002596 | 0.00065063
84 | 0.0017493 | 0.00043842
85 | 0.0020527 | 0.00051446
86 | 0.0082025 | 0.0020557
87 | 0.0066306 | 0.0016618
88 | 0.0085286 | 0.0021375
89 | 0.0020824 | 0.0005219
90 | 0.0017698 | 0.00044355
91 | 0.0022441 | 0.00056244
92 | 0.0021593 | 0.00054118
93 | 0.00096607 | 0.00024212
94 | 0.00069424 | 0.00017399
95 | 0.0022985 | 0.00057607
96 | 0.0022107 | 0.00055404
97 | 0.0018051 | 0.00045241
98 | 0.0025237 | 0.00063251
99 | 0.011978 | 0.0030021
100 | 0.0031424 | 0.00078757
101 | 0.0040824 | 0.0010231
102 | 0.0040851 | 0.0010238
103 | 0.004085 | 0.0010238
104 | 0.0020279 | 0.00050825
105 | 0.0056781 | 0.0014231
106 | 0.0017445 | 0.00043722
107 | 0.0056782 | 0.0014231
108 | 0.016806 | 0.004212
109 | 0.0018766 | 0.00047032

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1