## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_138-26_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_138-26_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_138-26_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_138-26_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_138-26_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_138-26_0_2_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_138-26_0_2_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_138-26_0_2_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_138-26_0_2_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_138-26_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_138-26_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_138-26_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_138-26_0_2_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_138-26_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_138-26_0_2_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_138-26_0_2_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_138-26_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_138-26_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_138-26_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_138-26_0_2_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_138-26_0_2_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_138-26_0_2_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_138-26_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_138-26_0_2_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_138-26_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_138-26_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_138-26_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_138-26_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_138-26_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_138-26_0_2_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_138-26_0_2_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_138-26_0_2_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_138-26_0_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_138-26_0_2_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_138-26_0_2_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_138-26_0_2_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_138-26_0_2_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_138-26_0_2_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_138-26_0_2_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_138-26_0_2_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_138-26_0_2_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_138-26_0_2_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_138-26_0_2_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_138-26_0_2_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_138-26_0_2_node_30 | 0.4 | n |  | TRUE
45 | bus_MV_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_138-26_0_2_load_0 | 0 | 0.00093356 | 0.00023397 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_138-26_0_2_load_1 | 1 | 0.0022207 | 0.00055656 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_138-26_0_2_load_3 | 3 | 0.00018847 | 4.7236e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_138-26_0_2_load_4 | 4 | 0.0014763 | 0.00037 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_138-26_0_2_load_13 | 5 | 0.00019684 | 4.9332e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_138-26_0_2_load_14 | 7 | 0.00019669 | 4.9296e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_138-26_0_2_load_9 | 8 | 0.0030529 | 0.00076513 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_138-26_0_2_load_5 | 9 | 0.0007603 | 0.00019055 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_138-26_0_2_load_6 | 10 | 0.00038259 | 9.5885e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_138-26_0_2_load_32 | 14 | 0.0010747 | 0.00026934 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_138-26_0_2_load_25 | 15 | 0.00028669 | 7.1851e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_138-26_0_2_load_11 | 16 | 0.0010153 | 0.00025446 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_138-26_0_2_load_29 | 17 | 0.001522 | 0.00038146 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_138-26_0_2_load_28 | 19 | 0.0024223 | 0.00060709 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_138-26_0_2_load_27 | 20 | 0.0016006 | 0.00040115 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_138-26_0_2_load_24 | 21 | 0.00021224 | 5.3193e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_138-26_0_2_load_19 | 22 | 0.0001075 | 2.6941e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_138-26_0_2_load_15 | 23 | 0.00022547 | 5.6507e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_138-26_0_2_load_16 | 24 | 0.00012537 | 3.1421e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_138-26_0_2_load_17 | 25 | 0.0002007 | 5.0301e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_138-26_0_2_load_18 | 26 | 0.00071 | 0.00017794 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_138-26_0_2_load_21 | 27 | 0.00065129 | 0.00016323 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_138-26_0_2_load_22 | 28 | 0.00030387 | 7.6158e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_138-26_0_2_load_31 | 29 | 0.0013382 | 0.00033538 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_138-26_0_2_load_26 | 30 | 0.00040534 | 0.00010159 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_138-26_0_2_load_33 | 32 | 0.0013817 | 0.00034628 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_138-26_0_2_load_34 | 33 | 0.00018978 | 4.7564e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_138-26_0_2_load_36 | 35 | 0.0002373 | 5.9472e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_138-26_0_2_load_37 | 36 | 0.00016456 | 4.1244e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_138-26_0_2_load_38 | 37 | 0.00025564 | 6.4069e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_138-26_0_2_load_39 | 38 | 0.00023954 | 6.0033e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_138-26_0_2_load_40 | 40 | 0.0056282 | 0.0014106 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_138-26_0_2_load_41 | 41 | 0.00091873 | 0.00023025 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_138-26_0_2_load_42 | 42 | 0.0014425 | 0.00036153 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_138-26_0_2_load_45 | 43 | 0.0012163 | 0.00030484 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_138-26_0_2_load_30 | 44 | 0.0043362 | 0.0010868 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_138-26_0_2_line_0 |  | 0 | 1 | 0.040184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_138-26_0_2_line_1 |  | 0 | 2 | 0.014694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_138-26_0_2_line_2 |  | 1 | 3 | 0.011107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_138-26_0_2_line_3 |  | 2 | 4 | 0.0090126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_138-26_0_2_line_4 |  | 3 | 5 | 0.010891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_138-26_0_2_line_5 |  | 4 | 6 | 0.01012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_138-26_0_2_line_6 |  | 5 | 7 | 0.0069049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_138-26_0_2_line_7 |  | 6 | 8 | 0.055075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_138-26_0_2_line_8 |  | 6 | 9 | 0.04357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_138-26_0_2_line_9 |  | 7 | 21 | 0.011597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_138-26_0_2_line_10 |  | 8 | 13 | 0.32213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_138-26_0_2_line_11 |  | 9 | 10 | 0.030226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_138-26_0_2_line_12 |  | 10 | 11 | 0.2594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_138-26_0_2_line_13 |  | 11 | 12 | 0.14482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_138-26_0_2_line_14 |  | 12 | 14 | 0.013582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_138-26_0_2_line_15 |  | 12 | 15 | 0.28488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_138-26_0_2_line_16 |  | 13 | 16 | 0.048806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_138-26_0_2_line_17 |  | 14 | 29 | 0.049241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_138-26_0_2_line_18 |  | 15 | 30 | 0.0055309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_138-26_0_2_line_19 |  | 16 | 17 | 0.013105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_138-26_0_2_line_20 |  | 17 | 18 | 0.012091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_138-26_0_2_line_21 |  | 18 | 19 | 0.01718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_138-26_0_2_line_22 |  | 19 | 20 | 0.043553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_138-26_0_2_line_23 |  | 21 | 22 | 0.00045128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_138-26_0_2_line_24 |  | 22 | 25 | 0.0059007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_138-26_0_2_line_25 |  | 23 | 24 | 0.0020057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_138-26_0_2_line_26 |  | 23 | 25 | 0.014515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_138-26_0_2_line_27 |  | 24 | 26 | 0.00040449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_138-26_0_2_line_28 |  | 26 | 27 | 0.0121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_138-26_0_2_line_29 |  | 27 | 28 | 0.0096036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_138-26_0_2_line_30 |  | 29 | 44 | 0.0096808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_138-26_0_2_line_31 |  | 30 | 31 | 0.34507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_138-26_0_2_line_32 |  | 31 | 38 | 0.03961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_138-26_0_2_line_33 |  | 31 | 41 | 0.11629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_138-26_0_2_line_34 |  | 32 | 33 | 0.023988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_138-26_0_2_line_35 |  | 32 | 34 | 0.1774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_138-26_0_2_line_36 |  | 33 | 35 | 0.014936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_138-26_0_2_line_37 |  | 34 | 36 | 0.032904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_138-26_0_2_line_38 |  | 34 | 37 | 0.018589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_138-26_0_2_line_39 |  | 35 | 38 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_138-26_0_2_line_40 |  | 36 | 39 | 0.014274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_138-26_0_2_line_41 |  | 39 | 43 | 0.020415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_138-26_0_2_line_42 |  | 40 | 41 | 0.03303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_138-26_0_2_line_43 |  | 40 | 42 | 0.017452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_138-26_0_2_trafo_25 | 0.63 MVA 20/0.4 kV | 45 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2693632.7979 | 1226893.3454 | 2693632.7979 | 1226893.3454 | 2693619.4248 | 1226931.2384
1 | 2693640.4693 | 1226880.8128 | 2693632.7979 | 1226893.3454
2 | 2693619.4248 | 1226931.2384 | 2693615.7283 | 1226941.7124
3 | 2693640.4693 | 1226880.8128 | 2693632.3945 | 1226876.8097
4 | 2693611.5024 | 1226951.7332 | 2693614.121 | 1226946.2669 | 2693615.7283 | 1226941.7124
5 | 2693623.3278 | 1226872.3148 | 2693632.3945 | 1226876.8097
6 | 2693608.5192 | 1226957.9605 | 2693611.5024 | 1226951.7332
7 | 2693623.3278 | 1226872.3148 | 2693588.5081 | 1226829.6433
8 | 2693623.3278 | 1226872.3148 | 2693580.069 | 1226867.1184
9 | 2693603.5088 | 1226968.4196 | 2693608.5192 | 1226957.9605
10 | 2693320.6028 | 1226651.7143 | 2693569.7828 | 1226811.5183 | 2693584.8723 | 1226825.1876 | 2693588.5081 | 1226829.6433
11 | 2693580.069 | 1226867.1184 | 2693566.7651 | 1226865.5203 | 2693550.6459 | 1226860.6916
12 | 2693293.9165 | 1226848.5577 | 2693407.706 | 1226847.8978 | 2693466.0178 | 1226841.8091 | 2693505.2761 | 1226847.0963 | 2693508.3166 | 1226848.0114 | 2693550.6459 | 1226860.6916
13 | 2693293.9165 | 1226848.5577 | 2693278.4962 | 1226854.976 | 2693196.8675 | 1226874.1551 | 2693183.9593 | 1226875.5539 | 2693170.7151 | 1226874.6904 | 2693152.4701 | 1226872.2363
14 | 2693152.4701 | 1226872.2363 | 2693149.9961 | 1226867.094 | 2693147.8268 | 1226859.5227
15 | 2693152.4701 | 1226872.2363 | 2693189.8725 | 1227154.654
16 | 2693320.6028 | 1226651.7143 | 2693315.0459 | 1226655.1185 | 2693294.4145 | 1226661.2327 | 2693273.6602 | 1226660.4066
17 | 2693147.8268 | 1226859.5227 | 2693142.6292 | 1226841.3826 | 2693139.9271 | 1226838.7051 | 2693135.9707 | 1226837.2199 | 2693133.3167 | 1226837.2784 | 2693114.1427 | 1226841.7411
18 | 2693184.422 | 1227155.5932 | 2693189.8725 | 1227154.654
19 | 2693273.6602 | 1226660.4066 | 2693260.5656 | 1226659.8853
20 | 2693248.503 | 1226659.0893 | 2693256.6116 | 1226659.728 | 2693260.5656 | 1226659.8853
21 | 2693248.503 | 1226659.0893 | 2693231.3737 | 1226657.7636
22 | 2693187.9137 | 1226655.0441 | 2693204.5441 | 1226655.6871 | 2693231.3737 | 1226657.7636
23 | 2693603.3139 | 1226968.8266 | 2693603.5088 | 1226968.4196
24 | 2693600.7646 | 1226974.1482 | 2693603.3139 | 1226968.8266
25 | 2693594.7819 | 1226987.3674 | 2693594.0125 | 1226989.2196
26 | 2693600.7646 | 1226974.1482 | 2693597.0663 | 1226981.8684 | 2693594.7819 | 1226987.3674
27 | 2693593.8573 | 1226989.5931 | 2693594.0125 | 1226989.2196
28 | 2693593.8573 | 1226989.5931 | 2693589.2155 | 1227000.767
29 | 2693585.5312 | 1227009.6358 | 2693589.2155 | 1227000.767
30 | 2693104.7139 | 1226843.9356 | 2693114.1427 | 1226841.7411
31 | 2693184.422 | 1227155.5932 | 2692999.2631 | 1227446.7808
32 | 2692999.2631 | 1227446.7808 | 2693001.3447 | 1227472.1535 | 2693007.4884 | 1227484.9021
33 | 2692999.2631 | 1227446.7808 | 2692914.9204 | 1227424.8698 | 2692886.3987 | 1227418.8827
34 | 2693047.0844 | 1227485.7338 | 2693038.9479 | 1227485.6065 | 2693024.9175 | 1227492.9809
35 | 2693168.4857 | 1227596.0008 | 2693159.325 | 1227583.7375 | 2693136.3212 | 1227547.0069 | 2693124.337 | 1227524.3476 | 2693112.5411 | 1227502.7254 | 2693087.3602 | 1227491.2455 | 2693061.6351 | 1227485.9616 | 2693047.0844 | 1227485.7338
36 | 2693024.9175 | 1227492.9809 | 2693020.1098 | 1227495.5079 | 2693013.4062 | 1227497.1821 | 2693012.2794 | 1227494.844
37 | 2693168.4857 | 1227596.0008 | 2693172.3978 | 1227601.2436 | 2693178.6873 | 1227626.8447
38 | 2693168.4857 | 1227596.0008 | 2693186.2305 | 1227590.4614
39 | 2693012.2794 | 1227494.844 | 2693007.4884 | 1227484.9021
40 | 2693188.3848 | 1227636.3967 | 2693179.5083 | 1227630.1866 | 2693178.6873 | 1227626.8447
41 | 2693188.3848 | 1227636.3967 | 2693167.9581 | 1227634.9869
42 | 2692854.0728 | 1227412.0972 | 2692886.3987 | 1227418.8827
43 | 2692854.0728 | 1227412.0972 | 2692848.3634 | 1227410.8987 | 2692836.8657 | 1227409.2308

## bus_geodata
| x | y | coords
0 | 2693632.7979 | 1226893.3454
1 | 2693619.4248 | 1226931.2384
2 | 2693640.4693 | 1226880.8128
3 | 2693615.7283 | 1226941.7124
4 | 2693632.3945 | 1226876.8097
5 | 2693611.5024 | 1226951.7332
6 | 2693623.3278 | 1226872.3148
7 | 2693608.5192 | 1226957.9605
8 | 2693588.5081 | 1226829.6433
9 | 2693580.069 | 1226867.1184
10 | 2693550.6459 | 1226860.6916
11 | 2693293.9165 | 1226848.5577
12 | 2693152.4701 | 1226872.2363
13 | 2693320.6028 | 1226651.7143
14 | 2693147.8268 | 1226859.5227
15 | 2693189.8725 | 1227154.654
16 | 2693273.6602 | 1226660.4066
17 | 2693260.5656 | 1226659.8853
18 | 2693248.503 | 1226659.0893
19 | 2693231.3737 | 1226657.7636
20 | 2693187.9137 | 1226655.0441
21 | 2693603.5088 | 1226968.4196
22 | 2693603.3139 | 1226968.8266
23 | 2693594.7819 | 1226987.3674
24 | 2693594.0125 | 1226989.2196
25 | 2693600.7646 | 1226974.1482
26 | 2693593.8573 | 1226989.5931
27 | 2693589.2155 | 1227000.767
28 | 2693585.5312 | 1227009.6358
29 | 2693114.1427 | 1226841.7411
30 | 2693184.422 | 1227155.5932
31 | 2692999.2631 | 1227446.7808
32 | 2693047.0844 | 1227485.7339
33 | 2693024.9175 | 1227492.9809
34 | 2693168.4857 | 1227596.0008
35 | 2693012.2794 | 1227494.844
36 | 2693178.6873 | 1227626.8447
37 | 2693186.2305 | 1227590.4614
38 | 2693007.4884 | 1227484.9021
39 | 2693188.3848 | 1227636.3967
40 | 2692854.0728 | 1227412.0972
41 | 2692886.3987 | 1227418.8827
42 | 2692836.8657 | 1227409.2308
43 | 2693167.9581 | 1227634.9869
44 | 2693104.7139 | 1226843.9356
45 | 2693189.8725 | 1227154.654

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98508 | -0.28721 | 0.00093356 | 0.00023397
1 | 0.98488 | -0.29107 | 0.0022207 | 0.00055656
2 | 0.98516 | -0.28556 | 0 | 0
3 | 0.98485 | -0.29169 | 0.00018847 | 4.7236e-05
4 | 0.98522 | -0.28454 | 0.0014763 | 0.00037
5 | 0.98482 | -0.29227 | 0.00019684 | 4.9332e-05
6 | 0.98529 | -0.28313 | 0 | 0
7 | 0.9848 | -0.29261 | 0.00019669 | 4.9296e-05
8 | 0.9848 | -0.29266 | 0.0030529 | 0.00076513
9 | 0.98599 | -0.26954 | 0.0007603 | 0.00019055
10 | 0.98649 | -0.25971 | 0.00038259 | 9.5885e-05
11 | 0.99091 | -0.174 | 0 | 0
12 | 0.99338 | -0.12645 | 0 | 0
13 | 0.98285 | -0.33077 | 0 | 0
14 | 0.9933 | -0.12807 | 0.0010747 | 0.00026934
15 | 1 | 0 | -0.03935 | -0.0095605
16 | 0.98256 | -0.33655 | 0.0010153 | 0.00025446
17 | 0.98249 | -0.33786 | 0.001522 | 0.00038146
18 | 0.98244 | -0.33874 | 0 | 0
19 | 0.98238 | -0.33999 | 0.0024223 | 0.00060709
20 | 0.98232 | -0.34125 | 0.0016006 | 0.00040115
21 | 0.98478 | -0.29314 | 0.00021224 | 5.3193e-05
22 | 0.98478 | -0.29316 | 0.0001075 | 2.6941e-05
23 | 0.98474 | -0.29392 | 0.00022547 | 5.6507e-05
24 | 0.98473 | -0.29398 | 0.00012537 | 3.1421e-05
25 | 0.98476 | -0.29339 | 0.0002007 | 5.0301e-05
26 | 0.98473 | -0.29399 | 0.00071 | 0.00017794
27 | 0.98472 | -0.2942 | 0.00065129 | 0.00016323
28 | 0.98472 | -0.29425 | 0.00030387 | 7.6158e-05
29 | 0.99304 | -0.13301 | 0.0013382 | 0.00033538
30 | 0.99994 | -0.0011673 | 0.00040534 | 0.00010159
31 | 0.99627 | -0.071788 | 0 | 0
32 | 0.99599 | -0.077149 | 0.0013817 | 0.00034628
33 | 0.99606 | -0.075873 | 0.00018978 | 4.7564e-05
34 | 0.99573 | -0.082269 | 0 | 0
35 | 0.9961 | -0.075029 | 0.0002373 | 5.9472e-05
36 | 0.99569 | -0.083069 | 0.00016456 | 4.1244e-05
37 | 0.99573 | -0.082353 | 0.00025564 | 6.4069e-05
38 | 0.99614 | -0.074359 | 0.00023954 | 6.0033e-05
39 | 0.99567 | -0.083374 | 0 | 0
40 | 0.99521 | -0.092233 | 0.0056282 | 0.0014106
41 | 0.99542 | -0.088123 | 0.00091873 | 0.00023025
42 | 0.99519 | -0.092676 | 0.0014425 | 0.00036153
43 | 0.99565 | -0.083811 | 0.0012163 | 0.00030484
44 | 0.99301 | -0.13375 | 0.0043362 | 0.0010868
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0053405 | 0.0013374 | -0.0053395 | -0.0013373 | 9.8058e-07 | 1.1611e-07 | 0.0080667 | 0.0080669 | 0.0080669 | 0.98508 | -0.28721 | 0.98488 | -0.29107 | 2.2162
1 | -0.006274 | -0.0015714 | 0.0062745 | 0.0015715 | 4.9489e-07 | 1.2964e-07 | 0.0094769 | 0.0094768 | 0.0094769 | 0.98508 | -0.28721 | 0.98516 | -0.28556 | 2.6035
2 | 0.0031188 | 0.00078071 | -0.0031187 | -0.00078079 | 9.247e-08 | -8.216e-08 | 0.0047118 | 0.0047118 | 0.0047118 | 0.98488 | -0.29107 | 0.98485 | -0.29169 | 1.2945
3 | -0.0062745 | -0.0015715 | 0.0062748 | 0.0015716 | 3.0353e-07 | 7.9498e-08 | 0.0094768 | 0.0094768 | 0.0094768 | 0.98516 | -0.28556 | 0.98522 | -0.28454 | 2.6035
4 | 0.0029303 | 0.00073355 | -0.0029302 | -0.00073364 | 8.0044e-08 | -8.7353e-08 | 0.004427 | 0.0044271 | 0.0044271 | 0.98485 | -0.29169 | 0.98482 | -0.29227 | 1.2162
5 | -0.0077512 | -0.0019416 | 0.0077517 | 0.0019418 | 5.2007e-07 | 2.0396e-07 | 0.011707 | 0.011707 | 0.011707 | 0.98522 | -0.28454 | 0.98529 | -0.28313 | 3.2161
6 | 0.0027333 | 0.00068431 | -0.0027333 | -0.00068437 | 4.4159e-08 | -5.9594e-08 | 0.0041297 | 0.0041297 | 0.0041297 | 0.98482 | -0.29227 | 0.9848 | -0.29261 | 1.1345
7 | 0.0096321 | 0.0024149 | -0.0096277 | -0.0024128 | 4.3706e-06 | 2.0961e-06 | 0.014547 | 0.014547 | 0.014547 | 0.98529 | -0.28313 | 0.9848 | -0.29266 | 3.9965
8 | -0.017384 | -0.0043567 | 0.017395 | 0.0043633 | 1.1261e-05 | 6.6519e-06 | 0.026254 | 0.026253 | 0.026254 | 0.98529 | -0.28313 | 0.98599 | -0.26954 | 7.2125
9 | 0.0025366 | 0.00063507 | -0.0025365 | -0.00063518 | 6.3879e-08 | -1.0667e-07 | 0.0038325 | 0.0038326 | 0.0038326 | 0.9848 | -0.29261 | 0.98478 | -0.29314 | 1.0529
10 | 0.0065748 | 0.0016477 | -0.0065629 | -0.0016441 | 1.1924e-05 | 3.5406e-06 | 0.0099344 | 0.0099359 | 0.0099359 | 0.9848 | -0.29266 | 0.98285 | -0.33077 | 2.7296
11 | -0.018155 | -0.0045539 | 0.018164 | 0.0045589 | 8.5102e-06 | 5.0608e-06 | 0.027401 | 0.027401 | 0.027401 | 0.98599 | -0.26954 | 0.98649 | -0.25971 | 7.5277
12 | -0.018546 | -0.0046548 | 0.018623 | 0.0047002 | 7.6138e-05 | 4.5402e-05 | 0.027978 | 0.027977 | 0.027978 | 0.98649 | -0.25971 | 0.99091 | -0.174 | 7.6862
13 | -0.018623 | -0.0047002 | 0.018665 | 0.0047256 | 4.2504e-05 | 2.5332e-05 | 0.027977 | 0.027976 | 0.027977 | 0.99091 | -0.174 | 0.99338 | -0.12645 | 7.6859
14 | 0.0067511 | 0.0016918 | -0.0067506 | -0.0016917 | 5.2088e-07 | 1.5753e-07 | 0.010113 | 0.010113 | 0.010113 | 0.99338 | -0.12645 | 0.9933 | -0.12807 | 2.7782
15 | -0.025416 | -0.0064174 | 0.025571 | 0.0065129 | 0.00015498 | 9.5473e-05 | 0.038088 | 0.038087 | 0.038088 | 0.99338 | -0.12645 | 1 | 0 | 10.4638
16 | 0.0065629 | 0.0016441 | -0.0065611 | -0.0016436 | 1.8068e-06 | 5.3805e-07 | 0.0099359 | 0.0099361 | 0.0099361 | 0.98285 | -0.33077 | 0.98256 | -0.33655 | 2.7297
17 | 0.0056759 | 0.0014223 | -0.0056745 | -0.0014221 | 1.335e-06 | 2.1719e-07 | 0.0085027 | 0.0085029 | 0.0085029 | 0.9933 | -0.12807 | 0.99304 | -0.13301 | 2.336
18 | 0.012129 | 0.0030475 | -0.012128 | -0.0030471 | 6.7577e-07 | 3.5994e-07 | 0.01805 | 0.01805 | 0.01805 | 1 | 0 | 0.99994 | -0.0011673 | 4.9589
19 | 0.0055458 | 0.0013892 | -0.0055455 | -0.0013891 | 3.4664e-07 | 5.5876e-08 | 0.0083985 | 0.0083985 | 0.0083985 | 0.98256 | -0.33655 | 0.98249 | -0.33786 | 2.3073
20 | 0.0040234 | 0.0010076 | -0.0040232 | -0.0010077 | 1.6835e-07 | -4.5368e-08 | 0.0060933 | 0.0060934 | 0.0060934 | 0.98249 | -0.33786 | 0.98244 | -0.33874 | 1.674
21 | 0.0040232 | 0.0010077 | -0.004023 | -0.0010077 | 2.3922e-07 | -6.4438e-08 | 0.0060934 | 0.0060935 | 0.0060935 | 0.98244 | -0.33874 | 0.98238 | -0.33999 | 1.674
22 | 0.0016007 | 0.00040066 | -0.0016006 | -0.00040115 | 9.6005e-08 | -4.8994e-07 | 0.0024244 | 0.0024246 | 0.0024246 | 0.98238 | -0.33999 | 0.98232 | -0.34125 | 0.6661
23 | 0.0023243 | 0.00058199 | -0.0023243 | -0.00058199 | 2.0869e-09 | -4.4057e-09 | 0.0035119 | 0.0035119 | 0.0035119 | 0.98478 | -0.29314 | 0.98478 | -0.29316 | 0.9648
24 | 0.0022168 | 0.00055505 | -0.0022168 | -0.00055511 | 2.4825e-08 | -5.9186e-08 | 0.0033494 | 0.0033495 | 0.0033495 | 0.98478 | -0.29316 | 0.98476 | -0.29339 | 0.92018
25 | 0.0017905 | 0.00044845 | -0.0017905 | -0.00044848 | 5.5057e-09 | -2.1992e-08 | 0.0027056 | 0.0027056 | 0.0027056 | 0.98474 | -0.29392 | 0.98473 | -0.29398 | 0.74329
26 | -0.002016 | -0.00050496 | 0.0020161 | 0.00050481 | 5.0509e-08 | -1.5234e-07 | 0.0030463 | 0.0030462 | 0.0030463 | 0.98474 | -0.29392 | 0.98476 | -0.29339 | 0.83688
27 | 0.0016652 | 0.00041705 | -0.0016652 | -0.00041706 | 9.6031e-10 | -4.5312e-09 | 0.0025161 | 0.0025161 | 0.0025161 | 0.98473 | -0.29398 | 0.98473 | -0.29399 | 0.69124
28 | 0.00095517 | 0.00023912 | -0.00095516 | -0.00023926 | 9.4516e-09 | -1.4788e-07 | 0.0014433 | 0.0014433 | 0.0014433 | 0.98473 | -0.29399 | 0.98472 | -0.2942 | 0.39651
29 | 0.00030387 | 7.6036e-05 | -0.00030387 | -7.6158e-05 | 7.5927e-10 | -1.2169e-07 | 0.00045914 | 0.00045919 | 0.00045919 | 0.98472 | -0.2942 | 0.98472 | -0.29425 | 0.12615
30 | 0.0043363 | 0.0010867 | -0.0043362 | -0.0010868 | 1.5327e-07 | -2.7145e-08 | 0.0064977 | 0.0064978 | 0.0064978 | 0.99304 | -0.13301 | 0.99301 | -0.13375 | 1.7851
31 | 0.011723 | 0.0029455 | -0.011683 | -0.0029248 | 3.9394e-05 | 2.0702e-05 | 0.017447 | 0.017449 | 0.017449 | 0.99994 | -0.0011673 | 0.99627 | -0.071788 | 4.7936
32 | 0.0036862 | 0.00091978 | -0.0036857 | -0.00092001 | 4.5002e-07 | -2.277e-07 | 0.0055042 | 0.0055044 | 0.0055044 | 0.99627 | -0.071788 | 0.99614 | -0.074359 | 1.5122
33 | 0.0079971 | 0.0020051 | -0.0079909 | -0.0020026 | 6.2219e-06 | 2.4691e-06 | 0.011945 | 0.011945 | 0.011945 | 0.99627 | -0.071788 | 0.99542 | -0.088123 | 3.2816
34 | -0.0030187 | -0.00075332 | 0.0030189 | 0.00075312 | 1.8287e-07 | -1.9517e-07 | 0.0045088 | 0.0045087 | 0.0045088 | 0.99599 | -0.077149 | 0.99606 | -0.075873 | 1.2387
35 | 0.001637 | 0.00040704 | -0.0016366 | -0.00040909 | 3.9767e-07 | -2.0536e-06 | 0.0024446 | 0.0024454 | 0.0024454 | 0.99599 | -0.077149 | 0.99573 | -0.082269 | 0.6718
36 | -0.0032087 | -0.00080069 | 0.0032088 | 0.00080058 | 1.2863e-07 | -1.121e-07 | 0.0047922 | 0.0047921 | 0.0047922 | 0.99606 | -0.075873 | 0.9961 | -0.075029 | 1.3165
37 | 0.001381 | 0.00034526 | -0.0013809 | -0.00034566 | 5.254e-08 | -3.9435e-07 | 0.0020634 | 0.0020636 | 0.0020636 | 0.99573 | -0.082269 | 0.99569 | -0.083069 | 0.56692
38 | 0.00025564 | 6.3828e-05 | -0.00025564 | -6.4069e-05 | 1.0172e-09 | -2.4115e-07 | 0.00038194 | 0.00038203 | 0.00038203 | 0.99573 | -0.082269 | 0.99573 | -0.082353 | 0.10495
39 | -0.0034461 | -0.00086005 | 0.0034462 | 0.00085997 | 1.0962e-07 | -7.3508e-08 | 0.0051466 | 0.0051466 | 0.0051466 | 0.9961 | -0.075029 | 0.99614 | -0.074359 | 1.4139
40 | 0.0012164 | 0.00030441 | -0.0012163 | -0.00030459 | 1.7686e-08 | -1.7434e-07 | 0.0018176 | 0.0018177 | 0.0018177 | 0.99569 | -0.083069 | 0.99567 | -0.083374 | 0.49937
41 | 0.0012163 | 0.00030459 | -0.0012163 | -0.00030484 | 2.5296e-08 | -2.4932e-07 | 0.0018177 | 0.0018178 | 0.0018178 | 0.99567 | -0.083374 | 0.99565 | -0.083811 | 0.4994
42 | -0.0070708 | -0.0017719 | 0.0070721 | 0.0017723 | 1.3844e-06 | 4.567e-07 | 0.010572 | 0.010572 | 0.010572 | 0.99521 | -0.092233 | 0.99542 | -0.088123 | 2.9044
43 | 0.0014426 | 0.00036132 | -0.0014425 | -0.00036153 | 3.0444e-08 | -2.0728e-07 | 0.0021568 | 0.0021569 | 0.0021569 | 0.99521 | -0.092233 | 0.99519 | -0.092676 | 0.59255

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.039636 | 0.0096323

## res_load
| p_mw | q_mvar
0 | 0.00093356 | 0.00023397
1 | 0.0022207 | 0.00055656
2 | 0.00018847 | 4.7236e-05
3 | 0.0014763 | 0.00037
4 | 0.00019684 | 4.9332e-05
5 | 0.00019669 | 4.9296e-05
6 | 0.0030529 | 0.00076513
7 | 0.0007603 | 0.00019055
8 | 0.00038259 | 9.5885e-05
9 | 0.0010747 | 0.00026934
10 | 0.00028669 | 7.1851e-05
11 | 0.0010153 | 0.00025446
12 | 0.001522 | 0.00038146
13 | 0.0024223 | 0.00060709
14 | 0.0016006 | 0.00040115
15 | 0.00021224 | 5.3193e-05
16 | 0.0001075 | 2.6941e-05
17 | 0.00022547 | 5.6507e-05
18 | 0.00012537 | 3.1421e-05
19 | 0.0002007 | 5.0301e-05
20 | 0.00071 | 0.00017794
21 | 0.00065129 | 0.00016323
22 | 0.00030387 | 7.6158e-05
23 | 0.0013382 | 0.00033538
24 | 0.00040534 | 0.00010159
25 | 0.0013817 | 0.00034628
26 | 0.00018978 | 4.7564e-05
27 | 0.0002373 | 5.9472e-05
28 | 0.00016456 | 4.1244e-05
29 | 0.00025564 | 6.4069e-05
30 | 0.00023954 | 6.0033e-05
31 | 0.0056282 | 0.0014106
32 | 0.00091873 | 0.00023025
33 | 0.0014425 | 0.00036153
34 | 0.0012163 | 0.00030484
35 | 0.0043362 | 0.0010868

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1