## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_139-13_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_139-13_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_139-13_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_139-13_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_139-13_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_139-13_0_5_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_139-13_0_5_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_139-13_0_5_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_139-13_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_139-13_0_5_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_139-13_0_5_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_139-13_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_139-13_0_5_node_51 | 0.4 | n |  | TRUE
13 | bus_LV_139-13_0_5_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_139-13_0_5_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_139-13_0_5_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_139-13_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_139-13_0_5_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_139-13_0_5_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_139-13_0_5_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_139-13_0_5_node_4 | 0.4 | n |  | TRUE
21 | bus_LV_139-13_0_5_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_139-13_0_5_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_139-13_0_5_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_139-13_0_5_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_139-13_0_5_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_139-13_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_139-13_0_5_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_139-13_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_139-13_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_139-13_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_139-13_0_5_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_139-13_0_5_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_139-13_0_5_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_139-13_0_5_node_50 | 0.4 | n |  | TRUE
35 | bus_MV_360_0_node_181 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_139-13_0_5_load_0 | 0 | 0.0033167 | 0.00083124 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_139-13_0_5_load_1 | 1 | 0.00012678 | 3.1774e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_139-13_0_5_load_3 | 4 | 0.00013429 | 3.3656e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_139-13_0_5_load_30 | 6 | 0.013865 | 0.003475 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_139-13_0_5_load_37 | 7 | 0.027528 | 0.0068993 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_139-13_0_5_load_34 | 9 | 0.0012899 | 0.00032327 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_139-13_0_5_load_32 | 10 | 0.0030535 | 0.00076527 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_139-13_0_5_load_51 | 12 | 0.02059 | 0.0051604 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_139-13_0_5_load_48 | 14 | 0.010053 | 0.0025196 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_139-13_0_5_load_54 | 15 | 0.042225 | 0.010583 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_139-13_0_5_load_52 | 17 | 0.00020162 | 5.053e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_139-13_0_5_load_55 | 18 | 0.010657 | 0.002671 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_139-13_0_5_load_56 | 19 | 0.086809 | 0.021757 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_139-13_0_5_load_4 | 20 | 0.00059987 | 0.00015034 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_139-13_0_5_load_22 | 21 | 0.0047261 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_139-13_0_5_load_33 | 22 | 0.0013026 | 0.00032647 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_139-13_0_5_load_49 | 23 | 0.030002 | 0.0075193 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_139-13_0_5_load_23 | 26 | 0.0027726 | 0.00069487 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_139-13_0_5_load_38 | 27 | 0.078831 | 0.019757 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_139-13_0_5_load_18 | 28 | 0.0019033 | 0.00047701 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_139-13_0_5_load_19 | 29 | 0.001449 | 0.00036315 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_139-13_0_5_load_20 | 30 | 0.0021201 | 0.00053134 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_139-13_0_5_load_24 | 31 | 0.0018112 | 0.00045392 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_139-13_0_5_load_36 | 32 | 0.087483 | 0.021925 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_139-13_0_5_load_35 | 33 | 0.0020183 | 0.00050584 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_139-13_0_5_load_50 | 34 | 0.081596 | 0.02045 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_139-13_0_5_line_0 |  | 0 | 1 | 0.077297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_139-13_0_5_line_1 |  | 1 | 2 | 0.018029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_139-13_0_5_line_2 |  | 2 | 3 | 0.14056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_139-13_0_5_line_3 |  | 2 | 4 | 0.033042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_139-13_0_5_line_4 |  | 3 | 5 | 0.1315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_139-13_0_5_line_5 |  | 3 | 6 | 0.0076075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_139-13_0_5_line_6 |  | 3 | 7 | 0.045498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_139-13_0_5_line_7 |  | 4 | 20 | 0.09618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_139-13_0_5_line_8 |  | 5 | 16 | 0.003756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_139-13_0_5_line_9 |  | 5 | 17 | 0.048926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_139-13_0_5_line_10 |  | 7 | 33 | 0.016403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_139-13_0_5_line_11 |  | 8 | 9 | 0.016684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_139-13_0_5_line_12 |  | 8 | 10 | 0.023353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_139-13_0_5_line_13 |  | 9 | 21 | 0.052206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_139-13_0_5_line_14 |  | 10 | 22 | 0.028819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_139-13_0_5_line_15 |  | 11 | 12 | 0.038441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_139-13_0_5_line_16 |  | 11 | 13 | 0.017437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_139-13_0_5_line_17 |  | 11 | 14 | 0.024001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_139-13_0_5_line_18 |  | 11 | 15 | 0.054404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_139-13_0_5_line_19 |  | 13 | 19 | 0.038318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_139-13_0_5_line_20 |  | 14 | 23 | 0.017635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_139-13_0_5_line_21 |  | 15 | 25 | 0.036888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_139-13_0_5_line_22 |  | 16 | 18 | 0.018847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_139-13_0_5_line_23 |  | 21 | 30 | 0.0048099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_139-13_0_5_line_24 |  | 23 | 34 | 0.00038097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_139-13_0_5_line_25 |  | 24 | 25 | 0.118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_139-13_0_5_line_26 |  | 24 | 26 | 0.042554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_139-13_0_5_line_27 |  | 25 | 27 | 0.010242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_139-13_0_5_line_28 |  | 26 | 31 | 0.042738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_139-13_0_5_line_29 |  | 26 | 29 | 0.048261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_139-13_0_5_line_30 |  | 27 | 32 | 0.00085805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_139-13_0_5_line_31 |  | 28 | 29 | 0.0078897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_139-13_0_5_line_32 |  | 28 | 30 | 0.031893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_139-13_0_5_line_33 |  | 32 | 33 | 0.021892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_139-13_0_5_trafo_14 | 0.63 MVA 20/0.4 kV | 35 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2683841.055 | 1240745.0371 | 2683830.709 | 1240737.9106 | 2683793.2184 | 1240718.4562 | 2683773.0366 | 1240708.5175
1 | 2683756.8627 | 1240700.5526 | 2683773.0366 | 1240708.5175
2 | 2683686.4356 | 1240590.1357 | 2683683.4698 | 1240593.9855 | 2683685.993 | 1240597.3902 | 2683723.705 | 1240627.4879 | 2683744.037 | 1240652.3481 | 2683754.3007 | 1240669.9055 | 2683755.7975 | 1240683.87 | 2683756.8627 | 1240700.5526
3 | 2683756.8627 | 1240700.5526 | 2683756.6909 | 1240728.7927 | 2683756.8946 | 1240733.5894
4 | 2683591.3176 | 1240550.3449 | 2683642.4911 | 1240541.3036 | 2683656.9753 | 1240540.6071 | 2683661.614 | 1240557.0287 | 2683666.5649 | 1240567.9285 | 2683676.0337 | 1240584.4961 | 2683683.4698 | 1240593.9855 | 2683686.4356 | 1240590.1357
5 | 2683686.4356 | 1240590.1357 | 2683681.8678 | 1240584.052
6 | 2683686.4356 | 1240590.1357 | 2683725.4621 | 1240566.7468
7 | 2683756.8946 | 1240733.5894 | 2683757.826 | 1240755.5168 | 2683765.3664 | 1240829.3652
8 | 2683591.3176 | 1240550.3449 | 2683590.0363 | 1240546.8132
9 | 2683591.3176 | 1240550.3449 | 2683575.5161 | 1240552.2127 | 2683542.5177 | 1240551.168
10 | 2683725.4621 | 1240566.7468 | 2683730.7455 | 1240559.972 | 2683733.118 | 1240554.2236 | 2683733.5893 | 1240552.7026
11 | 2683860.0382 | 1240651.0178 | 2683858.7469 | 1240635.3661 | 2683858.823 | 1240634.3896
12 | 2683860.0382 | 1240651.0178 | 2683883.1573 | 1240647.7198 | 2683883.1573 | 1240647.7198
13 | 2683874.3602 | 1240585.0792 | 2683866.5295 | 1240603.1973 | 2683859.9204 | 1240620.294 | 2683858.823 | 1240634.3896
14 | 2683910.6411 | 1240654.7915 | 2683907.3575 | 1240652.9989 | 2683898.9605 | 1240649.4554 | 2683891.4656 | 1240647.904 | 2683883.1573 | 1240647.7198
15 | 2683692.4411 | 1240473.7255 | 2683695.4191 | 1240467.9411 | 2683712.5011 | 1240440.9585
16 | 2683680.5212 | 1240483.4756 | 2683683.7604 | 1240480.0855 | 2683684.6815 | 1240479.12 | 2683689.3853 | 1240479.6645 | 2683692.4411 | 1240473.7255
17 | 2683692.4411 | 1240473.7255 | 2683672.3308 | 1240460.6244
18 | 2683692.4411 | 1240473.7255 | 2683745.698 | 1240484.84
19 | 2683680.5212 | 1240483.4756 | 2683670.9148 | 1240498.1063 | 2683653.3937 | 1240486.7624
20 | 2683672.3308 | 1240460.6244 | 2683657.5551 | 1240450.9986
21 | 2683743.3549 | 1240521.1886 | 2683745.9281 | 1240511.9405 | 2683747.2775 | 1240503.131 | 2683747.062 | 1240496.4342 | 2683745.698 | 1240484.84
22 | 2683581.8445 | 1240530.2972 | 2683586.6247 | 1240535.6127 | 2683590.0363 | 1240546.8132
23 | 2683874.3602 | 1240585.0792 | 2683876.2684 | 1240580.6641
24 | 2683657.2359 | 1240450.7907 | 2683657.5551 | 1240450.9986
25 | 2683743.3549 | 1240521.1886 | 2683774.3653 | 1240541.7631 | 2683795.5633 | 1240552.4255 | 2683797.6065 | 1240553.3994 | 2683808.085 | 1240558.4287 | 2683811.5381 | 1240561.3129 | 2683815.1648 | 1240562.6095 | 2683819.0702 | 1240562.3866 | 2683822.187 | 1240561.7747 | 2683840.6367 | 1240541.0758
26 | 2683840.6367 | 1240541.0758 | 2683847.7907 | 1240531.4477 | 2683863.9306 | 1240505.4986
27 | 2683743.3549 | 1240521.1886 | 2683740.3234 | 1240530.9715
28 | 2683886.7949 | 1240469.3915 | 2683867.9257 | 1240499.0755 | 2683863.9306 | 1240505.4986
29 | 2683892.5164 | 1240544.3833 | 2683863.9306 | 1240505.4986
30 | 2683740.0694 | 1240531.7911 | 2683740.3234 | 1240530.9715
31 | 2683888.9213 | 1240551.3885 | 2683890.4216 | 1240547.9173 | 2683892.5164 | 1240544.3833
32 | 2683888.9213 | 1240551.3885 | 2683876.2684 | 1240580.6641
33 | 2683733.5893 | 1240552.7026 | 2683740.0694 | 1240531.7911

## bus_geodata
| x | y | coords
0 | 2683841.055 | 1240745.0371
1 | 2683773.0366 | 1240708.5175
2 | 2683756.8627 | 1240700.5526
3 | 2683686.4356 | 1240590.1357
4 | 2683756.8946 | 1240733.5894
5 | 2683591.3176 | 1240550.3449
6 | 2683681.8678 | 1240584.052
7 | 2683725.4621 | 1240566.7468
8 | 2683860.0382 | 1240651.0178
9 | 2683858.823 | 1240634.3896
10 | 2683883.1573 | 1240647.7198
11 | 2683692.4411 | 1240473.7255
12 | 2683712.5011 | 1240440.9585
13 | 2683680.5212 | 1240483.4756
14 | 2683672.3308 | 1240460.6244
15 | 2683745.698 | 1240484.84
16 | 2683590.0363 | 1240546.8132
17 | 2683542.5177 | 1240551.168
18 | 2683581.8445 | 1240530.2972
19 | 2683653.3937 | 1240486.7624
20 | 2683765.3664 | 1240829.3652
21 | 2683874.3602 | 1240585.0792
22 | 2683910.6411 | 1240654.7915
23 | 2683657.5551 | 1240450.9986
24 | 2683840.6367 | 1240541.0758
25 | 2683743.3549 | 1240521.1886
26 | 2683863.9306 | 1240505.4986
27 | 2683740.3234 | 1240530.9715
28 | 2683888.9213 | 1240551.3885
29 | 2683892.5164 | 1240544.3833
30 | 2683876.2684 | 1240580.6641
31 | 2683886.7949 | 1240469.3915
32 | 2683740.0694 | 1240531.7911
33 | 2683733.5893 | 1240552.7026
34 | 2683657.2359 | 1240450.7907
35 | 2683689.3853 | 1240479.6645

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.988 | -0.2313 | 0.0033167 | 0.00083124
1 | 0.98824 | -0.22673 | 0.00012678 | 3.1774e-05
2 | 0.98829 | -0.22562 | 0 | 0
3 | 0.98883 | -0.21512 | 0 | 0
4 | 0.98827 | -0.22605 | 0.00013429 | 3.3656e-05
5 | 0.98752 | -0.24062 | 0 | 0
6 | 0.98874 | -0.217 | 0.013865 | 0.003475
7 | 0.99004 | -0.19169 | 0.027528 | 0.0068993
8 | 0.98808 | -0.22968 | 0 | 0
9 | 0.98815 | -0.22838 | 0.0012899 | 0.00032327
10 | 0.98799 | -0.2315 | 0.0030535 | 0.00076527
11 | 0.99829 | -0.032706 | 0 | 0
12 | 0.99757 | -0.046559 | 0.02059 | 0.0051604
13 | 1 | 0 | -0.52131 | -0.13146
14 | 0.99562 | -0.083908 | 0.010053 | 0.0025196
15 | 0.99471 | -0.10133 | 0.042225 | 0.010583
16 | 0.98748 | -0.24133 | 0 | 0
17 | 0.98751 | -0.2408 | 0.00020162 | 5.053e-05
18 | 0.9873 | -0.24492 | 0.010657 | 0.002671
19 | 0.99697 | -0.058153 | 0.086809 | 0.021757
20 | 0.98822 | -0.22708 | 0.00059987 | 0.00015034
21 | 0.98842 | -0.22312 | 0.0047261 | 0.0011845
22 | 0.98795 | -0.23217 | 0.0013026 | 0.00032647
23 | 0.99383 | -0.11857 | 0.030002 | 0.0075193
24 | 0.99043 | -0.18401 | 0 | 0
25 | 0.99264 | -0.14125 | 0 | 0
26 | 0.98964 | -0.19947 | 0.0027726 | 0.00069487
27 | 0.99212 | -0.15144 | 0.078831 | 0.019757
28 | 0.98883 | -0.21512 | 0.0019033 | 0.00047701
29 | 0.98893 | -0.2131 | 0.001449 | 0.00036315
30 | 0.98846 | -0.22223 | 0.0021201 | 0.00053134
31 | 0.98956 | -0.20085 | 0.0018112 | 0.00045392
32 | 0.99206 | -0.15255 | 0.087483 | 0.021925
33 | 0.99089 | -0.17524 | 0.0020183 | 0.00050584
34 | 0.9938 | -0.11912 | 0.081596 | 0.02045
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0033167 | -0.00083124 | 0.0033174 | 0.00083071 | 7.2322e-07 | -5.2727e-07 | 0.0049952 | 0.0049949 | 0.0049952 | 0.988 | -0.2313 | 0.98824 | -0.22673 | 1.3723
1 | -0.0034442 | -0.00086249 | 0.0034444 | 0.00086237 | 1.8181e-07 | -1.1465e-07 | 0.0051858 | 0.0051857 | 0.0051858 | 0.98824 | -0.22673 | 0.98829 | -0.22562 | 1.4247
2 | -0.0041786 | -0.0010447 | 0.0041807 | 0.0010443 | 2.0856e-06 | -4.6734e-07 | 0.0062906 | 0.0062899 | 0.0062906 | 0.98829 | -0.22562 | 0.98883 | -0.21512 | 1.7282
3 | 0.00073421 | 0.00018237 | -0.00073419 | -0.00018278 | 1.5128e-08 | -4.137e-07 | 0.0011049 | 0.001105 | 0.001105 | 0.98829 | -0.22562 | 0.98827 | -0.22605 | 0.30358
4 | 0.010874 | 0.0027287 | -0.010861 | -0.002722 | 1.3207e-05 | 6.7679e-06 | 0.016365 | 0.016366 | 0.016366 | 0.98883 | -0.21512 | 0.98752 | -0.24062 | 4.496
5 | 0.013867 | 0.0034757 | -0.013865 | -0.003475 | 1.2422e-06 | 6.9743e-07 | 0.020867 | 0.020867 | 0.020867 | 0.98883 | -0.21512 | 0.98874 | -0.217 | 5.7327
6 | -0.028922 | -0.0072487 | 0.028954 | 0.0072688 | 3.2318e-05 | 2.0099e-05 | 0.043522 | 0.043522 | 0.043522 | 0.98883 | -0.21512 | 0.99004 | -0.19169 | 11.9566
7 | 0.0005999 | 0.00014913 | -0.00059987 | -0.00015034 | 2.9412e-08 | -1.2135e-06 | 0.00090282 | 0.00090326 | 0.00090326 | 0.98827 | -0.22605 | 0.98822 | -0.22708 | 0.24815
8 | 0.010659 | 0.0026721 | -0.010659 | -0.0026719 | 3.6338e-07 | 1.8451e-07 | 0.016062 | 0.016062 | 0.016062 | 0.98752 | -0.24062 | 0.98748 | -0.24133 | 4.4127
9 | 0.00020162 | 4.9905e-05 | -0.00020162 | -5.053e-05 | 1.6922e-09 | -6.2487e-07 | 0.00030358 | 0.0003038 | 0.0003038 | 0.98752 | -0.24062 | 0.98751 | -0.2408 | 0.083463
10 | -0.056482 | -0.014168 | 0.056527 | 0.014196 | 4.4332e-05 | 2.8162e-05 | 0.084896 | 0.084896 | 0.084896 | 0.99004 | -0.19169 | 0.99089 | -0.17524 | 23.3232
11 | -0.0043565 | -0.0010913 | 0.0043568 | 0.0010913 | 2.6929e-07 | -4.1371e-08 | 0.0065606 | 0.0065605 | 0.0065606 | 0.98808 | -0.22968 | 0.98815 | -0.22838 | 1.8023
12 | 0.0043565 | 0.0010913 | -0.0043561 | -0.0010914 | 3.7693e-07 | -5.7852e-08 | 0.0065606 | 0.0065607 | 0.0065607 | 0.98808 | -0.22968 | 0.98799 | -0.2315 | 1.8024
13 | -0.0056466 | -0.0014146 | 0.005648 | 0.0014148 | 1.4154e-06 | 2.3688e-07 | 0.0085028 | 0.0085026 | 0.0085028 | 0.98815 | -0.22838 | 0.98842 | -0.22312 | 2.3359
14 | 0.0013027 | 0.00032612 | -0.0013026 | -0.00032647 | 4.1597e-08 | -3.4243e-07 | 0.0019618 | 0.0019619 | 0.0019619 | 0.98799 | -0.2315 | 0.98795 | -0.23217 | 0.539
15 | 0.020604 | 0.0051686 | -0.02059 | -0.0051604 | 1.3598e-05 | 8.2006e-06 | 0.030713 | 0.030713 | 0.030713 | 0.99829 | -0.032706 | 0.99757 | -0.046559 | 8.4377
16 | -0.43193 | -0.10911 | 0.4326 | 0.10955 | 0.00067825 | 0.00043316 | 0.64412 | 0.64412 | 0.64412 | 0.99829 | -0.032706 | 1 | 0 | 44.239
17 | 0.12214 | 0.030799 | -0.12184 | -0.030608 | 0.00029852 | 0.00019074 | 0.18212 | 0.18212 | 0.18212 | 0.99829 | -0.032706 | 0.99562 | -0.083908 | 50.0328
18 | 0.28919 | 0.073147 | -0.28824 | -0.072542 | 0.00094872 | 0.00060435 | 0.43129 | 0.43129 | 0.43129 | 0.99829 | -0.032706 | 0.99471 | -0.10133 | 29.6215
19 | 0.087051 | 0.02191 | -0.086809 | -0.021757 | 0.00024122 | 0.00015388 | 0.12957 | 0.12957 | 0.12957 | 1 | 0 | 0.99697 | -0.058153 | 35.595
20 | 0.11178 | 0.028088 | -0.1116 | -0.02797 | 0.00018464 | 0.00011794 | 0.16709 | 0.16709 | 0.16709 | 0.99562 | -0.083908 | 0.99383 | -0.11857 | 45.905
21 | 0.24601 | 0.06196 | -0.24554 | -0.061662 | 0.00046864 | 0.00029802 | 0.36812 | 0.36812 | 0.36812 | 0.99471 | -0.10133 | 0.99264 | -0.14125 | 25.2832
22 | 0.010659 | 0.0026719 | -0.010657 | -0.002671 | 1.8234e-06 | 9.259e-07 | 0.016062 | 0.016062 | 0.016062 | 0.98748 | -0.24133 | 0.9873 | -0.24492 | 4.4127
23 | -0.010374 | -0.0025993 | 0.010375 | 0.0025995 | 4.3993e-07 | 2.199e-07 | 0.015617 | 0.015617 | 0.015617 | 0.98842 | -0.22312 | 0.98846 | -0.22223 | 4.2905
24 | 0.081598 | 0.020451 | -0.081596 | -0.02045 | 2.1324e-06 | 1.3598e-06 | 0.12217 | 0.12217 | 0.12217 | 0.99383 | -0.11857 | 0.9938 | -0.11912 | 33.5641
25 | -0.020462 | -0.0051375 | 0.020504 | 0.0051627 | 4.1825e-05 | 2.5246e-05 | 0.030745 | 0.030744 | 0.030745 | 0.99043 | -0.18401 | 0.99264 | -0.14125 | 8.4464
26 | 0.020462 | 0.0051375 | -0.020447 | -0.0051284 | 1.5084e-05 | 9.1066e-06 | 0.030745 | 0.030745 | 0.030745 | 0.99043 | -0.18401 | 0.98964 | -0.19947 | 8.4464
27 | 0.22504 | 0.056499 | -0.22493 | -0.05643 | 0.00010929 | 6.9417e-05 | 0.33738 | 0.33738 | 0.33738 | 0.99264 | -0.14125 | 0.99212 | -0.15144 | 23.1717
28 | 0.0018113 | 0.00045345 | -0.0018112 | -0.00045392 | 1.1887e-07 | -4.7301e-07 | 0.0027233 | 0.0027235 | 0.0027235 | 0.98964 | -0.19947 | 0.98956 | -0.20085 | 0.7482
29 | 0.015863 | 0.00398 | -0.015853 | -0.0039741 | 1.0297e-05 | 5.9706e-06 | 0.023853 | 0.023853 | 0.023853 | 0.98964 | -0.19947 | 0.98893 | -0.2131 | 6.5531
30 | 0.1461 | 0.036673 | -0.14609 | -0.036668 | 7.7264e-06 | 4.9227e-06 | 0.21915 | 0.21915 | 0.21915 | 0.99212 | -0.15144 | 0.99206 | -0.15255 | 30.1024
31 | -0.014402 | -0.0036101 | 0.014404 | 0.0036109 | 1.3897e-06 | 7.882e-07 | 0.021673 | 0.021673 | 0.021673 | 0.98883 | -0.21512 | 0.98893 | -0.2131 | 5.9541
32 | 0.012499 | 0.0031331 | -0.012495 | -0.0031308 | 4.2311e-06 | 2.2989e-06 | 0.018809 | 0.018809 | 0.018809 | 0.98883 | -0.21512 | 0.98846 | -0.22223 | 5.1673
33 | 0.058608 | 0.014742 | -0.058545 | -0.014702 | 6.3471e-05 | 4.0339e-05 | 0.087927 | 0.087927 | 0.087927 | 0.99206 | -0.15255 | 0.99089 | -0.17524 | 24.1558

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52131 | 0.13146

## res_load
| p_mw | q_mvar
0 | 0.0033167 | 0.00083124
1 | 0.00012678 | 3.1774e-05
2 | 0.00013429 | 3.3656e-05
3 | 0.013865 | 0.003475
4 | 0.027528 | 0.0068993
5 | 0.0012899 | 0.00032327
6 | 0.0030535 | 0.00076527
7 | 0.02059 | 0.0051604
8 | 0.010053 | 0.0025196
9 | 0.042225 | 0.010583
10 | 0.00020162 | 5.053e-05
11 | 0.010657 | 0.002671
12 | 0.086809 | 0.021757
13 | 0.00059987 | 0.00015034
14 | 0.0047261 | 0.0011845
15 | 0.0013026 | 0.00032647
16 | 0.030002 | 0.0075193
17 | 0.0027726 | 0.00069487
18 | 0.078831 | 0.019757
19 | 0.0019033 | 0.00047701
20 | 0.001449 | 0.00036315
21 | 0.0021201 | 0.00053134
22 | 0.0018112 | 0.00045392
23 | 0.087483 | 0.021925
24 | 0.0020183 | 0.00050584
25 | 0.081596 | 0.02045

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1