## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_139-13_1_2_node_10 | 0.4 | n |  | TRUE
1 | bus_LV_139-13_1_2_node_57 | 0.4 | n |  | TRUE
2 | bus_LV_139-13_1_2_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_139-13_1_2_node_26 | 0.4 | n |  | TRUE
4 | bus_LV_139-13_1_2_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_139-13_1_2_node_53 | 0.4 | n |  | TRUE
6 | bus_LV_139-13_1_2_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_139-13_1_2_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_139-13_1_2_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_139-13_1_2_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_139-13_1_2_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_139-13_1_2_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_139-13_1_2_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_139-13_1_2_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_139-13_1_2_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_139-13_1_2_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_139-13_1_2_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_139-13_1_2_node_46 | 0.4 | n |  | TRUE
18 | bus_MV_360_0_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_139-13_1_2_load_57 | 1 | 0.01723 | 0.0043184 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_139-13_1_2_load_53 | 5 | 0.0031025 | 0.00077755 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_139-13_1_2_load_44 | 7 | 0.003392 | 0.00085012 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_139-13_1_2_load_47 | 8 | 0.010393 | 0.0026047 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_139-13_1_2_load_31 | 9 | 0.010201 | 0.0025567 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_139-13_1_2_load_45 | 11 | 0.010012 | 0.0025092 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_139-13_1_2_load_39 | 12 | 0.0030467 | 0.00076358 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_139-13_1_2_load_40 | 13 | 0.0015993 | 0.00040083 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_139-13_1_2_load_42 | 15 | 0.0039409 | 0.00098767 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_139-13_1_2_load_43 | 16 | 0.0054559 | 0.0013674 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_139-13_1_2_load_46 | 17 | 0.0063276 | 0.0015859 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_139-13_1_2_line_0 |  | 0 | 1 | 0.11175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_139-13_1_2_line_1 |  | 0 | 2 | 0.12227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_139-13_1_2_line_2 |  | 0 | 3 | 0.27457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_139-13_1_2_line_3 |  | 2 | 9 | 0.038782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_139-13_1_2_line_4 |  | 2 | 4 | 0.050078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_139-13_1_2_line_5 |  | 2 | 6 | 0.083207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_139-13_1_2_line_6 |  | 3 | 10 | 0.23025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_139-13_1_2_line_7 |  | 4 | 5 | 0.11154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_139-13_1_2_line_8 |  | 6 | 7 | 0.038322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_139-13_1_2_line_9 |  | 6 | 8 | 0.058349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_139-13_1_2_line_10 |  | 7 | 14 | 0.046262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_139-13_1_2_line_11 |  | 10 | 11 | 0.041835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_139-13_1_2_line_12 |  | 12 | 13 | 0.030418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_139-13_1_2_line_13 |  | 12 | 14 | 0.0291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_139-13_1_2_line_14 |  | 13 | 15 | 0.00099649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_139-13_1_2_line_15 |  | 14 | 16 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_139-13_1_2_line_16 |  | 16 | 17 | 0.013808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_139-13_1_2_trafo_13 | 0.63 MVA 20/0.4 kV | 18 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2683833.647 | 1240290.1968 | 2683827.2122 | 1240286.3699 | 2683826.8546 | 1240282.7733 | 2683837.9449 | 1240262.204 | 2683846.8752 | 1240251.0555 | 2683863.8448 | 1240234.561 | 2683894.6641 | 1240209.8898
1 | 2683817.6264 | 1240291.9941 | 2683822.0627 | 1240278.2914 | 2683826.6957 | 1240268.3274 | 2683830.2992 | 1240261.6512 | 2683838.5353 | 1240250.9265 | 2683853.5769 | 1240235.9948 | 2683882.6858 | 1240211.4105 | 2683890.9203 | 1240205.089 | 2683894.6641 | 1240209.8898
2 | 2683894.6641 | 1240209.8898 | 2683900.4657 | 1240217.3104 | 2683915.2143 | 1240231.1399 | 2683936.751 | 1240245.1877 | 2683910.926 | 1240312.9714 | 2683904.3493 | 1240327.2109 | 2683904.1943 | 1240334.9588 | 2683907.2244 | 1240343.6968 | 2683910.8095 | 1240345.8045 | 2683902.3721 | 1240360.607 | 2683882.0297 | 1240401.1821 | 2683881.8556 | 1240405.4716 | 2683882.862 | 1240409.1774 | 2683885.0239 | 1240411.921 | 2683907.3919 | 1240423.8345 | 2683908.8567 | 1240426.1346 | 2683910.0371 | 1240429.8318 | 2683909.522 | 1240433.6383
3 | 2683817.6264 | 1240291.9941 | 2683810.8612 | 1240309.956 | 2683802.018 | 1240325.1198 | 2683800.9083 | 1240326.8243
4 | 2683790.5896 | 1240320.9222 | 2683796.598 | 1240324.4095 | 2683804.901 | 1240310.0163 | 2683809.2868 | 1240292.3878 | 2683817.6264 | 1240291.9941
5 | 2683741.0227 | 1240276.5244 | 2683753.0124 | 1240276.8604 | 2683759.4507 | 1240277.2293 | 2683777.2562 | 1240278.637 | 2683784.4726 | 1240280.1288 | 2683789.7886 | 1240282.3165 | 2683792.4903 | 1240284.8676 | 2683794.9954 | 1240289.017 | 2683796.7846 | 1240292.9896 | 2683809.2868 | 1240292.3878 | 2683817.6264 | 1240291.9941
6 | 2683820.4859 | 1240411.3202 | 2683821.6772 | 1240407.2897 | 2683823.9734 | 1240404.2755 | 2683827.6289 | 1240401.4029 | 2683831.6987 | 1240400.7932 | 2683835.5224 | 1240402.0703 | 2683840.4379 | 1240405.2976 | 2683842.4117 | 1240409.0393 | 2683843.4854 | 1240413.3353 | 2683837.3573 | 1240483.0878 | 2683847.5335 | 1240466.6975 | 2683875.573 | 1240413.9 | 2683878.0614 | 1240412.2673 | 2683881.5961 | 1240411.5278 | 2683885.0239 | 1240411.921 | 2683907.3919 | 1240423.8345 | 2683908.8567 | 1240426.1346 | 2683910.0371 | 1240429.8318 | 2683909.522 | 1240433.6383
7 | 2683790.5896 | 1240320.9222 | 2683730.3435 | 1240414.797
8 | 2683741.0227 | 1240276.5244 | 2683741.5707 | 1240282.1695 | 2683740.7199 | 1240285.1152 | 2683738.1678 | 1240287.5031 | 2683733.3048 | 1240288.5909 | 2683727.1788 | 1240289.1382 | 2683719.3884 | 1240293.487 | 2683715.0569 | 1240297.687
9 | 2683741.0227 | 1240276.5244 | 2683722.1516 | 1240276.1358 | 2683683.627 | 1240273.4574 | 2683682.7757 | 1240273.3649
10 | 2683679.735 | 1240327.4191 | 2683700.1964 | 1240312.0965 | 2683715.0569 | 1240297.687
11 | 2683820.4859 | 1240411.3202 | 2683817.7904 | 1240394.4145 | 2683816.4775 | 1240390.9935 | 2683814.1898 | 1240388.5817 | 2683798.3914 | 1240380.5412
12 | 2683699.9743 | 1240347.1103 | 2683705.1603 | 1240350.4941 | 2683693.3245 | 1240368.7403 | 2683691.2346 | 1240367.4104
13 | 2683679.735 | 1240327.4191 | 2683685.0773 | 1240337.3905 | 2683699.9743 | 1240347.1103
14 | 2683690.3939 | 1240366.8755 | 2683691.2346 | 1240367.4104
15 | 2683679.735 | 1240327.4191 | 2683673.7298 | 1240326.3782 | 2683668.5452 | 1240329.8854 | 2683662.242 | 1240339.9085
16 | 2683654.891 | 1240351.5975 | 2683662.242 | 1240339.9085

## bus_geodata
| x | y | coords
0 | 2683894.6641 | 1240209.8898
1 | 2683833.647 | 1240290.1968
2 | 2683817.6264 | 1240291.9941
3 | 2683909.522 | 1240433.6383
4 | 2683790.5896 | 1240320.9222
5 | 2683730.3435 | 1240414.797
6 | 2683741.0227 | 1240276.5244
7 | 2683715.0569 | 1240297.687
8 | 2683682.7757 | 1240273.3649
9 | 2683800.9083 | 1240326.8243
10 | 2683820.4859 | 1240411.3202
11 | 2683798.3914 | 1240380.5412
12 | 2683699.9743 | 1240347.1103
13 | 2683691.2346 | 1240367.4104
14 | 2683679.735 | 1240327.4191
15 | 2683690.3939 | 1240366.8755
16 | 2683662.242 | 1240339.9085
17 | 2683654.891 | 1240351.5975
18 | 2683796.598 | 1240324.4095

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99367 | -0.1214 | 0 | 0
1 | 0.99191 | -0.15545 | 0.01723 | 0.0043184
2 | 0.99672 | -0.062734 | 0 | 0
3 | 0.99115 | -0.17012 | 0 | 0
4 | 1 | 0 | -0.076851 | -0.019025
5 | 0.99969 | -0.0060372 | 0.0031025 | 0.00077755
6 | 0.99413 | -0.11274 | 0 | 0
7 | 0.99329 | -0.12881 | 0.003392 | 0.00085012
8 | 0.99357 | -0.12344 | 0.010393 | 0.0026047
9 | 0.99636 | -0.069678 | 0.010201 | 0.0025567
10 | 0.98904 | -0.21112 | 0 | 0
11 | 0.98865 | -0.21859 | 0.010012 | 0.0025092
12 | 0.99221 | -0.1499 | 0.0030467 | 0.00076358
13 | 0.99205 | -0.15289 | 0.0015993 | 0.00040083
14 | 0.99243 | -0.14548 | 0 | 0
15 | 0.99205 | -0.15296 | 0.0039409 | 0.00098767
16 | 0.99217 | -0.15053 | 0.0054559 | 0.0013674
17 | 0.99209 | -0.15207 | 0.0063276 | 0.0015859
18 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.017258 | 0.0043348 | -0.01723 | -0.0043184 | 2.7999e-05 | 1.6474e-05 | 0.025848 | 0.025848 | 0.025848 | 0.99367 | -0.1214 | 0.99191 | -0.15545 | 7.1012
1 | -0.027317 | -0.0068668 | 0.027394 | 0.0069144 | 7.675e-05 | 4.7531e-05 | 0.040914 | 0.040914 | 0.040914 | 0.99367 | -0.1214 | 0.99672 | -0.062734 | 11.2402
2 | 0.010059 | 0.002532 | -0.010035 | -0.0025206 | 2.3375e-05 | 1.1412e-05 | 0.015066 | 0.015068 | 0.015068 | 0.99367 | -0.1214 | 0.99115 | -0.17012 | 4.1395
3 | 0.010205 | 0.0025584 | -0.010201 | -0.0025567 | 3.3756e-06 | 1.6551e-06 | 0.015235 | 0.015235 | 0.015235 | 0.99672 | -0.062734 | 0.99636 | -0.069678 | 4.1855
4 | -0.071881 | -0.01811 | 0.072098 | 0.018248 | 0.0002164 | 0.00013784 | 0.10735 | 0.10735 | 0.10735 | 0.99672 | -0.062734 | 1 | 0 | 29.4906
5 | 0.034283 | 0.0086375 | -0.034201 | -0.0085863 | 8.1788e-05 | 5.1263e-05 | 0.051197 | 0.051198 | 0.051198 | 0.99672 | -0.062734 | 0.99413 | -0.11274 | 14.0653
6 | 0.010035 | 0.0025206 | -0.010016 | -0.002511 | 1.9605e-05 | 9.5858e-06 | 0.015068 | 0.015069 | 0.015069 | 0.99115 | -0.17012 | 0.98904 | -0.21112 | 4.1398
7 | 0.0031034 | 0.00077666 | -0.0031025 | -0.00077755 | 8.9193e-07 | -8.9208e-07 | 0.0046175 | 0.004618 | 0.004618 | 1 | 0 | 0.99969 | -0.0060372 | 1.2687
8 | 0.023803 | 0.0059789 | -0.023785 | -0.0059677 | 1.8247e-05 | 1.1181e-05 | 0.035633 | 0.035633 | 0.035633 | 0.99413 | -0.11274 | 0.99329 | -0.12881 | 9.7893
9 | 0.010398 | 0.0026074 | -0.010393 | -0.0026047 | 5.301e-06 | 2.6365e-06 | 0.015565 | 0.015565 | 0.015565 | 0.99413 | -0.11274 | 0.99357 | -0.12344 | 4.2761
10 | 0.020393 | 0.0051176 | -0.020376 | -0.0051078 | 1.6193e-05 | 9.7653e-06 | 0.030552 | 0.030552 | 0.030552 | 0.99329 | -0.12881 | 0.99243 | -0.14548 | 8.3934
11 | 0.010016 | 0.002511 | -0.010012 | -0.0025092 | 3.5623e-06 | 1.7432e-06 | 0.015069 | 0.015069 | 0.015069 | 0.98904 | -0.21112 | 0.98865 | -0.21859 | 4.1398
12 | 0.005541 | 0.0013886 | -0.0055402 | -0.0013885 | 7.8769e-07 | 1.1131e-07 | 0.0083098 | 0.0083099 | 0.0083099 | 0.99221 | -0.1499 | 0.99205 | -0.15289 | 2.283
13 | -0.0085877 | -0.0021522 | 0.0085895 | 0.002153 | 1.81e-06 | 7.8248e-07 | 0.012879 | 0.012879 | 0.012879 | 0.99221 | -0.1499 | 0.99243 | -0.14548 | 3.5382
14 | 0.0039409 | 0.00098767 | -0.0039409 | -0.00098767 | 1.3057e-08 | -4.51e-09 | 0.0059111 | 0.0059111 | 0.0059111 | 0.99205 | -0.15289 | 0.99205 | -0.15296 | 1.6239
15 | 0.011787 | 0.0029548 | -0.011784 | -0.0029533 | 2.8338e-06 | 1.5011e-06 | 0.017673 | 0.017673 | 0.017673 | 0.99243 | -0.14548 | 0.99217 | -0.15053 | 4.8552
16 | 0.0063281 | 0.001586 | -0.0063276 | -0.0015859 | 4.6641e-07 | 1.2018e-07 | 0.0094906 | 0.0094907 | 0.0094907 | 0.99217 | -0.15053 | 0.99209 | -0.15207 | 2.6073

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.076851 | 0.019025

## res_load
| p_mw | q_mvar
0 | 0.01723 | 0.0043184
1 | 0.0031025 | 0.00077755
2 | 0.003392 | 0.00085012
3 | 0.010393 | 0.0026047
4 | 0.010201 | 0.0025567
5 | 0.010012 | 0.0025092
6 | 0.0030467 | 0.00076358
7 | 0.0015993 | 0.00040083
8 | 0.0039409 | 0.00098767
9 | 0.0054559 | 0.0013674
10 | 0.0063276 | 0.0015859

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1