## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_139-5_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_139-5_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_139-5_0_6_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_139-5_0_6_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_139-5_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_139-5_0_6_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_139-5_0_6_node_63 | 0.4 | n |  | TRUE
7 | bus_LV_139-5_0_6_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_139-5_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_139-5_0_6_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_139-5_0_6_node_61 | 0.4 | n |  | TRUE
11 | bus_LV_139-5_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_139-5_0_6_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_139-5_0_6_node_107 | 0.4 | n |  | TRUE
14 | bus_LV_139-5_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_139-5_0_6_node_94 | 0.4 | n |  | TRUE
16 | bus_LV_139-5_0_6_node_95 | 0.4 | n |  | TRUE
17 | bus_LV_139-5_0_6_node_93 | 0.4 | n |  | TRUE
18 | bus_LV_139-5_0_6_node_117 | 0.4 | n |  | TRUE
19 | bus_LV_139-5_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_139-5_0_6_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_139-5_0_6_node_137 | 0.4 | n |  | TRUE
22 | bus_LV_139-5_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_139-5_0_6_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_139-5_0_6_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_139-5_0_6_node_104 | 0.4 | n |  | TRUE
26 | bus_LV_139-5_0_6_node_60 | 0.4 | n |  | TRUE
27 | bus_LV_139-5_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_139-5_0_6_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_139-5_0_6_node_138 | 0.4 | n |  | TRUE
30 | bus_LV_139-5_0_6_node_149 | 0.4 | n |  | TRUE
31 | bus_LV_139-5_0_6_node_108 | 0.4 | n |  | TRUE
32 | bus_LV_139-5_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_139-5_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_139-5_0_6_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_139-5_0_6_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_139-5_0_6_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_139-5_0_6_node_73 | 0.4 | n |  | TRUE
38 | bus_LV_139-5_0_6_node_83 | 0.4 | n |  | TRUE
39 | bus_LV_139-5_0_6_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_139-5_0_6_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_139-5_0_6_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_139-5_0_6_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_139-5_0_6_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_139-5_0_6_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_139-5_0_6_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_139-5_0_6_node_96 | 0.4 | n |  | TRUE
47 | bus_LV_139-5_0_6_node_101 | 0.4 | n |  | TRUE
48 | bus_LV_139-5_0_6_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_139-5_0_6_node_82 | 0.4 | n |  | TRUE
50 | bus_LV_139-5_0_6_node_86 | 0.4 | n |  | TRUE
51 | bus_LV_139-5_0_6_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_139-5_0_6_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_139-5_0_6_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_139-5_0_6_node_105 | 0.4 | n |  | TRUE
55 | bus_LV_139-5_0_6_node_97 | 0.4 | n |  | TRUE
56 | bus_LV_139-5_0_6_node_103 | 0.4 | n |  | TRUE
57 | bus_LV_139-5_0_6_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_139-5_0_6_node_148 | 0.4 | n |  | TRUE
59 | bus_LV_139-5_0_6_node_99 | 0.4 | n |  | TRUE
60 | bus_LV_139-5_0_6_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_139-5_0_6_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_139-5_0_6_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_139-5_0_6_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_139-5_0_6_node_130 | 0.4 | n |  | TRUE
65 | bus_LV_139-5_0_6_node_111 | 0.4 | n |  | TRUE
66 | bus_LV_139-5_0_6_node_116 | 0.4 | n |  | TRUE
67 | bus_LV_139-5_0_6_node_139 | 0.4 | n |  | TRUE
68 | bus_LV_139-5_0_6_node_144 | 0.4 | n |  | TRUE
69 | bus_LV_139-5_0_6_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_139-5_0_6_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_139-5_0_6_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_139-5_0_6_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_139-5_0_6_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_139-5_0_6_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_139-5_0_6_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_139-5_0_6_node_160 | 0.4 | n |  | TRUE
77 | bus_LV_139-5_0_6_node_31 | 0.4 | n |  | TRUE
78 | bus_LV_139-5_0_6_node_32 | 0.4 | n |  | TRUE
79 | bus_LV_139-5_0_6_node_33 | 0.4 | n |  | TRUE
80 | bus_LV_139-5_0_6_node_34 | 0.4 | n |  | TRUE
81 | bus_LV_139-5_0_6_node_35 | 0.4 | n |  | TRUE
82 | bus_LV_139-5_0_6_node_39 | 0.4 | n |  | TRUE
83 | bus_LV_139-5_0_6_node_40 | 0.4 | n |  | TRUE
84 | bus_LV_139-5_0_6_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_139-5_0_6_node_44 | 0.4 | n |  | TRUE
86 | bus_LV_139-5_0_6_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_139-5_0_6_node_50 | 0.4 | n |  | TRUE
88 | bus_LV_139-5_0_6_node_36 | 0.4 | n |  | TRUE
89 | bus_LV_139-5_0_6_node_37 | 0.4 | n |  | TRUE
90 | bus_LV_139-5_0_6_node_38 | 0.4 | n |  | TRUE
91 | bus_LV_139-5_0_6_node_51 | 0.4 | n |  | TRUE
92 | bus_LV_139-5_0_6_node_58 | 0.4 | n |  | TRUE
93 | bus_LV_139-5_0_6_node_47 | 0.4 | n |  | TRUE
94 | bus_LV_139-5_0_6_node_54 | 0.4 | n |  | TRUE
95 | bus_LV_139-5_0_6_node_53 | 0.4 | n |  | TRUE
96 | bus_LV_139-5_0_6_node_52 | 0.4 | n |  | TRUE
97 | bus_LV_139-5_0_6_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_139-5_0_6_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_139-5_0_6_node_55 | 0.4 | n |  | TRUE
100 | bus_LV_139-5_0_6_node_56 | 0.4 | n |  | TRUE
101 | bus_LV_139-5_0_6_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_139-5_0_6_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_139-5_0_6_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_139-5_0_6_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_139-5_0_6_node_72 | 0.4 | n |  | TRUE
106 | bus_LV_139-5_0_6_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_139-5_0_6_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_139-5_0_6_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_139-5_0_6_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_139-5_0_6_node_141 | 0.4 | n |  | TRUE
111 | bus_LV_139-5_0_6_node_140 | 0.4 | n |  | TRUE
112 | bus_LV_139-5_0_6_node_142 | 0.4 | n |  | TRUE
113 | bus_LV_139-5_0_6_node_143 | 0.4 | n |  | TRUE
114 | bus_LV_139-5_0_6_node_157 | 0.4 | n |  | TRUE
115 | bus_LV_139-5_0_6_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_139-5_0_6_node_145 | 0.4 | n |  | TRUE
117 | bus_LV_139-5_0_6_node_152 | 0.4 | n |  | TRUE
118 | bus_LV_139-5_0_6_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_139-5_0_6_node_154 | 0.4 | n |  | TRUE
120 | bus_LV_139-5_0_6_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_139-5_0_6_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_139-5_0_6_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_139-5_0_6_node_127 | 0.4 | n |  | TRUE
124 | bus_LV_139-5_0_6_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_139-5_0_6_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_139-5_0_6_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_139-5_0_6_node_126 | 0.4 | n |  | TRUE
128 | bus_LV_139-5_0_6_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_139-5_0_6_node_124 | 0.4 | n |  | TRUE
130 | bus_LV_139-5_0_6_node_131 | 0.4 | n |  | TRUE
131 | bus_LV_139-5_0_6_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_139-5_0_6_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_139-5_0_6_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_139-5_0_6_node_132 | 0.4 | n |  | TRUE
135 | bus_LV_139-5_0_6_node_155 | 0.4 | n |  | TRUE
136 | bus_LV_139-5_0_6_node_134 | 0.4 | n |  | TRUE
137 | bus_LV_139-5_0_6_node_135 | 0.4 | n |  | TRUE
138 | bus_LV_139-5_0_6_node_136 | 0.4 | n |  | TRUE
139 | bus_LV_139-5_0_6_node_151 | 0.4 | n |  | TRUE
140 | bus_LV_139-5_0_6_node_150 | 0.4 | n |  | TRUE
141 | bus_LV_139-5_0_6_node_156 | 0.4 | n |  | TRUE
142 | bus_LV_139-5_0_6_node_147 | 0.4 | n |  | TRUE
143 | bus_LV_139-5_0_6_node_146 | 0.4 | n |  | TRUE
144 | bus_LV_139-5_0_6_node_153 | 0.4 | n |  | TRUE
145 | bus_LV_139-5_0_6_node_158 | 0.4 | n |  | TRUE
146 | bus_LV_139-5_0_6_node_159 | 0.4 | n |  | TRUE
147 | bus_MV_491_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_139-5_0_6_load_0 | 0 | 0.020143 | 0.0050482 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_139-5_0_6_load_4 | 2 | 0.012061 | 0.0030227 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_139-5_0_6_load_5 | 4 | 0.061056 | 0.015302 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_139-5_0_6_load_61 | 10 | 0.0073627 | 0.0018453 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_139-5_0_6_load_107 | 13 | 0.0038579 | 0.00096687 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_139-5_0_6_load_94 | 15 | 0.0027284 | 0.00068381 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_139-5_0_6_load_95 | 16 | 0.0026002 | 0.00065168 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_139-5_0_6_load_93 | 17 | 0.0028475 | 0.00071365 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_139-5_0_6_load_117 | 18 | 0.0028776 | 0.00072119 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_139-5_0_6_load_98 | 20 | 0.0026648 | 0.00066786 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_139-5_0_6_load_137 | 21 | 0.0010418 | 0.00026111 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_139-5_0_6_load_102 | 23 | 0.013757 | 0.0034479 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_139-5_0_6_load_104 | 25 | 0.01897 | 0.0047544 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_139-5_0_6_load_60 | 26 | 0.0044134 | 0.0011061 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_139-5_0_6_load_149 | 30 | 0.0031056 | 0.00077833 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_139-5_0_6_load_108 | 31 | 0.0027572 | 0.00069102 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_139-5_0_6_load_85 | 34 | 0.017166 | 0.0043022 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_139-5_0_6_load_73 | 37 | 0.003205 | 0.00080326 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_139-5_0_6_load_83 | 38 | 0.0032401 | 0.00081206 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_139-5_0_6_load_84 | 40 | 0.015009 | 0.0037616 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_139-5_0_6_load_69 | 41 | 0.0071223 | 0.001785 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_139-5_0_6_load_66 | 42 | 0.0048263 | 0.0012096 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_139-5_0_6_load_49 | 43 | 0.0042448 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_139-5_0_6_load_96 | 46 | 0.0032679 | 0.00081902 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_139-5_0_6_load_101 | 47 | 0.0016927 | 0.00042423 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_139-5_0_6_load_86 | 50 | 0.0089423 | 0.0022412 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_139-5_0_6_load_64 | 51 | 0.0071454 | 0.0017908 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_139-5_0_6_load_75 | 53 | 0.016789 | 0.0042077 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_139-5_0_6_load_97 | 55 | 0.0053448 | 0.0013395 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_139-5_0_6_load_103 | 56 | 0.011253 | 0.0028204 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_139-5_0_6_load_148 | 58 | 0.0063237 | 0.0015849 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_139-5_0_6_load_43 | 60 | 0.0042108 | 0.0010553 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_139-5_0_6_load_59 | 62 | 0.0027028 | 0.00067739 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_139-5_0_6_load_130 | 64 | 0.0029123 | 0.00072989 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_139-5_0_6_load_111 | 65 | 0.0012817 | 0.00032121 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_139-5_0_6_load_71 | 69 | 0.01058 | 0.0026515 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_139-5_0_6_load_57 | 70 | 0.0012432 | 0.00031159 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_139-5_0_6_load_67 | 71 | 0.0072234 | 0.0018103 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_139-5_0_6_load_48 | 72 | 0.0048665 | 0.0012197 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_139-5_0_6_load_45 | 74 | 0.0071846 | 0.0018006 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_139-5_0_6_load_46 | 75 | 0.0028743 | 0.00072037 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_139-5_0_6_load_160 | 76 | 0.0035591 | 0.00089201 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_139-5_0_6_load_31 | 77 | 0.0051435 | 0.0012891 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_139-5_0_6_load_32 | 78 | 0.0044172 | 0.001107 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_139-5_0_6_load_33 | 79 | 0.0022376 | 0.00056078 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_139-5_0_6_load_34 | 80 | 0.0038612 | 0.0009677 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_139-5_0_6_load_40 | 83 | 0.0013829 | 0.00034658 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_139-5_0_6_load_41 | 84 | 0.0035322 | 0.00088525 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_139-5_0_6_load_44 | 85 | 0.0030707 | 0.00076959 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_139-5_0_6_load_76 | 86 | 0.0030613 | 0.00076724 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_139-5_0_6_load_50 | 87 | 0.004119 | 0.0010323 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_139-5_0_6_load_36 | 88 | 0.0037326 | 0.00093547 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_139-5_0_6_load_37 | 89 | 0.00090965 | 0.00022798 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_139-5_0_6_load_38 | 90 | 0.0065515 | 0.001642 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_139-5_0_6_load_51 | 91 | 0.003553 | 0.00089048 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_139-5_0_6_load_58 | 92 | 0.0067884 | 0.0017013 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_139-5_0_6_load_47 | 93 | 0.0034105 | 0.00085474 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_139-5_0_6_load_54 | 94 | 0.0025062 | 0.00062812 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_139-5_0_6_load_53 | 95 | 0.0027145 | 0.00068032 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_139-5_0_6_load_52 | 96 | 0.0021869 | 0.00054808 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_139-5_0_6_load_65 | 97 | 0.0037678 | 0.00094429 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_139-5_0_6_load_77 | 98 | 0.0031652 | 0.00079327 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_139-5_0_6_load_55 | 99 | 0.0026657 | 0.00066809 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_139-5_0_6_load_56 | 100 | 0.0010043 | 0.00025171 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_139-5_0_6_load_78 | 101 | 0.0017203 | 0.00043115 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_139-5_0_6_load_68 | 102 | 0.0081593 | 0.0020449 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_139-5_0_6_load_74 | 104 | 0.002457 | 0.00061578 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_139-5_0_6_load_72 | 105 | 0.0030151 | 0.00075567 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_139-5_0_6_load_79 | 106 | 0.008368 | 0.0020972 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_139-5_0_6_load_87 | 107 | 0.0051433 | 0.001289 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_139-5_0_6_load_88 | 108 | 0.010194 | 0.0025549 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_139-5_0_6_load_90 | 109 | 0.0056216 | 0.0014089 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_139-5_0_6_load_141 | 110 | 0.011385 | 0.0028534 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_139-5_0_6_load_140 | 111 | 0.0035636 | 0.00089312 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_139-5_0_6_load_157 | 114 | 0.0069482 | 0.0017414 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_139-5_0_6_load_106 | 115 | 0.010718 | 0.0026863 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_139-5_0_6_load_152 | 117 | 0.0032818 | 0.00082249 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_139-5_0_6_load_115 | 118 | 0.0084471 | 0.002117 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_139-5_0_6_load_154 | 119 | 0.0028984 | 0.0007264 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_139-5_0_6_load_110 | 120 | 0.00179 | 0.00044862 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_139-5_0_6_load_113 | 121 | 0.011436 | 0.0028661 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_139-5_0_6_load_129 | 122 | 0.0034404 | 0.00086225 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_139-5_0_6_load_127 | 123 | 0.002464 | 0.00061754 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_139-5_0_6_load_118 | 124 | 0.0006684 | 0.00016752 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_139-5_0_6_load_119 | 125 | 0.0022336 | 0.00055978 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_139-5_0_6_load_121 | 126 | 0.0028459 | 0.00071325 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_139-5_0_6_load_133 | 128 | 0.0028244 | 0.00070785 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_139-5_0_6_load_124 | 129 | 0.001059 | 0.00026541 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_139-5_0_6_load_131 | 130 | 0.0019635 | 0.0004921 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_139-5_0_6_load_128 | 131 | 0.0014646 | 0.00036707 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_139-5_0_6_load_123 | 132 | 0.0015109 | 0.00037866 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_139-5_0_6_load_132 | 134 | 0.011087 | 0.0027785 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_139-5_0_6_load_136 | 138 | 0.0044741 | 0.0011213 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_139-5_0_6_load_151 | 139 | 0.011147 | 0.0027937 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_139-5_0_6_load_150 | 140 | 0.0046408 | 0.0011631 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_139-5_0_6_load_156 | 141 | 0.0025799 | 0.00064659 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_139-5_0_6_load_147 | 142 | 0.0046063 | 0.0011545 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_139-5_0_6_load_153 | 144 | 0.0075276 | 0.0018866 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_139-5_0_6_load_158 | 145 | 0.0027213 | 0.00068202 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_139-5_0_6_load_159 | 146 | 0.0025504 | 0.00063919 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_139-5_0_6_line_0 |  | 0 | 1 | 0.025203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_139-5_0_6_line_1 |  | 1 | 2 | 0.013403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_139-5_0_6_line_2 |  | 2 | 6 | 0.028366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_139-5_0_6_line_3 |  | 3 | 4 | 0.033155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_139-5_0_6_line_4 |  | 3 | 5 | 0.10629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_139-5_0_6_line_5 |  | 4 | 7 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_139-5_0_6_line_6 |  | 5 | 22 | 0.032969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_139-5_0_6_line_7 |  | 5 | 23 | 0.035975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_139-5_0_6_line_8 |  | 6 | 53 | 0.021595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_139-5_0_6_line_9 |  | 6 | 52 | 0.003155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_139-5_0_6_line_10 |  | 7 | 32 | 0.031773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_139-5_0_6_line_11 |  | 8 | 9 | 0.011098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_139-5_0_6_line_12 |  | 8 | 10 | 0.041779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_139-5_0_6_line_13 |  | 9 | 26 | 0.0058633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_139-5_0_6_line_14 |  | 10 | 52 | 0.037019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_139-5_0_6_line_15 |  | 11 | 12 | 0.086208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_139-5_0_6_line_16 |  | 11 | 13 | 0.034595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_139-5_0_6_line_17 |  | 12 | 18 | 0.079979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_139-5_0_6_line_18 |  | 13 | 28 | 0.03178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_139-5_0_6_line_19 |  | 14 | 15 | 0.014351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_139-5_0_6_line_20 |  | 14 | 16 | 0.040576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_139-5_0_6_line_21 |  | 14 | 17 | 0.032984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_139-5_0_6_line_22 |  | 15 | 46 | 0.0204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_139-5_0_6_line_23 |  | 16 | 54 | 0.0040642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_139-5_0_6_line_24 |  | 19 | 20 | 0.016698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_139-5_0_6_line_25 |  | 19 | 21 | 0.016178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_139-5_0_6_line_26 |  | 20 | 55 | 0.0069904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_139-5_0_6_line_27 |  | 21 | 29 | 0.012985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_139-5_0_6_line_28 |  | 22 | 24 | 0.044898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_139-5_0_6_line_29 |  | 22 | 25 | 0.0047086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_139-5_0_6_line_30 |  | 23 | 56 | 0.027575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_139-5_0_6_line_31 |  | 24 | 47 | 0.0043428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_139-5_0_6_line_32 |  | 24 | 45 | 0.0093609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_139-5_0_6_line_33 |  | 26 | 62 | 0.0058575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_139-5_0_6_line_34 |  | 27 | 28 | 0.010871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_139-5_0_6_line_35 |  | 27 | 29 | 0.003718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_139-5_0_6_line_36 |  | 27 | 30 | 0.026373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_139-5_0_6_line_37 |  | 28 | 31 | 0.022043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_139-5_0_6_line_38 |  | 29 | 67 | 0.003431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_139-5_0_6_line_39 |  | 30 | 68 | 0.012398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_139-5_0_6_line_40 |  | 32 | 33 | 0.026512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_139-5_0_6_line_41 |  | 32 | 34 | 0.012241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_139-5_0_6_line_42 |  | 33 | 41 | 0.069479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_139-5_0_6_line_43 |  | 33 | 42 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_139-5_0_6_line_44 |  | 35 | 36 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_139-5_0_6_line_45 |  | 35 | 37 | 0.028379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_139-5_0_6_line_46 |  | 35 | 38 | 0.045164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_139-5_0_6_line_47 |  | 36 | 39 | 0.023362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_139-5_0_6_line_48 |  | 36 | 40 | 0.0070122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_139-5_0_6_line_49 |  | 37 | 69 | 0.014011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_139-5_0_6_line_50 |  | 38 | 70 | 0.0015116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_139-5_0_6_line_51 |  | 39 | 43 | 0.068852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_139-5_0_6_line_52 |  | 39 | 44 | 0.00909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_139-5_0_6_line_53 |  | 42 | 71 | 0.021968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_139-5_0_6_line_54 |  | 43 | 72 | 0.045905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_139-5_0_6_line_55 |  | 44 | 73 | 0.010658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_139-5_0_6_line_56 |  | 45 | 46 | 0.031918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_139-5_0_6_line_57 |  | 47 | 59 | 0.018354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_139-5_0_6_line_58 |  | 48 | 49 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_139-5_0_6_line_59 |  | 48 | 50 | 0.031618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_139-5_0_6_line_60 |  | 49 | 76 | 0.026382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_139-5_0_6_line_61 |  | 49 | 73 | 0.011241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_139-5_0_6_line_62 |  | 51 | 52 | 0.013945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_139-5_0_6_line_63 |  | 54 | 109 | 0.013181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_139-5_0_6_line_64 |  | 55 | 59 | 0.0034115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_139-5_0_6_line_65 |  | 57 | 58 | 0.010375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_139-5_0_6_line_66 |  | 57 | 59 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_139-5_0_6_line_67 |  | 60 | 61 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_139-5_0_6_line_68 |  | 61 | 85 | 0.019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_139-5_0_6_line_69 |  | 61 | 80 | 0.017106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_139-5_0_6_line_70 |  | 62 | 92 | 0.025525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_139-5_0_6_line_71 |  | 63 | 64 | 0.015797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_139-5_0_6_line_72 |  | 63 | 65 | 0.047364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_139-5_0_6_line_73 |  | 63 | 66 | 0.002362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_139-5_0_6_line_74 |  | 64 | 119 | 0.023618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_139-5_0_6_line_75 |  | 65 | 120 | 0.026799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_139-5_0_6_line_76 |  | 66 | 118 | 0.046831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_139-5_0_6_line_77 |  | 67 | 142 | 0.0096633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_139-5_0_6_line_78 |  | 68 | 116 | 0.014574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_139-5_0_6_line_79 |  | 68 | 140 | 0.022932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_139-5_0_6_line_80 |  | 69 | 105 | 0.0025064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_139-5_0_6_line_81 |  | 70 | 100 | 0.02192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_139-5_0_6_line_82 |  | 71 | 102 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_139-5_0_6_line_83 |  | 72 | 90 | 0.033364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_139-5_0_6_line_84 |  | 73 | 106 | 0.014145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_139-5_0_6_line_85 |  | 74 | 75 | 0.028267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_139-5_0_6_line_86 |  | 75 | 93 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_139-5_0_6_line_87 |  | 77 | 78 | 0.0081702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_139-5_0_6_line_88 |  | 77 | 79 | 0.026763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_139-5_0_6_line_89 |  | 78 | 80 | 0.020464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_139-5_0_6_line_90 |  | 79 | 81 | 0.0062476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_139-5_0_6_line_91 |  | 81 | 82 | 0.005944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_139-5_0_6_line_92 |  | 81 | 83 | 0.013005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_139-5_0_6_line_93 |  | 81 | 84 | 0.026179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_139-5_0_6_line_94 |  | 82 | 86 | 0.0037881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_139-5_0_6_line_95 |  | 83 | 87 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_139-5_0_6_line_96 |  | 85 | 92 | 0.0038261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_139-5_0_6_line_97 |  | 87 | 91 | 0.011964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_139-5_0_6_line_98 |  | 88 | 89 | 0.026711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_139-5_0_6_line_99 |  | 89 | 90 | 0.049739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_139-5_0_6_line_100 |  | 91 | 96 | 0.012628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_139-5_0_6_line_101 |  | 93 | 94 | 0.0013182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_139-5_0_6_line_102 |  | 94 | 95 | 0.041104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_139-5_0_6_line_103 |  | 95 | 99 | 0.00022477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_139-5_0_6_line_104 |  | 96 | 97 | 0.017196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_139-5_0_6_line_105 |  | 97 | 98 | 0.0022253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_139-5_0_6_line_106 |  | 98 | 101 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_139-5_0_6_line_107 |  | 99 | 100 | 0.020126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_139-5_0_6_line_108 |  | 101 | 103 | 0.023993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_139-5_0_6_line_109 |  | 102 | 103 | 0.0083589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_139-5_0_6_line_110 |  | 103 | 104 | 0.011151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_139-5_0_6_line_111 |  | 104 | 105 | 0.016158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_139-5_0_6_line_112 |  | 107 | 108 | 0.019961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_139-5_0_6_line_113 |  | 108 | 109 | 0.0063046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_139-5_0_6_line_114 |  | 110 | 111 | 0.022131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_139-5_0_6_line_115 |  | 111 | 112 | 0.0039238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_139-5_0_6_line_116 |  | 112 | 113 | 0.004428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_139-5_0_6_line_117 |  | 113 | 143 | 0.016793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_139-5_0_6_line_118 |  | 113 | 114 | 0.0084927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_139-5_0_6_line_119 |  | 115 | 116 | 0.018122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_139-5_0_6_line_120 |  | 116 | 117 | 0.013785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_139-5_0_6_line_121 |  | 117 | 143 | 0.03002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_139-5_0_6_line_122 |  | 119 | 135 | 0.0088276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_139-5_0_6_line_123 |  | 121 | 122 | 0.034688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_139-5_0_6_line_124 |  | 122 | 123 | 0.03058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_139-5_0_6_line_125 |  | 123 | 133 | 0.048372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_139-5_0_6_line_126 |  | 124 | 125 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_139-5_0_6_line_127 |  | 125 | 126 | 0.0072473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_139-5_0_6_line_128 |  | 126 | 127 | 0.052419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_139-5_0_6_line_129 |  | 127 | 128 | 0.051927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_139-5_0_6_line_130 |  | 127 | 129 | 0.028762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_139-5_0_6_line_131 |  | 128 | 134 | 0.011788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_139-5_0_6_line_132 |  | 129 | 132 | 0.00023283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_139-5_0_6_line_133 |  | 130 | 131 | 0.021237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_139-5_0_6_line_134 |  | 131 | 133 | 0.01491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_139-5_0_6_line_135 |  | 132 | 133 | 0.018024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_139-5_0_6_line_136 |  | 134 | 136 | 0.013707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_139-5_0_6_line_137 |  | 135 | 141 | 0.04235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_139-5_0_6_line_138 |  | 135 | 138 | 0.037221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_139-5_0_6_line_139 |  | 136 | 137 | 0.022625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_139-5_0_6_line_140 |  | 136 | 138 | 0.005781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_139-5_0_6_line_141 |  | 137 | 139 | 0.031888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_139-5_0_6_line_142 |  | 137 | 140 | 0.025984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_139-5_0_6_line_143 |  | 141 | 146 | 0.020383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_139-5_0_6_line_144 |  | 143 | 144 | 0.021943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_139-5_0_6_line_145 |  | 144 | 145 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_139-5_0_6_trafo_2 | 0.63 MVA 20/0.4 kV | 147 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2684456.4031 | 1240263.4251 | 2684453.4147 | 1240265.0949 | 2684451.0418 | 1240267.6296 | 2684444.9886 | 1240284.9072
1 | 2684456.4031 | 1240263.4251 | 2684459.6822 | 1240263.1159 | 2684469.2317 | 1240266.4344
2 | 2684496.1179 | 1240275.4543 | 2684490.7777 | 1240273.9217 | 2684469.2317 | 1240266.4344
3 | 2684429.7421 | 1240328.426 | 2684429.4919 | 1240331.1244 | 2684430.1923 | 1240335.582 | 2684432.3368 | 1240339.5376 | 2684439.0931 | 1240346.7722 | 2684442.9733 | 1240353.6435 | 2684443.8921 | 1240357.1685
4 | 2684342.6959 | 1240333.7149 | 2684350.566 | 1240325.9211 | 2684360.4621 | 1240327.2293 | 2684363.1096 | 1240327.1891 | 2684364.9221 | 1240326.8369 | 2684366.2277 | 1240325.4322 | 2684367.3853 | 1240323.2693 | 2684371.499 | 1240310.0071 | 2684385.3181 | 1240314.6513 | 2684386.0176 | 1240314.3832 | 2684396.2621 | 1240314.0619 | 2684402.3632 | 1240314.738 | 2684403.7796 | 1240316.1814 | 2684418.342 | 1240323.8606 | 2684420.936 | 1240324.9205 | 2684426.1249 | 1240326.9847 | 2684429.7421 | 1240328.426
5 | 2684454.7629 | 1240374.9376 | 2684447.014 | 1240366.2433 | 2684445.3469 | 1240362.7504 | 2684443.8921 | 1240357.1685
6 | 2684323.7228 | 1240324.55 | 2684346.3464 | 1240325.3608 | 2684341.7084 | 1240330.2985 | 2684342.6959 | 1240333.7149
7 | 2684342.6959 | 1240333.7149 | 2684342.7144 | 1240339.3304 | 2684336.82 | 1240369.1124
8 | 2684496.1179 | 1240275.4543 | 2684516.8789 | 1240281.3972
9 | 2684496.9403 | 1240272.4083 | 2684496.1179 | 1240275.4543
10 | 2684478.9115 | 1240395.5738 | 2684474.5454 | 1240392.565 | 2684457.2121 | 1240377.6744 | 2684454.7629 | 1240374.9376
11 | 2684526.0317 | 1240198.7915 | 2684515.2405 | 1240196.0693
12 | 2684515.2405 | 1240196.0693 | 2684506.809 | 1240229.9737 | 2684507.4072 | 1240233.1067 | 2684506.4672 | 1240236.6364
13 | 2684526.0317 | 1240198.7915 | 2684531.6209 | 1240200.5632
14 | 2684496.9403 | 1240272.4083 | 2684506.4672 | 1240236.6364
15 | 2684276.7902 | 1240154.5947 | 2684280.5333 | 1240161.5529 | 2684294.9678 | 1240188.9219 | 2684297.6834 | 1240196.3324 | 2684297.4647 | 1240202.6783 | 2684296.1911 | 1240210.8773 | 2684293.9568 | 1240217.4948 | 2684290.3771 | 1240224.0598 | 2684285.7756 | 1240233.3456
16 | 2684285.7756 | 1240233.3456 | 2684281.4805 | 1240241.824 | 2684277.5138 | 1240247.4162 | 2684274.0606 | 1240251.9927 | 2684270.0907 | 1240255.1497 | 2684264.085 | 1240259.5222
17 | 2684276.7902 | 1240154.5947 | 2684270.9928 | 1240159.6828 | 2684269.16 | 1240163.0592 | 2684267.8738 | 1240167.3551 | 2684262.2872 | 1240192.216 | 2684248.0296 | 1240227.9338
18 | 2684238.3926 | 1240278.2277 | 2684264.085 | 1240259.5222
19 | 2684300.902 | 1240377.5418 | 2684302.262 | 1240366.4532 | 2684302.4458 | 1240363.2791
20 | 2684300.902 | 1240377.5418 | 2684292.2306 | 1240374.6722 | 2684279.4558 | 1240365.1952 | 2684271.9082 | 1240360.9405 | 2684265.4104 | 1240358.7033
21 | 2684300.902 | 1240377.5418 | 2684296.7738 | 1240406.215 | 2684295.901 | 1240410.1342
22 | 2684302.4458 | 1240363.2791 | 2684303.6253 | 1240342.9134
23 | 2684261.5677 | 1240357.3801 | 2684265.4104 | 1240358.7033
24 | 2684262.4537 | 1240273.688 | 2684276.0962 | 1240283.3158
25 | 2684262.4537 | 1240273.688 | 2684258.6475 | 1240276.5027 | 2684253.3764 | 1240279.152 | 2684248.5843 | 1240281.9403
26 | 2684281.8075 | 1240287.3464 | 2684276.0962 | 1240283.3158
27 | 2684237.6657 | 1240288.9473 | 2684243.3028 | 1240285.0133 | 2684248.5843 | 1240281.9403
28 | 2684300.0068 | 1240305.3438 | 2684300.3523 | 1240309.7742 | 2684301.5716 | 1240311.7818 | 2684301.9177 | 1240314.5665 | 2684301.0668 | 1240317.501 | 2684299.4359 | 1240318.9122 | 2684298.0857 | 1240319.7269 | 2684298.3128 | 1240322.3765 | 2684299.816 | 1240323.5654 | 2684302.6905 | 1240323.5173 | 2684317.9278 | 1240324.1563 | 2684323.7228 | 1240324.55
29 | 2684323.7228 | 1240324.55 | 2684322.6041 | 1240323.4444 | 2684320.1205 | 1240321.53
30 | 2684336.82 | 1240369.1124 | 2684336.3591 | 1240371.441 | 2684328.5955 | 1240395.4161
31 | 2684300.0068 | 1240305.3438 | 2684296.8749 | 1240304.3431 | 2684296.2075 | 1240303.5262
32 | 2684300.0068 | 1240305.3438 | 2684300.3523 | 1240309.7742 | 2684302.7049 | 1240310.2635 | 2684305.0989 | 1240311.0313
33 | 2684537.209 | 1240202.3181 | 2684536.9034 | 1240202.2377 | 2684531.6209 | 1240200.5632
34 | 2684235.4927 | 1240285.9254 | 2684233.1564 | 1240282.6899 | 2684238.3926 | 1240278.2277
35 | 2684235.4927 | 1240285.9254 | 2684237.6657 | 1240288.9473
36 | 2684235.4927 | 1240285.9254 | 2684228.2467 | 1240292.3828 | 2684223.8045 | 1240298.9801 | 2684219.1767 | 1240306.3628
37 | 2684238.3926 | 1240278.2277 | 2684220.0277 | 1240266.0372
38 | 2684237.6657 | 1240288.9473 | 2684235.0327 | 1240291.156
39 | 2684212.5922 | 1240316.8673 | 2684219.1767 | 1240306.3628
40 | 2684501.8782 | 1240408.9213 | 2684480.6489 | 1240396.7771 | 2684478.9115 | 1240395.5738
41 | 2684478.9115 | 1240395.5738 | 2684480.9335 | 1240389.0089 | 2684483.3861 | 1240384.2291
42 | 2684523.6381 | 1240342.9279 | 2684515.0409 | 1240368.8353 | 2684501.8782 | 1240408.9213
43 | 2684501.8782 | 1240408.9213 | 2684511.5109 | 1240411.716 | 2684514.5269 | 1240411.8839
44 | 2684618.1306 | 1240447.0822 | 2684619.7889 | 1240446.9391 | 2684621.7227 | 1240446.0326 | 2684623.7268 | 1240444.4378 | 2684625.448 | 1240441.4713 | 2684628.3429 | 1240423.5552
45 | 2684628.3429 | 1240423.5552 | 2684626.9841 | 1240423.3802 | 2684600.4657 | 1240418.2581
46 | 2684628.3429 | 1240423.5552 | 2684634.5226 | 1240378.8163
47 | 2684618.1306 | 1240447.0822 | 2684617.139 | 1240450.8597 | 2684624.7401 | 1240452.4024 | 2684630.0118 | 1240452.889 | 2684636.4182 | 1240452.8248
48 | 2684618.1306 | 1240447.0822 | 2684611.1994 | 1240446.0199
49 | 2684586.7086 | 1240415.6008 | 2684600.4657 | 1240418.2581
50 | 2684634.7294 | 1240377.3189 | 2684634.5226 | 1240378.8163
51 | 2684636.4182 | 1240452.8248 | 2684639.5687 | 1240424.9385 | 2684641.6942 | 1240411.1255 | 2684645.1241 | 1240384.533
52 | 2684636.4182 | 1240452.8248 | 2684645.5335 | 1240452.6546
53 | 2684514.5269 | 1240411.8839 | 2684536.4608 | 1240413.1054
54 | 2684645.1241 | 1240384.533 | 2684645.8013 | 1240379.2833 | 2684648.5056 | 1240363.5994 | 2684650.3144 | 1240350.7827 | 2684650.6434 | 1240342.0366 | 2684651.0538 | 1240339.0645
55 | 2684656.1953 | 1240452.7511 | 2684652.5104 | 1240452.3538 | 2684645.5335 | 1240452.6546
56 | 2684305.0989 | 1240311.0313 | 2684304.4767 | 1240328.2127 | 2684303.6253 | 1240342.9134
57 | 2684284.5948 | 1240289.3135 | 2684296.2075 | 1240303.5262
58 | 2684643.3459 | 1240468.1679 | 2684646.1318 | 1240465.3167 | 2684651.4112 | 1240462.0785 | 2684655.181 | 1240463.9447
59 | 2684643.3459 | 1240468.1679 | 2684638.6342 | 1240466.0659 | 2684634.4015 | 1240465.3717 | 2684618.8537 | 1240462.1367 | 2684618.4344 | 1240465.0217 | 2684616.9656 | 1240468.058
60 | 2684655.181 | 1240463.9447 | 2684659.7012 | 1240465.6882 | 2684670.5901 | 1240484.2695
61 | 2684656.1953 | 1240452.7511 | 2684655.181 | 1240463.9447
62 | 2684496.9403 | 1240272.4083 | 2684483.6844 | 1240268.078
63 | 2684261.5677 | 1240357.3801 | 2684256.3852 | 1240369.4997
64 | 2684284.5948 | 1240289.3135 | 2684281.8075 | 1240287.3464
65 | 2684281.2848 | 1240309.3699 | 2684271.2861 | 1240306.5992
66 | 2684284.5948 | 1240289.3135 | 2684282.1674 | 1240296.7511 | 2684281.0236 | 1240305.3966 | 2684281.2848 | 1240309.3699
67 | 2684584.4015 | 1240214.7342 | 2684587.8709 | 1240197.3875
68 | 2684584.4015 | 1240214.7342 | 2684565.5945 | 1240209.7862
69 | 2684584.4015 | 1240214.7342 | 2684581.0477 | 1240231.508
70 | 2684561.8943 | 1240208.8127 | 2684537.209 | 1240202.3181
71 | 2684176.2582 | 1240225.3751 | 2684173.2593 | 1240240.885
72 | 2684176.2582 | 1240225.3751 | 2684166.8812 | 1240215.713 | 2684162.2127 | 1240209.4757 | 2684159.0433 | 1240203.1151 | 2684157.2297 | 1240193.4158 | 2684156.4564 | 1240184.3141
73 | 2684177.841 | 1240223.6185 | 2684176.2582 | 1240225.3751
74 | 2684173.2593 | 1240240.885 | 2684172.5854 | 1240244.3701 | 2684166.4841 | 1240263.4889
75 | 2684150.0221 | 1240158.4644 | 2684153.0147 | 1240165.8584 | 2684155.914 | 1240177.9304 | 2684156.4564 | 1240184.3141
76 | 2684177.841 | 1240223.6185 | 2684163.4606 | 1240207.3363 | 2684160.8703 | 1240201.2063 | 2684159.0325 | 1240182.8449
77 | 2684235.0327 | 1240291.156 | 2684238.3897 | 1240294.9508 | 2684242.6443 | 1240296.6911
78 | 2684212.5922 | 1240316.8673 | 2684207.6728 | 1240326.7157 | 2684210.7944 | 1240328.439
79 | 2684212.5922 | 1240316.8673 | 2684207.2019 | 1240315.6677 | 2684199.1605 | 1240319.5565 | 2684190.7193 | 1240318.7759
80 | 2684586.7086 | 1240415.6008 | 2684584.2477 | 1240415.1255
81 | 2684637.7286 | 1240355.6053 | 2684634.7294 | 1240377.3189
82 | 2684536.4608 | 1240413.1054 | 2684541.2914 | 1240413.3744 | 2684549.9969 | 1240413.039
83 | 2684655.618 | 1240306.0137 | 2684651.0538 | 1240339.0645
84 | 2684656.1953 | 1240452.7511 | 2684657.2641 | 1240440.9134 | 2684656.7889 | 1240438.705
85 | 2684654.6759 | 1240245.1026 | 2684653.3423 | 1240251.988 | 2684649.664 | 1240272.9208
86 | 2684646.3176 | 1240293.4233 | 2684647.2596 | 1240286.604 | 2684649.664 | 1240272.9208
87 | 2684575.4337 | 1240259.586 | 2684577.0356 | 1240251.5744
88 | 2684575.4337 | 1240259.586 | 2684573.0578 | 1240271.4691 | 2684574.2121 | 1240286.0682
89 | 2684577.0356 | 1240251.5744 | 2684581.0477 | 1240231.508
90 | 2684574.7046 | 1240292.2964 | 2684574.2121 | 1240286.0682
91 | 2684574.7046 | 1240292.2964 | 2684570.5076 | 1240296.5174
92 | 2684574.7046 | 1240292.2964 | 2684576.9572 | 1240305.1044
93 | 2684574.7046 | 1240292.2964 | 2684549.252 | 1240286.1731
94 | 2684570.5076 | 1240296.5174 | 2684567.0617 | 1240294.9439
95 | 2684576.9572 | 1240305.1044 | 2684576.6243 | 1240324.7471 | 2684576.5096 | 1240325.7611
96 | 2684561.8943 | 1240208.8127 | 2684565.5945 | 1240209.7862
97 | 2684575.1658 | 1240337.6494 | 2684576.5096 | 1240325.7611
98 | 2684669.7748 | 1240230.8969 | 2684664.6436 | 1240257.1101
99 | 2684655.618 | 1240306.0137 | 2684656.6906 | 1240298.2468 | 2684664.0319 | 1240260.2352 | 2684664.6436 | 1240257.1101
100 | 2684575.1658 | 1240337.6494 | 2684574.2877 | 1240345.4176 | 2684573.072 | 1240350.0719
101 | 2684646.3176 | 1240293.4233 | 2684646.1373 | 1240294.7291
102 | 2684640.5131 | 1240335.4462 | 2684646.1373 | 1240294.7291
103 | 2684640.4824 | 1240335.6689 | 2684640.5131 | 1240335.4462
104 | 2684568.7264 | 1240366.7096 | 2684573.072 | 1240350.0719
105 | 2684568.1641 | 1240368.8627 | 2684568.7264 | 1240366.7096
106 | 2684568.1641 | 1240368.8627 | 2684563.4967 | 1240386.7323
107 | 2684640.4824 | 1240335.6689 | 2684637.7286 | 1240355.6053
108 | 2684557.4335 | 1240409.9463 | 2684563.4967 | 1240386.7323
109 | 2684557.4335 | 1240409.9463 | 2684553.088 | 1240412.9199 | 2684549.9969 | 1240413.039
110 | 2684557.4335 | 1240409.9463 | 2684568.3825 | 1240412.0611
111 | 2684584.2477 | 1240415.1255 | 2684568.3825 | 1240412.0611
112 | 2684246.0582 | 1240393.65 | 2684253.9064 | 1240375.2966
113 | 2684256.3852 | 1240369.4997 | 2684253.9064 | 1240375.2966
114 | 2684175.6886 | 1240382.2944 | 2684171.4753 | 1240384.4662 | 2684166.4971 | 1240401.1299
115 | 2684179.5482 | 1240382.0789 | 2684176.1986 | 1240382.0314 | 2684175.6886 | 1240382.2944
116 | 2684179.5482 | 1240382.0789 | 2684183.9573 | 1240382.6085
117 | 2684190.4239 | 1240367.1113 | 2684184.9031 | 1240379.9089 | 2684183.9573 | 1240382.6085
118 | 2684183.9573 | 1240382.6085 | 2684181.1541 | 1240390.6252
119 | 2684210.7944 | 1240328.439 | 2684223.2847 | 1240338.7903 | 2684224.9262 | 1240339.7467
120 | 2684210.7944 | 1240328.439 | 2684203.9751 | 1240340.4187
121 | 2684190.4239 | 1240367.1113 | 2684198.9582 | 1240350.865 | 2684199.7188 | 1240347.8959 | 2684203.9751 | 1240340.4187
122 | 2684163.8003 | 1240271.8987 | 2684166.4841 | 1240263.4889
123 | 2684076.1688 | 1240242.6777 | 2684083.2055 | 1240208.7113
124 | 2684076.1688 | 1240242.6777 | 2684069.9653 | 1240272.6224
125 | 2684060.1445 | 1240319.9871 | 2684060.2494 | 1240319.5216 | 2684069.9653 | 1240272.6224
126 | 2684082.875 | 1240397.3369 | 2684086.1322 | 1240387.3773
127 | 2684086.1322 | 1240387.3773 | 2684088.385 | 1240380.489
128 | 2684105.8401 | 1240331.0644 | 2684090.594 | 1240373.7347 | 2684088.385 | 1240380.489
129 | 2684105.8401 | 1240331.0644 | 2684114.1961 | 1240301.7728 | 2684121.2889 | 1240296.5139 | 2684133.3275 | 1240300.3586
130 | 2684105.8401 | 1240331.0644 | 2684077.8872 | 1240324.2882
131 | 2684144.5568 | 1240303.9447 | 2684133.3275 | 1240300.3586
132 | 2684077.8872 | 1240324.2882 | 2684077.6609 | 1240324.2333
133 | 2684042.2848 | 1240348.7714 | 2684044.792 | 1240342.4304 | 2684056.8529 | 1240334.5287
134 | 2684060.1445 | 1240319.9871 | 2684056.8529 | 1240334.5287
135 | 2684060.1445 | 1240319.9871 | 2684077.6609 | 1240324.2333
136 | 2684157.6145 | 1240308.1148 | 2684144.5568 | 1240303.9447
137 | 2684163.8003 | 1240271.8987 | 2684127.7831 | 1240265.7283 | 2684122.471 | 1240268.0769
138 | 2684163.8003 | 1240271.8987 | 2684153.4052 | 1240300.9611 | 2684159.5296 | 1240302.6603
139 | 2684157.6145 | 1240308.1148 | 2684165.9411 | 1240310.7792 | 2684166.644 | 1240324.6658
140 | 2684157.6145 | 1240308.1148 | 2684159.5296 | 1240302.6603
141 | 2684166.644 | 1240324.6658 | 2684154.8419 | 1240354.2976
142 | 2684166.644 | 1240324.6658 | 2684178.851 | 1240317.6783 | 2684190.7193 | 1240318.7759
143 | 2684113.8974 | 1240286.5687 | 2684122.471 | 1240268.0769
144 | 2684190.4239 | 1240367.1113 | 2684211.1979 | 1240374.1779
145 | 2684218.3514 | 1240389.0453 | 2684219.7479 | 1240381.2373 | 2684217.1523 | 1240377.0864 | 2684213.2436 | 1240374.8738 | 2684211.1979 | 1240374.1779

## bus_geodata
| x | y | coords
0 | 2684444.9886 | 1240284.9072
1 | 2684456.4031 | 1240263.4251
2 | 2684469.2317 | 1240266.4344
3 | 2684429.7421 | 1240328.426
4 | 2684443.8921 | 1240357.1685
5 | 2684342.6959 | 1240333.7149
6 | 2684496.1179 | 1240275.4543
7 | 2684454.7629 | 1240374.9376
8 | 2684515.2405 | 1240196.0693
9 | 2684526.0317 | 1240198.7915
10 | 2684506.4672 | 1240236.6364
11 | 2684285.7756 | 1240233.3456
12 | 2684276.7902 | 1240154.5947
13 | 2684264.085 | 1240259.5222
14 | 2684300.902 | 1240377.5418
15 | 2684302.4458 | 1240363.2791
16 | 2684265.4104 | 1240358.7033
17 | 2684295.901 | 1240410.1342
18 | 2684248.0296 | 1240227.9338
19 | 2684262.4537 | 1240273.688
20 | 2684276.0962 | 1240283.3158
21 | 2684248.5843 | 1240281.9403
22 | 2684323.7228 | 1240324.55
23 | 2684336.82 | 1240369.1124
24 | 2684300.0068 | 1240305.3438
25 | 2684320.1205 | 1240321.53
26 | 2684531.6209 | 1240200.5632
27 | 2684235.4927 | 1240285.9254
28 | 2684238.3926 | 1240278.2277
29 | 2684237.6657 | 1240288.9473
30 | 2684219.1767 | 1240306.3628
31 | 2684220.0277 | 1240266.0372
32 | 2684478.9115 | 1240395.5738
33 | 2684501.8782 | 1240408.9213
34 | 2684483.3861 | 1240384.2291
35 | 2684628.3429 | 1240423.5552
36 | 2684618.1306 | 1240447.0822
37 | 2684600.4657 | 1240418.2581
38 | 2684634.5226 | 1240378.8163
39 | 2684636.4182 | 1240452.8248
40 | 2684611.1994 | 1240446.0199
41 | 2684523.6381 | 1240342.9279
42 | 2684514.5269 | 1240411.8839
43 | 2684645.1241 | 1240384.533
44 | 2684645.5335 | 1240452.6546
45 | 2684305.0989 | 1240311.0313
46 | 2684303.6253 | 1240342.9134
47 | 2684296.2075 | 1240303.5262
48 | 2684643.3459 | 1240468.1679
49 | 2684655.181 | 1240463.9447
50 | 2684616.9656 | 1240468.058
51 | 2684483.6844 | 1240268.078
52 | 2684496.9403 | 1240272.4083
53 | 2684516.8789 | 1240281.3972
54 | 2684261.5677 | 1240357.3801
55 | 2684281.8075 | 1240287.3464
56 | 2684328.5955 | 1240395.4161
57 | 2684281.2848 | 1240309.3699
58 | 2684271.2861 | 1240306.5992
59 | 2684284.5948 | 1240289.3135
60 | 2684587.8709 | 1240197.3875
61 | 2684584.4015 | 1240214.7342
62 | 2684537.209 | 1240202.3181
63 | 2684176.2582 | 1240225.3751
64 | 2684173.2593 | 1240240.885
65 | 2684156.4564 | 1240184.3141
66 | 2684177.841 | 1240223.6185
67 | 2684235.0327 | 1240291.156
68 | 2684212.5922 | 1240316.8673
69 | 2684586.7086 | 1240415.6008
70 | 2684634.7294 | 1240377.3189
71 | 2684536.4608 | 1240413.1054
72 | 2684651.0538 | 1240339.0645
73 | 2684656.1953 | 1240452.7511
74 | 2684654.6759 | 1240245.1026
75 | 2684649.664 | 1240272.9208
76 | 2684670.5901 | 1240484.2695
77 | 2684575.4337 | 1240259.586
78 | 2684577.0356 | 1240251.5744
79 | 2684574.2121 | 1240286.0682
80 | 2684581.0477 | 1240231.508
81 | 2684574.7046 | 1240292.2964
82 | 2684570.5076 | 1240296.5174
83 | 2684576.9572 | 1240305.1044
84 | 2684549.252 | 1240286.1731
85 | 2684565.5945 | 1240209.7862
86 | 2684567.0617 | 1240294.9439
87 | 2684576.5096 | 1240325.7611
88 | 2684669.7748 | 1240230.8969
89 | 2684664.6436 | 1240257.1101
90 | 2684655.618 | 1240306.0137
91 | 2684575.1658 | 1240337.6494
92 | 2684561.8943 | 1240208.8127
93 | 2684646.3176 | 1240293.4233
94 | 2684646.1373 | 1240294.7291
95 | 2684640.5131 | 1240335.4462
96 | 2684573.072 | 1240350.0719
97 | 2684568.7264 | 1240366.7096
98 | 2684568.1641 | 1240368.8627
99 | 2684640.4824 | 1240335.6689
100 | 2684637.7286 | 1240355.6053
101 | 2684563.4967 | 1240386.7323
102 | 2684549.9969 | 1240413.039
103 | 2684557.4335 | 1240409.9463
104 | 2684568.3825 | 1240412.0611
105 | 2684584.2477 | 1240415.1255
106 | 2684656.7889 | 1240438.705
107 | 2684246.0582 | 1240393.65
108 | 2684253.9064 | 1240375.2966
109 | 2684256.3852 | 1240369.4997
110 | 2684166.4971 | 1240401.1299
111 | 2684175.6886 | 1240382.2944
112 | 2684179.5482 | 1240382.0789
113 | 2684183.9573 | 1240382.6085
114 | 2684181.1541 | 1240390.6252
115 | 2684224.9262 | 1240339.7467
116 | 2684210.7944 | 1240328.439
117 | 2684203.9751 | 1240340.4187
118 | 2684159.0325 | 1240182.8449
119 | 2684166.4841 | 1240263.4889
120 | 2684150.0221 | 1240158.4644
121 | 2684083.2055 | 1240208.7113
122 | 2684076.1688 | 1240242.6777
123 | 2684069.9653 | 1240272.6224
124 | 2684082.875 | 1240397.3369
125 | 2684086.1322 | 1240387.3773
126 | 2684088.385 | 1240380.489
127 | 2684105.8401 | 1240331.0644
128 | 2684133.3275 | 1240300.3586
129 | 2684077.8872 | 1240324.2882
130 | 2684042.2848 | 1240348.7714
131 | 2684056.8529 | 1240334.5287
132 | 2684077.6609 | 1240324.2333
133 | 2684060.1445 | 1240319.9871
134 | 2684144.5568 | 1240303.9447
135 | 2684163.8003 | 1240271.8987
136 | 2684157.6145 | 1240308.1148
137 | 2684166.644 | 1240324.6658
138 | 2684159.5296 | 1240302.6603
139 | 2684154.8419 | 1240354.2976
140 | 2684190.7193 | 1240318.7759
141 | 2684122.471 | 1240268.0769
142 | 2684242.6443 | 1240296.6911
143 | 2684190.4239 | 1240367.1113
144 | 2684211.1979 | 1240374.1779
145 | 2684218.3514 | 1240389.0453
146 | 2684113.8974 | 1240286.5687
147 | 2684426.1249 | 1240326.9847

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97016 | -0.57651 | 0.020143 | 0.0050482
1 | 0.97063 | -0.56711 | 0 | 0
2 | 0.97088 | -0.56212 | 0.012061 | 0.0030227
3 | 1 | 0 | -0.58854 | -0.15081
4 | 0.99658 | -0.0647 | 0.061056 | 0.015302
5 | 0.99205 | -0.15101 | 0 | 0
6 | 0.97174 | -0.54524 | 0 | 0
7 | 0.99478 | -0.098838 | 0 | 0
8 | 0.9763 | -0.45548 | 0 | 0
9 | 0.97696 | -0.4426 | 0 | 0
10 | 0.97382 | -0.50412 | 0.0073627 | 0.0018453
11 | 0.98277 | -0.33038 | 0 | 0
12 | 0.98254 | -0.33486 | 0 | 0
13 | 0.98286 | -0.32858 | 0.0038579 | 0.00096687
14 | 0.98496 | -0.2879 | 0 | 0
15 | 0.98531 | -0.2811 | 0.0027284 | 0.00068381
16 | 0.98408 | -0.3051 | 0.0026002 | 0.00065168
17 | 0.98488 | -0.28959 | 0.0028475 | 0.00071365
18 | 0.98232 | -0.33902 | 0.0028776 | 0.00072119
19 | 0.98466 | -0.29343 | 0 | 0
20 | 0.98544 | -0.27842 | 0.0026648 | 0.00066786
21 | 0.98391 | -0.308 | 0.0010418 | 0.00026111
22 | 0.98984 | -0.19345 | 0 | 0
23 | 0.99123 | -0.16696 | 0.013757 | 0.0034479
24 | 0.98709 | -0.24647 | 0 | 0
25 | 0.98976 | -0.19504 | 0.01897 | 0.0047544
26 | 0.97731 | -0.4358 | 0.0044134 | 0.0011061
27 | 0.98315 | -0.32285 | 0 | 0
28 | 0.98306 | -0.32471 | 0 | 0
29 | 0.98332 | -0.31962 | 0 | 0
30 | 0.98205 | -0.34428 | 0.0031056 | 0.00077833
31 | 0.983 | -0.32581 | 0.0027572 | 0.00069102
32 | 0.99209 | -0.15003 | 0 | 0
33 | 0.98999 | -0.19026 | 0 | 0
34 | 0.9919 | -0.15375 | 0.017166 | 0.0043022
35 | 0.97964 | -0.39061 | 0 | 0
36 | 0.97818 | -0.41915 | 0 | 0
37 | 0.98183 | -0.3479 | 0.003205 | 0.00080326
38 | 0.97851 | -0.41266 | 0.0032401 | 0.00081206
39 | 0.97729 | -0.4367 | 0 | 0
40 | 0.97808 | -0.42107 | 0.015009 | 0.0037616
41 | 0.98953 | -0.19906 | 0.0071223 | 0.001785
42 | 0.98898 | -0.20957 | 0.0048263 | 0.0012096
43 | 0.97599 | -0.46225 | 0.0042448 | 0.0010639
44 | 0.97711 | -0.44016 | 0 | 0
45 | 0.98681 | -0.2519 | 0 | 0
46 | 0.98586 | -0.27043 | 0.0032679 | 0.00081902
47 | 0.98687 | -0.25077 | 0.0016927 | 0.00042423
48 | 0.97666 | -0.44914 | 0 | 0
49 | 0.97678 | -0.44679 | 0 | 0
50 | 0.97639 | -0.4543 | 0.0089423 | 0.0022412
51 | 0.97179 | -0.54423 | 0.0071454 | 0.0017908
52 | 0.97188 | -0.54239 | 0 | 0
53 | 0.9714 | -0.55194 | 0.016789 | 0.0042077
54 | 0.984 | -0.30663 | 0 | 0
55 | 0.98577 | -0.27203 | 0.0053448 | 0.0013395
56 | 0.99095 | -0.17246 | 0.011253 | 0.0028204
57 | 0.98582 | -0.27113 | 0 | 0
58 | 0.98576 | -0.27231 | 0.0063237 | 0.0015849
59 | 0.98594 | -0.2688 | 0 | 0
60 | 0.97903 | -0.40219 | 0.0042108 | 0.0010553
61 | 0.9791 | -0.40083 | 0 | 0
62 | 0.97768 | -0.42854 | 0.0027028 | 0.00067739
63 | 0.97694 | -0.44428 | 0 | 0
64 | 0.97711 | -0.44096 | 0.0029123 | 0.00072989
65 | 0.97681 | -0.44694 | 0.0012817 | 0.00032121
66 | 0.97692 | -0.44465 | 0 | 0
67 | 0.9833 | -0.31991 | 0 | 0
68 | 0.98154 | -0.35413 | 0 | 0
69 | 0.98295 | -0.32608 | 0.01058 | 0.0026515
70 | 0.97848 | -0.41331 | 0.0012432 | 0.00031159
71 | 0.98732 | -0.24154 | 0.0072234 | 0.0018103
72 | 0.9753 | -0.47575 | 0.0048665 | 0.0012197
73 | 0.97691 | -0.44422 | 0 | 0
74 | 0.97661 | -0.44999 | 0.0071846 | 0.0018006
75 | 0.9768 | -0.44627 | 0.0028743 | 0.00072037
76 | 0.97669 | -0.44851 | 0.0035591 | 0.00089201
77 | 0.98035 | -0.3765 | 0.0051435 | 0.0012891
78 | 0.98011 | -0.38109 | 0.0044172 | 0.001107
79 | 0.98116 | -0.36063 | 0.0022376 | 0.00056078
80 | 0.97955 | -0.39206 | 0.0038612 | 0.0009677
81 | 0.98136 | -0.35685 | 0 | 0
82 | 0.98134 | -0.35718 | 0 | 0
83 | 0.98179 | -0.34846 | 0.0013829 | 0.00034658
84 | 0.98127 | -0.35852 | 0.0035322 | 0.00088525
85 | 0.97861 | -0.41032 | 0.0030707 | 0.00076959
86 | 0.98133 | -0.35739 | 0.0030613 | 0.00076724
87 | 0.98248 | -0.33498 | 0.004119 | 0.0010323
88 | 0.97465 | -0.48867 | 0.0037326 | 0.00093547
89 | 0.97474 | -0.48684 | 0.00090965 | 0.00022798
90 | 0.97496 | -0.4826 | 0.0065515 | 0.001642
91 | 0.9829 | -0.32688 | 0.003553 | 0.00089048
92 | 0.97852 | -0.41212 | 0.0067884 | 0.0017013
93 | 0.977 | -0.44246 | 0.0034105 | 0.00085474
94 | 0.97701 | -0.44213 | 0.0025062 | 0.00062812
95 | 0.97762 | -0.43015 | 0.0027145 | 0.00068032
96 | 0.98335 | -0.31808 | 0.0021869 | 0.00054808
97 | 0.98398 | -0.30587 | 0.0037678 | 0.00094429
98 | 0.98407 | -0.30424 | 0.0031652 | 0.00079327
99 | 0.97763 | -0.43007 | 0.0026657 | 0.00066809
100 | 0.97803 | -0.42224 | 0.0010043 | 0.00025171
101 | 0.98479 | -0.29039 | 0.0017203 | 0.00043115
102 | 0.98632 | -0.26072 | 0.0081593 | 0.0020449
103 | 0.98573 | -0.27217 | 0 | 0
104 | 0.98467 | -0.29265 | 0.002457 | 0.00061578
105 | 0.98317 | -0.3217 | 0.0030151 | 0.00075567
106 | 0.9768 | -0.44638 | 0.008368 | 0.0020972
107 | 0.98356 | -0.31519 | 0.0051433 | 0.001289
108 | 0.98366 | -0.31335 | 0.010194 | 0.0025549
109 | 0.98375 | -0.3116 | 0.0056216 | 0.0014089
110 | 0.97889 | -0.40621 | 0.011385 | 0.0028534
111 | 0.97912 | -0.40163 | 0.0035636 | 0.00089312
112 | 0.97917 | -0.40056 | 0 | 0
113 | 0.97924 | -0.39936 | 0 | 0
114 | 0.97918 | -0.40043 | 0.0069482 | 0.0017414
115 | 0.98074 | -0.36983 | 0.010718 | 0.0026863
116 | 0.98092 | -0.36631 | 0 | 0
117 | 0.98047 | -0.37516 | 0.0032818 | 0.00082249
118 | 0.97656 | -0.45187 | 0.0084471 | 0.002117
119 | 0.97743 | -0.43474 | 0.0028984 | 0.0007264
120 | 0.97676 | -0.44782 | 0.00179 | 0.00044862
121 | 0.97363 | -0.50934 | 0.011436 | 0.0028661
122 | 0.974 | -0.50205 | 0.0034404 | 0.00086225
123 | 0.97443 | -0.49369 | 0.002464 | 0.00061754
124 | 0.97588 | -0.46509 | 0.0006684 | 0.00016752
125 | 0.97589 | -0.46496 | 0.0022336 | 0.00055978
126 | 0.97591 | -0.46457 | 0.0028459 | 0.00071325
127 | 0.97619 | -0.45906 | 0 | 0
128 | 0.97759 | -0.43147 | 0.0028244 | 0.00070785
129 | 0.97556 | -0.47135 | 0.001059 | 0.00026541
130 | 0.97512 | -0.48001 | 0.0019635 | 0.0004921
131 | 0.97516 | -0.47924 | 0.0014646 | 0.00036707
132 | 0.97556 | -0.47144 | 0.0015109 | 0.00037866
133 | 0.97521 | -0.4783 | 0 | 0
134 | 0.97794 | -0.42461 | 0.011087 | 0.0027785
135 | 0.97757 | -0.43195 | 0 | 0
136 | 0.97849 | -0.41387 | 0 | 0
137 | 0.97996 | -0.3851 | 0 | 0
138 | 0.97834 | -0.4167 | 0.0044741 | 0.0011213
139 | 0.97963 | -0.39156 | 0.011147 | 0.0027937
140 | 0.98094 | -0.366 | 0.0046408 | 0.0011631
141 | 0.97737 | -0.43591 | 0.0025799 | 0.00064659
142 | 0.98326 | -0.32071 | 0.0046063 | 0.0011545
143 | 0.97958 | -0.39267 | 0 | 0
144 | 0.97937 | -0.39676 | 0.0075276 | 0.0018866
145 | 0.97932 | -0.39772 | 0.0027213 | 0.00068202
146 | 0.97732 | -0.43686 | 0.0025504 | 0.00063919
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020143 | -0.0050482 | 0.020152 | 0.0050537 | 9.0207e-06 | 5.4619e-06 | 0.030894 | 0.030894 | 0.030894 | 0.97016 | -0.57651 | 0.97063 | -0.56711 | 8.4875
1 | -0.020152 | -0.0050537 | 0.020156 | 0.0050566 | 4.7973e-06 | 2.9046e-06 | 0.030894 | 0.030894 | 0.030894 | 0.97063 | -0.56711 | 0.97088 | -0.56212 | 8.4875
2 | -0.032217 | -0.0080792 | 0.032243 | 0.0080955 | 2.5936e-05 | 1.6248e-05 | 0.049379 | 0.049379 | 0.049379 | 0.97088 | -0.56212 | 0.97174 | -0.54524 | 13.5656
3 | 0.34027 | 0.087434 | -0.33921 | -0.086753 | 0.0010657 | 0.00068075 | 0.5071 | 0.5071 | 0.5071 | 1 | 0 | 0.99658 | -0.0647 | 46.4376
4 | 0.24662 | 0.063373 | -0.24482 | -0.062228 | 0.0017947 | 0.0011444 | 0.36753 | 0.36753 | 0.36753 | 1 | 0 | 0.99205 | -0.15101 | 33.6566
5 | 0.27815 | 0.071451 | -0.27769 | -0.071158 | 0.00046029 | 0.00029376 | 0.41594 | 0.41594 | 0.41594 | 0.99658 | -0.0647 | 0.99478 | -0.098838 | 38.0894
6 | 0.21979 | 0.055947 | -0.21934 | -0.055661 | 0.00044874 | 0.00028592 | 0.32998 | 0.32998 | 0.32998 | 0.99205 | -0.15101 | 0.98984 | -0.19345 | 30.218
7 | 0.025033 | 0.0062815 | -0.025013 | -0.0062698 | 1.9022e-05 | 1.171e-05 | 0.03755 | 0.03755 | 0.03755 | 0.99205 | -0.15101 | 0.99123 | -0.16696 | 10.3159
8 | 0.016794 | 0.0042109 | -0.016789 | -0.0042077 | 5.3561e-06 | 3.1605e-06 | 0.025718 | 0.025718 | 0.025718 | 0.97174 | -0.54524 | 0.9714 | -0.55194 | 7.0653
9 | -0.049037 | -0.012306 | 0.049044 | 0.012311 | 6.6722e-06 | 4.2311e-06 | 0.075096 | 0.075096 | 0.075096 | 0.97174 | -0.54524 | 0.97188 | -0.54239 | 20.6309
10 | 0.27769 | 0.071158 | -0.27701 | -0.070719 | 0.0006871 | 0.00043851 | 0.41594 | 0.41594 | 0.41594 | 0.99478 | -0.098838 | 0.99209 | -0.15003 | 38.0894
11 | -0.063804 | -0.016107 | 0.063843 | 0.016132 | 3.939e-05 | 2.5071e-05 | 0.097287 | 0.097287 | 0.097287 | 0.9763 | -0.45548 | 0.97696 | -0.4426 | 26.7273
12 | 0.063804 | 0.016107 | -0.063655 | -0.016012 | 0.00014829 | 9.4384e-05 | 0.097287 | 0.097288 | 0.097288 | 0.9763 | -0.45548 | 0.97382 | -0.50412 | 26.7274
13 | -0.063843 | -0.016132 | 0.063864 | 0.016145 | 2.0811e-05 | 1.3245e-05 | 0.097287 | 0.097287 | 0.097287 | 0.97696 | -0.4426 | 0.97731 | -0.4358 | 26.7273
14 | 0.056293 | 0.014167 | -0.05619 | -0.014102 | 0.00010276 | 6.5307e-05 | 0.086037 | 0.086037 | 0.086037 | 0.97382 | -0.50412 | 0.97188 | -0.54239 | 23.6367
15 | 0.0028788 | 0.00071985 | -0.0028782 | -0.00072055 | 6.1409e-07 | -6.9907e-07 | 0.0043582 | 0.0043586 | 0.0043586 | 0.98277 | -0.33038 | 0.98254 | -0.33486 | 1.1974
16 | -0.0028788 | -0.00071985 | 0.002879 | 0.00071957 | 2.464e-07 | -2.8069e-07 | 0.0043582 | 0.004358 | 0.0043582 | 0.98277 | -0.33038 | 0.98286 | -0.32858 | 1.1973
17 | 0.0028782 | 0.00072055 | -0.0028776 | -0.00072119 | 5.6982e-07 | -6.4804e-07 | 0.0043586 | 0.004359 | 0.004359 | 0.98254 | -0.33486 | 0.98232 | -0.33902 | 1.1975
18 | -0.0067369 | -0.0016864 | 0.0067381 | 0.0016868 | 1.2396e-06 | 3.9049e-07 | 0.010199 | 0.010199 | 0.010199 | 0.98286 | -0.32858 | 0.98306 | -0.32471 | 2.8018
19 | -0.026435 | -0.0066345 | 0.026443 | 0.0066398 | 8.5845e-06 | 5.3113e-06 | 0.039939 | 0.039939 | 0.039939 | 0.98496 | -0.2879 | 0.98531 | -0.2811 | 10.9723
20 | 0.023587 | 0.0059211 | -0.023568 | -0.0059093 | 1.9325e-05 | 1.1852e-05 | 0.035637 | 0.035637 | 0.035637 | 0.98496 | -0.2879 | 0.98408 | -0.3051 | 9.7905
21 | 0.0028477 | 0.00071338 | -0.0028475 | -0.00071365 | 2.2893e-07 | -2.7326e-07 | 0.0043021 | 0.0043022 | 0.0043022 | 0.98496 | -0.2879 | 0.98488 | -0.28959 | 1.1819
22 | -0.029172 | -0.0073236 | 0.029187 | 0.0073329 | 1.485e-05 | 9.2443e-06 | 0.04406 | 0.044059 | 0.04406 | 0.98531 | -0.2811 | 0.98586 | -0.27043 | 12.1043
23 | 0.020967 | 0.0052576 | -0.020966 | -0.0052566 | 1.532e-06 | 9.2888e-07 | 0.031705 | 0.031705 | 0.031705 | 0.98408 | -0.3051 | 0.984 | -0.30663 | 8.7103
24 | -0.15098 | -0.038162 | 0.15109 | 0.038231 | 0.00010877 | 6.8974e-05 | 0.22828 | 0.22828 | 0.22828 | 0.98466 | -0.29343 | 0.98544 | -0.27842 | 20.9048
25 | 0.15098 | 0.038162 | -0.15088 | -0.038095 | 0.00010538 | 6.6827e-05 | 0.22828 | 0.22828 | 0.22828 | 0.98466 | -0.29343 | 0.98391 | -0.308 | 20.9048
26 | -0.15376 | -0.038898 | 0.1538 | 0.038928 | 4.7155e-05 | 2.9912e-05 | 0.2323 | 0.2323 | 0.2323 | 0.98544 | -0.27842 | 0.98577 | -0.27203 | 21.2733
27 | 0.14984 | 0.037834 | -0.14975 | -0.037781 | 8.3418e-05 | 5.2893e-05 | 0.22671 | 0.22671 | 0.22671 | 0.98391 | -0.308 | 0.98332 | -0.31962 | 20.7606
28 | 0.20037 | 0.050906 | -0.19986 | -0.050581 | 0.00051003 | 0.00032469 | 0.30146 | 0.30146 | 0.30146 | 0.98984 | -0.19345 | 0.98709 | -0.24647 | 27.6063
29 | 0.018972 | 0.0047553 | -0.01897 | -0.0047544 | 1.4362e-06 | 8.5867e-07 | 0.02852 | 0.02852 | 0.02852 | 0.98984 | -0.19345 | 0.98976 | -0.19504 | 7.8352
30 | 0.011256 | 0.0028219 | -0.011253 | -0.0028204 | 2.9527e-06 | 1.5344e-06 | 0.016898 | 0.016898 | 0.016898 | 0.99123 | -0.16696 | 0.99095 | -0.17246 | 4.6424
31 | 0.16737 | 0.042406 | -0.16733 | -0.042384 | 3.4602e-05 | 2.1979e-05 | 0.25247 | 0.25247 | 0.25247 | 0.98709 | -0.24647 | 0.98687 | -0.25077 | 23.1199
32 | 0.032492 | 0.0081751 | -0.032483 | -0.0081699 | 8.4255e-06 | 5.2727e-06 | 0.048992 | 0.048992 | 0.048992 | 0.98709 | -0.24647 | 0.98681 | -0.2519 | 13.4593
33 | -0.068277 | -0.017251 | 0.068301 | 0.017266 | 2.3761e-05 | 1.5134e-05 | 0.10401 | 0.10401 | 0.10401 | 0.97731 | -0.4358 | 0.97768 | -0.42854 | 28.5734
34 | 0.0094963 | 0.0023781 | -0.0094955 | -0.0023777 | 8.4203e-07 | 4.0106e-07 | 0.014372 | 0.014372 | 0.014372 | 0.98315 | -0.32285 | 0.98306 | -0.32471 | 3.9484
35 | -0.14512 | -0.036612 | 0.14515 | 0.036626 | 2.244e-05 | 1.422e-05 | 0.21973 | 0.21973 | 0.21973 | 0.98315 | -0.32285 | 0.98332 | -0.31962 | 20.1222
36 | 0.13563 | 0.034234 | -0.13549 | -0.034146 | 0.00013903 | 8.7976e-05 | 0.20536 | 0.20536 | 0.20536 | 0.98315 | -0.32285 | 0.98205 | -0.34428 | 18.8061
37 | 0.0027574 | 0.00069083 | -0.0027572 | -0.00069102 | 1.4399e-07 | -1.873e-07 | 0.0041736 | 0.0041737 | 0.0041737 | 0.98306 | -0.32471 | 0.983 | -0.32581 | 1.1466
38 | 0.0046066 | 0.0011544 | -0.0046065 | -0.0011544 | 6.2522e-08 | -3.508e-09 | 0.0069709 | 0.0069709 | 0.0069709 | 0.98332 | -0.31962 | 0.9833 | -0.31991 | 1.9151
39 | 0.13238 | 0.033368 | -0.13232 | -0.033328 | 6.2396e-05 | 3.9463e-05 | 0.20066 | 0.20066 | 0.20066 | 0.98205 | -0.34428 | 0.98154 | -0.35413 | 18.3752
40 | 0.25984 | 0.066415 | -0.25933 | -0.066093 | 0.00050454 | 0.00032188 | 0.39019 | 0.39019 | 0.39019 | 0.99209 | -0.15003 | 0.98999 | -0.19026 | 35.7313
41 | 0.017169 | 0.004304 | -0.017166 | -0.0043022 | 3.0442e-06 | 1.7903e-06 | 0.025752 | 0.025752 | 0.025752 | 0.99209 | -0.15003 | 0.9919 | -0.15375 | 7.0747
42 | 0.0071253 | 0.001786 | -0.0071223 | -0.001785 | 2.9886e-06 | 1.0198e-06 | 0.01071 | 0.01071 | 0.01071 | 0.98999 | -0.19026 | 0.98953 | -0.19906 | 2.9424
43 | 0.25221 | 0.064307 | -0.25197 | -0.064157 | 0.00023491 | 0.00014984 | 0.37948 | 0.37948 | 0.37948 | 0.98999 | -0.19026 | 0.98898 | -0.20957 | 34.7505
44 | 0.05635 | 0.014182 | -0.056273 | -0.014133 | 7.6758e-05 | 4.8774e-05 | 0.085613 | 0.085614 | 0.085614 | 0.97964 | -0.39061 | 0.97818 | -0.41915 | 23.5202
45 | -0.083252 | -0.020945 | 0.083423 | 0.021054 | 0.00017025 | 0.0001086 | 0.12648 | 0.12648 | 0.12648 | 0.97964 | -0.39061 | 0.98183 | -0.3479 | 34.7485
46 | 0.026903 | 0.0067631 | -0.026874 | -0.0067456 | 2.8291e-05 | 1.7538e-05 | 0.040871 | 0.040871 | 0.040871 | 0.97964 | -0.39061 | 0.97851 | -0.41266 | 11.2283
47 | 0.041262 | 0.010371 | -0.041228 | -0.010349 | 3.4529e-05 | 2.1805e-05 | 0.062779 | 0.06278 | 0.06278 | 0.97818 | -0.41915 | 0.97729 | -0.4367 | 17.2471
48 | 0.01501 | 0.0037624 | -0.015009 | -0.0037616 | 1.3711e-06 | 7.8946e-07 | 0.022834 | 0.022834 | 0.022834 | 0.97818 | -0.41915 | 0.97808 | -0.42107 | 6.2731
49 | -0.086628 | -0.021857 | 0.086718 | 0.021915 | 9.064e-05 | 5.7832e-05 | 0.13134 | 0.13134 | 0.13134 | 0.98183 | -0.3479 | 0.98295 | -0.32608 | 36.0829
50 | 0.023634 | 0.0059336 | -0.023633 | -0.0059331 | 7.3237e-07 | 4.4973e-07 | 0.035944 | 0.035944 | 0.035944 | 0.97851 | -0.41266 | 0.97848 | -0.41331 | 9.8747
51 | 0.020345 | 0.0051118 | -0.02032 | -0.0050968 | 2.4784e-05 | 1.5e-05 | 0.030982 | 0.030982 | 0.030982 | 0.97729 | -0.4367 | 0.97599 | -0.46225 | 8.5117
52 | 0.020883 | 0.0052375 | -0.020879 | -0.0052354 | 3.4465e-06 | 2.0919e-06 | 0.031797 | 0.031797 | 0.031797 | 0.97729 | -0.4367 | 0.97711 | -0.44016 | 8.7356
53 | 0.24715 | 0.062948 | -0.24676 | -0.062705 | 0.00038044 | 0.00024264 | 0.37221 | 0.37221 | 0.37221 | 0.98898 | -0.20957 | 0.98732 | -0.24154 | 34.0856
54 | 0.016076 | 0.0040329 | -0.016065 | -0.0040269 | 1.0342e-05 | 6.0456e-06 | 0.024511 | 0.024511 | 0.024511 | 0.97599 | -0.46225 | 0.9753 | -0.47575 | 6.7337
55 | 0.020879 | 0.0052354 | -0.020875 | -0.0052329 | 4.041e-06 | 2.4528e-06 | 0.031797 | 0.031798 | 0.031798 | 0.97711 | -0.44016 | 0.97691 | -0.44422 | 8.7356
56 | 0.032483 | 0.0081699 | -0.032455 | -0.0081519 | 2.8729e-05 | 1.7979e-05 | 0.048992 | 0.048992 | 0.048992 | 0.98681 | -0.2519 | 0.98586 | -0.27043 | 13.4593
57 | 0.16564 | 0.04196 | -0.1655 | -0.041869 | 0.00014329 | 9.1004e-05 | 0.24992 | 0.24992 | 0.24992 | 0.98687 | -0.25077 | 0.98594 | -0.2688 | 22.8862
58 | -0.0089445 | -0.0022422 | 0.0089455 | 0.0022426 | 9.9995e-07 | 4.6027e-07 | 0.013628 | 0.013628 | 0.013628 | 0.97666 | -0.44914 | 0.97678 | -0.44679 | 3.7439
59 | 0.0089445 | 0.0022422 | -0.0089423 | -0.0022412 | 2.202e-06 | 1.0137e-06 | 0.013628 | 0.013628 | 0.013628 | 0.97666 | -0.44914 | 0.97639 | -0.4543 | 3.744
60 | 0.0035594 | 0.00089186 | -0.0035591 | -0.00089201 | 2.9088e-07 | -1.4402e-07 | 0.0054224 | 0.0054225 | 0.0054225 | 0.97678 | -0.44679 | 0.97669 | -0.44851 | 1.4897
61 | -0.012505 | -0.0031345 | 0.012506 | 0.0031353 | 1.5298e-06 | 8.3834e-07 | 0.01905 | 0.01905 | 0.01905 | 0.97678 | -0.44679 | 0.97691 | -0.44422 | 5.2336
62 | -0.0071454 | -0.0017908 | 0.0071461 | 0.001791 | 6.2601e-07 | 2.2785e-07 | 0.010941 | 0.010941 | 0.010941 | 0.97179 | -0.54423 | 0.97188 | -0.54239 | 3.0058
63 | 0.020966 | 0.0052566 | -0.020961 | -0.0052536 | 4.9688e-06 | 3.0127e-06 | 0.031705 | 0.031706 | 0.031706 | 0.984 | -0.30663 | 0.98375 | -0.3116 | 8.7103
64 | -0.15915 | -0.040268 | 0.15917 | 0.040283 | 2.4639e-05 | 1.5639e-05 | 0.24037 | 0.24037 | 0.24037 | 0.98577 | -0.27203 | 0.98594 | -0.2688 | 22.0121
65 | 0.006324 | 0.001585 | -0.0063237 | -0.0015849 | 3.5453e-07 | 9.4622e-08 | 0.0095457 | 0.0095457 | 0.0095457 | 0.98582 | -0.27113 | 0.98576 | -0.27231 | 2.6224
66 | -0.006324 | -0.001585 | 0.0063247 | 0.0015851 | 7.014e-07 | 1.8715e-07 | 0.0095457 | 0.0095456 | 0.0095457 | 0.98582 | -0.27113 | 0.98594 | -0.2688 | 2.6224
67 | -0.0042108 | -0.0010553 | 0.0042111 | 0.0010553 | 2.7172e-07 | -4.8566e-08 | 0.0064 | 0.0063999 | 0.0064 | 0.97903 | -0.40219 | 0.9791 | -0.40083 | 1.7582
68 | 0.080962 | 0.020477 | -0.080926 | -0.020454 | 3.6844e-05 | 2.2847e-05 | 0.12311 | 0.12311 | 0.12311 | 0.9791 | -0.40083 | 0.97861 | -0.41032 | 11.274
69 | -0.085174 | -0.021532 | 0.085209 | 0.021554 | 3.5865e-05 | 2.2308e-05 | 0.12951 | 0.12951 | 0.12951 | 0.9791 | -0.40083 | 0.97955 | -0.39206 | 11.8601
70 | -0.071004 | -0.017944 | 0.07106 | 0.017979 | 5.5949e-05 | 3.5166e-05 | 0.10812 | 0.10812 | 0.10812 | 0.97768 | -0.42854 | 0.97852 | -0.41212 | 14.8517
71 | -0.011522 | -0.0028876 | 0.011524 | 0.0028886 | 1.8246e-06 | 9.6989e-07 | 0.01755 | 0.01755 | 0.01755 | 0.97694 | -0.44428 | 0.97711 | -0.44096 | 4.8214
72 | 0.0030721 | 0.0007692 | -0.0030717 | -0.00076955 | 3.8887e-07 | -3.4409e-07 | 0.004679 | 0.0046792 | 0.0046792 | 0.97694 | -0.44428 | 0.97681 | -0.44694 | 1.2855
73 | 0.0084502 | 0.0021184 | -0.00845 | -0.0021183 | 1.4674e-07 | 6.4336e-08 | 0.012871 | 0.012871 | 0.012871 | 0.97694 | -0.44428 | 0.97692 | -0.44465 | 3.536
74 | -0.014436 | -0.0036184 | 0.014441 | 0.0036209 | 4.2809e-06 | 2.4438e-06 | 0.021985 | 0.021985 | 0.021985 | 0.97711 | -0.44096 | 0.97743 | -0.43474 | 6.0398
75 | 0.0017901 | 0.00044833 | -0.00179 | -0.00044862 | 7.4727e-08 | -2.8762e-07 | 0.0027268 | 0.0027269 | 0.0027269 | 0.97681 | -0.44694 | 0.97676 | -0.44782 | 0.74916
76 | 0.00845 | 0.0021183 | -0.0084471 | -0.002117 | 2.9094e-06 | 1.2759e-06 | 0.012871 | 0.012871 | 0.012871 | 0.97692 | -0.44465 | 0.97656 | -0.45187 | 3.536
77 | 0.0046065 | 0.0011544 | -0.0046063 | -0.0011545 | 1.7609e-07 | -9.8723e-09 | 0.0069709 | 0.006971 | 0.006971 | 0.9833 | -0.31991 | 0.98326 | -0.32071 | 1.9151
78 | 0.04623 | 0.011617 | -0.046203 | -0.0116 | 2.6854e-05 | 1.7002e-05 | 0.070096 | 0.070096 | 0.070096 | 0.98154 | -0.35413 | 0.98092 | -0.36631 | 19.2571
79 | 0.086091 | 0.021711 | -0.086042 | -0.021681 | 4.8863e-05 | 3.0403e-05 | 0.13056 | 0.13056 | 0.13056 | 0.98154 | -0.35413 | 0.98094 | -0.366 | 11.9562
80 | -0.097298 | -0.024567 | 0.097318 | 0.02458 | 2.0409e-05 | 1.303e-05 | 0.14736 | 0.14736 | 0.14736 | 0.98295 | -0.32608 | 0.98317 | -0.3217 | 40.4829
81 | 0.02239 | 0.0056215 | -0.022381 | -0.0056157 | 9.532e-06 | 5.8253e-06 | 0.034053 | 0.034053 | 0.034053 | 0.97848 | -0.41331 | 0.97803 | -0.42224 | 9.3553
82 | 0.23954 | 0.060895 | -0.23932 | -0.060754 | 0.00022113 | 0.00014101 | 0.36133 | 0.36133 | 0.36133 | 0.98732 | -0.24154 | 0.98632 | -0.26072 | 33.0887
83 | 0.011199 | 0.0028072 | -0.011195 | -0.0028053 | 3.6526e-06 | 1.9214e-06 | 0.017086 | 0.017086 | 0.017086 | 0.9753 | -0.47575 | 0.97496 | -0.4826 | 4.694
84 | 0.0083688 | 0.0020976 | -0.008368 | -0.0020972 | 8.6193e-07 | 3.7456e-07 | 0.012747 | 0.012747 | 0.012747 | 0.97691 | -0.44422 | 0.9768 | -0.44638 | 3.502
85 | -0.0071846 | -0.0018006 | 0.0071859 | 0.0018011 | 1.2702e-06 | 4.5917e-07 | 0.010947 | 0.010947 | 0.010947 | 0.97661 | -0.44999 | 0.9768 | -0.44627 | 3.0074
86 | -0.01006 | -0.0025215 | 0.010062 | 0.0025224 | 1.8299e-06 | 9.11e-07 | 0.015325 | 0.015325 | 0.015325 | 0.9768 | -0.44627 | 0.977 | -0.44246 | 4.2102
87 | 0.093555 | 0.023671 | -0.093535 | -0.023658 | 2.0617e-05 | 1.2886e-05 | 0.14208 | 0.14208 | 0.14208 | 0.98035 | -0.3765 | 0.98011 | -0.38109 | 13.0113
88 | -0.098699 | -0.02496 | 0.098774 | 0.025007 | 7.5161e-05 | 4.709e-05 | 0.14989 | 0.14989 | 0.14989 | 0.98035 | -0.3765 | 0.98116 | -0.36063 | 13.7262
89 | 0.089118 | 0.022551 | -0.089071 | -0.022522 | 4.6879e-05 | 2.923e-05 | 0.13538 | 0.13538 | 0.13538 | 0.98011 | -0.38109 | 0.97955 | -0.39206 | 12.3972
90 | -0.10101 | -0.025568 | 0.10103 | 0.02558 | 1.8349e-05 | 1.1507e-05 | 0.15328 | 0.15328 | 0.15328 | 0.98116 | -0.36063 | 0.98136 | -0.35685 | 14.0369
91 | 0.0030614 | 0.00076717 | -0.0030614 | -0.00076721 | 4.803e-08 | -4.436e-08 | 0.0046419 | 0.0046419 | 0.0046419 | 0.98136 | -0.35685 | 0.98134 | -0.35718 | 1.2753
92 | -0.10762 | -0.027232 | 0.10767 | 0.027259 | 4.3339e-05 | 2.7244e-05 | 0.16328 | 0.16328 | 0.16328 | 0.98136 | -0.35685 | 0.98179 | -0.34846 | 14.9525
93 | 0.0035325 | 0.0008851 | -0.0035322 | -0.00088525 | 2.8164e-07 | -1.5048e-07 | 0.0053562 | 0.0053563 | 0.0053563 | 0.98136 | -0.35685 | 0.98127 | -0.35852 | 1.4715
94 | 0.0030614 | 0.00076721 | -0.0030613 | -0.00076724 | 3.0609e-08 | -2.8269e-08 | 0.0046419 | 0.004642 | 0.004642 | 0.98134 | -0.35718 | 0.98133 | -0.35739 | 1.2753
95 | -0.10905 | -0.027606 | 0.10912 | 0.02765 | 7.065e-05 | 4.4432e-05 | 0.16538 | 0.16538 | 0.16538 | 0.98179 | -0.34846 | 0.98248 | -0.33498 | 15.1444
96 | 0.077855 | 0.019684 | -0.077848 | -0.01968 | 6.7095e-06 | 4.1499e-06 | 0.11844 | 0.11844 | 0.11844 | 0.97861 | -0.41032 | 0.97852 | -0.41212 | 10.8465
97 | -0.11324 | -0.028682 | 0.11328 | 0.02871 | 4.4045e-05 | 2.7734e-05 | 0.17162 | 0.17161 | 0.17162 | 0.98248 | -0.33498 | 0.9829 | -0.32688 | 15.7157
98 | -0.0037326 | -0.00093547 | 0.0037329 | 0.00093534 | 3.2527e-07 | -1.2474e-07 | 0.0056986 | 0.0056984 | 0.0056986 | 0.97465 | -0.48867 | 0.97474 | -0.48684 | 1.5655
99 | -0.0046425 | -0.0011633 | 0.0046435 | 0.0011633 | 9.3681e-07 | -2.0568e-08 | 0.0070871 | 0.0070869 | 0.0070871 | 0.97474 | -0.48684 | 0.97496 | -0.4826 | 1.947
100 | -0.11684 | -0.029601 | 0.11689 | 0.029632 | 4.945e-05 | 3.1167e-05 | 0.17699 | 0.17699 | 0.17699 | 0.9829 | -0.32688 | 0.98335 | -0.31808 | 16.2082
101 | -0.013472 | -0.0033771 | 0.013473 | 0.0033772 | 2.0813e-07 | 1.167e-07 | 0.020519 | 0.020519 | 0.020519 | 0.977 | -0.44246 | 0.97701 | -0.44213 | 5.6372
102 | -0.015979 | -0.0040053 | 0.015988 | 0.0040107 | 9.129e-06 | 5.3275e-06 | 0.024336 | 0.024336 | 0.024336 | 0.97701 | -0.44213 | 0.97762 | -0.43015 | 6.6858
103 | -0.018703 | -0.004691 | 0.018703 | 0.004691 | 6.8309e-08 | 4.09e-08 | 0.028468 | 0.028468 | 0.028468 | 0.97762 | -0.43015 | 0.97763 | -0.43007 | 7.8209
104 | -0.11907 | -0.03018 | 0.11914 | 0.030224 | 6.9878e-05 | 4.4067e-05 | 0.1803 | 0.1803 | 0.1803 | 0.98335 | -0.31808 | 0.98398 | -0.30587 | 16.5113
105 | -0.12291 | -0.031168 | 0.12292 | 0.031174 | 9.6234e-06 | 6.0742e-06 | 0.186 | 0.186 | 0.186 | 0.98398 | -0.30587 | 0.98407 | -0.30424 | 17.033
106 | -0.12609 | -0.031968 | 0.12617 | 0.032021 | 8.4033e-05 | 5.3076e-05 | 0.19079 | 0.19079 | 0.19079 | 0.98407 | -0.30424 | 0.98479 | -0.29039 | 17.4713
107 | -0.021368 | -0.0053591 | 0.021376 | 0.005364 | 7.9841e-06 | 4.8574e-06 | 0.032525 | 0.032525 | 0.032525 | 0.97763 | -0.43007 | 0.97803 | -0.42224 | 8.9355
108 | -0.12789 | -0.032452 | 0.128 | 0.032523 | 0.00011216 | 7.0866e-05 | 0.19339 | 0.19339 | 0.19339 | 0.98479 | -0.29039 | 0.98573 | -0.27217 | 17.7093
109 | 0.23116 | 0.058709 | -0.23103 | -0.058628 | 0.00012728 | 8.1139e-05 | 0.34902 | 0.34902 | 0.34902 | 0.98632 | -0.26072 | 0.98573 | -0.27217 | 31.9614
110 | 0.10303 | 0.026105 | -0.10293 | -0.02604 | 0.00010129 | 6.4684e-05 | 0.15563 | 0.15563 | 0.15563 | 0.98573 | -0.27217 | 0.98467 | -0.29265 | 42.7565
111 | 0.10047 | 0.025425 | -0.10033 | -0.025335 | 0.00013985 | 8.9299e-05 | 0.15192 | 0.15192 | 0.15192 | 0.98467 | -0.29265 | 0.98317 | -0.3217 | 41.7365
112 | -0.0051433 | -0.001289 | 0.0051438 | 0.0012891 | 4.5322e-07 | 3.6699e-08 | 0.0077813 | 0.0077812 | 0.0077813 | 0.98356 | -0.31519 | 0.98366 | -0.31335 | 2.1377
113 | -0.015338 | -0.003844 | 0.015339 | 0.0038447 | 1.2728e-06 | 7.3454e-07 | 0.023202 | 0.023202 | 0.023202 | 0.98366 | -0.31335 | 0.98375 | -0.3116 | 6.3743
114 | -0.011385 | -0.0028534 | 0.011388 | 0.0028547 | 2.4859e-06 | 1.3127e-06 | 0.017307 | 0.017307 | 0.017307 | 0.97889 | -0.40621 | 0.97912 | -0.40163 | 4.7546
115 | -0.014951 | -0.0037479 | 0.014952 | 0.0037483 | 7.5971e-07 | 4.3686e-07 | 0.022723 | 0.022723 | 0.022723 | 0.97912 | -0.40163 | 0.97917 | -0.40056 | 6.2425
116 | -0.014952 | -0.0037483 | 0.014953 | 0.0037488 | 8.5734e-07 | 4.9299e-07 | 0.022723 | 0.022723 | 0.022723 | 0.97917 | -0.40056 | 0.97924 | -0.39936 | 6.2425
117 | -0.021902 | -0.0054903 | 0.021909 | 0.0054945 | 6.9752e-06 | 4.2528e-06 | 0.033281 | 0.033281 | 0.033281 | 0.97924 | -0.39936 | 0.97958 | -0.39267 | 9.1432
118 | 0.0069486 | 0.0017415 | -0.0069482 | -0.0017414 | 3.5507e-07 | 1.2041e-07 | 0.010559 | 0.010559 | 0.010559 | 0.97924 | -0.39936 | 0.97918 | -0.40043 | 2.9008
119 | -0.010718 | -0.0026863 | 0.01072 | 0.0026872 | 1.7972e-06 | 9.2151e-07 | 0.016262 | 0.016262 | 0.016262 | 0.98074 | -0.36983 | 0.98092 | -0.36631 | 4.4677
120 | 0.035483 | 0.0089127 | -0.035468 | -0.0089033 | 1.4981e-05 | 9.4137e-06 | 0.053834 | 0.053834 | 0.053834 | 0.98092 | -0.36631 | 0.98047 | -0.37516 | 14.7894
121 | 0.032186 | 0.0080808 | -0.03216 | -0.008064 | 2.6868e-05 | 1.6817e-05 | 0.048853 | 0.048853 | 0.048853 | 0.98047 | -0.37516 | 0.97958 | -0.39267 | 13.4212
122 | -0.017339 | -0.0043473 | 0.017341 | 0.0043487 | 2.3067e-06 | 1.3656e-06 | 0.026397 | 0.026397 | 0.026397 | 0.97743 | -0.43474 | 0.97757 | -0.43195 | 7.252
123 | -0.011436 | -0.0028661 | 0.01144 | 0.0028682 | 3.9734e-06 | 2.1114e-06 | 0.017478 | 0.017477 | 0.017478 | 0.97363 | -0.50934 | 0.974 | -0.50205 | 4.8015
124 | -0.01488 | -0.0037304 | 0.014886 | 0.0037339 | 5.9265e-06 | 3.4122e-06 | 0.022733 | 0.022733 | 0.022733 | 0.974 | -0.50205 | 0.97443 | -0.49369 | 6.2454
125 | -0.01735 | -0.0043514 | 0.017363 | 0.0043589 | 1.2735e-05 | 7.5471e-06 | 0.026496 | 0.026496 | 0.026496 | 0.97443 | -0.49369 | 0.97521 | -0.4783 | 7.2791
126 | -0.0006684 | -0.00016752 | 0.0006684 | 0.00016739 | 4.0814e-09 | -1.2831e-07 | 0.0010192 | 0.0010191 | 0.0010192 | 0.97588 | -0.46509 | 0.97589 | -0.46496 | 0.27999
127 | -0.002902 | -0.00072717 | 0.002902 | 0.00072711 | 5.321e-08 | -5.6497e-08 | 0.0044248 | 0.0044248 | 0.0044248 | 0.97589 | -0.46496 | 0.97591 | -0.46457 | 1.2156
128 | -0.0057479 | -0.0014404 | 0.0057494 | 0.0014407 | 1.5098e-06 | 3.1112e-07 | 0.0087641 | 0.0087638 | 0.0087641 | 0.97591 | -0.46457 | 0.97619 | -0.45906 | 2.4077
129 | -0.029131 | -0.0073152 | 0.02917 | 0.0073391 | 3.8405e-05 | 2.3929e-05 | 0.04441 | 0.04441 | 0.04441 | 0.97619 | -0.45906 | 0.97759 | -0.43147 | 12.2006
130 | 0.023382 | 0.0058745 | -0.023368 | -0.0058661 | 1.3705e-05 | 8.4121e-06 | 0.035646 | 0.035646 | 0.035646 | 0.97619 | -0.45906 | 0.97556 | -0.47135 | 9.793
131 | -0.031994 | -0.0080469 | 0.032004 | 0.0080535 | 1.0488e-05 | 6.5645e-06 | 0.048709 | 0.048709 | 0.048709 | 0.97759 | -0.43147 | 0.97794 | -0.42461 | 13.3816
132 | 0.022309 | 0.0056007 | -0.022309 | -0.0056006 | 1.0112e-07 | 6.1808e-08 | 0.034031 | 0.034031 | 0.034031 | 0.97556 | -0.47135 | 0.97556 | -0.47144 | 9.3492
133 | -0.0019635 | -0.0004921 | 0.0019636 | 0.00049188 | 7.1497e-08 | -2.1918e-07 | 0.0029963 | 0.0029962 | 0.0029963 | 0.97512 | -0.48001 | 0.97516 | -0.47924 | 0.82315
134 | -0.0034282 | -0.00085895 | 0.0034284 | 0.00085886 | 1.5299e-07 | -8.8099e-08 | 0.0052311 | 0.005231 | 0.0052311 | 0.97516 | -0.47924 | 0.97521 | -0.4783 | 1.4371
135 | 0.020798 | 0.0052219 | -0.020791 | -0.0052178 | 6.8034e-06 | 4.1292e-06 | 0.031727 | 0.031727 | 0.031727 | 0.97556 | -0.47144 | 0.97521 | -0.4783 | 8.7161
136 | -0.043091 | -0.010832 | 0.043113 | 0.010846 | 2.2106e-05 | 1.3976e-05 | 0.065578 | 0.065578 | 0.065578 | 0.97794 | -0.42461 | 0.97849 | -0.41387 | 18.0159
137 | 0.0051314 | 0.0012857 | -0.0051304 | -0.0012856 | 9.6889e-07 | 8.9242e-08 | 0.0078107 | 0.0078109 | 0.0078109 | 0.97757 | -0.43195 | 0.97737 | -0.43591 | 2.1458
138 | -0.022473 | -0.0056343 | 0.022489 | 0.0056443 | 1.6333e-05 | 9.9863e-06 | 0.034208 | 0.034208 | 0.034208 | 0.97757 | -0.43195 | 0.97834 | -0.4167 | 9.3978
139 | -0.07008 | -0.017614 | 0.070176 | 0.017675 | 9.6396e-05 | 6.1409e-05 | 0.10659 | 0.10659 | 0.10659 | 0.97849 | -0.41387 | 0.97996 | -0.3851 | 29.2831
140 | 0.026967 | 0.0067679 | -0.026963 | -0.0067657 | 3.6465e-06 | 2.2611e-06 | 0.041013 | 0.041013 | 0.041013 | 0.97849 | -0.41387 | 0.97834 | -0.4167 | 11.2672
141 | 0.01115 | 0.0027955 | -0.011147 | -0.0027937 | 3.4282e-06 | 1.7924e-06 | 0.016932 | 0.016932 | 0.016932 | 0.97996 | -0.3851 | 0.97963 | -0.39156 | 4.6516
142 | -0.081327 | -0.020471 | 0.081401 | 0.020518 | 7.4337e-05 | 4.692e-05 | 0.12352 | 0.12352 | 0.12352 | 0.97996 | -0.3851 | 0.98094 | -0.366 | 16.9673
143 | 0.0025505 | 0.00063901 | -0.0025504 | -0.00063919 | 1.1525e-07 | -1.8167e-07 | 0.003883 | 0.0038831 | 0.0038831 | 0.97737 | -0.43591 | 0.97732 | -0.43686 | 1.0668
144 | 0.010251 | 0.0025695 | -0.010249 | -0.0025685 | 1.9953e-06 | 1.0008e-06 | 0.015572 | 0.015572 | 0.015572 | 0.97958 | -0.39267 | 0.97937 | -0.39676 | 4.278
145 | 0.0027214 | 0.00068186 | -0.0027213 | -0.00068202 | 1.2489e-07 | -1.6518e-07 | 0.0041348 | 0.0041349 | 0.0041349 | 0.97937 | -0.39676 | 0.97932 | -0.39772 | 1.136

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58854 | 0.15081

## res_load
| p_mw | q_mvar
0 | 0.020143 | 0.0050482
1 | 0.012061 | 0.0030227
2 | 0.061056 | 0.015302
3 | 0.0073627 | 0.0018453
4 | 0.0038579 | 0.00096687
5 | 0.0027284 | 0.00068381
6 | 0.0026002 | 0.00065168
7 | 0.0028475 | 0.00071365
8 | 0.0028776 | 0.00072119
9 | 0.0026648 | 0.00066786
10 | 0.0010418 | 0.00026111
11 | 0.013757 | 0.0034479
12 | 0.01897 | 0.0047544
13 | 0.0044134 | 0.0011061
14 | 0.0031056 | 0.00077833
15 | 0.0027572 | 0.00069102
16 | 0.017166 | 0.0043022
17 | 0.003205 | 0.00080326
18 | 0.0032401 | 0.00081206
19 | 0.015009 | 0.0037616
20 | 0.0071223 | 0.001785
21 | 0.0048263 | 0.0012096
22 | 0.0042448 | 0.0010639
23 | 0.0032679 | 0.00081902
24 | 0.0016927 | 0.00042423
25 | 0.0089423 | 0.0022412
26 | 0.0071454 | 0.0017908
27 | 0.016789 | 0.0042077
28 | 0.0053448 | 0.0013395
29 | 0.011253 | 0.0028204
30 | 0.0063237 | 0.0015849
31 | 0.0042108 | 0.0010553
32 | 0.0027028 | 0.00067739
33 | 0.0029123 | 0.00072989
34 | 0.0012817 | 0.00032121
35 | 0.01058 | 0.0026515
36 | 0.0012432 | 0.00031159
37 | 0.0072234 | 0.0018103
38 | 0.0048665 | 0.0012197
39 | 0.0071846 | 0.0018006
40 | 0.0028743 | 0.00072037
41 | 0.0035591 | 0.00089201
42 | 0.0051435 | 0.0012891
43 | 0.0044172 | 0.001107
44 | 0.0022376 | 0.00056078
45 | 0.0038612 | 0.0009677
46 | 0.0013829 | 0.00034658
47 | 0.0035322 | 0.00088525
48 | 0.0030707 | 0.00076959
49 | 0.0030613 | 0.00076724
50 | 0.004119 | 0.0010323
51 | 0.0037326 | 0.00093547
52 | 0.00090965 | 0.00022798
53 | 0.0065515 | 0.001642
54 | 0.003553 | 0.00089048
55 | 0.0067884 | 0.0017013
56 | 0.0034105 | 0.00085474
57 | 0.0025062 | 0.00062812
58 | 0.0027145 | 0.00068032
59 | 0.0021869 | 0.00054808
60 | 0.0037678 | 0.00094429
61 | 0.0031652 | 0.00079327
62 | 0.0026657 | 0.00066809
63 | 0.0010043 | 0.00025171
64 | 0.0017203 | 0.00043115
65 | 0.0081593 | 0.0020449
66 | 0.002457 | 0.00061578
67 | 0.0030151 | 0.00075567
68 | 0.008368 | 0.0020972
69 | 0.0051433 | 0.001289
70 | 0.010194 | 0.0025549
71 | 0.0056216 | 0.0014089
72 | 0.011385 | 0.0028534
73 | 0.0035636 | 0.00089312
74 | 0.0069482 | 0.0017414
75 | 0.010718 | 0.0026863
76 | 0.0032818 | 0.00082249
77 | 0.0084471 | 0.002117
78 | 0.0028984 | 0.0007264
79 | 0.00179 | 0.00044862
80 | 0.011436 | 0.0028661
81 | 0.0034404 | 0.00086225
82 | 0.002464 | 0.00061754
83 | 0.0006684 | 0.00016752
84 | 0.0022336 | 0.00055978
85 | 0.0028459 | 0.00071325
86 | 0.0028244 | 0.00070785
87 | 0.001059 | 0.00026541
88 | 0.0019635 | 0.0004921
89 | 0.0014646 | 0.00036707
90 | 0.0015109 | 0.00037866
91 | 0.011087 | 0.0027785
92 | 0.0044741 | 0.0011213
93 | 0.011147 | 0.0027937
94 | 0.0046408 | 0.0011631
95 | 0.0025799 | 0.00064659
96 | 0.0046063 | 0.0011545
97 | 0.0075276 | 0.0018866
98 | 0.0027213 | 0.00068202
99 | 0.0025504 | 0.00063919

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1