## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_141-19_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_141-19_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_141-19_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_141-19_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_141-19_0_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_141-19_0_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_141-19_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_141-19_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_141-19_0_3_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_141-19_0_3_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_141-19_0_3_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_141-19_0_3_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_141-19_0_3_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_141-19_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_141-19_0_3_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_141-19_0_3_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_141-19_0_3_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_141-19_0_3_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_141-19_0_3_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_141-19_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_141-19_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_141-19_0_3_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_141-19_0_3_node_5 | 0.4 | n |  | TRUE
23 | bus_LV_141-19_0_3_node_6 | 0.4 | n |  | TRUE
24 | bus_LV_141-19_0_3_node_8 | 0.4 | n |  | TRUE
25 | bus_LV_141-19_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_141-19_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_141-19_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_141-19_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_141-19_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_141-19_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_141-19_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_MV_491_0_node_152 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_141-19_0_3_load_0 | 0 | 0.0053393 | 0.0013382 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_141-19_0_3_load_1 | 1 | 0.011791 | 0.0029552 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_141-19_0_3_load_2 | 2 | 0.0054639 | 0.0013694 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_141-19_0_3_load_22 | 6 | 0.0095103 | 0.0023835 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_141-19_0_3_load_37 | 8 | 0.021195 | 0.005312 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_141-19_0_3_load_36 | 10 | 0.0018426 | 0.00046181 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_141-19_0_3_load_34 | 11 | 0.079463 | 0.019915 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_141-19_0_3_load_32 | 12 | 0.070196 | 0.017593 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_141-19_0_3_load_35 | 15 | 0.018164 | 0.0045524 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_141-19_0_3_load_38 | 18 | 0.012069 | 0.0030248 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_141-19_0_3_load_27 | 20 | 0.0080156 | 0.0020089 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_141-19_0_3_load_29 | 21 | 0.0071695 | 0.0017968 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_141-19_0_3_load_5 | 22 | 0.0053986 | 0.001353 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_141-19_0_3_load_6 | 23 | 0.0064536 | 0.0016174 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_141-19_0_3_load_21 | 25 | 0.031828 | 0.0079769 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_141-19_0_3_load_25 | 26 | 0.055504 | 0.013911 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_141-19_0_3_load_23 | 27 | 0.0062001 | 0.0015539 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_141-19_0_3_load_28 | 29 | 0.0073046 | 0.0018307 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_141-19_0_3_load_31 | 30 | 0.043734 | 0.010961 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_141-19_0_3_load_26 | 31 | 0.075663 | 0.018963 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_141-19_0_3_line_0 |  | 0 | 1 | 0.034489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_141-19_0_3_line_1 |  | 0 | 2 | 0.021292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_141-19_0_3_line_2 |  | 1 | 3 | 0.0061462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_141-19_0_3_line_3 |  | 3 | 4 | 0.015388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_141-19_0_3_line_4 |  | 4 | 5 | 0.019617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_141-19_0_3_line_5 |  | 4 | 6 | 0.03028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_141-19_0_3_line_6 |  | 5 | 11 | 0.021807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_141-19_0_3_line_7 |  | 5 | 12 | 0.021607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_141-19_0_3_line_8 |  | 5 | 13 | 0.052964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_141-19_0_3_line_9 |  | 6 | 24 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_141-19_0_3_line_10 |  | 7 | 8 | 0.026417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_141-19_0_3_line_11 |  | 7 | 9 | 0.010966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_141-19_0_3_line_12 |  | 7 | 10 | 0.016463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_141-19_0_3_line_13 |  | 8 | 18 | 0.02983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_141-19_0_3_line_14 |  | 9 | 30 | 0.019643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_141-19_0_3_line_15 |  | 9 | 12 | 0.014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_141-19_0_3_line_16 |  | 10 | 14 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_141-19_0_3_line_17 |  | 13 | 21 | 0.023543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_141-19_0_3_line_18 |  | 13 | 19 | 0.030799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_141-19_0_3_line_19 |  | 14 | 15 | 0.0058623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_141-19_0_3_line_20 |  | 16 | 17 | 0.004989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_141-19_0_3_line_21 |  | 16 | 18 | 0.004272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_141-19_0_3_line_22 |  | 17 | 31 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_141-19_0_3_line_23 |  | 19 | 20 | 0.015586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_141-19_0_3_line_24 |  | 20 | 29 | 0.015262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_141-19_0_3_line_25 |  | 22 | 23 | 0.018074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_141-19_0_3_line_26 |  | 23 | 24 | 0.030723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_141-19_0_3_line_27 |  | 24 | 25 | 0.014426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_141-19_0_3_line_28 |  | 25 | 26 | 0.0031546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_141-19_0_3_line_29 |  | 26 | 28 | 0.010388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_141-19_0_3_line_30 |  | 27 | 28 | 0.050047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_141-19_0_3_trafo_34 | 0.63 MVA 20/0.4 kV | 32 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22
0 | 2684823.9869 | 1238939.3773 | 2684822.9298 | 1238941.8996 | 2684819.0171 | 1238952.0843 | 2684817.5111 | 1238957.9559 | 2684815.6049 | 1238964.8336 | 2684812.735 | 1238971.92
1 | 2684823.9869 | 1238939.3773 | 2684827.942 | 1238929.9404 | 2684832.4634 | 1238919.8474
2 | 2684809.3035 | 1238977.0191 | 2684812.735 | 1238971.92
3 | 2684809.3035 | 1238977.0191 | 2684805.2086 | 1238981.9641 | 2684801.6933 | 1238986.0502 | 2684800.1341 | 1238989.2858
4 | 2684800.1341 | 1238989.2858 | 2684798.5084 | 1238993.4767 | 2684797.5227 | 1238997.8769 | 2684797.569 | 1239003.1035 | 2684797.5052 | 1239007.5725 | 2684797.4014 | 1239008.4828
5 | 2684800.1341 | 1238989.2858 | 2684814.0646 | 1238991.0971 | 2684828.4054 | 1238998.7006
6 | 2684797.4014 | 1239008.4828 | 2684802.2441 | 1239009.4415 | 2684808.7011 | 1239012.2913 | 2684811.8341 | 1239013.259 | 2684816.2458 | 1239014.2004 | 2684817.3226 | 1239012.4256
7 | 2684797.4014 | 1239008.4828 | 2684796.4912 | 1239016.5978 | 2684794.5228 | 1239027.8333 | 2684794.2317 | 1239029.8468
8 | 2684784.632 | 1239039.2448 | 2684786.2954 | 1239027.1154 | 2684786.8025 | 1239019.6839 | 2684786.4788 | 1239010.5728 | 2684785.6278 | 1239003.9559 | 2684786.4399 | 1239003.7673 | 2684790.1283 | 1239002.9194 | 2684791.0165 | 1239002.6986 | 2684791.8251 | 1239002.7546 | 2684796.2917 | 1239003.0297 | 2684797.569 | 1239003.1035 | 2684797.5052 | 1239007.5725 | 2684797.4014 | 1239008.4828
9 | 2684842.9235 | 1239006.3981 | 2684828.4054 | 1238998.7006
10 | 2684791.0336 | 1239055.5034 | 2684796.1972 | 1239057.8232 | 2684812.3656 | 1239070.8385
11 | 2684791.0336 | 1239055.5034 | 2684791.508 | 1239050.362 | 2684792.1954 | 1239044.601
12 | 2684791.0336 | 1239055.5034 | 2684790.4624 | 1239067.426 | 2684790.2932 | 1239071.9492
13 | 2684832.8836 | 1239092.2607 | 2684821.7206 | 1239078.3691 | 2684812.3656 | 1239070.8385
14 | 2684792.1954 | 1239044.601 | 2684795.2876 | 1239049.482 | 2684801.0904 | 1239055.2357 | 2684805.4617 | 1239058.8831
15 | 2684792.1954 | 1239044.601 | 2684792.6426 | 1239040.8381 | 2684794.2317 | 1239029.8468
16 | 2684789.8469 | 1239087.2092 | 2684789.9483 | 1239081.173 | 2684790.2932 | 1239071.9492
17 | 2684784.632 | 1239039.2448 | 2684783.2073 | 1239039.4246 | 2684781.8411 | 1239039.7497 | 2684780.769 | 1239040.1347 | 2684779.9998 | 1239040.5018 | 2684779.4273 | 1239040.8605 | 2684778.87 | 1239041.2195 | 2684778.3572 | 1239041.6347 | 2684777.3313 | 1239042.4984 | 2684776.4033 | 1239043.3858 | 2684775.9062 | 1239043.7679 | 2684775.335 | 1239044.0377 | 2684774.8193 | 1239044.1304 | 2684774.2983 | 1239044.0674 | 2684773.8318 | 1239043.8939 | 2684773.3966 | 1239043.6431 | 2684771.2349 | 1239041.9332 | 2684769.6578 | 1239040.6098 | 2684768.8735 | 1239039.9092 | 2684768.0899 | 1239039.1641 | 2684766.2941 | 1239037.2594 | 2684765.6965 | 1239036.7282 | 2684765.351 | 1239036.4979
18 | 2684782.3857 | 1239069.9347 | 2684782.8317 | 1239056.1868 | 2684784.0318 | 1239043.6616 | 2684784.632 | 1239039.2448
19 | 2684789.8469 | 1239087.2092 | 2684792.4325 | 1239087.3017 | 2684794.686 | 1239087.8788 | 2684795.4728 | 1239088.409
20 | 2684838.0615 | 1239084.5736 | 2684835.2716 | 1239088.7145
21 | 2684832.8836 | 1239092.2607 | 2684835.2716 | 1239088.7145
22 | 2684838.0615 | 1239084.5736 | 2684848.0748 | 1239069.7079
23 | 2684782.3857 | 1239069.9347 | 2684780.7973 | 1239069.9231 | 2684780.0027 | 1239069.9452 | 2684779.1992 | 1239070.0671 | 2684778.5291 | 1239070.38 | 2684777.9104 | 1239070.7937 | 2684777.3889 | 1239071.2977 | 2684777.0094 | 1239071.9149 | 2684775.8993 | 1239074.4342 | 2684775.3469 | 1239075.5049 | 2684774.6021 | 1239076.2837 | 2684773.6196 | 1239076.7478 | 2684772.5913 | 1239076.722 | 2684771.4756 | 1239076.4503 | 2684770.4624 | 1239075.891
24 | 2684761.6055 | 1239063.7627 | 2684762.1948 | 1239064.2313 | 2684763.9109 | 1239065.8903 | 2684765.4759 | 1239067.5361 | 2684766.7106 | 1239068.9992 | 2684767.2228 | 1239069.6848 | 2684767.5829 | 1239070.4238 | 2684767.8791 | 1239071.3954 | 2684768.338 | 1239072.6361 | 2684768.9403 | 1239073.8901 | 2684769.5756 | 1239074.9555 | 2684770.4624 | 1239075.891
25 | 2684868.2634 | 1238964.7053 | 2684865.8929 | 1238968.5658 | 2684858.7606 | 1238980.0797
26 | 2684842.9235 | 1239006.3981 | 2684846.8447 | 1238999.3157 | 2684858.7606 | 1238980.0797
27 | 2684842.9235 | 1239006.3981 | 2684855.3386 | 1239013.7444
28 | 2684858.0535 | 1239015.3509 | 2684855.3386 | 1239013.7444
29 | 2684866.9939 | 1239020.6411 | 2684858.0535 | 1239015.3509
30 | 2684866.9939 | 1239020.6411 | 2684868.8143 | 1239018.7102 | 2684882.1186 | 1238996.5956 | 2684891.6698 | 1238977.2381

## bus_geodata
| x | y | coords
0 | 2684823.9869 | 1238939.3773
1 | 2684812.735 | 1238971.92
2 | 2684832.4634 | 1238919.8474
3 | 2684809.3035 | 1238977.0191
4 | 2684800.1341 | 1238989.2858
5 | 2684797.4014 | 1239008.4828
6 | 2684828.4054 | 1238998.7006
7 | 2684791.0336 | 1239055.5034
8 | 2684812.3656 | 1239070.8385
9 | 2684792.1954 | 1239044.601
10 | 2684790.2932 | 1239071.9492
11 | 2684817.3226 | 1239012.4256
12 | 2684794.2317 | 1239029.8468
13 | 2684784.632 | 1239039.2448
14 | 2684789.8469 | 1239087.2092
15 | 2684795.4728 | 1239088.409
16 | 2684835.2716 | 1239088.7145
17 | 2684838.0615 | 1239084.5736
18 | 2684832.8836 | 1239092.2607
19 | 2684782.3857 | 1239069.9347
20 | 2684770.4624 | 1239075.891
21 | 2684765.351 | 1239036.4979
22 | 2684868.2634 | 1238964.7053
23 | 2684858.7606 | 1238980.0797
24 | 2684842.9235 | 1239006.3981
25 | 2684855.3386 | 1239013.7444
26 | 2684858.0535 | 1239015.3509
27 | 2684891.6698 | 1238977.2381
28 | 2684866.9939 | 1239020.6411
29 | 2684761.6055 | 1239063.7627
30 | 2684805.4617 | 1239058.8831
31 | 2684848.0748 | 1239069.7079
32 | 2684797.4014 | 1239008.4828

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99406 | -0.1137 | 0.0053393 | 0.0013382
1 | 0.9944 | -0.10713 | 0.011791 | 0.0029552
2 | 0.99396 | -0.11576 | 0.0054639 | 0.0013694
3 | 0.99453 | -0.10469 | 0 | 0
4 | 0.99485 | -0.098561 | 0 | 0
5 | 0.99732 | -0.051178 | 0 | 0
6 | 0.99166 | -0.16003 | 0.0095103 | 0.0023835
7 | 0.99324 | -0.12946 | 0 | 0
8 | 0.9906 | -0.18044 | 0.021195 | 0.005312
9 | 0.99454 | -0.10451 | 0 | 0
10 | 0.99294 | -0.13528 | 0.0018426 | 0.00046181
11 | 1 | 0 | -0.40781 | -0.10308
12 | 0.99572 | -0.08188 | 0.070196 | 0.017593
13 | 0.99623 | -0.072077 | 0 | 0
14 | 0.99269 | -0.14019 | 0 | 0
15 | 0.99259 | -0.14207 | 0.018164 | 0.0045524
16 | 0.9879 | -0.23281 | 0 | 0
17 | 0.98755 | -0.23955 | 0 | 0
18 | 0.98819 | -0.22703 | 0.012069 | 0.0030248
19 | 0.9958 | -0.080368 | 0 | 0
20 | 0.99559 | -0.084566 | 0.0080156 | 0.0020089
21 | 0.99608 | -0.075042 | 0.0071695 | 0.0017968
22 | 0.98965 | -0.19898 | 0.0053986 | 0.001353
23 | 0.98974 | -0.19725 | 0.0064536 | 0.0016174
24 | 0.99007 | -0.19077 | 0 | 0
25 | 0.98883 | -0.21479 | 0.031828 | 0.0079769
26 | 0.98865 | -0.21826 | 0.055504 | 0.013911
27 | 0.98831 | -0.22495 | 0.0062001 | 0.0015539
28 | 0.98859 | -0.21941 | 0 | 0
29 | 0.99549 | -0.086526 | 0.0073046 | 0.0018307
30 | 0.99376 | -0.11966 | 0.043734 | 0.010961
31 | 0.9863 | -0.26382 | 0.075663 | 0.018963
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010804 | -0.0027076 | 0.010807 | 0.0027093 | 3.3826e-06 | 1.7176e-06 | 0.016172 | 0.016172 | 0.016172 | 0.99406 | -0.1137 | 0.9944 | -0.10713 | 4.4429
1 | 0.0054644 | 0.0013694 | -0.0054639 | -0.0013694 | 5.3422e-07 | 6.5905e-08 | 0.0081797 | 0.0081798 | 0.0081798 | 0.99406 | -0.1137 | 0.99396 | -0.11576 | 2.2472
2 | -0.022599 | -0.0056645 | 0.022601 | 0.0056661 | 2.6357e-06 | 1.6071e-06 | 0.033817 | 0.033816 | 0.033817 | 0.9944 | -0.10713 | 0.99453 | -0.10469 | 9.2902
3 | -0.022601 | -0.0056661 | 0.022608 | 0.0056702 | 6.5989e-06 | 4.0235e-06 | 0.033816 | 0.033816 | 0.033816 | 0.99453 | -0.10469 | 0.99485 | -0.098561 | 9.2902
4 | -0.13812 | -0.034859 | 0.13844 | 0.03506 | 0.00031423 | 0.00020085 | 0.20668 | 0.20668 | 0.20668 | 0.99485 | -0.098561 | 0.99732 | -0.051178 | 56.7792
5 | 0.11551 | 0.029189 | -0.11517 | -0.028972 | 0.00033929 | 0.00021675 | 0.17286 | 0.17286 | 0.17286 | 0.99485 | -0.098561 | 0.99166 | -0.16003 | 47.489
6 | -0.40516 | -0.10244 | 0.40616 | 0.10308 | 0.00099717 | 0.00063733 | 0.60483 | 0.60483 | 0.60483 | 0.99732 | -0.051178 | 1 | 0 | 55.3871
7 | 0.24421 | 0.061723 | -0.24385 | -0.061494 | 0.00035892 | 0.00022887 | 0.36454 | 0.36454 | 0.36454 | 0.99732 | -0.051178 | 0.99572 | -0.08188 | 33.383
8 | 0.022523 | 0.0056559 | -0.0225 | -0.0056423 | 2.2434e-05 | 1.3668e-05 | 0.033608 | 0.033609 | 0.033609 | 0.99732 | -0.051178 | 0.99623 | -0.072077 | 9.2332
9 | 0.10566 | 0.026588 | -0.10551 | -0.026489 | 0.00015498 | 9.8977e-05 | 0.15859 | 0.15859 | 0.15859 | 0.99166 | -0.16003 | 0.99007 | -0.19077 | 43.5686
10 | 0.10952 | 0.02768 | -0.10926 | -0.027509 | 0.00026697 | 0.00017052 | 0.16416 | 0.16416 | 0.16416 | 0.99324 | -0.12946 | 0.9906 | -0.18044 | 45.0997
11 | -0.12954 | -0.032701 | 0.1297 | 0.0328 | 0.00015502 | 9.9068e-05 | 0.19415 | 0.19415 | 0.19415 | 0.99324 | -0.12946 | 0.99454 | -0.10451 | 53.3392
12 | 0.020018 | 0.0050211 | -0.020013 | -0.0050177 | 5.5531e-06 | 3.341e-06 | 0.029992 | 0.029992 | 0.029992 | 0.99324 | -0.12946 | 0.99294 | -0.13528 | 8.2395
13 | 0.088061 | 0.022197 | -0.087865 | -0.022072 | 0.00019587 | 0.00012498 | 0.13233 | 0.13233 | 0.13233 | 0.9906 | -0.18044 | 0.98819 | -0.22703 | 36.3531
14 | 0.043765 | 0.010981 | -0.043734 | -0.010961 | 3.1588e-05 | 1.9962e-05 | 0.065485 | 0.065485 | 0.065485 | 0.99454 | -0.10451 | 0.99376 | -0.11966 | 17.9905
15 | -0.17346 | -0.043781 | 0.17365 | 0.043901 | 0.00018827 | 0.00012011 | 0.25964 | 0.25964 | 0.25964 | 0.99454 | -0.10451 | 0.99572 | -0.08188 | 35.6648
16 | 0.01817 | 0.0045559 | -0.018166 | -0.0045534 | 4.2453e-06 | 2.5196e-06 | 0.027231 | 0.027231 | 0.027231 | 0.99294 | -0.13528 | 0.99269 | -0.14019 | 7.4809
17 | 0.0071705 | 0.0017972 | -0.0071695 | -0.0017968 | 1.0127e-06 | 3.4165e-07 | 0.01071 | 0.01071 | 0.01071 | 0.99623 | -0.072077 | 0.99608 | -0.075042 | 2.9424
18 | 0.01533 | 0.0038451 | -0.015324 | -0.0038416 | 6.056e-06 | 3.475e-06 | 0.022898 | 0.022899 | 0.022899 | 0.99623 | -0.072077 | 0.9958 | -0.080368 | 6.2908
19 | 0.018166 | 0.0045534 | -0.018164 | -0.0045524 | 1.6301e-06 | 9.6748e-07 | 0.027231 | 0.027231 | 0.027231 | 0.99269 | -0.14019 | 0.99259 | -0.14207 | 7.481
20 | 0.075775 | 0.019034 | -0.075751 | -0.019019 | 2.4379e-05 | 1.5538e-05 | 0.11415 | 0.11415 | 0.11415 | 0.9879 | -0.23281 | 0.98755 | -0.23955 | 31.3603
21 | -0.075775 | -0.019034 | 0.075796 | 0.019048 | 2.0875e-05 | 1.3305e-05 | 0.11415 | 0.11415 | 0.11415 | 0.9879 | -0.23281 | 0.98819 | -0.22703 | 31.3603
22 | 0.075751 | 0.019019 | -0.075663 | -0.018963 | 8.7583e-05 | 5.5824e-05 | 0.11415 | 0.11415 | 0.11415 | 0.98755 | -0.23955 | 0.9863 | -0.26382 | 31.3603
23 | 0.015324 | 0.0038416 | -0.015321 | -0.0038398 | 3.0647e-06 | 1.7587e-06 | 0.022899 | 0.022899 | 0.022899 | 0.9958 | -0.080368 | 0.99559 | -0.084566 | 6.2909
24 | 0.0073052 | 0.0018309 | -0.0073046 | -0.0018307 | 6.8232e-07 | 2.3823e-07 | 0.010919 | 0.010919 | 0.010919 | 0.99559 | -0.084566 | 0.99549 | -0.086526 | 2.9996
25 | -0.0053986 | -0.001353 | 0.005399 | 0.0013531 | 4.4658e-07 | 5.3555e-08 | 0.0081172 | 0.0081171 | 0.0081172 | 0.98965 | -0.19898 | 0.98974 | -0.19725 | 2.23
26 | -0.011853 | -0.0029705 | 0.011856 | 0.0029724 | 3.6585e-06 | 1.9465e-06 | 0.01782 | 0.01782 | 0.01782 | 0.98974 | -0.19725 | 0.99007 | -0.19077 | 4.8956
27 | 0.093652 | 0.023517 | -0.093545 | -0.023449 | 0.0001072 | 6.8422e-05 | 0.14077 | 0.14077 | 0.14077 | 0.99007 | -0.19077 | 0.98883 | -0.21479 | 38.6731
28 | 0.061717 | 0.015472 | -0.061706 | -0.015465 | 1.0204e-05 | 6.49e-06 | 0.092874 | 0.092874 | 0.092874 | 0.98883 | -0.21479 | 0.98865 | -0.21826 | 25.5148
29 | 0.0062021 | 0.0015544 | -0.0062017 | -0.0015543 | 3.3945e-07 | 8.4046e-08 | 0.0093347 | 0.0093347 | 0.0093347 | 0.98865 | -0.21826 | 0.98859 | -0.21941 | 2.5645
30 | -0.0062001 | -0.0015539 | 0.0062017 | 0.0015543 | 1.6354e-06 | 4.0516e-07 | 0.009335 | 0.0093347 | 0.009335 | 0.98831 | -0.22495 | 0.98859 | -0.21941 | 2.5646

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48727 | 0.12299

## res_load
| p_mw | q_mvar
0 | 0.0053393 | 0.0013382
1 | 0.011791 | 0.0029552
2 | 0.0054639 | 0.0013694
3 | 0.0095103 | 0.0023835
4 | 0.021195 | 0.005312
5 | 0.0018426 | 0.00046181
6 | 0.079463 | 0.019915
7 | 0.070196 | 0.017593
8 | 0.018164 | 0.0045524
9 | 0.012069 | 0.0030248
10 | 0.0080156 | 0.0020089
11 | 0.0071695 | 0.0017968
12 | 0.0053986 | 0.001353
13 | 0.0064536 | 0.0016174
14 | 0.031828 | 0.0079769
15 | 0.055504 | 0.013911
16 | 0.0062001 | 0.0015539
17 | 0.0073046 | 0.0018307
18 | 0.043734 | 0.010961
19 | 0.075663 | 0.018963

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1