## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_141-24_1_3_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_141-24_1_3_node_70 | 0.4 | n |  | TRUE
2 | bus_LV_141-24_1_3_node_130 | 0.4 | n |  | TRUE
3 | bus_LV_141-24_1_3_node_51 | 0.4 | n |  | TRUE
4 | bus_LV_141-24_1_3_node_131 | 0.4 | n |  | TRUE
5 | bus_LV_141-24_1_3_node_58 | 0.4 | n |  | TRUE
6 | bus_LV_141-24_1_3_node_135 | 0.4 | n |  | TRUE
7 | bus_LV_141-24_1_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_141-24_1_3_node_136 | 0.4 | n |  | TRUE
9 | bus_LV_141-24_1_3_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_141-24_1_3_node_138 | 0.4 | n |  | TRUE
11 | bus_LV_141-24_1_3_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_141-24_1_3_node_139 | 0.4 | n |  | TRUE
13 | bus_LV_141-24_1_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_141-24_1_3_node_97 | 0.4 | n |  | TRUE
15 | bus_LV_141-24_1_3_node_66 | 0.4 | n |  | TRUE
16 | bus_LV_141-24_1_3_node_95 | 0.4 | n |  | TRUE
17 | bus_LV_141-24_1_3_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_141-24_1_3_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_141-24_1_3_node_122 | 0.4 | n |  | TRUE
20 | bus_LV_141-24_1_3_node_117 | 0.4 | n |  | TRUE
21 | bus_LV_141-24_1_3_node_127 | 0.4 | n |  | TRUE
22 | bus_LV_141-24_1_3_node_126 | 0.4 | n |  | TRUE
23 | bus_LV_141-24_1_3_node_96 | 0.4 | n |  | TRUE
24 | bus_LV_141-24_1_3_node_120 | 0.4 | n |  | TRUE
25 | bus_LV_141-24_1_3_node_121 | 0.4 | n |  | TRUE
26 | bus_MV_491_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_141-24_1_3_load_128 | 0 | 0.00096269 | 0.00024127 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_141-24_1_3_load_130 | 2 | 0.001263 | 0.00031654 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_141-24_1_3_load_131 | 4 | 0.00084714 | 0.00021231 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_141-24_1_3_load_135 | 6 | 0.013554 | 0.003397 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_141-24_1_3_load_136 | 8 | 0.0043059 | 0.0010792 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_141-24_1_3_load_138 | 10 | 0.0050447 | 0.0012643 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_141-24_1_3_load_139 | 12 | 0.00057413 | 0.00014389 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_141-24_1_3_load_97 | 14 | 0.00056028 | 0.00014042 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_141-24_1_3_load_95 | 16 | 0.0013197 | 0.00033074 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_141-24_1_3_load_122 | 19 | 0.0054418 | 0.0013638 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_141-24_1_3_load_117 | 20 | 0.01971 | 0.0049398 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_141-24_1_3_load_127 | 21 | 0.00093516 | 0.00023437 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_141-24_1_3_load_126 | 22 | 0.0010382 | 0.00026019 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_141-24_1_3_load_96 | 23 | 0.0040108 | 0.0010052 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_141-24_1_3_load_120 | 24 | 0.0022908 | 0.00057412 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_141-24_1_3_load_121 | 25 | 0.01857 | 0.0046541 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_141-24_1_3_line_0 |  | 0 | 1 | 0.028899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_141-24_1_3_line_1 |  | 1 | 22 | 0.010356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_141-24_1_3_line_2 |  | 2 | 3 | 0.010307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_141-24_1_3_line_3 |  | 3 | 11 | 0.17394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_141-24_1_3_line_4 |  | 3 | 14 | 0.0095915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_141-24_1_3_line_5 |  | 3 | 7 | 0.049298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_141-24_1_3_line_6 |  | 4 | 5 | 0.012312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_141-24_1_3_line_7 |  | 5 | 15 | 0.03668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_141-24_1_3_line_8 |  | 5 | 17 | 0.022517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_141-24_1_3_line_9 |  | 6 | 7 | 0.04864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_141-24_1_3_line_10 |  | 7 | 9 | 0.05133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_141-24_1_3_line_11 |  | 8 | 9 | 0.004042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_141-24_1_3_line_12 |  | 10 | 11 | 0.042526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_141-24_1_3_line_13 |  | 11 | 12 | 0.014955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_141-24_1_3_line_14 |  | 13 | 14 | 0.025527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_141-24_1_3_line_15 |  | 13 | 15 | 0.13556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_141-24_1_3_line_16 |  | 13 | 16 | 0.032935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_141-24_1_3_line_17 |  | 15 | 21 | 0.066336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_141-24_1_3_line_18 |  | 16 | 23 | 0.11453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_141-24_1_3_line_19 |  | 17 | 18 | 0.10733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_141-24_1_3_line_20 |  | 17 | 19 | 0.034867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_141-24_1_3_line_21 |  | 18 | 20 | 0.032724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_141-24_1_3_line_22 |  | 19 | 24 | 0.054565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_141-24_1_3_line_23 |  | 21 | 22 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_141-24_1_3_line_24 |  | 24 | 25 | 0.032909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_141-24_1_3_trafo_66 | 0.63 MVA 20/0.4 kV | 26 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2684400.5809 | 1237899.3148 | 2684378.7092 | 1237880.4258
1 | 2684400.5809 | 1237899.3148 | 2684407.4133 | 1237891.5328
2 | 2684463.5965 | 1237933.8685 | 2684457.299 | 1237942.0403
3 | 2684457.299 | 1237942.0403 | 2684452.2723 | 1237949.6966 | 2684470.7799 | 1237966.0492 | 2684492.101 | 1237979.273 | 2684510.0204 | 1237983.7867 | 2684516.2092 | 1237982.1847 | 2684524.7971 | 1237978.4042 | 2684529.5998 | 1237975.8596 | 2684564.0557 | 1237953.434 | 2684569.0162 | 1237949.9021 | 2684571.9248 | 1237947.0081 | 2684574.3328 | 1237950.0446 | 2684576.5908 | 1237953.5237 | 2684578.0031 | 1237947.8619 | 2684579.0047 | 1237946.0638 | 2684583.0472 | 1237942.7079 | 2684585.4442 | 1237941.2076
4 | 2684457.299 | 1237942.0403 | 2684451.4576 | 1237934.4328
5 | 2684420.4825 | 1237973.5395 | 2684439.5269 | 1237955.8753 | 2684452.2723 | 1237949.6966 | 2684457.299 | 1237942.0403
6 | 2684452.875 | 1237783.9646 | 2684446.1648 | 1237785.5037 | 2684442.7957 | 1237789.759
7 | 2684442.0914 | 1237816.5568 | 2684446.699 | 1237812.3082 | 2684446.8977 | 1237811.099 | 2684448.0078 | 1237808.0571 | 2684451.2254 | 1237803.6552 | 2684454.0648 | 1237798.7143 | 2684452.875 | 1237783.9646
8 | 2684452.875 | 1237783.9646 | 2684459.4086 | 1237783.6684 | 2684459.5368 | 1237774.1301 | 2684460.6328 | 1237774.2013 | 2684464.6317 | 1237774.4472 | 2684465.9621 | 1237774.5329
9 | 2684420.4825 | 1237973.5395 | 2684407.1116 | 1237985.9361 | 2684403.7159 | 1238016.1761
10 | 2684420.4825 | 1237973.5395 | 2684430.4427 | 1237983.9107 | 2684437.2645 | 1237986.2093 | 2684441.6431 | 1237976.7759 | 2684446.2203 | 1237983.1566 | 2684449.7147 | 1237988.0098 | 2684452.9345 | 1237992.4921
11 | 2684456.2288 | 1237990.1372 | 2684452.9345 | 1237992.4921
12 | 2684585.4442 | 1237941.2076 | 2684585.4448 | 1237945.9443 | 2684584.3781 | 1237957.0926 | 2684595.2057 | 1237978.2508 | 2684597.9331 | 1237979.0458
13 | 2684585.4442 | 1237941.2076 | 2684589.4893 | 1237937.1401 | 2684598.7082 | 1237937.9386
14 | 2684457.4236 | 1237912.5433 | 2684447.9247 | 1237929.8317 | 2684451.4576 | 1237934.4328
15 | 2684442.0914 | 1237816.5568 | 2684445.019 | 1237819.2448 | 2684448.1064 | 1237821.8683 | 2684451.4135 | 1237820.2142 | 2684455.6619 | 1237819.941 | 2684459.5061 | 1237821.4857 | 2684462.9154 | 1237830.7296 | 2684466.1174 | 1237838.0582 | 2684473.3995 | 1237852.6833 | 2684481.9367 | 1237864.7022 | 2684492.7168 | 1237878.0761 | 2684457.4236 | 1237912.5433
16 | 2684457.4236 | 1237912.5433 | 2684439.1224 | 1237930.0623 | 2684433.8095 | 1237935.4975
17 | 2684442.0914 | 1237816.5568 | 2684439.0278 | 1237821.3055 | 2684437.9805 | 1237826.8501 | 2684434.5862 | 1237844.2032 | 2684428.3187 | 1237864.0949 | 2684422.3908 | 1237874.4737 | 2684419.3875 | 1237877.8944
18 | 2684433.8095 | 1237935.4975 | 2684361.5963 | 1238009.3729 | 2684354.6458 | 1238018.1863
19 | 2684542.9604 | 1237749.0656 | 2684512.699 | 1237775.4538 | 2684486.8924 | 1237788.6851 | 2684472.6534 | 1237792.3963 | 2684468.0908 | 1237792.954 | 2684465.6918 | 1237786.6154 | 2684465.9621 | 1237774.5329
20 | 2684465.9621 | 1237774.5329 | 2684466.3337 | 1237762.2405 | 2684469.0637 | 1237742.6653 | 2684469.7269 | 1237739.9403
21 | 2684542.9604 | 1237749.0656 | 2684566.8452 | 1237726.6962
22 | 2684484.8179 | 1237687.53 | 2684474.2709 | 1237721.2686 | 2684469.7269 | 1237739.9403
23 | 2684407.4133 | 1237891.5328 | 2684419.3875 | 1237877.8944
24 | 2684484.8179 | 1237687.53 | 2684490.9334 | 1237667.9675 | 2684494.6689 | 1237656.13

## bus_geodata
| x | y | coords
0 | 2684378.7092 | 1237880.4258
1 | 2684400.5809 | 1237899.3148
2 | 2684463.5965 | 1237933.8685
3 | 2684457.299 | 1237942.0403
4 | 2684442.7957 | 1237789.759
5 | 2684452.875 | 1237783.9646
6 | 2684403.7159 | 1238016.1761
7 | 2684420.4825 | 1237973.5395
8 | 2684456.2288 | 1237990.1372
9 | 2684452.9345 | 1237992.4921
10 | 2684597.9331 | 1237979.0458
11 | 2684585.4442 | 1237941.2076
12 | 2684598.7082 | 1237937.9386
13 | 2684457.4236 | 1237912.5433
14 | 2684451.4576 | 1237934.4328
15 | 2684442.0914 | 1237816.5568
16 | 2684433.8095 | 1237935.4975
17 | 2684465.9621 | 1237774.5329
18 | 2684542.9604 | 1237749.0656
19 | 2684469.7268 | 1237739.9403
20 | 2684566.8452 | 1237726.6962
21 | 2684419.3875 | 1237877.8944
22 | 2684407.4133 | 1237891.5328
23 | 2684354.6458 | 1238018.1863
24 | 2684484.8179 | 1237687.53
25 | 2684494.6689 | 1237656.13
26 | 2684445.019 | 1237819.2448

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99976 | -0.0046918 | 0.00096269 | 0.00024127
1 | 0.99978 | -0.0042065 | 0 | 0
2 | 0.9954 | -0.088466 | 0.001263 | 0.00031654
3 | 0.99541 | -0.088237 | 0 | 0
4 | 0.99842 | -0.030194 | 0.00084714 | 0.00021231
5 | 0.99843 | -0.030012 | 0 | 0
6 | 0.994 | -0.11536 | 0.013554 | 0.003397
7 | 0.99461 | -0.10374 | 0 | 0
8 | 0.99439 | -0.10794 | 0.0043059 | 0.0010792
9 | 0.9944 | -0.10764 | 0 | 0
10 | 0.99432 | -0.10924 | 0.0050447 | 0.0012643
11 | 0.99452 | -0.10546 | 0 | 0
12 | 0.99451 | -0.10561 | 0.00057413 | 0.00014389
13 | 0.99621 | -0.072705 | 0 | 0
14 | 0.99562 | -0.084061 | 0.00056028 | 0.00014042
15 | 1 | 0 | -0.082437 | -0.020371
16 | 0.99605 | -0.075791 | 0.0013197 | 0.00033074
17 | 0.99749 | -0.048148 | 0 | 0
18 | 0.99556 | -0.085281 | 0 | 0
19 | 0.99665 | -0.064228 | 0.0054418 | 0.0013638
20 | 0.99497 | -0.09663 | 0.01971 | 0.0049398
21 | 0.99982 | -0.0033987 | 0.00093516 | 0.00023437
22 | 0.99979 | -0.0040324 | 0.0010382 | 0.00026019
23 | 0.99564 | -0.083868 | 0.0040108 | 0.0010052
24 | 0.99562 | -0.084224 | 0.0022908 | 0.00057412
25 | 0.99506 | -0.094976 | 0.01857 | 0.0046541
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00096269 | -0.00024127 | 0.00096271 | 0.00024091 | 2.2247e-08 | -3.6472e-07 | 0.0014329 | 0.0014327 | 0.0014329 | 0.99976 | -0.0046918 | 0.99978 | -0.0042065 | 0.39364
1 | -0.00096271 | -0.00024091 | 0.00096272 | 0.00024078 | 7.9711e-09 | -1.307e-07 | 0.0014327 | 0.0014327 | 0.0014327 | 0.99978 | -0.0042065 | 0.99979 | -0.0040324 | 0.3936
2 | -0.001263 | -0.00031654 | 0.001263 | 0.00031642 | 1.3778e-08 | -1.2516e-07 | 0.0018881 | 0.001888 | 0.0018881 | 0.9954 | -0.088466 | 0.99541 | -0.088237 | 0.5187
3 | 0.0056244 | 0.0014087 | -0.0056198 | -0.0014081 | 4.611e-06 | 6.9204e-07 | 0.0084075 | 0.0084083 | 0.0084083 | 0.99541 | -0.088237 | 0.99452 | -0.10546 | 2.31
4 | -0.024769 | -0.0062131 | 0.024774 | 0.0062162 | 4.9317e-06 | 3.0316e-06 | 0.037029 | 0.037029 | 0.037029 | 0.99541 | -0.088237 | 0.99562 | -0.084061 | 10.1727
5 | 0.017882 | 0.004488 | -0.017868 | -0.0044802 | 1.3212e-05 | 7.8154e-06 | 0.026733 | 0.026733 | 0.026733 | 0.99541 | -0.088237 | 0.99461 | -0.10374 | 7.3444
6 | -0.00084714 | -0.00021231 | 0.00084715 | 0.00021216 | 7.3593e-09 | -1.5631e-07 | 0.0012626 | 0.0012625 | 0.0012626 | 0.99842 | -0.030194 | 0.99843 | -0.030012 | 0.34686
7 | -0.046995 | -0.011827 | 0.047063 | 0.01187 | 6.7508e-05 | 4.2724e-05 | 0.070057 | 0.070056 | 0.070057 | 0.99843 | -0.030012 | 1 | 0 | 19.2463
8 | 0.046148 | 0.011615 | -0.046108 | -0.011589 | 3.9963e-05 | 2.5282e-05 | 0.068794 | 0.068794 | 0.068794 | 0.99843 | -0.030012 | 0.99749 | -0.048148 | 18.8995
9 | -0.013554 | -0.003397 | 0.013562 | 0.0034012 | 7.5094e-06 | 4.1752e-06 | 0.020291 | 0.02029 | 0.020291 | 0.994 | -0.11536 | 0.99461 | -0.10374 | 5.5743
10 | 0.0043068 | 0.001079 | -0.004306 | -0.0010791 | 7.9912e-07 | -1.5459e-07 | 0.0064431 | 0.0064434 | 0.0064434 | 0.99461 | -0.10374 | 0.9944 | -0.10764 | 1.7702
11 | -0.0043059 | -0.0010792 | 0.004306 | 0.0010791 | 6.293e-08 | -1.216e-08 | 0.0064434 | 0.0064434 | 0.0064434 | 0.99439 | -0.10794 | 0.9944 | -0.10764 | 1.7702
12 | -0.0050447 | -0.0012643 | 0.0050456 | 0.0012644 | 9.0889e-07 | 2.9987e-08 | 0.0075495 | 0.0075493 | 0.0075495 | 0.99432 | -0.10924 | 0.99452 | -0.10546 | 2.074
13 | 0.00057414 | 0.0001437 | -0.00057413 | -0.00014389 | 4.1381e-09 | -1.914e-07 | 0.00085896 | 0.00085903 | 0.00085903 | 0.99452 | -0.10546 | 0.99451 | -0.10561 | 0.236
14 | 0.025348 | 0.0063651 | -0.025334 | -0.0063566 | 1.3726e-05 | 8.4522e-06 | 0.037866 | 0.037866 | 0.037866 | 0.99621 | -0.072705 | 0.99562 | -0.084061 | 10.4028
15 | -0.030681 | -0.0077006 | 0.030788 | 0.0077671 | 0.00010678 | 6.6567e-05 | 0.045831 | 0.04583 | 0.045831 | 0.99621 | -0.072705 | 1 | 0 | 12.5909
16 | 0.0053328 | 0.0013355 | -0.005332 | -0.0013354 | 7.8357e-07 | 7.2729e-08 | 0.007965 | 0.0079652 | 0.0079652 | 0.99621 | -0.072705 | 0.99605 | -0.075791 | 2.1882
17 | 0.0029366 | 0.00073457 | -0.0029361 | -0.00073514 | 4.7491e-07 | -5.6618e-07 | 0.0043692 | 0.0043695 | 0.0043695 | 1 | 0 | 0.99982 | -0.0033987 | 1.2004
18 | 0.0040123 | 0.0010047 | -0.0040108 | -0.0010052 | 1.5431e-06 | -5.0255e-07 | 0.0059937 | 0.0059942 | 0.0059942 | 0.99605 | -0.075791 | 0.99564 | -0.083868 | 1.6468
19 | 0.019756 | 0.0049672 | -0.019721 | -0.0049462 | 3.497e-05 | 2.0983e-05 | 0.029477 | 0.029477 | 0.029477 | 0.99749 | -0.048148 | 0.99556 | -0.085281 | 8.0981
20 | 0.026352 | 0.0066222 | -0.026332 | -0.0066098 | 2.0213e-05 | 1.2481e-05 | 0.039318 | 0.039318 | 0.039318 | 0.99749 | -0.048148 | 0.99665 | -0.064228 | 10.8016
21 | 0.019721 | 0.0049462 | -0.01971 | -0.0049398 | 1.0663e-05 | 6.3989e-06 | 0.029477 | 0.029477 | 0.029477 | 0.99556 | -0.085281 | 0.99497 | -0.09663 | 8.0981
22 | 0.02089 | 0.0052459 | -0.02087 | -0.0052339 | 1.991e-05 | 1.2032e-05 | 0.031193 | 0.031193 | 0.031193 | 0.99665 | -0.064228 | 0.99562 | -0.084224 | 8.5696
23 | 0.0020009 | 0.00050077 | -0.0020009 | -0.00050097 | 6.0348e-08 | -1.9939e-07 | 0.0029777 | 0.0029778 | 0.0029778 | 0.99982 | -0.0033987 | 0.99979 | -0.0040324 | 0.81808
24 | 0.01858 | 0.0046598 | -0.01857 | -0.0046541 | 9.5168e-06 | 5.663e-06 | 0.02777 | 0.02777 | 0.02777 | 0.99562 | -0.084224 | 0.99506 | -0.094976 | 7.6291

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.082437 | 0.020371

## res_load
| p_mw | q_mvar
0 | 0.00096269 | 0.00024127
1 | 0.001263 | 0.00031654
2 | 0.00084714 | 0.00021231
3 | 0.013554 | 0.003397
4 | 0.0043059 | 0.0010792
5 | 0.0050447 | 0.0012643
6 | 0.00057413 | 0.00014389
7 | 0.00056028 | 0.00014042
8 | 0.0013197 | 0.00033074
9 | 0.0054418 | 0.0013638
10 | 0.01971 | 0.0049398
11 | 0.00093516 | 0.00023437
12 | 0.0010382 | 0.00026019
13 | 0.0040108 | 0.0010052
14 | 0.0022908 | 0.00057412
15 | 0.01857 | 0.0046541

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1