## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_141-27_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_141-27_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_141-27_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_141-27_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_141-27_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_141-27_0_5_node_121 | 0.4 | n |  | TRUE
6 | bus_LV_141-27_0_5_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_141-27_0_5_node_58 | 0.4 | n |  | TRUE
8 | bus_LV_141-27_0_5_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_141-27_0_5_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_141-27_0_5_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_141-27_0_5_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_141-27_0_5_node_50 | 0.4 | n |  | TRUE
13 | bus_LV_141-27_0_5_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_141-27_0_5_node_47 | 0.4 | n |  | TRUE
15 | bus_LV_141-27_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_141-27_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_141-27_0_5_node_116 | 0.4 | n |  | TRUE
18 | bus_LV_141-27_0_5_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_141-27_0_5_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_141-27_0_5_node_115 | 0.4 | n |  | TRUE
21 | bus_LV_141-27_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_141-27_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_141-27_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_141-27_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_141-27_0_5_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_141-27_0_5_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_141-27_0_5_node_84 | 0.4 | n |  | TRUE
28 | bus_LV_141-27_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_141-27_0_5_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_141-27_0_5_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_141-27_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_141-27_0_5_node_104 | 0.4 | n |  | TRUE
33 | bus_LV_141-27_0_5_node_107 | 0.4 | n |  | TRUE
34 | bus_LV_141-27_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_141-27_0_5_node_122 | 0.4 | n |  | TRUE
36 | bus_LV_141-27_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_141-27_0_5_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_141-27_0_5_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_141-27_0_5_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_141-27_0_5_node_109 | 0.4 | n |  | TRUE
41 | bus_LV_141-27_0_5_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_141-27_0_5_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_141-27_0_5_node_111 | 0.4 | n |  | TRUE
44 | bus_LV_141-27_0_5_node_90 | 0.4 | n |  | TRUE
45 | bus_LV_141-27_0_5_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_141-27_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_141-27_0_5_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_141-27_0_5_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_141-27_0_5_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_141-27_0_5_node_103 | 0.4 | n |  | TRUE
51 | bus_LV_141-27_0_5_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_141-27_0_5_node_75 | 0.4 | n |  | TRUE
53 | bus_LV_141-27_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_141-27_0_5_node_80 | 0.4 | n |  | TRUE
55 | bus_LV_141-27_0_5_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_141-27_0_5_node_91 | 0.4 | n |  | TRUE
57 | bus_LV_141-27_0_5_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_141-27_0_5_node_126 | 0.4 | n |  | TRUE
59 | bus_LV_141-27_0_5_node_99 | 0.4 | n |  | TRUE
60 | bus_LV_141-27_0_5_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_141-27_0_5_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_141-27_0_5_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_141-27_0_5_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_141-27_0_5_node_74 | 0.4 | n |  | TRUE
65 | bus_LV_141-27_0_5_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_141-27_0_5_node_120 | 0.4 | n |  | TRUE
67 | bus_LV_141-27_0_5_node_128 | 0.4 | n |  | TRUE
68 | bus_LV_141-27_0_5_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_141-27_0_5_node_129 | 0.4 | n |  | TRUE
70 | bus_LV_141-27_0_5_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_141-27_0_5_node_76 | 0.4 | n |  | TRUE
72 | bus_LV_141-27_0_5_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_141-27_0_5_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_141-27_0_5_node_125 | 0.4 | n |  | TRUE
75 | bus_LV_141-27_0_5_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_141-27_0_5_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_141-27_0_5_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_141-27_0_5_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_141-27_0_5_node_101 | 0.4 | n |  | TRUE
80 | bus_LV_141-27_0_5_node_124 | 0.4 | n |  | TRUE
81 | bus_LV_141-27_0_5_node_87 | 0.4 | n |  | TRUE
82 | bus_LV_141-27_0_5_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_141-27_0_5_node_60 | 0.4 | n |  | TRUE
84 | bus_LV_141-27_0_5_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_141-27_0_5_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_141-27_0_5_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_141-27_0_5_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_141-27_0_5_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_141-27_0_5_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_141-27_0_5_node_123 | 0.4 | n |  | TRUE
91 | bus_LV_141-27_0_5_node_112 | 0.4 | n |  | TRUE
92 | bus_LV_141-27_0_5_node_118 | 0.4 | n |  | TRUE
93 | bus_LV_141-27_0_5_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_141-27_0_5_node_105 | 0.4 | n |  | TRUE
95 | bus_LV_141-27_0_5_node_108 | 0.4 | n |  | TRUE
96 | bus_LV_141-27_0_5_node_110 | 0.4 | n |  | TRUE
97 | bus_LV_141-27_0_5_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_141-27_0_5_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_141-27_0_5_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_141-27_0_5_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_141-27_0_5_node_127 | 0.4 | n |  | TRUE
102 | bus_LV_141-27_0_5_node_117 | 0.4 | n |  | TRUE
103 | bus_LV_141-27_0_5_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_141-27_0_5_node_100 | 0.4 | n |  | TRUE
105 | bus_LV_141-27_0_5_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_141-27_0_5_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_141-27_0_5_node_56 | 0.4 | n |  | TRUE
108 | bus_LV_141-27_0_5_node_52 | 0.4 | n |  | TRUE
109 | bus_LV_141-27_0_5_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_141-27_0_5_node_67 | 0.4 | n |  | TRUE
111 | bus_LV_141-27_0_5_node_61 | 0.4 | n |  | TRUE
112 | bus_LV_141-27_0_5_node_65 | 0.4 | n |  | TRUE
113 | bus_LV_141-27_0_5_node_82 | 0.4 | n |  | TRUE
114 | bus_LV_141-27_0_5_node_69 | 0.4 | n |  | TRUE
115 | bus_LV_141-27_0_5_node_70 | 0.4 | n |  | TRUE
116 | bus_LV_141-27_0_5_node_72 | 0.4 | n |  | TRUE
117 | bus_LV_141-27_0_5_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_141-27_0_5_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_141-27_0_5_node_113 | 0.4 | n |  | TRUE
120 | bus_MV_349_2_node_185 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_141-27_0_5_load_0 | 0 | 0.0022842 | 0.00057248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_141-27_0_5_load_4 | 3 | 0.0074364 | 0.0018637 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_141-27_0_5_load_5 | 4 | 0.0008273 | 0.00020734 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_141-27_0_5_load_121 | 5 | 0.0050944 | 0.0012768 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_141-27_0_5_load_57 | 9 | 0.00069031 | 0.00017301 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_141-27_0_5_load_51 | 11 | 0.0069826 | 0.00175 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_141-27_0_5_load_50 | 12 | 0.014891 | 0.0037319 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_141-27_0_5_load_46 | 13 | 0.0016055 | 0.00040238 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_141-27_0_5_load_47 | 14 | 0.0024451 | 0.00061281 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_141-27_0_5_load_8 | 15 | 0.0013389 | 0.00033557 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_141-27_0_5_load_116 | 17 | 0.0007832 | 0.00019629 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_141-27_0_5_load_55 | 18 | 0.0019079 | 0.00047817 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_141-27_0_5_load_53 | 19 | 0.0015156 | 0.00037983 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_141-27_0_5_load_115 | 20 | 0.0011024 | 0.0002763 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_141-27_0_5_load_13 | 21 | 0.01794 | 0.0044963 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_141-27_0_5_load_84 | 27 | 0.0053111 | 0.0013311 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_141-27_0_5_load_104 | 32 | 0.0051933 | 0.0013016 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_141-27_0_5_load_107 | 33 | 0.0039299 | 0.00098491 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_141-27_0_5_load_122 | 35 | 0.031553 | 0.0079079 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_141-27_0_5_load_109 | 40 | 0.012828 | 0.0032151 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_141-27_0_5_load_111 | 43 | 0.0059598 | 0.0014937 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_141-27_0_5_load_90 | 44 | 0.0094534 | 0.0023693 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_141-27_0_5_load_88 | 45 | 0.0086644 | 0.0021715 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_141-27_0_5_load_79 | 48 | 0.0064631 | 0.0016198 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_141-27_0_5_load_103 | 50 | 0.042989 | 0.010774 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_141-27_0_5_load_80 | 54 | 0.0018419 | 0.00046163 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_141-27_0_5_load_92 | 55 | 0.0070666 | 0.0017711 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_141-27_0_5_load_91 | 56 | 0.016644 | 0.0041715 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_141-27_0_5_load_126 | 58 | 0.0046763 | 0.001172 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_141-27_0_5_load_99 | 59 | 0.0077884 | 0.001952 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_141-27_0_5_load_89 | 60 | 0.0055768 | 0.0013977 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_141-27_0_5_load_85 | 61 | 0.0039619 | 0.00099294 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_141-27_0_5_load_74 | 64 | 0.0016631 | 0.00041681 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_141-27_0_5_load_120 | 66 | 0.0010403 | 0.00026072 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_141-27_0_5_load_128 | 67 | 0.020742 | 0.0051984 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_141-27_0_5_load_129 | 69 | 0.015392 | 0.0038575 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_141-27_0_5_load_76 | 71 | 0.0053012 | 0.0013286 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_141-27_0_5_load_68 | 72 | 0.00097151 | 0.00024348 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_141-27_0_5_load_125 | 74 | 0.0038302 | 0.00095995 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_141-27_0_5_load_102 | 77 | 0.026326 | 0.0065979 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_141-27_0_5_load_101 | 79 | 0.034307 | 0.0085981 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_141-27_0_5_load_124 | 80 | 0.027998 | 0.0070169 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_141-27_0_5_load_62 | 84 | 0.0020334 | 0.00050963 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_141-27_0_5_load_59 | 85 | 0.0053041 | 0.0013293 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_141-27_0_5_load_83 | 86 | 0.0031252 | 0.00078324 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_141-27_0_5_load_81 | 87 | 0.0028671 | 0.00071856 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_141-27_0_5_load_66 | 88 | 0.0053097 | 0.0013307 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_141-27_0_5_load_123 | 90 | 0.0067809 | 0.0016995 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_141-27_0_5_load_118 | 92 | 0.0053092 | 0.0013306 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_141-27_0_5_load_105 | 94 | 0.0051357 | 0.0012871 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_141-27_0_5_load_108 | 95 | 0.019179 | 0.0048066 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_141-27_0_5_load_110 | 96 | 0.0059622 | 0.0014943 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_141-27_0_5_load_95 | 97 | 0.0094518 | 0.0023688 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_141-27_0_5_load_78 | 98 | 0.0017117 | 0.000429 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_141-27_0_5_load_77 | 99 | 0.0040838 | 0.0010235 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_141-27_0_5_load_127 | 101 | 0.005321 | 0.0013336 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_141-27_0_5_load_96 | 103 | 0.0094486 | 0.002368 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_141-27_0_5_load_93 | 105 | 0.0023228 | 0.00058216 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_141-27_0_5_load_86 | 106 | 0.0021057 | 0.00052774 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_141-27_0_5_load_56 | 107 | 0.00046144 | 0.00011565 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_141-27_0_5_load_52 | 108 | 0.0004291 | 0.00010754 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_141-27_0_5_load_73 | 109 | 0.00070827 | 0.00017751 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_141-27_0_5_load_67 | 110 | 0.000809 | 0.00020275 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_141-27_0_5_load_65 | 112 | 0.0020366 | 0.00051043 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_141-27_0_5_load_82 | 113 | 0.0026202 | 0.00065669 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_141-27_0_5_load_70 | 115 | 0.0011333 | 0.00028403 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_141-27_0_5_load_72 | 116 | 0.0011641 | 0.00029176 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_141-27_0_5_load_94 | 117 | 0.0058547 | 0.0014673 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_141-27_0_5_load_97 | 118 | 0.019258 | 0.0048265 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_141-27_0_5_load_113 | 119 | 0.0050265 | 0.0012598 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_141-27_0_5_line_0 |  | 0 | 1 | 0.089338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_141-27_0_5_line_1 |  | 1 | 2 | 0.035284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_141-27_0_5_line_2 |  | 1 | 3 | 0.10311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_141-27_0_5_line_3 |  | 1 | 4 | 0.027645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_141-27_0_5_line_4 |  | 2 | 5 | 0.008084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_141-27_0_5_line_5 |  | 3 | 6 | 0.061705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_141-27_0_5_line_6 |  | 4 | 7 | 0.028045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_141-27_0_5_line_7 |  | 6 | 8 | 0.071217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_141-27_0_5_line_8 |  | 7 | 9 | 0.062081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_141-27_0_5_line_9 |  | 8 | 17 | 0.033384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_141-27_0_5_line_10 |  | 8 | 16 | 0.14698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_141-27_0_5_line_11 |  | 9 | 107 | 0.018623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_141-27_0_5_line_12 |  | 10 | 11 | 0.024685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_141-27_0_5_line_13 |  | 10 | 12 | 0.041803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_141-27_0_5_line_14 |  | 12 | 65 | 0.051551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_141-27_0_5_line_15 |  | 13 | 14 | 0.079694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_141-27_0_5_line_16 |  | 14 | 65 | 0.0073005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_141-27_0_5_line_17 |  | 15 | 16 | 0.034427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_141-27_0_5_line_18 |  | 17 | 20 | 0.016074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_141-27_0_5_line_19 |  | 18 | 19 | 0.01366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_141-27_0_5_line_20 |  | 19 | 108 | 0.088771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_141-27_0_5_line_21 |  | 21 | 22 | 0.012763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_141-27_0_5_line_22 |  | 21 | 23 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_141-27_0_5_line_23 |  | 22 | 24 | 0.004311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_141-27_0_5_line_24 |  | 23 | 25 | 0.059575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_141-27_0_5_line_25 |  | 23 | 26 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_141-27_0_5_line_26 |  | 24 | 27 | 0.0103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_141-27_0_5_line_27 |  | 25 | 67 | 0.008756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_141-27_0_5_line_28 |  | 25 | 68 | 0.074156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_141-27_0_5_line_29 |  | 26 | 82 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_141-27_0_5_line_30 |  | 26 | 71 | 0.012798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_141-27_0_5_line_31 |  | 27 | 28 | 0.016968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_141-27_0_5_line_32 |  | 28 | 29 | 0.031339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_141-27_0_5_line_33 |  | 29 | 86 | 0.014064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_141-27_0_5_line_34 |  | 29 | 87 | 0.017545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_141-27_0_5_line_35 |  | 30 | 31 | 0.028196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_141-27_0_5_line_36 |  | 30 | 32 | 0.047576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_141-27_0_5_line_37 |  | 31 | 33 | 0.028902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_141-27_0_5_line_38 |  | 32 | 94 | 0.056936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_141-27_0_5_line_39 |  | 33 | 95 | 0.0039787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_141-27_0_5_line_40 |  | 34 | 35 | 0.024286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_141-27_0_5_line_41 |  | 34 | 36 | 0.0095152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_141-27_0_5_line_42 |  | 36 | 49 | 0.061732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_141-27_0_5_line_43 |  | 36 | 50 | 0.010637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_141-27_0_5_line_44 |  | 36 | 37 | 0.036854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_141-27_0_5_line_45 |  | 37 | 38 | 0.043786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_141-27_0_5_line_46 |  | 37 | 39 | 0.048877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_141-27_0_5_line_47 |  | 37 | 40 | 0.037359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_141-27_0_5_line_48 |  | 38 | 57 | 0.009352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_141-27_0_5_line_49 |  | 38 | 58 | 0.036515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_141-27_0_5_line_50 |  | 39 | 59 | 0.052793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_141-27_0_5_line_51 |  | 41 | 42 | 0.014934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_141-27_0_5_line_52 |  | 41 | 43 | 0.03793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_141-27_0_5_line_53 |  | 42 | 44 | 0.0228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_141-27_0_5_line_54 |  | 42 | 45 | 0.046121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_141-27_0_5_line_55 |  | 43 | 96 | 0.031037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_141-27_0_5_line_56 |  | 44 | 97 | 0.02786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_141-27_0_5_line_57 |  | 45 | 53 | 0.032347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_141-27_0_5_line_58 |  | 46 | 47 | 0.21732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_141-27_0_5_line_59 |  | 46 | 48 | 0.067845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_141-27_0_5_line_60 |  | 47 | 65 | 0.13426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_141-27_0_5_line_61 |  | 47 | 66 | 0.1181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_141-27_0_5_line_62 |  | 48 | 98 | 0.024463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_141-27_0_5_line_63 |  | 49 | 55 | 0.003105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_141-27_0_5_line_64 |  | 49 | 56 | 0.044463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_141-27_0_5_line_65 |  | 51 | 52 | 0.006433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_141-27_0_5_line_66 |  | 51 | 53 | 0.041973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_141-27_0_5_line_67 |  | 51 | 54 | 0.06642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_141-27_0_5_line_68 |  | 52 | 99 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_141-27_0_5_line_69 |  | 52 | 100 | 0.006872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_141-27_0_5_line_70 |  | 53 | 60 | 0.037617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_141-27_0_5_line_71 |  | 53 | 61 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_141-27_0_5_line_72 |  | 54 | 98 | 0.024598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_141-27_0_5_line_73 |  | 57 | 101 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_141-27_0_5_line_74 |  | 57 | 102 | 0.046991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_141-27_0_5_line_75 |  | 59 | 104 | 0.0034603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_141-27_0_5_line_76 |  | 60 | 105 | 9.3148e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_141-27_0_5_line_77 |  | 61 | 106 | 0.022277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_141-27_0_5_line_78 |  | 62 | 63 | 0.074612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_141-27_0_5_line_79 |  | 62 | 64 | 0.1111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_141-27_0_5_line_80 |  | 63 | 107 | 0.010809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_141-27_0_5_line_81 |  | 63 | 108 | 0.034442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_141-27_0_5_line_82 |  | 64 | 109 | 0.026282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_141-27_0_5_line_83 |  | 68 | 69 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_141-27_0_5_line_84 |  | 70 | 71 | 0.022839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_141-27_0_5_line_85 |  | 70 | 72 | 0.043301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_141-27_0_5_line_86 |  | 72 | 110 | 0.021504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_141-27_0_5_line_87 |  | 73 | 74 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_141-27_0_5_line_88 |  | 73 | 75 | 0.045126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_141-27_0_5_line_89 |  | 75 | 104 | 0.015874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_141-27_0_5_line_90 |  | 76 | 77 | 0.042861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_141-27_0_5_line_91 |  | 76 | 78 | 0.040739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_141-27_0_5_line_92 |  | 76 | 79 | 0.058234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_141-27_0_5_line_93 |  | 78 | 80 | 0.016227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_141-27_0_5_line_94 |  | 78 | 81 | 0.020998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_141-27_0_5_line_95 |  | 81 | 106 | 0.065356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_141-27_0_5_line_96 |  | 82 | 88 | 0.01949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_141-27_0_5_line_97 |  | 83 | 84 | 0.001123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_141-27_0_5_line_98 |  | 83 | 85 | 0.0087363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_141-27_0_5_line_99 |  | 85 | 111 | 0.0097214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_141-27_0_5_line_100 |  | 87 | 113 | 0.018285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_141-27_0_5_line_101 |  | 88 | 111 | 0.010262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_141-27_0_5_line_102 |  | 89 | 90 | 0.013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_141-27_0_5_line_103 |  | 89 | 91 | 0.022872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_141-27_0_5_line_104 |  | 91 | 119 | 0.026364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_141-27_0_5_line_105 |  | 91 | 96 | 0.035548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_141-27_0_5_line_106 |  | 92 | 93 | 0.0151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_141-27_0_5_line_107 |  | 93 | 102 | 0.022096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_141-27_0_5_line_108 |  | 93 | 94 | 0.014351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_141-27_0_5_line_109 |  | 97 | 103 | 0.03353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_141-27_0_5_line_110 |  | 99 | 115 | 0.022091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_141-27_0_5_line_111 |  | 100 | 116 | 0.085769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_141-27_0_5_line_112 |  | 102 | 119 | 0.051047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_141-27_0_5_line_113 |  | 105 | 117 | 0.020314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_141-27_0_5_line_114 |  | 109 | 116 | 0.0081674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_141-27_0_5_line_115 |  | 110 | 114 | 0.013959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_141-27_0_5_line_116 |  | 111 | 112 | 0.019486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_141-27_0_5_line_117 |  | 114 | 115 | 0.014768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_141-27_0_5_line_118 |  | 117 | 118 | 0.049099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_141-27_0_5_trafo_124 | 0.63 MVA 20/0.4 kV | 120 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2684149.5588 | 1238233.1582 | 2684159.3987 | 1238250.9548 | 2684179.6047 | 1238279.2947 | 2684185.8219 | 1238289.5346 | 2684189.0391 | 1238299.5318 | 2684196.7313 | 1238308.3675
1 | 2684149.5588 | 1238233.1582 | 2684146.5413 | 1238250.6947 | 2684141.3944 | 1238267.4115
2 | 2684149.5588 | 1238233.1582 | 2684202.9493 | 1238144.9454
3 | 2684149.5588 | 1238233.1582 | 2684146.7342 | 1238226.9471 | 2684129.0903 | 1238215.8901
4 | 2684141.3944 | 1238267.4115 | 2684133.6592 | 1238264.9891
5 | 2684234.8998 | 1238092.1561 | 2684202.9493 | 1238144.9454
6 | 2684105.326 | 1238200.9977 | 2684129.0903 | 1238215.8901
7 | 2684279.6732 | 1238043.6344 | 2684253.7005 | 1238078.2795 | 2684250.7723 | 1238080.9621 | 2684240.4893 | 1238083.1957 | 2684233.0725 | 1238087.6381 | 2684234.8998 | 1238092.1561
8 | 2684105.326 | 1238200.9977 | 2684055.7278 | 1238167.3049 | 2684053.9084 | 1238166.2148
9 | 2684279.6732 | 1238043.6344 | 2684276.039 | 1238043.2937 | 2684267.326 | 1238048.4404 | 2684253.9123 | 1238048.9616 | 2684247.8055 | 1238047.95
10 | 2684279.6732 | 1238043.6344 | 2684302.648 | 1238013.9392 | 2684334.6053 | 1237975.5988 | 2684373.1766 | 1237930.2587
11 | 2684037.9333 | 1238156.6434 | 2684053.9084 | 1238166.2148
12 | 2683811.2849 | 1238417.7738 | 2683835.6377 | 1238421.8124
13 | 2683811.2849 | 1238417.7738 | 2683816.6499 | 1238409.11 | 2683817.6804 | 1238385.9525 | 2683812.9219 | 1238378.9915
14 | 2683843.2081 | 1238348.2636 | 2683821.3696 | 1238352.3917 | 2683815.0308 | 1238358.7623 | 2683812.9219 | 1238378.9915
15 | 2683865.0782 | 1238432.052 | 2683864.9048 | 1238424.8468 | 2683863.4374 | 1238417.3319 | 2683856.2447 | 1238395.259 | 2683849.843 | 1238378.2342 | 2683844.6488 | 1238357.6685 | 2683844.3135 | 1238355.48
16 | 2683843.2081 | 1238348.2636 | 2683844.3135 | 1238355.48
17 | 2684373.1766 | 1237930.2587 | 2684370.7265 | 1237928.0445 | 2684358.4657 | 1237929.9384 | 2684346.9432 | 1237926.7391 | 2684340.7844 | 1237929.526
18 | 2684232.7771 | 1238042.5856 | 2684234.7153 | 1238043.8524 | 2684244.5153 | 1238047.405 | 2684247.8055 | 1238047.95
19 | 2684091.8548 | 1238032.8615 | 2684089.576 | 1238034.3002 | 2684082.3463 | 1238042.5436
20 | 2684039.7319 | 1238118.4738 | 2684054.8721 | 1238073.8706 | 2684082.3463 | 1238042.5436
21 | 2684162.3922 | 1237842.4057 | 2684150.1502 | 1237846.0135
22 | 2684133.9544 | 1237850.7866 | 2684150.1502 | 1237846.0135
23 | 2684162.3922 | 1237842.4057 | 2684163.5134 | 1237846.569
24 | 2684115.37 | 1237802.3889 | 2684117.6953 | 1237811.8175 | 2684115.8702 | 1237827.425 | 2684116.8166 | 1237840.1919 | 2684124.2593 | 1237843.5441 | 2684131.9325 | 1237846.1102 | 2684133.9544 | 1237850.7866
25 | 2684125.7028 | 1237857.5301 | 2684124.5411 | 1237853.5553 | 2684133.9544 | 1237850.7866
26 | 2684163.5134 | 1237846.569 | 2684166.1944 | 1237856.5141
27 | 2684115.37 | 1237802.3889 | 2684106.8796 | 1237804.6259
28 | 2684115.37 | 1237802.3889 | 2684117.6953 | 1237811.8175 | 2684126.5048 | 1237809.485 | 2684142.4262 | 1237807.687 | 2684160.9106 | 1237802.8232 | 2684163.0846 | 1237796.2382 | 2684163.7812 | 1237788.7316 | 2684166.6883 | 1237783.8026
29 | 2684129.8955 | 1237871.8553 | 2684125.7028 | 1237857.5301
30 | 2684125.7028 | 1237857.5301 | 2684114.6875 | 1237860.6986 | 2684113.3611 | 1237860.8559
31 | 2684180.7372 | 1237856.4312 | 2684178.5197 | 1237855.4102 | 2684175.9403 | 1237855.9073 | 2684173.1709 | 1237858.5922 | 2684169.0438 | 1237855.6539 | 2684166.1944 | 1237856.5141
32 | 2684180.7372 | 1237856.4312 | 2684178.6135 | 1237860.0037 | 2684174.8313 | 1237870.0906 | 2684177.6278 | 1237880.4265 | 2684178.8132 | 1237880.0653 | 2684179.9397 | 1237884.3843
33 | 2684184.242 | 1237896.8431 | 2684182.4131 | 1237890.3014 | 2684181.5545 | 1237890.556 | 2684179.9397 | 1237884.3843
34 | 2684179.9397 | 1237884.3843 | 2684196.7973 | 1237879.5198
35 | 2683923.2214 | 1237697.8522 | 2683908.2877 | 1237695.0615 | 2683900.3691 | 1237684.6756
36 | 2683900.3691 | 1237684.6756 | 2683888.9796 | 1237691.8198 | 2683876.7977 | 1237694.0049 | 2683869.8797 | 1237702.2242 | 2683869.9804 | 1237713.235
37 | 2683923.2214 | 1237697.8522 | 2683916.8368 | 1237713.2952 | 2683906.8747 | 1237720.3219
38 | 2683869.9804 | 1237713.235 | 2683870.1295 | 1237729.5249 | 2683872.3324 | 1237734.2594 | 2683879.7619 | 1237741.2359 | 2683889.6041 | 1237743.9991 | 2683904.6108 | 1237743.7338
39 | 2683903.6234 | 1237722.6152 | 2683906.8747 | 1237720.3219
40 | 2683855.5586 | 1237863.8705 | 2683846.5332 | 1237856.8603 | 2683847.3125 | 1237844.0066
41 | 2683838.141 | 1237843.0542 | 2683839.5807 | 1237842.8966 | 2683843.5818 | 1237842.4528 | 2683847.3125 | 1237844.0066
42 | 2683838.141 | 1237843.0542 | 2683839.5807 | 1237842.8966 | 2683838.7327 | 1237850.9793 | 2683837.7298 | 1237867.3435 | 2683837.3545 | 1237873.5648 | 2683838.0579 | 1237888.0406 | 2683841.718 | 1237902.6249
43 | 2683838.141 | 1237843.0542 | 2683835.6652 | 1237845.8546 | 2683831.8745 | 1237851.6192
44 | 2683838.141 | 1237843.0542 | 2683839.5807 | 1237842.8966 | 2683840.964 | 1237826.3822 | 2683841.4036 | 1237819.3612 | 2683842.145 | 1237807.5855
45 | 2683842.145 | 1237807.5855 | 2683844.123 | 1237796.6389 | 2683847.8718 | 1237789.4089 | 2683855.2913 | 1237777.8165 | 2683863.5969 | 1237770.9844
46 | 2683856.0521 | 1237791.9818 | 2683853.4943 | 1237797.3717 | 2683850.995 | 1237805.5867 | 2683849.7727 | 1237816.5996 | 2683849.4835 | 1237819.9312 | 2683845.206 | 1237819.5928 | 2683841.4036 | 1237819.3612 | 2683842.145 | 1237807.5855
47 | 2683842.145 | 1237807.5855 | 2683839.6096 | 1237807.6386 | 2683830.7729 | 1237817.7989 | 2683813.323 | 1237805.4837
48 | 2683863.5969 | 1237770.9844 | 2683872.0007 | 1237766.8335
49 | 2683839.1154 | 1237746.7438 | 2683838.5062 | 1237749.704 | 2683839.5005 | 1237752.1531 | 2683855.6358 | 1237761.999 | 2683863.5969 | 1237770.9844
50 | 2683856.0521 | 1237791.9818 | 2683864.6104 | 1237788.678 | 2683866.8133 | 1237793.9462 | 2683873.3841 | 1237796.9078 | 2683887.7778 | 1237806.8403 | 2683892.9238 | 1237807.2911 | 2683899.4984 | 1237811.9329
51 | 2684090.0685 | 1237766.683 | 2684093.7467 | 1237759.1297 | 2684096.0426 | 1237753.0134
52 | 2684096.0426 | 1237753.0134 | 2684085.7934 | 1237751.7563 | 2684065.5084 | 1237747.5218 | 2684058.756 | 1237746.1928
53 | 2684090.0685 | 1237766.683 | 2684088.3741 | 1237762.923 | 2684085.1606 | 1237760.6426 | 2684070.7783 | 1237757.437
54 | 2684090.0685 | 1237766.683 | 2684083.0316 | 1237781.683 | 2684070.849 | 1237799.9458 | 2684066.1997 | 1237805.9572
55 | 2684028.036 | 1237742.3462 | 2684043.3489 | 1237743.1606 | 2684058.756 | 1237746.1928
56 | 2684070.7783 | 1237757.437 | 2684053.1969 | 1237753.5185 | 2684043.4843 | 1237751.8986
57 | 2684046.4101 | 1237831.5447 | 2684066.1997 | 1237805.9572
58 | 2683851.3466 | 1238215.5728 | 2683859.2828 | 1238198.9619 | 2683869.5895 | 1238180.572 | 2683884.7692 | 1238147.674 | 2683900.7051 | 1238103.034 | 2683911.1865 | 1238075.518 | 2683930.9003 | 1238037.1358 | 2683943.151 | 1238019.3407
59 | 2683943.151 | 1238019.3407 | 2683948.8707 | 1238019.8663 | 2683986.5232 | 1237972.9318 | 2683987.6808 | 1237971.387
60 | 2683851.3466 | 1238215.5728 | 2683838.8226 | 1238276.3282 | 2683838.4632 | 1238307.6677 | 2683843.2081 | 1238348.2636
61 | 2683851.3466 | 1238215.5728 | 2683834.0302 | 1238213.3823 | 2683821.363 | 1238215.7163 | 2683814.9584 | 1238221.9193 | 2683812.994 | 1238228.6964 | 2683802.0231 | 1238299.6424
62 | 2684001.6722 | 1237951.3582 | 2683997.8434 | 1237957.8255 | 2683987.6808 | 1237971.387
63 | 2683841.718 | 1237902.6249 | 2683838.6405 | 1237903.0373
64 | 2683841.718 | 1237902.6249 | 2683847.3075 | 1237915.5908 | 2683853.5367 | 1237930.9452 | 2683858.9732 | 1237943.6012
65 | 2684041.5428 | 1237870.726 | 2684036.0602 | 1237867.3349
66 | 2684036.0602 | 1237867.3349 | 2684032.5538 | 1237864.3721 | 2684036.6946 | 1237855.6578 | 2684048.395 | 1237834.5638 | 2684046.4101 | 1237831.5447
67 | 2684036.0602 | 1237867.3349 | 2684029.6805 | 1237884.0232 | 2684018.7633 | 1237917.1479 | 2684013.1174 | 1237929.6049
68 | 2684041.5428 | 1237870.726 | 2684050.424 | 1237875.3764
69 | 2684041.5428 | 1237870.726 | 2684044.2223 | 1237877.0573
70 | 2684046.4101 | 1237831.5447 | 2684043.1068 | 1237826.5277 | 2684040.3049 | 1237806.396 | 2684029.0984 | 1237807.7198
71 | 2684046.4101 | 1237831.5447 | 2684036.3846 | 1237846.7828
72 | 2684001.6722 | 1237951.3582 | 2684006.1602 | 1237943.7776 | 2684012.9998 | 1237929.8644 | 2684013.1174 | 1237929.6049
73 | 2683869.5209 | 1237754.9233 | 2683868.8366 | 1237760.5176 | 2683872.0007 | 1237766.8335
74 | 2683872.0007 | 1237766.8335 | 2683880.1959 | 1237764.0694 | 2683890.5104 | 1237762.8476 | 2683902.1086 | 1237764.4792 | 2683918.4508 | 1237765.5664
75 | 2683902.3252 | 1237813.9286 | 2683899.4984 | 1237811.9329
76 | 2684029.0059 | 1237807.7307 | 2684029.0984 | 1237807.7198
77 | 2684036.3846 | 1237846.7828 | 2684035.6468 | 1237847.9041 | 2684033.0243 | 1237852.5147 | 2684029.9073 | 1237859.4533 | 2684022.9285 | 1237863.413
78 | 2683980.8925 | 1238097.1185 | 2683981.6355 | 1238105.0235 | 2683985.8325 | 1238114.245 | 2684006.5893 | 1238134.7643 | 2684028.6613 | 1238151.0881
79 | 2683980.8925 | 1238097.1185 | 2683983.9117 | 1238081.5723 | 2683989.1577 | 1238066.9138 | 2683997.9261 | 1238050.8819 | 2684004.5913 | 1238036.4548 | 2684017.6212 | 1237996.7663 | 2684018.8539 | 1237993.2212
80 | 2684028.6613 | 1238151.0881 | 2684037.9333 | 1238156.6434
81 | 2684028.6613 | 1238151.0881 | 2684039.7319 | 1238118.4738
82 | 2684018.8539 | 1237993.2212 | 2684027.4853 | 1237968.3975
83 | 2684166.6883 | 1237783.8026 | 2684171.9455 | 1237786.5457 | 2684178.5385 | 1237785.7942
84 | 2684090.7099 | 1237860.8036 | 2684101.2886 | 1237862.2878 | 2684113.3611 | 1237860.8559
85 | 2684090.7099 | 1237860.8036 | 2684092.584 | 1237873.239 | 2684098.2022 | 1237884.6823 | 2684104.01 | 1237886.4769 | 2684103.9419 | 1237887.5434 | 2684094.6318 | 1237893.076
86 | 2684076.1458 | 1237904.0616 | 2684094.6318 | 1237893.076
87 | 2683892.6061 | 1237864.027 | 2683884.9536 | 1237859.4601 | 2683887.6466 | 1237855.2062
88 | 2683915.3224 | 1237823.0965 | 2683913.8644 | 1237825.0773 | 2683903.4537 | 1237829.9004 | 2683899.8905 | 1237833.0856 | 2683898.0213 | 1237835.7945 | 2683896.4254 | 1237844.3225 | 2683891.8189 | 1237851.2068 | 2683890.0204 | 1237851.5927 | 2683887.6466 | 1237855.2062
89 | 2683915.3224 | 1237823.0965 | 2683902.3252 | 1237813.9286
90 | 2683959.1208 | 1237933.8499 | 2683945.0051 | 1237951.8966 | 2683941.0831 | 1237970.8324 | 2683940.8969 | 1237971.4155
91 | 2683991.5061 | 1237943.7259 | 2683986.391 | 1237950.7252 | 2683959.1208 | 1237933.8499
92 | 2683959.1208 | 1237933.8499 | 2683949.7756 | 1237928.0692 | 2683906.9577 | 1237948.0371
93 | 2683991.5061 | 1237943.7259 | 2683978.9185 | 1237933.4405
94 | 2683991.5061 | 1237943.7259 | 2684000.7084 | 1237924.8425
95 | 2684000.7084 | 1237924.8425 | 2684009.7448 | 1237902.7212 | 2684022.9285 | 1237863.413
96 | 2684129.8955 | 1237871.8553 | 2684131.5409 | 1237877.4715 | 2684130.842 | 1237877.6728 | 2684134.3628 | 1237890.0943
97 | 2684151.5266 | 1237905.986 | 2684151.1025 | 1237904.9459
98 | 2684151.1025 | 1237904.9459 | 2684148.631 | 1237898.8955 | 2684146.6627 | 1237897.9113
99 | 2684137.1612 | 1237899.9671 | 2684146.6627 | 1237897.9113
100 | 2684196.7973 | 1237879.5198 | 2684196.7973 | 1237879.5198 | 2684198.6951 | 1237885.4731 | 2684203.152 | 1237884.3577 | 2684204.8136 | 1237891.6119
101 | 2684137.1612 | 1237899.9671 | 2684134.3628 | 1237890.0943
102 | 2683976.8273 | 1237729.3656 | 2683990.4409 | 1237729.7361
103 | 2683976.8273 | 1237729.3656 | 2683979.545 | 1237734.6077 | 2683992.6782 | 1237745.4011
104 | 2683992.6782 | 1237745.4011 | 2683972.714 | 1237751.1118 | 2683967.5282 | 1237753.2239
105 | 2683992.6782 | 1237745.4011 | 2684009.9172 | 1237742.9987 | 2684025.4008 | 1237742.2061 | 2684028.036 | 1237742.3462
106 | 2683918.9598 | 1237743.4801 | 2683920.5416 | 1237743.4468 | 2683933.8756 | 1237741.2272
107 | 2683918.9598 | 1237743.4801 | 2683918.8361 | 1237751.1616 | 2683918.4508 | 1237765.5664
108 | 2683918.9598 | 1237743.4801 | 2683904.6108 | 1237743.7338
109 | 2684010.0618 | 1237751.3453 | 2684015.4901 | 1237750.7053 | 2684029.8977 | 1237750.5645 | 2684041.9049 | 1237751.6351 | 2684043.4843 | 1237751.8986
110 | 2684066.3366 | 1237887.6406 | 2684066.6416 | 1237883.8683 | 2684050.424 | 1237875.3764
111 | 2684044.2223 | 1237877.0573 | 2684044.8615 | 1237898.704 | 2684043.5169 | 1237916.72 | 2684041.2895 | 1237928.6971 | 2684030.1676 | 1237960.6832
112 | 2683918.4508 | 1237765.5664 | 2683927.3097 | 1237765.0912 | 2683940.629 | 1237763.2559 | 2683950.9728 | 1237759.9664 | 2683967.5282 | 1237753.2239
113 | 2684008.8841 | 1237810.4367 | 2684012.6507 | 1237809.6627 | 2684029.0059 | 1237807.7307
114 | 2684030.1676 | 1237960.6832 | 2684027.4853 | 1237968.3975
115 | 2684065.1465 | 1237902.3603 | 2684069.8161 | 1237904.9282 | 2684073.7751 | 1237901.5708 | 2684076.1458 | 1237904.0616
116 | 2684137.1612 | 1237899.9671 | 2684126.0684 | 1237908.605 | 2684126.1501 | 1237914.0545
117 | 2684065.1465 | 1237902.3603 | 2684066.3366 | 1237887.6406
118 | 2684008.8841 | 1237810.4367 | 2683990.934 | 1237814.1254 | 2683960.4772 | 1237809.7192

## bus_geodata
| x | y | coords
0 | 2684196.7313 | 1238308.3675
1 | 2684149.5588 | 1238233.1582
2 | 2684141.3944 | 1238267.4115
3 | 2684202.9493 | 1238144.9454
4 | 2684129.0903 | 1238215.8901
5 | 2684133.6592 | 1238264.9891
6 | 2684234.8998 | 1238092.1561
7 | 2684105.326 | 1238200.9977
8 | 2684279.6732 | 1238043.6344
9 | 2684053.9084 | 1238166.2148
10 | 2683811.2849 | 1238417.7738
11 | 2683835.6377 | 1238421.8124
12 | 2683812.9219 | 1238378.9915
13 | 2683865.0782 | 1238432.052
14 | 2683844.3135 | 1238355.48
15 | 2684340.7844 | 1237929.526
16 | 2684373.1766 | 1237930.2587
17 | 2684247.8055 | 1238047.95
18 | 2684091.8548 | 1238032.8615
19 | 2684082.3463 | 1238042.5436
20 | 2684232.7771 | 1238042.5856
21 | 2684150.1502 | 1237846.0135
22 | 2684162.3922 | 1237842.4057
23 | 2684133.9544 | 1237850.7866
24 | 2684163.5134 | 1237846.569
25 | 2684115.37 | 1237802.3889
26 | 2684125.7028 | 1237857.5301
27 | 2684166.1944 | 1237856.5141
28 | 2684180.7372 | 1237856.4312
29 | 2684179.9397 | 1237884.3843
30 | 2683900.3691 | 1237684.6756
31 | 2683923.2214 | 1237697.8522
32 | 2683869.9804 | 1237713.235
33 | 2683906.8747 | 1237720.3219
34 | 2683847.3125 | 1237844.0066
35 | 2683855.5586 | 1237863.8705
36 | 2683838.141 | 1237843.0542
37 | 2683842.145 | 1237807.5855
38 | 2683863.5969 | 1237770.9844
39 | 2683856.0521 | 1237791.9818
40 | 2683813.323 | 1237805.4837
41 | 2684096.0426 | 1237753.0134
42 | 2684090.0685 | 1237766.683
43 | 2684058.756 | 1237746.1928
44 | 2684070.7783 | 1237757.437
45 | 2684066.1997 | 1237805.9572
46 | 2683943.151 | 1238019.3407
47 | 2683851.3466 | 1238215.5728
48 | 2683987.6808 | 1237971.387
49 | 2683841.718 | 1237902.6249
50 | 2683831.8745 | 1237851.6192
51 | 2684036.0602 | 1237867.3349
52 | 2684041.5428 | 1237870.726
53 | 2684046.4101 | 1237831.5447
54 | 2684013.1174 | 1237929.6049
55 | 2683838.6405 | 1237903.0373
56 | 2683858.9732 | 1237943.6012
57 | 2683872.0007 | 1237766.8335
58 | 2683839.1154 | 1237746.7438
59 | 2683899.4984 | 1237811.9329
60 | 2684029.0984 | 1237807.7198
61 | 2684036.3846 | 1237846.7828
62 | 2683980.8925 | 1238097.1185
63 | 2684028.6613 | 1238151.0881
64 | 2684018.8539 | 1237993.2212
65 | 2683843.2081 | 1238348.2636
66 | 2683802.0231 | 1238299.6424
67 | 2684106.8796 | 1237804.6259
68 | 2684166.6883 | 1237783.8026
69 | 2684178.5385 | 1237785.7942
70 | 2684090.7099 | 1237860.8036
71 | 2684113.3611 | 1237860.8559
72 | 2684094.6318 | 1237893.076
73 | 2683887.6466 | 1237855.2062
74 | 2683892.6061 | 1237864.027
75 | 2683915.3224 | 1237823.0965
76 | 2683959.1208 | 1237933.8499
77 | 2683940.8969 | 1237971.4155
78 | 2683991.5061 | 1237943.7259
79 | 2683906.9577 | 1237948.0371
80 | 2683978.9185 | 1237933.4405
81 | 2684000.7084 | 1237924.8425
82 | 2684129.8955 | 1237871.8553
83 | 2684151.1025 | 1237904.9459
84 | 2684151.5266 | 1237905.986
85 | 2684146.6627 | 1237897.9113
86 | 2684184.242 | 1237896.8431
87 | 2684196.7973 | 1237879.5198
88 | 2684134.3628 | 1237890.0943
89 | 2683976.8273 | 1237729.3656
90 | 2683990.4409 | 1237729.7361
91 | 2683992.6782 | 1237745.4011
92 | 2683933.8756 | 1237741.2272
93 | 2683918.9598 | 1237743.4801
94 | 2683904.6108 | 1237743.7338
95 | 2683903.6234 | 1237722.6152
96 | 2684028.036 | 1237742.3462
97 | 2684043.4843 | 1237751.8986
98 | 2684001.6722 | 1237951.3582
99 | 2684050.424 | 1237875.3764
100 | 2684044.2223 | 1237877.0573
101 | 2683869.5209 | 1237754.9233
102 | 2683918.4508 | 1237765.5664
103 | 2684010.0618 | 1237751.3453
104 | 2683902.3252 | 1237813.9286
105 | 2684029.0059 | 1237807.7307
106 | 2684022.9285 | 1237863.413
107 | 2684037.9333 | 1238156.6434
108 | 2684039.7319 | 1238118.4738
109 | 2684027.4853 | 1237968.3975
110 | 2684076.1458 | 1237904.0616
111 | 2684137.1612 | 1237899.9671
112 | 2684126.1501 | 1237914.0545
113 | 2684204.8136 | 1237891.6119
114 | 2684065.1465 | 1237902.3603
115 | 2684066.3366 | 1237887.6406
116 | 2684030.1676 | 1237960.6832
117 | 2684008.8841 | 1237810.4367
118 | 2683960.4772 | 1237809.7192
119 | 2683967.5282 | 1237753.2239
120 | 2683991.5061 | 1237943.7259

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97694 | -0.44329 | 0.0022842 | 0.00057248
1 | 0.97713 | -0.43957 | 0 | 0
2 | 0.97696 | -0.44285 | 0 | 0
3 | 0.97611 | -0.45968 | 0.0074364 | 0.0018637
4 | 0.97759 | -0.43046 | 0.0008273 | 0.00020734
5 | 0.97693 | -0.4436 | 0.0050944 | 0.0012768
6 | 0.97592 | -0.46333 | 0 | 0
7 | 0.97808 | -0.4208 | 0 | 0
8 | 0.97571 | -0.46755 | 0 | 0
9 | 0.97917 | -0.39946 | 0.00069031 | 0.00017301
10 | 0.97271 | -0.52576 | 0 | 0
11 | 0.97255 | -0.52894 | 0.0069826 | 0.00175
12 | 0.97298 | -0.52039 | 0.014891 | 0.0037319
13 | 0.97388 | -0.50254 | 0.0016055 | 0.00040238
14 | 0.974 | -0.50019 | 0.0024451 | 0.00061281
15 | 0.97549 | -0.472 | 0.0013389 | 0.00033557
16 | 0.97553 | -0.47116 | 0 | 0
17 | 0.97565 | -0.4687 | 0.0007832 | 0.00019629
18 | 0.97928 | -0.39731 | 0.0019079 | 0.00047817
19 | 0.97931 | -0.39683 | 0.0015156 | 0.00037983
20 | 0.97564 | -0.46902 | 0.0011024 | 0.0002763
21 | 0.97506 | -0.47951 | 0.01794 | 0.0044963
22 | 0.97489 | -0.48277 | 0 | 0
23 | 0.97556 | -0.46965 | 0 | 0
24 | 0.97483 | -0.48387 | 0 | 0
25 | 0.97355 | -0.50916 | 0 | 0
26 | 0.97644 | -0.45229 | 0 | 0
27 | 0.9747 | -0.4865 | 0.0053111 | 0.0013311
28 | 0.97456 | -0.48918 | 0 | 0
29 | 0.97431 | -0.49414 | 0 | 0
30 | 0.97458 | -0.4888 | 0 | 0
31 | 0.97398 | -0.50076 | 0 | 0
32 | 0.97561 | -0.46864 | 0.0051933 | 0.0013016
33 | 0.97336 | -0.51304 | 0.0039299 | 0.00098491
34 | 0.97333 | -0.51342 | 0 | 0
35 | 0.97262 | -0.52753 | 0.031553 | 0.0079079
36 | 0.97361 | -0.5079 | 0 | 0
37 | 0.9753 | -0.47467 | 0 | 0
38 | 0.97697 | -0.4419 | 0 | 0
39 | 0.97477 | -0.48508 | 0 | 0
40 | 0.97485 | -0.48345 | 0.012828 | 0.0032151
41 | 0.98454 | -0.29465 | 0 | 0
42 | 0.98508 | -0.28417 | 0 | 0
43 | 0.98316 | -0.32132 | 0.0059598 | 0.0014937
44 | 0.98448 | -0.29579 | 0.0094534 | 0.0023693
45 | 0.987 | -0.2472 | 0.0086644 | 0.0021715
46 | 0.98274 | -0.32948 | 0 | 0
47 | 0.97727 | -0.4359 | 0 | 0
48 | 0.98444 | -0.2965 | 0.0064631 | 0.0016198
49 | 0.97225 | -0.53486 | 0 | 0
50 | 0.97319 | -0.51631 | 0.042989 | 0.010774
51 | 0.98715 | -0.24426 | 0 | 0
52 | 0.987 | -0.24708 | 0 | 0
53 | 0.98839 | -0.22035 | 0 | 0
54 | 0.98601 | -0.26627 | 0.0018419 | 0.00046163
55 | 0.97223 | -0.53526 | 0.0070666 | 0.0017711
56 | 0.97156 | -0.54851 | 0.016644 | 0.0041715
57 | 0.97719 | -0.43755 | 0 | 0
58 | 0.97681 | -0.44502 | 0.0046763 | 0.001172
59 | 0.9742 | -0.49634 | 0.0077884 | 0.001952
60 | 0.98725 | -0.24253 | 0.0055768 | 0.0013977
61 | 0.98983 | -0.19274 | 0.0039619 | 0.00099294
62 | 0.98136 | -0.35657 | 0 | 0
63 | 0.97971 | -0.3889 | 0 | 0
64 | 0.98383 | -0.30863 | 0.0016631 | 0.00041681
65 | 0.97403 | -0.49965 | 0 | 0
66 | 0.97716 | -0.43814 | 0.0010403 | 0.00026072
67 | 0.97338 | -0.5125 | 0.020742 | 0.0051984
68 | 0.97249 | -0.53017 | 0 | 0
69 | 0.97231 | -0.53373 | 0.015392 | 0.0038575
70 | 0.97929 | -0.39636 | 0 | 0
71 | 0.97742 | -0.43296 | 0.0053012 | 0.0013286
72 | 0.98284 | -0.32736 | 0.00097151 | 0.00024348
73 | 0.97397 | -0.50088 | 0 | 0
74 | 0.97392 | -0.50186 | 0.0038302 | 0.00095995
75 | 0.97413 | -0.49771 | 0 | 0
76 | 0.99627 | -0.071123 | 0 | 0
77 | 0.99524 | -0.090958 | 0.026326 | 0.0065979
78 | 0.99852 | -0.027842 | 0 | 0
79 | 0.99445 | -0.10627 | 0.034307 | 0.0085981
80 | 1 | 0 | -0.50246 | -0.12915
81 | 0.99684 | -0.059525 | 0 | 0
82 | 0.97624 | -0.45629 | 0 | 0
83 | 0.9758 | -0.46492 | 0 | 0
84 | 0.9758 | -0.46496 | 0.0020334 | 0.00050963
85 | 0.97581 | -0.4646 | 0.0053041 | 0.0013293
86 | 0.97427 | -0.49495 | 0.0031252 | 0.00078324
87 | 0.97422 | -0.49591 | 0.0028671 | 0.00071856
88 | 0.97597 | -0.46153 | 0.0053097 | 0.0013307
89 | 0.98071 | -0.36892 | 0 | 0
90 | 0.98062 | -0.37059 | 0.0067809 | 0.0016995
91 | 0.98085 | -0.36611 | 0 | 0
92 | 0.97748 | -0.43188 | 0.0053092 | 0.0013306
93 | 0.97756 | -0.43042 | 0 | 0
94 | 0.97711 | -0.43918 | 0.0051357 | 0.0012871
95 | 0.97328 | -0.51445 | 0.019179 | 0.0048066
96 | 0.98206 | -0.34253 | 0.0059622 | 0.0014943
97 | 0.984 | -0.30527 | 0.0094518 | 0.0023688
98 | 0.9852 | -0.28179 | 0.0017117 | 0.000429
99 | 0.98683 | -0.25049 | 0.0040838 | 0.0010235
100 | 0.98683 | -0.25046 | 0 | 0
101 | 0.97713 | -0.43879 | 0.005321 | 0.0013336
102 | 0.97835 | -0.41481 | 0 | 0
103 | 0.98371 | -0.31097 | 0.0094486 | 0.002368
104 | 0.97419 | -0.49659 | 0 | 0
105 | 0.98725 | -0.24258 | 0.0023228 | 0.00058216
106 | 0.99161 | -0.15882 | 0.0021057 | 0.00052774
107 | 0.97951 | -0.39283 | 0.00046144 | 0.00011565
108 | 0.97959 | -0.39131 | 0.0004291 | 0.00010754
109 | 0.98445 | -0.29654 | 0.00070827 | 0.00017751
110 | 0.98462 | -0.29291 | 0.000809 | 0.00020275
111 | 0.97588 | -0.46329 | 0 | 0
112 | 0.97584 | -0.46402 | 0.0020366 | 0.00051043
113 | 0.97418 | -0.49679 | 0.0026202 | 0.00065669
114 | 0.98579 | -0.2704 | 0 | 0
115 | 0.9862 | -0.26248 | 0.0011333 | 0.00028403
116 | 0.98465 | -0.29268 | 0.0011641 | 0.00029176
117 | 0.98678 | -0.25171 | 0.0058547 | 0.0014673
118 | 0.98591 | -0.26865 | 0.019258 | 0.0048265
119 | 0.97998 | -0.38299 | 0.0050265 | 0.0012598
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022842 | -0.00057248 | 0.0022846 | 0.00057162 | 4.0549e-07 | -8.5933e-07 | 0.0034792 | 0.0034788 | 0.0034792 | 0.97694 | -0.44329 | 0.97713 | -0.43957 | 0.95582
1 | 0.0050953 | 0.0012769 | -0.0050946 | -0.0012768 | 7.9665e-07 | 6.7963e-08 | 0.0077594 | 0.0077595 | 0.0077595 | 0.97713 | -0.43957 | 0.97696 | -0.44285 | 2.1317
2 | 0.010673 | 0.0026736 | -0.010663 | -0.0026684 | 1.0214e-05 | 5.2467e-06 | 0.016253 | 0.016253 | 0.016253 | 0.97713 | -0.43957 | 0.97611 | -0.45968 | 4.4651
3 | -0.018053 | -0.0045221 | 0.018061 | 0.0045268 | 7.8348e-06 | 4.6678e-06 | 0.027491 | 0.027491 | 0.027491 | 0.97713 | -0.43957 | 0.97759 | -0.43046 | 7.5524
4 | 0.0050946 | 0.0012768 | -0.0050944 | -0.0012768 | 1.8253e-07 | 1.5595e-08 | 0.0077595 | 0.0077595 | 0.0077595 | 0.97696 | -0.44285 | 0.97693 | -0.4436 | 2.1317
5 | 0.0032262 | 0.00080464 | -0.0032256 | -0.00080505 | 5.594e-07 | -4.1315e-07 | 0.0049167 | 0.004917 | 0.004917 | 0.97611 | -0.45968 | 0.97592 | -0.46333 | 1.3508
6 | -0.018888 | -0.0047341 | 0.018897 | 0.0047393 | 8.6928e-06 | 5.2116e-06 | 0.02875 | 0.02875 | 0.02875 | 0.97759 | -0.43046 | 0.97808 | -0.4208 | 7.8983
7 | 0.0032256 | 0.00080505 | -0.003225 | -0.00080553 | 6.4571e-07 | -4.7642e-07 | 0.004917 | 0.0049173 | 0.0049173 | 0.97592 | -0.46333 | 0.97571 | -0.46755 | 1.3509
8 | -0.018897 | -0.0047393 | 0.018916 | 0.0047509 | 1.9242e-05 | 1.1535e-05 | 0.02875 | 0.028749 | 0.02875 | 0.97808 | -0.4208 | 0.97917 | -0.39946 | 7.8983
9 | 0.0018858 | 0.00047205 | -0.0018857 | -0.0004724 | 1.0353e-07 | -3.5067e-07 | 0.0028757 | 0.0028759 | 0.0028759 | 0.97571 | -0.46755 | 0.97565 | -0.4687 | 0.79007
10 | 0.0013392 | 0.00033348 | -0.001339 | -0.00033517 | 2.2982e-07 | -1.6884e-06 | 0.0020416 | 0.0020423 | 0.0020423 | 0.97571 | -0.46755 | 0.97553 | -0.47116 | 0.56106
11 | -0.019606 | -0.0049239 | 0.019612 | 0.0049276 | 6.2011e-06 | 3.7344e-06 | 0.029799 | 0.029798 | 0.029799 | 0.97917 | -0.39946 | 0.97951 | -0.39283 | 8.1864
12 | 0.0069836 | 0.0017504 | -0.0069826 | -0.00175 | 1.0566e-06 | 3.6983e-07 | 0.010683 | 0.010683 | 0.010683 | 0.97271 | -0.52576 | 0.97255 | -0.52894 | 2.935
13 | -0.0069836 | -0.0017504 | 0.0069854 | 0.001751 | 1.7892e-06 | 6.2602e-07 | 0.010683 | 0.010683 | 0.010683 | 0.97271 | -0.52576 | 0.97298 | -0.52039 | 2.935
14 | -0.021876 | -0.0054829 | 0.021898 | 0.0054961 | 2.1638e-05 | 1.3207e-05 | 0.033456 | 0.033456 | 0.033456 | 0.97298 | -0.52039 | 0.97403 | -0.49965 | 9.1912
15 | -0.0016055 | -0.00040238 | 0.0016057 | 0.0004015 | 1.7981e-07 | -8.7667e-07 | 0.0024531 | 0.0024527 | 0.0024531 | 0.97388 | -0.50254 | 0.974 | -0.50019 | 0.67393
16 | -0.0040508 | -0.0010143 | 0.0040509 | 0.0010143 | 1.0484e-07 | -2.3769e-08 | 0.0061882 | 0.0061882 | 0.0061882 | 0.974 | -0.50019 | 0.97403 | -0.49965 | 1.7001
17 | -0.0013389 | -0.00033557 | 0.001339 | 0.00033517 | 5.3849e-08 | -3.9534e-07 | 0.0020424 | 0.0020423 | 0.0020424 | 0.97549 | -0.472 | 0.97553 | -0.47116 | 0.5611
18 | 0.0011025 | 0.00027611 | -0.0011024 | -0.0002763 | 1.7041e-08 | -1.8983e-07 | 0.0016814 | 0.0016814 | 0.0016814 | 0.97565 | -0.4687 | 0.97564 | -0.46902 | 0.46193
19 | -0.0019079 | -0.00047817 | 0.001908 | 0.00047803 | 4.3051e-08 | -1.4431e-07 | 0.0028991 | 0.002899 | 0.0028991 | 0.97928 | -0.39731 | 0.97931 | -0.39683 | 0.79645
20 | -0.0034235 | -0.00085786 | 0.0034244 | 0.00085732 | 9.0071e-07 | -5.4078e-07 | 0.0052018 | 0.0052014 | 0.0052018 | 0.97931 | -0.39683 | 0.97959 | -0.39131 | 1.4291
21 | 0.013932 | 0.0034934 | -0.01393 | -0.0034922 | 2.1636e-06 | 1.2255e-06 | 0.021262 | 0.021262 | 0.021262 | 0.97506 | -0.47951 | 0.97489 | -0.48277 | 5.8412
22 | -0.031872 | -0.0079897 | 0.031887 | 0.0079991 | 1.498e-05 | 9.3766e-06 | 0.04864 | 0.04864 | 0.04864 | 0.97506 | -0.47951 | 0.97556 | -0.46965 | 13.3628
23 | 0.01393 | 0.0034922 | -0.013929 | -0.0034918 | 7.3084e-07 | 4.1399e-07 | 0.021262 | 0.021262 | 0.021262 | 0.97489 | -0.48277 | 0.97483 | -0.48387 | 5.8412
24 | 0.036223 | 0.0091113 | -0.036155 | -0.0090684 | 6.8229e-05 | 4.2924e-05 | 0.055263 | 0.055263 | 0.055263 | 0.97556 | -0.46965 | 0.97355 | -0.50916 | 15.1822
25 | -0.06811 | -0.01711 | 0.068167 | 0.017146 | 5.6489e-05 | 3.5979e-05 | 0.1039 | 0.1039 | 0.1039 | 0.97556 | -0.46965 | 0.97644 | -0.45229 | 28.5449
26 | 0.013929 | 0.0034918 | -0.013927 | -0.0034908 | 1.7462e-06 | 9.8915e-07 | 0.021262 | 0.021262 | 0.021262 | 0.97483 | -0.48387 | 0.9747 | -0.4865 | 5.8412
27 | 0.020745 | 0.0052004 | -0.020742 | -0.0051984 | 3.3013e-06 | 2.004e-06 | 0.031708 | 0.031708 | 0.031708 | 0.97355 | -0.50916 | 0.97338 | -0.5125 | 8.7111
28 | 0.01541 | 0.003868 | -0.015394 | -0.003859 | 1.5429e-05 | 8.9537e-06 | 0.023555 | 0.023555 | 0.023555 | 0.97355 | -0.50916 | 0.97249 | -0.53017 | 6.4712
29 | 0.014692 | 0.0036841 | -0.014689 | -0.0036825 | 2.8055e-06 | 1.6089e-06 | 0.02239 | 0.02239 | 0.02239 | 0.97644 | -0.45229 | 0.97624 | -0.45629 | 6.151
30 | -0.082859 | -0.02083 | 0.082935 | 0.020879 | 7.6546e-05 | 4.8829e-05 | 0.12629 | 0.12629 | 0.12629 | 0.97644 | -0.45229 | 0.97742 | -0.43296 | 34.6959
31 | 0.0086163 | 0.0021597 | -0.0086152 | -0.0021592 | 1.101e-06 | 4.9318e-07 | 0.013154 | 0.013154 | 0.013154 | 0.9747 | -0.4865 | 0.97456 | -0.48918 | 3.6138
32 | 0.0086152 | 0.0021592 | -0.0086132 | -0.0021583 | 2.0335e-06 | 9.1105e-07 | 0.013154 | 0.013154 | 0.013154 | 0.97456 | -0.48918 | 0.97431 | -0.49414 | 3.6138
33 | 0.0031253 | 0.00078314 | -0.0031252 | -0.00078324 | 1.2015e-07 | -9.8248e-08 | 0.004773 | 0.0047731 | 0.0047731 | 0.97431 | -0.49414 | 0.97427 | -0.49495 | 1.3113
34 | 0.0054879 | 0.0013752 | -0.0054874 | -0.0013751 | 4.6219e-07 | 7.731e-08 | 0.0083813 | 0.0083814 | 0.0083814 | 0.97431 | -0.49414 | 0.97422 | -0.49591 | 2.3026
35 | 0.023136 | 0.0058087 | -0.023123 | -0.0058006 | 1.3197e-05 | 8.095e-06 | 0.035329 | 0.035329 | 0.035329 | 0.97458 | -0.4888 | 0.97398 | -0.50076 | 9.7058
36 | -0.023136 | -0.0058087 | 0.023159 | 0.0058223 | 2.2267e-05 | 1.3658e-05 | 0.035329 | 0.035329 | 0.035329 | 0.97458 | -0.4888 | 0.97561 | -0.46864 | 9.7057
37 | 0.023123 | 0.0058006 | -0.02311 | -0.0057923 | 1.3527e-05 | 8.2981e-06 | 0.035329 | 0.035329 | 0.035329 | 0.97398 | -0.50076 | 0.97336 | -0.51304 | 9.7058
38 | -0.028352 | -0.0071239 | 0.028392 | 0.0071487 | 3.9937e-05 | 2.4848e-05 | 0.04325 | 0.043249 | 0.04325 | 0.97561 | -0.46864 | 0.97711 | -0.43918 | 11.8817
39 | 0.01918 | 0.0048074 | -0.019179 | -0.0048066 | 1.2827e-06 | 7.7151e-07 | 0.029321 | 0.029321 | 0.029321 | 0.97336 | -0.51304 | 0.97328 | -0.51445 | 8.0553
40 | 0.031574 | 0.0079212 | -0.031553 | -0.0079079 | 2.1222e-05 | 1.3281e-05 | 0.048273 | 0.048273 | 0.048273 | 0.97333 | -0.51342 | 0.97262 | -0.52753 | 13.2618
41 | -0.031574 | -0.0079212 | 0.031582 | 0.0079264 | 8.3149e-06 | 5.2033e-06 | 0.048273 | 0.048273 | 0.048273 | 0.97333 | -0.51342 | 0.97361 | -0.5079 | 13.2618
42 | 0.023753 | 0.0059677 | -0.023722 | -0.005949 | 3.0517e-05 | 1.8764e-05 | 0.036307 | 0.036308 | 0.036308 | 0.97361 | -0.5079 | 0.97225 | -0.53486 | 9.9747
43 | 0.043006 | 0.010785 | -0.042989 | -0.010774 | 1.7234e-05 | 1.0898e-05 | 0.065731 | 0.065731 | 0.065731 | 0.97361 | -0.5079 | 0.97319 | -0.51631 | 18.0578
44 | -0.098341 | -0.024679 | 0.098497 | 0.024778 | 0.00015612 | 9.9001e-05 | 0.15031 | 0.15031 | 0.15031 | 0.97361 | -0.5079 | 0.9753 | -0.47467 | 20.6471
45 | -0.12296 | -0.030914 | 0.12316 | 0.031036 | 0.0001927 | 0.00012169 | 0.18764 | 0.18764 | 0.18764 | 0.9753 | -0.47467 | 0.97697 | -0.4419 | 17.1831
46 | 0.011632 | 0.002918 | -0.011626 | -0.0029149 | 5.7731e-06 | 3.0852e-06 | 0.017747 | 0.017748 | 0.017748 | 0.9753 | -0.47467 | 0.97477 | -0.48508 | 4.8757
47 | 0.012834 | 0.0032181 | -0.012828 | -0.0032151 | 5.3717e-06 | 2.9719e-06 | 0.019581 | 0.019581 | 0.019581 | 0.9753 | -0.47467 | 0.97485 | -0.48345 | 5.3795
48 | -0.12783 | -0.032208 | 0.12786 | 0.032224 | 2.6606e-05 | 1.6442e-05 | 0.19476 | 0.19476 | 0.19476 | 0.97697 | -0.4419 | 0.97719 | -0.43755 | 10.7012
49 | 0.004677 | 0.001172 | -0.0046763 | -0.001172 | 6.9485e-07 | -1.2459e-08 | 0.0071234 | 0.0071236 | 0.0071236 | 0.97697 | -0.4419 | 0.97681 | -0.44502 | 1.957
50 | 0.011626 | 0.0029149 | -0.01162 | -0.0029116 | 6.2359e-06 | 3.3333e-06 | 0.017748 | 0.017748 | 0.017748 | 0.97477 | -0.48508 | 0.9742 | -0.49634 | 4.8758
51 | -0.197 | -0.050057 | 0.1971 | 0.05012 | 9.9458e-05 | 6.2703e-05 | 0.29799 | 0.29799 | 0.29799 | 0.98454 | -0.29465 | 0.98508 | -0.28417 | 16.3729
52 | 0.197 | 0.050057 | -0.19675 | -0.049898 | 0.00025261 | 0.00015926 | 0.29799 | 0.29799 | 0.29799 | 0.98454 | -0.29465 | 0.98316 | -0.32132 | 16.373
53 | 0.028381 | 0.0071222 | -0.028365 | -0.0071125 | 1.5716e-05 | 9.7683e-06 | 0.042874 | 0.042874 | 0.042874 | 0.98508 | -0.28417 | 0.98448 | -0.29579 | 11.7786
54 | -0.22548 | -0.057242 | 0.22588 | 0.057497 | 0.0004019 | 0.00025427 | 0.34086 | 0.34086 | 0.34086 | 0.98508 | -0.28417 | 0.987 | -0.2472 | 18.7286
55 | 0.19079 | 0.048405 | -0.19059 | -0.048282 | 0.00019438 | 0.00012244 | 0.28897 | 0.28897 | 0.28897 | 0.98316 | -0.32132 | 0.98206 | -0.34253 | 15.8774
56 | 0.018912 | 0.0047432 | -0.018903 | -0.0047381 | 8.5368e-06 | 5.1095e-06 | 0.028585 | 0.028586 | 0.028586 | 0.98448 | -0.29579 | 0.984 | -0.30527 | 7.8532
57 | -0.23455 | -0.059668 | 0.23485 | 0.059861 | 0.00030389 | 0.00019242 | 0.35392 | 0.35392 | 0.35392 | 0.987 | -0.2472 | 0.98839 | -0.22035 | 19.4463
58 | 0.027207 | 0.0069046 | -0.027068 | -0.0068187 | 0.00013851 | 8.5908e-05 | 0.041226 | 0.041227 | 0.041227 | 0.98274 | -0.32948 | 0.97727 | -0.4359 | 11.3261
59 | -0.027207 | -0.0069046 | 0.02725 | 0.0069314 | 4.324e-05 | 2.6813e-05 | 0.041226 | 0.041226 | 0.041226 | 0.98274 | -0.32948 | 0.98444 | -0.2965 | 11.3258
60 | 0.026028 | 0.0065594 | -0.025949 | -0.0065104 | 7.9125e-05 | 4.8963e-05 | 0.039643 | 0.039644 | 0.039644 | 0.97727 | -0.4359 | 0.97403 | -0.49965 | 10.8912
61 | 0.0010404 | 0.00025931 | -0.0010403 | -0.00026072 | 1.111e-07 | -1.4084e-06 | 0.0015836 | 0.0015841 | 0.0015841 | 0.97727 | -0.4359 | 0.97716 | -0.43814 | 0.4352
62 | -0.033713 | -0.0085512 | 0.033737 | 0.0085662 | 2.3855e-05 | 1.4956e-05 | 0.050995 | 0.050995 | 0.050995 | 0.98444 | -0.2965 | 0.9852 | -0.28179 | 14.0095
63 | 0.0070667 | 0.0017711 | -0.0070666 | -0.0017711 | 1.3621e-07 | 4.8667e-08 | 0.010816 | 0.010816 | 0.010816 | 0.97225 | -0.53486 | 0.97223 | -0.53526 | 2.9713
64 | 0.016655 | 0.0041779 | -0.016644 | -0.0041715 | 1.0836e-05 | 6.3838e-06 | 0.025492 | 0.025492 | 0.025492 | 0.97225 | -0.53486 | 0.97156 | -0.54851 | 7.0034
65 | 0.12369 | 0.031482 | -0.12367 | -0.031472 | 1.6803e-05 | 1.0343e-05 | 0.18662 | 0.18662 | 0.18662 | 0.98715 | -0.24426 | 0.987 | -0.24708 | 10.2538
66 | -0.16105 | -0.040979 | 0.16123 | 0.041096 | 0.00018585 | 0.00011626 | 0.24298 | 0.24298 | 0.24298 | 0.98715 | -0.24426 | 0.98839 | -0.22035 | 13.3505
67 | 0.037357 | 0.0094971 | -0.037317 | -0.0094735 | 3.9558e-05 | 2.3621e-05 | 0.056359 | 0.05636 | 0.05636 | 0.98715 | -0.24426 | 0.98601 | -0.26627 | 7.7417
68 | 0.096033 | 0.024469 | -0.096017 | -0.02446 | 1.5792e-05 | 9.4661e-06 | 0.14492 | 0.14492 | 0.14492 | 0.987 | -0.24708 | 0.98683 | -0.25049 | 7.9629
69 | 0.027639 | 0.0070026 | -0.027635 | -0.0069998 | 4.4803e-06 | 2.7796e-06 | 0.041696 | 0.041696 | 0.041696 | 0.987 | -0.24708 | 0.98683 | -0.25046 | 11.455
70 | 0.033074 | 0.0083117 | -0.033039 | -0.0082897 | 3.4985e-05 | 2.1909e-05 | 0.0498 | 0.0498 | 0.0498 | 0.98839 | -0.22035 | 0.98725 | -0.24253 | 13.6814
71 | -0.42915 | -0.10927 | 0.42973 | 0.10963 | 0.00057214 | 0.000365 | 0.6467 | 0.6467 | 0.6467 | 0.98839 | -0.22035 | 0.98983 | -0.19274 | 35.5329
72 | 0.035475 | 0.0090118 | -0.035449 | -0.0089952 | 2.6481e-05 | 1.6634e-05 | 0.05358 | 0.05358 | 0.05358 | 0.98601 | -0.26627 | 0.9852 | -0.28179 | 14.7198
73 | 0.0053213 | 0.0013336 | -0.005321 | -0.0013336 | 3.1263e-07 | 4.103e-08 | 0.008103 | 0.0081031 | 0.0081031 | 0.97719 | -0.43755 | 0.97713 | -0.43879 | 2.2261
74 | -0.13318 | -0.033558 | 0.13333 | 0.033648 | 0.00014504 | 8.9879e-05 | 0.20286 | 0.20286 | 0.20286 | 0.97719 | -0.43755 | 0.97835 | -0.41481 | 11.1464
75 | 0.0038313 | 0.00095962 | -0.0038312 | -0.00095963 | 4.4434e-08 | -1.4646e-08 | 0.0058517 | 0.0058518 | 0.0058518 | 0.9742 | -0.49634 | 0.97419 | -0.49659 | 1.6076
76 | 0.027462 | 0.0068921 | -0.027462 | -0.006892 | 5.9855e-08 | 3.7116e-08 | 0.041395 | 0.041395 | 0.041395 | 0.98725 | -0.24253 | 0.98725 | -0.24258 | 11.3722
77 | -0.43369 | -0.11063 | 0.4344 | 0.11108 | 0.00071168 | 0.00045404 | 0.65265 | 0.65265 | 0.65265 | 0.98983 | -0.19274 | 0.99161 | -0.15882 | 35.8601
78 | 0.023969 | 0.006033 | -0.023932 | -0.0060102 | 3.6975e-05 | 2.2723e-05 | 0.036352 | 0.036352 | 0.036352 | 0.98136 | -0.35657 | 0.97971 | -0.3889 | 9.9869
79 | -0.023969 | -0.006033 | 0.024024 | 0.0060668 | 5.5054e-05 | 3.3827e-05 | 0.036352 | 0.036352 | 0.036352 | 0.98136 | -0.35657 | 0.98383 | -0.30863 | 9.9869
80 | 0.020078 | 0.0050455 | -0.020074 | -0.0050433 | 3.7705e-06 | 2.277e-06 | 0.030499 | 0.030499 | 0.030499 | 0.97971 | -0.3889 | 0.97951 | -0.39283 | 8.379
81 | 0.003854 | 0.00096471 | -0.0038535 | -0.00096486 | 4.4249e-07 | -1.5046e-07 | 0.0058531 | 0.0058533 | 0.0058533 | 0.97971 | -0.3889 | 0.97959 | -0.39131 | 1.608
82 | -0.025687 | -0.0064836 | 0.025702 | 0.0064928 | 1.4888e-05 | 9.1945e-06 | 0.038867 | 0.038867 | 0.038867 | 0.98383 | -0.30863 | 0.98445 | -0.29654 | 10.6778
83 | 0.015394 | 0.003859 | -0.015392 | -0.0038575 | 2.6075e-06 | 1.5134e-06 | 0.023555 | 0.023555 | 0.023555 | 0.97249 | -0.53017 | 0.97231 | -0.53373 | 6.4712
84 | 0.088391 | 0.022307 | -0.088236 | -0.022208 | 0.00015463 | 9.8673e-05 | 0.13436 | 0.13436 | 0.13436 | 0.97929 | -0.39636 | 0.97742 | -0.43296 | 36.9131
85 | -0.088391 | -0.022307 | 0.088684 | 0.022494 | 0.00029315 | 0.00018707 | 0.13436 | 0.13436 | 0.13436 | 0.97929 | -0.39636 | 0.98284 | -0.32736 | 36.913
86 | -0.089656 | -0.022737 | 0.089805 | 0.022832 | 0.00014879 | 9.4951e-05 | 0.13583 | 0.13583 | 0.13583 | 0.98284 | -0.32736 | 0.98462 | -0.29291 | 37.3171
87 | 0.0038304 | 0.00095989 | -0.0038302 | -0.00095995 | 1.7881e-07 | -5.883e-08 | 0.005852 | 0.0058521 | 0.0058521 | 0.97397 | -0.50088 | 0.97392 | -0.50186 | 1.6077
88 | -0.0038304 | -0.00095989 | 0.003831 | 0.0009597 | 5.795e-07 | -1.9081e-07 | 0.005852 | 0.0058518 | 0.005852 | 0.97397 | -0.50088 | 0.97413 | -0.49771 | 1.6077
89 | -0.003831 | -0.0009597 | 0.0038312 | 0.00095963 | 2.0384e-07 | -6.7172e-08 | 0.0058518 | 0.0058518 | 0.0058518 | 0.97413 | -0.49771 | 0.97419 | -0.49659 | 1.6076
90 | 0.026351 | 0.0066133 | -0.026326 | -0.0065979 | 2.4901e-05 | 1.5379e-05 | 0.039361 | 0.039361 | 0.039361 | 0.99627 | -0.071123 | 0.99524 | -0.090958 | 10.8134
91 | -0.060715 | -0.015248 | 0.060841 | 0.015327 | 0.00012566 | 7.9891e-05 | 0.090695 | 0.090695 | 0.090695 | 0.99627 | -0.071123 | 0.99852 | -0.027842 | 24.9161
92 | 0.034365 | 0.0086342 | -0.034307 | -0.0085981 | 5.7547e-05 | 3.6073e-05 | 0.051334 | 0.051334 | 0.051334 | 0.99627 | -0.071123 | 0.99445 | -0.10627 | 14.1029
93 | -0.50013 | -0.12871 | 0.50081 | 0.12915 | 0.00067821 | 0.00043299 | 0.74651 | 0.7465 | 0.74651 | 0.99852 | -0.027842 | 1 | 0 | 41.0168
94 | 0.43929 | 0.11338 | -0.43861 | -0.11295 | 0.00067733 | 0.00043212 | 0.65581 | 0.65581 | 0.65581 | 0.99852 | -0.027842 | 0.99684 | -0.059525 | 36.0336
95 | 0.43861 | 0.11295 | -0.43651 | -0.11161 | 0.0021082 | 0.001345 | 0.65581 | 0.65581 | 0.65581 | 0.99684 | -0.059525 | 0.99161 | -0.15882 | 36.0337
96 | 0.014689 | 0.0036825 | -0.014685 | -0.0036804 | 3.664e-06 | 2.1013e-06 | 0.02239 | 0.02239 | 0.02239 | 0.97624 | -0.45629 | 0.97597 | -0.46153 | 6.1511
97 | 0.0020335 | 0.00050962 | -0.0020334 | -0.00050963 | 4.0492e-09 | -1.1437e-08 | 0.0031009 | 0.0031009 | 0.0031009 | 0.9758 | -0.46492 | 0.9758 | -0.46496 | 0.85188
98 | -0.0020335 | -0.00050962 | 0.0020335 | 0.00050953 | 3.15e-08 | -8.8975e-08 | 0.0031009 | 0.0031008 | 0.0031009 | 0.9758 | -0.46492 | 0.97581 | -0.4646 | 0.85188
99 | -0.0073376 | -0.0018389 | 0.0073381 | 0.001839 | 4.564e-07 | 1.7065e-07 | 0.011189 | 0.011189 | 0.011189 | 0.97581 | -0.4646 | 0.97588 | -0.46329 | 3.0739
100 | 0.0026203 | 0.00065653 | -0.0026202 | -0.00065669 | 1.0983e-07 | -1.5738e-07 | 0.0040022 | 0.0040023 | 0.0040023 | 0.97422 | -0.49591 | 0.97418 | -0.49679 | 1.0995
101 | 0.0093756 | 0.0023496 | -0.0093748 | -0.0023493 | 7.8631e-07 | 3.7501e-07 | 0.014294 | 0.014295 | 0.014295 | 0.97597 | -0.46153 | 0.97588 | -0.46329 | 3.9271
102 | 0.0067815 | 0.0016996 | -0.0067809 | -0.0016995 | 5.3908e-07 | 1.737e-07 | 0.010289 | 0.01029 | 0.01029 | 0.98071 | -0.36892 | 0.98062 | -0.37059 | 2.8268
103 | -0.0067815 | -0.0016996 | 0.0067824 | 0.0016999 | 9.0807e-07 | 2.9252e-07 | 0.010289 | 0.010289 | 0.010289 | 0.98071 | -0.36892 | 0.98085 | -0.36611 | 2.8268
104 | 0.17764 | 0.044956 | -0.17749 | -0.044866 | 0.00014377 | 9.035e-05 | 0.26965 | 0.26965 | 0.26965 | 0.98085 | -0.36611 | 0.97998 | -0.38299 | 14.8158
105 | -0.18442 | -0.046656 | 0.18463 | 0.046788 | 0.00020893 | 0.00013147 | 0.27994 | 0.27993 | 0.27994 | 0.98085 | -0.36611 | 0.98206 | -0.34253 | 15.3811
106 | -0.0053092 | -0.0013306 | 0.0053096 | 0.0013307 | 3.6987e-07 | 4.7428e-08 | 0.0080822 | 0.0080821 | 0.0080822 | 0.97748 | -0.43188 | 0.97756 | -0.43042 | 2.2204
107 | -0.038851 | -0.0097753 | 0.03888 | 0.0097936 | 2.8993e-05 | 1.8278e-05 | 0.059152 | 0.059152 | 0.059152 | 0.97756 | -0.43042 | 0.97835 | -0.41481 | 16.2506
108 | 0.033542 | 0.0084447 | -0.033528 | -0.0084359 | 1.4036e-05 | 8.8035e-06 | 0.05107 | 0.05107 | 0.05107 | 0.97756 | -0.43042 | 0.97711 | -0.43918 | 14.0303
109 | 0.0094512 | 0.0023693 | -0.0094486 | -0.002368 | 2.5685e-06 | 1.2181e-06 | 0.014292 | 0.014293 | 0.014293 | 0.984 | -0.30527 | 0.98371 | -0.31097 | 3.9265
110 | 0.091933 | 0.023436 | -0.09188 | -0.023403 | 5.3173e-05 | 3.3185e-05 | 0.13877 | 0.13877 | 0.13877 | 0.98683 | -0.25049 | 0.9862 | -0.26248 | 12.7075
111 | 0.027635 | 0.0069998 | -0.027579 | -0.0069651 | 5.5919e-05 | 3.4695e-05 | 0.041696 | 0.041697 | 0.041697 | 0.98683 | -0.25046 | 0.98465 | -0.29268 | 11.4551
112 | -0.17221 | -0.043441 | 0.17247 | 0.043606 | 0.00026283 | 0.000165 | 0.26202 | 0.26201 | 0.26202 | 0.97835 | -0.41481 | 0.97998 | -0.38299 | 14.3965
113 | 0.025139 | 0.0063099 | -0.025128 | -0.0063031 | 1.0939e-05 | 6.7411e-06 | 0.037894 | 0.037894 | 0.037894 | 0.98725 | -0.24258 | 0.98678 | -0.25171 | 10.4104
114 | -0.02641 | -0.0066703 | 0.026415 | 0.0066733 | 4.8851e-06 | 3.0226e-06 | 0.039937 | 0.039937 | 0.039937 | 0.98445 | -0.29654 | 0.98465 | -0.29268 | 10.9718
115 | -0.090614 | -0.023035 | 0.090712 | 0.023098 | 9.8328e-05 | 6.2752e-05 | 0.13706 | 0.13706 | 0.13706 | 0.98462 | -0.29291 | 0.98579 | -0.2704 | 37.6529
116 | 0.0020367 | 0.00051023 | -0.0020366 | -0.00051043 | 7.0472e-08 | -1.9835e-07 | 0.0031055 | 0.0031056 | 0.0031056 | 0.97588 | -0.46329 | 0.97584 | -0.46402 | 0.85317
117 | -0.090712 | -0.023098 | 0.090747 | 0.023119 | 3.4676e-05 | 2.1627e-05 | 0.13706 | 0.13706 | 0.13706 | 0.98579 | -0.2704 | 0.9862 | -0.26248 | 12.551
118 | 0.019273 | 0.0048358 | -0.019258 | -0.0048265 | 1.5554e-05 | 9.3281e-06 | 0.029065 | 0.029065 | 0.029065 | 0.98678 | -0.25171 | 0.98591 | -0.26865 | 7.985

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53046 | 0.13616

## res_load
| p_mw | q_mvar
0 | 0.0022842 | 0.00057248
1 | 0.0074364 | 0.0018637
2 | 0.0008273 | 0.00020734
3 | 0.0050944 | 0.0012768
4 | 0.00069031 | 0.00017301
5 | 0.0069826 | 0.00175
6 | 0.014891 | 0.0037319
7 | 0.0016055 | 0.00040238
8 | 0.0024451 | 0.00061281
9 | 0.0013389 | 0.00033557
10 | 0.0007832 | 0.00019629
11 | 0.0019079 | 0.00047817
12 | 0.0015156 | 0.00037983
13 | 0.0011024 | 0.0002763
14 | 0.01794 | 0.0044963
15 | 0.0053111 | 0.0013311
16 | 0.0051933 | 0.0013016
17 | 0.0039299 | 0.00098491
18 | 0.031553 | 0.0079079
19 | 0.012828 | 0.0032151
20 | 0.0059598 | 0.0014937
21 | 0.0094534 | 0.0023693
22 | 0.0086644 | 0.0021715
23 | 0.0064631 | 0.0016198
24 | 0.042989 | 0.010774
25 | 0.0018419 | 0.00046163
26 | 0.0070666 | 0.0017711
27 | 0.016644 | 0.0041715
28 | 0.0046763 | 0.001172
29 | 0.0077884 | 0.001952
30 | 0.0055768 | 0.0013977
31 | 0.0039619 | 0.00099294
32 | 0.0016631 | 0.00041681
33 | 0.0010403 | 0.00026072
34 | 0.020742 | 0.0051984
35 | 0.015392 | 0.0038575
36 | 0.0053012 | 0.0013286
37 | 0.00097151 | 0.00024348
38 | 0.0038302 | 0.00095995
39 | 0.026326 | 0.0065979
40 | 0.034307 | 0.0085981
41 | 0.027998 | 0.0070169
42 | 0.0020334 | 0.00050963
43 | 0.0053041 | 0.0013293
44 | 0.0031252 | 0.00078324
45 | 0.0028671 | 0.00071856
46 | 0.0053097 | 0.0013307
47 | 0.0067809 | 0.0016995
48 | 0.0053092 | 0.0013306
49 | 0.0051357 | 0.0012871
50 | 0.019179 | 0.0048066
51 | 0.0059622 | 0.0014943
52 | 0.0094518 | 0.0023688
53 | 0.0017117 | 0.000429
54 | 0.0040838 | 0.0010235
55 | 0.005321 | 0.0013336
56 | 0.0094486 | 0.002368
57 | 0.0023228 | 0.00058216
58 | 0.0021057 | 0.00052774
59 | 0.00046144 | 0.00011565
60 | 0.0004291 | 0.00010754
61 | 0.00070827 | 0.00017751
62 | 0.000809 | 0.00020275
63 | 0.0020366 | 0.00051043
64 | 0.0026202 | 0.00065669
65 | 0.0011333 | 0.00028403
66 | 0.0011641 | 0.00029176
67 | 0.0058547 | 0.0014673
68 | 0.019258 | 0.0048265
69 | 0.0050265 | 0.0012598

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1