## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_141-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_141-2_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_141-2_0_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_141-2_0_3_node_18 | 0.4 | n |  | TRUE
4 | bus_LV_141-2_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_141-2_0_3_node_64 | 0.4 | n |  | TRUE
6 | bus_LV_141-2_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_141-2_0_3_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_141-2_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_141-2_0_3_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_141-2_0_3_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_141-2_0_3_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_141-2_0_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_141-2_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_141-2_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_141-2_0_3_node_66 | 0.4 | n |  | TRUE
16 | bus_LV_141-2_0_3_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_141-2_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_141-2_0_3_node_68 | 0.4 | n |  | TRUE
19 | bus_LV_141-2_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_141-2_0_3_node_83 | 0.4 | n |  | TRUE
21 | bus_LV_141-2_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_141-2_0_3_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_141-2_0_3_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_141-2_0_3_node_54 | 0.4 | n |  | TRUE
25 | bus_LV_141-2_0_3_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_141-2_0_3_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_141-2_0_3_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_141-2_0_3_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_141-2_0_3_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_141-2_0_3_node_67 | 0.4 | n |  | TRUE
31 | bus_LV_141-2_0_3_node_59 | 0.4 | n |  | TRUE
32 | bus_LV_141-2_0_3_node_60 | 0.4 | n |  | TRUE
33 | bus_LV_141-2_0_3_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_141-2_0_3_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_141-2_0_3_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_141-2_0_3_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_141-2_0_3_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_141-2_0_3_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_141-2_0_3_node_72 | 0.4 | n |  | TRUE
40 | bus_LV_141-2_0_3_node_81 | 0.4 | n |  | TRUE
41 | bus_LV_141-2_0_3_node_80 | 0.4 | n |  | TRUE
42 | bus_MV_491_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_141-2_0_3_load_0 | 0 | 0.051951 | 0.01302 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_141-2_0_3_load_64 | 5 | 0.0016105 | 0.00040362 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_141-2_0_3_load_53 | 7 | 0.0095689 | 0.0023982 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_141-2_0_3_load_33 | 9 | 0.0064655 | 0.0016204 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_141-2_0_3_load_34 | 10 | 0.018547 | 0.0046482 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_141-2_0_3_load_32 | 11 | 0.024931 | 0.0062483 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_141-2_0_3_load_30 | 12 | 0.038003 | 0.0095245 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_141-2_0_3_load_66 | 15 | 0.010182 | 0.0025519 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_141-2_0_3_load_65 | 16 | 0.00055424 | 0.00013891 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_141-2_0_3_load_68 | 18 | 0.0012733 | 0.00031911 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_141-2_0_3_load_83 | 20 | 0.011793 | 0.0029557 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_141-2_0_3_load_70 | 22 | 0.021768 | 0.0054556 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_141-2_0_3_load_35 | 23 | 0.004847 | 0.0012148 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_141-2_0_3_load_58 | 25 | 0.0065447 | 0.0016403 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_141-2_0_3_load_55 | 26 | 0.0062849 | 0.0015751 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_141-2_0_3_load_52 | 27 | 0.0057421 | 0.0014391 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_141-2_0_3_load_31 | 29 | 0.019817 | 0.0049667 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_141-2_0_3_load_67 | 30 | 0.0022485 | 0.00056354 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_141-2_0_3_load_59 | 31 | 0.027111 | 0.0067947 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_141-2_0_3_load_69 | 33 | 0.0042538 | 0.0010661 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_141-2_0_3_load_56 | 34 | 0.0093285 | 0.0023379 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_141-2_0_3_load_57 | 35 | 0.0094165 | 0.00236 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_141-2_0_3_load_63 | 36 | 0.011771 | 0.0029501 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_141-2_0_3_load_62 | 37 | 0.0078837 | 0.0019758 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_141-2_0_3_load_81 | 40 | 0.0070773 | 0.0017737 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_141-2_0_3_load_80 | 41 | 0.0029602 | 0.00074189 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_141-2_0_3_line_0 |  | 0 | 1 | 0.025334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_141-2_0_3_line_1 |  | 1 | 2 | 0.0084875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_141-2_0_3_line_2 |  | 1 | 3 | 0.0489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_141-2_0_3_line_3 |  | 2 | 12 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_141-2_0_3_line_4 |  | 3 | 23 | 0.0054594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_141-2_0_3_line_5 |  | 4 | 5 | 0.0057662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_141-2_0_3_line_6 |  | 4 | 6 | 0.029684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_141-2_0_3_line_7 |  | 4 | 7 | 0.017243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_141-2_0_3_line_8 |  | 5 | 28 | 0.024629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_141-2_0_3_line_9 |  | 6 | 17 | 0.045975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_141-2_0_3_line_10 |  | 6 | 18 | 0.024018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_141-2_0_3_line_11 |  | 7 | 27 | 0.036355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_141-2_0_3_line_12 |  | 8 | 9 | 0.031907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_141-2_0_3_line_13 |  | 8 | 10 | 0.011232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_141-2_0_3_line_14 |  | 8 | 11 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_141-2_0_3_line_15 |  | 9 | 25 | 0.014484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_141-2_0_3_line_16 |  | 11 | 29 | 0.02057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_141-2_0_3_line_17 |  | 12 | 29 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_141-2_0_3_line_18 |  | 13 | 14 | 0.052662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_141-2_0_3_line_19 |  | 13 | 15 | 0.0035976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_141-2_0_3_line_20 |  | 14 | 16 | 0.054401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_141-2_0_3_line_21 |  | 16 | 17 | 0.0084248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_141-2_0_3_line_22 |  | 18 | 30 | 0.046436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_141-2_0_3_line_23 |  | 19 | 20 | 0.089396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_141-2_0_3_line_24 |  | 19 | 21 | 0.070686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_141-2_0_3_line_25 |  | 21 | 22 | 0.084138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_141-2_0_3_line_26 |  | 22 | 33 | 0.016977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_141-2_0_3_line_27 |  | 24 | 25 | 0.020153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_141-2_0_3_line_28 |  | 24 | 26 | 0.0046083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_141-2_0_3_line_29 |  | 26 | 34 | 0.035084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_141-2_0_3_line_30 |  | 28 | 39 | 0.098655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_141-2_0_3_line_31 |  | 28 | 38 | 0.034705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_141-2_0_3_line_32 |  | 31 | 32 | 0.027193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_141-2_0_3_line_33 |  | 32 | 38 | 0.018636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_141-2_0_3_line_34 |  | 32 | 37 | 0.01073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_141-2_0_3_line_35 |  | 33 | 38 | 0.032321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_141-2_0_3_line_36 |  | 34 | 35 | 0.021658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_141-2_0_3_line_37 |  | 35 | 36 | 0.041421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_141-2_0_3_line_38 |  | 36 | 37 | 0.024604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_141-2_0_3_line_39 |  | 39 | 40 | 0.014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_141-2_0_3_line_40 |  | 39 | 41 | 0.010638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_141-2_0_3_trafo_59 | 0.63 MVA 20/0.4 kV | 42 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2685239.902 | 1238897.9936 | 2685245.1317 | 1238889.9184 | 2685243.4022 | 1238886.0353 | 2685249.2746 | 1238876.1913
1 | 2685239.902 | 1238897.9936 | 2685243.1906 | 1238900.2424 | 2685246.9292 | 1238902.7534
2 | 2685209.9523 | 1238934.4678 | 2685220.8788 | 1238919.4805 | 2685238.4191 | 1238896.9605 | 2685239.902 | 1238897.9936
3 | 2685246.9292 | 1238902.7534 | 2685253.7308 | 1238891.6209 | 2685257.1342 | 1238891.136
4 | 2685209.9523 | 1238934.4678 | 2685206.6334 | 1238938.8027
5 | 2685373.8836 | 1239004.8616 | 2685372.599 | 1239004.7653 | 2685368.1332 | 1239004.4342
6 | 2685373.8836 | 1239004.8616 | 2685376.3165 | 1239011.8905 | 2685381.7987 | 1239019.9195 | 2685381.5794 | 1239025.6983 | 2685380.191 | 1239032.2942
7 | 2685373.8836 | 1239004.8616 | 2685372.5416 | 1238998.2375 | 2685372.4346 | 1238990.4304 | 2685372.7613 | 1238987.7739
8 | 2685347.9647 | 1238990.3564 | 2685358.7306 | 1238998.6504 | 2685368.1332 | 1239004.4342
9 | 2685380.191 | 1239032.2942 | 2685381.2378 | 1239033.1432 | 2685384.5576 | 1239035.8373 | 2685385.0137 | 1239036.2108 | 2685385.6713 | 1239036.7651 | 2685388.7358 | 1239039.3332 | 2685389.9316 | 1239040.34 | 2685393.3678 | 1239035.4748 | 2685406.1899 | 1239042.7978 | 2685413.7259 | 1239032.6767
10 | 2685380.191 | 1239032.2942 | 2685368.1842 | 1239048.7445 | 2685365.781 | 1239051.4948
11 | 2685384.8577 | 1238953.6352 | 2685373.3683 | 1238982.8383 | 2685372.7613 | 1238987.7739
12 | 2685282.0913 | 1238849.9648 | 2685310.4074 | 1238864.6709
13 | 2685282.0913 | 1238849.9648 | 2685283.2378 | 1238848.091 | 2685287.8674 | 1238840.3314
14 | 2685282.0913 | 1238849.9648 | 2685280.4477 | 1238852.7432 | 2685275.3912 | 1238861.0702
15 | 2685310.4074 | 1238864.6709 | 2685323.261 | 1238871.3465
16 | 2685264.7147 | 1238878.6524 | 2685275.3912 | 1238861.0702
17 | 2685257.1342 | 1238891.136 | 2685264.7147 | 1238878.6524
18 | 2685416.6028 | 1238946.8452 | 2685423.2548 | 1238957.1594 | 2685430.4681 | 1238962.6338 | 2685422.7953 | 1238973.8426 | 2685423.8057 | 1238974.591 | 2685427.1516 | 1238977.052 | 2685428.0798 | 1238977.7325 | 2685428.7463 | 1238978.198 | 2685432.2586 | 1238980.6614 | 2685437.2386 | 1238984.1578
19 | 2685416.6028 | 1238946.8452 | 2685414.5268 | 1238943.9071
20 | 2685437.2386 | 1238984.1578 | 2685405.7874 | 1239026.6137 | 2685407.0305 | 1239027.5631
21 | 2685413.7259 | 1239032.6767 | 2685407.0305 | 1239027.5631
22 | 2685334.4374 | 1239085.7499 | 2685348.6485 | 1239070.6239 | 2685357.2169 | 1239061.2959 | 2685365.781 | 1239051.4948
23 | 2685247.6009 | 1238962.3726 | 2685247.274 | 1238970.9074 | 2685201.3022 | 1239031.1576 | 2685199.0878 | 1239031.5483 | 2685196.2608 | 1239030.874
24 | 2685196.2608 | 1239030.874 | 2685192.8632 | 1239032.0149 | 2685194.7296 | 1239036.3671 | 2685195.4582 | 1239039.3574 | 2685201.4039 | 1239043.568 | 2685204.746 | 1239048.9309 | 2685213.0397 | 1239053.9757 | 2685215.2832 | 1239058.9337 | 2685223.4784 | 1239063.4657 | 2685231.005 | 1239072.4135 | 2685233.2037 | 1239073.6459 | 2685235.9191 | 1239074.1852 | 2685240.0584 | 1239073.5442
25 | 2685240.0584 | 1239073.5442 | 2685259.5078 | 1239045.0029 | 2685290.5653 | 1239006.33
26 | 2685301.1957 | 1238993.093 | 2685290.5653 | 1239006.33
27 | 2685341.1459 | 1238880.6351 | 2685323.261 | 1238871.3465
28 | 2685341.1459 | 1238880.6351 | 2685338.8816 | 1238884.6488
29 | 2685338.8816 | 1238884.6488 | 2685321.6426 | 1238915.2055
30 | 2685347.9647 | 1238990.3564 | 2685343.0549 | 1238993.0211 | 2685342.7026 | 1238997.5304 | 2685341.2295 | 1239001.601 | 2685331.8803 | 1239012.619 | 2685331.5282 | 1239015.5383 | 2685333.4552 | 1239020.4028 | 2685332.9928 | 1239023.6318 | 2685320.751 | 1239038.5444 | 2685316.4514 | 1239042.441 | 2685311.1936 | 1239044.0555 | 2685306.6352 | 1239045.9581 | 2685303.3405 | 1239048.8795 | 2685299.9259 | 1239052.7777 | 2685296.5122 | 1239055.564 | 2685292.377 | 1239057.4949 | 2685288.1479 | 1239058.5905
31 | 2685347.9647 | 1238990.3564 | 2685321.4339 | 1238967.8924
32 | 2685307.4894 | 1238955.4831 | 2685285.0674 | 1238940.0975
33 | 2685307.4894 | 1238955.4831 | 2685321.4339 | 1238967.8924
34 | 2685307.4894 | 1238955.4831 | 2685317.6644 | 1238958.8904
35 | 2685321.4339 | 1238967.8924 | 2685301.1957 | 1238993.093
36 | 2685321.6426 | 1238915.2055 | 2685320.4437 | 1238917.3307 | 2685319.9099 | 1238920.2585 | 2685320.3577 | 1238923.3115 | 2685321.8058 | 1238925.1892 | 2685330.7117 | 1238931.2712
37 | 2685340.5694 | 1238961.7629 | 2685340.5694 | 1238961.7629 | 2685348.099 | 1238948.4059 | 2685348.3854 | 1238944.7964 | 2685346.7207 | 1238942.2039 | 2685330.7117 | 1238931.2712
38 | 2685340.5694 | 1238961.7629 | 2685337.7827 | 1238964.069 | 2685333.5446 | 1238964.2082 | 2685317.6644 | 1238958.8904
39 | 2685288.1479 | 1239058.5905 | 2685282.8402 | 1239054.2112 | 2685281.8252 | 1239051.6725 | 2685282.0775 | 1239048.8519 | 2685283.6781 | 1239046.9624
40 | 2685288.1479 | 1239058.5905 | 2685295.7336 | 1239066.0493

## bus_geodata
| x | y | coords
0 | 2685249.2746 | 1238876.1913
1 | 2685239.902 | 1238897.9936
2 | 2685246.9292 | 1238902.7534
3 | 2685209.9522 | 1238934.4678
4 | 2685373.8836 | 1239004.8616
5 | 2685368.1332 | 1239004.4342
6 | 2685380.191 | 1239032.2942
7 | 2685372.7613 | 1238987.7739
8 | 2685282.0913 | 1238849.9648
9 | 2685310.4074 | 1238864.6709
10 | 2685287.8674 | 1238840.3314
11 | 2685275.3912 | 1238861.0702
12 | 2685257.1342 | 1238891.136
13 | 2685416.6028 | 1238946.8452
14 | 2685437.2386 | 1238984.1578
15 | 2685414.5268 | 1238943.9071
16 | 2685407.0305 | 1239027.5631
17 | 2685413.7259 | 1239032.6767
18 | 2685365.781 | 1239051.4948
19 | 2685196.2608 | 1239030.874
20 | 2685247.6009 | 1238962.3726
21 | 2685240.0584 | 1239073.5442
22 | 2685290.5653 | 1239006.33
23 | 2685206.6334 | 1238938.8027
24 | 2685341.1459 | 1238880.6351
25 | 2685323.261 | 1238871.3465
26 | 2685338.8816 | 1238884.6488
27 | 2685384.8577 | 1238953.6352
28 | 2685347.9647 | 1238990.3564
29 | 2685264.7147 | 1238878.6524
30 | 2685334.4374 | 1239085.7499
31 | 2685285.0674 | 1238940.0975
32 | 2685307.4894 | 1238955.4831
33 | 2685301.1957 | 1238993.093
34 | 2685321.6426 | 1238915.2055
35 | 2685330.7117 | 1238931.2712
36 | 2685340.5694 | 1238961.7629
37 | 2685317.6644 | 1238958.8904
38 | 2685321.4339 | 1238967.8924
39 | 2685288.1479 | 1239058.5905
40 | 2685283.6781 | 1239046.9624
41 | 2685295.7336 | 1239066.0493
42 | 2685307.4894 | 1238955.4831

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97753 | -0.43321 | 0.051951 | 0.01302
1 | 0.97875 | -0.40923 | 0 | 0
2 | 0.9792 | -0.40047 | 0 | 0
3 | 0.97853 | -0.41355 | 0 | 0
4 | 0.99403 | -0.11425 | 0 | 0
5 | 0.99419 | -0.11125 | 0.0016105 | 0.00040362
6 | 0.99365 | -0.12173 | 0 | 0
7 | 0.99379 | -0.11891 | 0.0095689 | 0.0023982
8 | 0.98521 | -0.28324 | 0 | 0
9 | 0.98754 | -0.23805 | 0.0064655 | 0.0016204
10 | 0.98502 | -0.28698 | 0.018547 | 0.0046482
11 | 0.98354 | -0.31579 | 0.024931 | 0.0062483
12 | 0.98007 | -0.38346 | 0.038003 | 0.0095245
13 | 0.99212 | -0.15133 | 0 | 0
14 | 0.99261 | -0.14184 | 0 | 0
15 | 0.99208 | -0.15198 | 0.010182 | 0.0025519
16 | 0.99311 | -0.13205 | 0.00055424 | 0.00013891
17 | 0.9932 | -0.13045 | 0 | 0
18 | 0.99357 | -0.12322 | 0.0012733 | 0.00031911
19 | 0.99289 | -0.13632 | 0 | 0
20 | 0.99193 | -0.15498 | 0.011793 | 0.0029557
21 | 0.99365 | -0.12159 | 0 | 0
22 | 0.99456 | -0.10407 | 0.021768 | 0.0054556
23 | 0.97851 | -0.41403 | 0.004847 | 0.0012148
24 | 0.98934 | -0.20337 | 0 | 0
25 | 0.98828 | -0.22386 | 0.0065447 | 0.0016403
26 | 0.98959 | -0.19869 | 0.0062849 | 0.0015751
27 | 0.9936 | -0.1226 | 0.0057421 | 0.0014391
28 | 0.99489 | -0.097708 | 0 | 0
29 | 0.98135 | -0.35837 | 0.019817 | 0.0049667
30 | 0.99347 | -0.12506 | 0.0022485 | 0.00056354
31 | 1 | 0 | -0.30024 | -0.076279
32 | 0.99754 | -0.046701 | 0 | 0
33 | 0.99508 | -0.094038 | 0.0042538 | 0.0010661
34 | 0.9915 | -0.16184 | 0.0093285 | 0.0023379
35 | 0.99275 | -0.13797 | 0.0094165 | 0.00236
36 | 0.99525 | -0.090191 | 0.011771 | 0.0029501
37 | 0.99683 | -0.060232 | 0.0078837 | 0.0019758
38 | 0.9962 | -0.072543 | 0 | 0
39 | 0.99399 | -0.11517 | 0 | 0
40 | 0.99389 | -0.11703 | 0.0070773 | 0.0017737
41 | 0.99396 | -0.11572 | 0.0029602 | 0.00074189
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.051951 | -0.01302 | 0.05201 | 0.013058 | 5.9412e-05 | 3.7706e-05 | 0.07908 | 0.07908 | 0.07908 | 0.97753 | -0.43321 | 0.97875 | -0.40923 | 21.7254
1 | -0.056858 | -0.014273 | 0.056882 | 0.014288 | 2.3788e-05 | 1.5117e-05 | 0.086451 | 0.086451 | 0.086451 | 0.97875 | -0.40923 | 0.9792 | -0.40047 | 23.7502
2 | 0.0048481 | 0.0012148 | -0.0048471 | -0.0012148 | 9.962e-07 | 2.3146e-08 | 0.0073705 | 0.0073707 | 0.0073707 | 0.97875 | -0.40923 | 0.97853 | -0.41355 | 2.0249
3 | -0.056882 | -0.014288 | 0.056928 | 0.014317 | 4.6198e-05 | 2.9359e-05 | 0.086451 | 0.086451 | 0.086451 | 0.9792 | -0.40047 | 0.98007 | -0.38346 | 23.7502
4 | 0.0048471 | 0.0012148 | -0.004847 | -0.0012148 | 1.1123e-07 | 2.6037e-09 | 0.0073707 | 0.0073708 | 0.0073708 | 0.97853 | -0.41355 | 0.97851 | -0.41403 | 2.0249
5 | -0.029594 | -0.0074226 | 0.029599 | 0.0074253 | 4.2442e-06 | 2.6415e-06 | 0.044303 | 0.044303 | 0.044303 | 0.99403 | -0.11425 | 0.99419 | -0.11125 | 12.1712
6 | 0.014279 | 0.0035832 | -0.014274 | -0.0035803 | 5.0865e-06 | 2.8707e-06 | 0.021376 | 0.021376 | 0.021376 | 0.99403 | -0.11425 | 0.99365 | -0.12173 | 5.8726
7 | 0.015315 | 0.0038394 | -0.015312 | -0.0038375 | 3.3989e-06 | 1.9518e-06 | 0.022927 | 0.022927 | 0.022927 | 0.99403 | -0.11425 | 0.99379 | -0.11891 | 6.2986
8 | -0.031209 | -0.0078289 | 0.031229 | 0.0078415 | 2.0154e-05 | 1.2579e-05 | 0.046714 | 0.046713 | 0.046714 | 0.99419 | -0.11125 | 0.99489 | -0.097708 | 12.8334
9 | 0.010752 | 0.0026983 | -0.010747 | -0.002696 | 4.4701e-06 | 2.2656e-06 | 0.016102 | 0.016102 | 0.016102 | 0.99365 | -0.12173 | 0.9932 | -0.13045 | 4.4237
10 | 0.0035222 | 0.00088202 | -0.003522 | -0.00088217 | 2.5057e-07 | -1.5072e-07 | 0.0052744 | 0.0052745 | 0.0052745 | 0.99365 | -0.12173 | 0.99357 | -0.12322 | 1.449
11 | 0.0057431 | 0.0014393 | -0.0057421 | -0.0014391 | 1.0081e-06 | 1.7425e-07 | 0.0085992 | 0.0085994 | 0.0085994 | 0.99379 | -0.11891 | 0.9936 | -0.1226 | 2.3625
12 | -0.1588 | -0.040069 | 0.15914 | 0.040288 | 0.00034441 | 0.00021961 | 0.23993 | 0.23993 | 0.23993 | 0.98521 | -0.28324 | 0.98754 | -0.23805 | 32.958
13 | 0.01855 | 0.0046502 | -0.018547 | -0.0046482 | 3.3065e-06 | 1.9731e-06 | 0.028017 | 0.028017 | 0.028017 | 0.98521 | -0.28324 | 0.98502 | -0.28698 | 7.6971
14 | 0.14025 | 0.035418 | -0.14003 | -0.035279 | 0.00021843 | 0.00013963 | 0.21192 | 0.21192 | 0.21192 | 0.98521 | -0.28324 | 0.98354 | -0.31579 | 58.219
15 | -0.16561 | -0.041909 | 0.16572 | 0.04198 | 0.00011286 | 7.1675e-05 | 0.24968 | 0.24968 | 0.24968 | 0.98754 | -0.23805 | 0.98828 | -0.22386 | 22.8641
16 | 0.1151 | 0.02903 | -0.11486 | -0.028881 | 0.00023407 | 0.00014955 | 0.1742 | 0.1742 | 0.1742 | 0.98354 | -0.31579 | 0.98135 | -0.35837 | 47.8568
17 | -0.094932 | -0.023842 | 0.095045 | 0.023914 | 0.0001138 | 7.2651e-05 | 0.14415 | 0.14415 | 0.14415 | 0.98007 | -0.38346 | 0.98135 | -0.35837 | 39.6017
18 | -0.010183 | -0.0025521 | 0.010187 | 0.0025543 | 4.6061e-06 | 2.2675e-06 | 0.015272 | 0.015272 | 0.015272 | 0.99212 | -0.15133 | 0.99261 | -0.14184 | 4.1957
19 | 0.010183 | 0.0025521 | -0.010182 | -0.0025519 | 3.1467e-07 | 1.5493e-07 | 0.015272 | 0.015272 | 0.015272 | 0.99212 | -0.15133 | 0.99208 | -0.15198 | 4.1957
20 | -0.010187 | -0.0025543 | 0.010192 | 0.0025567 | 4.758e-06 | 2.3416e-06 | 0.015272 | 0.015272 | 0.015272 | 0.99261 | -0.14184 | 0.99311 | -0.13205 | 4.1956
21 | -0.010746 | -0.0026956 | 0.010747 | 0.002696 | 8.1915e-07 | 4.1524e-07 | 0.016102 | 0.016102 | 0.016102 | 0.99311 | -0.13205 | 0.9932 | -0.13045 | 4.4237
22 | 0.0022487 | 0.00056306 | -0.0022485 | -0.00056354 | 1.975e-07 | -4.7494e-07 | 0.0033676 | 0.0033678 | 0.0033678 | 0.99357 | -0.12322 | 0.99347 | -0.12506 | 0.92523
23 | 0.011804 | 0.0029613 | -0.011793 | -0.0029557 | 1.0492e-05 | 5.56e-06 | 0.017691 | 0.017692 | 0.017692 | 0.99289 | -0.13632 | 0.99193 | -0.15498 | 4.8603
24 | -0.011804 | -0.0029613 | 0.011812 | 0.0029657 | 8.296e-06 | 4.3945e-06 | 0.017691 | 0.017691 | 0.017691 | 0.99289 | -0.13632 | 0.99365 | -0.12159 | 4.8602
25 | -0.011812 | -0.0029657 | 0.011822 | 0.0029709 | 9.8744e-06 | 5.2287e-06 | 0.017691 | 0.01769 | 0.017691 | 0.99365 | -0.12159 | 0.99456 | -0.10407 | 4.8601
26 | -0.03359 | -0.0084264 | 0.033606 | 0.0084365 | 1.6081e-05 | 1.0071e-05 | 0.050259 | 0.050259 | 0.050259 | 0.99456 | -0.10407 | 0.99508 | -0.094038 | 13.8073
27 | 0.17243 | 0.043728 | -0.17226 | -0.043621 | 0.00016968 | 0.00010782 | 0.25953 | 0.25953 | 0.25953 | 0.98934 | -0.20337 | 0.98828 | -0.22386 | 23.7665
28 | -0.17243 | -0.043728 | 0.17247 | 0.043753 | 3.88e-05 | 2.4654e-05 | 0.25953 | 0.25953 | 0.25953 | 0.98934 | -0.20337 | 0.98959 | -0.19869 | 23.7665
29 | -0.17876 | -0.045328 | 0.17907 | 0.04553 | 0.00031729 | 0.00020171 | 0.26898 | 0.26898 | 0.26898 | 0.98959 | -0.19869 | 0.9915 | -0.16184 | 24.6319
30 | 0.010047 | 0.0025198 | -0.010038 | -0.0025158 | 8.3541e-06 | 4.0667e-06 | 0.015027 | 0.015027 | 0.015027 | 0.99489 | -0.097708 | 0.99399 | -0.11517 | 4.1284
31 | -0.041276 | -0.010361 | 0.041325 | 0.010393 | 4.9609e-05 | 3.1298e-05 | 0.06174 | 0.06174 | 0.06174 | 0.99489 | -0.097708 | 0.9962 | -0.072543 | 16.9616
32 | 0.29859 | 0.076279 | -0.29792 | -0.07585 | 0.00067256 | 0.00042937 | 0.44482 | 0.44482 | 0.44482 | 1 | 0 | 0.99754 | -0.046701 | 40.7343
33 | 0.079322 | 0.019982 | -0.079224 | -0.01992 | 9.7902e-05 | 6.2414e-05 | 0.11836 | 0.11836 | 0.11836 | 0.99754 | -0.046701 | 0.9962 | -0.072543 | 32.5164
34 | 0.2186 | 0.055868 | -0.21845 | -0.055776 | 0.00014295 | 9.1067e-05 | 0.32646 | 0.32646 | 0.32646 | 0.99754 | -0.046701 | 0.99683 | -0.060232 | 29.8956
35 | -0.03786 | -0.0095026 | 0.037899 | 0.0095271 | 3.8855e-05 | 2.4447e-05 | 0.05662 | 0.056619 | 0.05662 | 0.99508 | -0.094038 | 0.9962 | -0.072543 | 15.5548
36 | -0.1884 | -0.047868 | 0.18862 | 0.048006 | 0.00021678 | 0.0001379 | 0.28298 | 0.28298 | 0.28298 | 0.9915 | -0.16184 | 0.99275 | -0.13797 | 25.9139
37 | -0.19804 | -0.050366 | 0.19849 | 0.050657 | 0.000457 | 0.00029087 | 0.29709 | 0.29709 | 0.29709 | 0.99275 | -0.13797 | 0.99525 | -0.090191 | 27.2064
38 | -0.21026 | -0.053607 | 0.21057 | 0.053801 | 0.00030457 | 0.00019397 | 0.31469 | 0.31469 | 0.31469 | 0.99525 | -0.090191 | 0.99683 | -0.060232 | 28.8179
39 | 0.0070779 | 0.0017739 | -0.0070773 | -0.0017737 | 6.2766e-07 | 2.0848e-07 | 0.010596 | 0.010596 | 0.010596 | 0.99399 | -0.11517 | 0.99389 | -0.11703 | 2.911
40 | 0.0029603 | 0.00074181 | -0.0029602 | -0.00074189 | 7.8347e-08 | -8.7749e-08 | 0.0044315 | 0.0044316 | 0.0044316 | 0.99399 | -0.11517 | 0.99396 | -0.11572 | 1.2175

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32735 | 0.083074

## res_load
| p_mw | q_mvar
0 | 0.051951 | 0.01302
1 | 0.0016105 | 0.00040362
2 | 0.0095689 | 0.0023982
3 | 0.0064655 | 0.0016204
4 | 0.018547 | 0.0046482
5 | 0.024931 | 0.0062483
6 | 0.038003 | 0.0095245
7 | 0.010182 | 0.0025519
8 | 0.00055424 | 0.00013891
9 | 0.0012733 | 0.00031911
10 | 0.011793 | 0.0029557
11 | 0.021768 | 0.0054556
12 | 0.004847 | 0.0012148
13 | 0.0065447 | 0.0016403
14 | 0.0062849 | 0.0015751
15 | 0.0057421 | 0.0014391
16 | 0.019817 | 0.0049667
17 | 0.0022485 | 0.00056354
18 | 0.027111 | 0.0067947
19 | 0.0042538 | 0.0010661
20 | 0.0093285 | 0.0023379
21 | 0.0094165 | 0.00236
22 | 0.011771 | 0.0029501
23 | 0.0078837 | 0.0019758
24 | 0.0070773 | 0.0017737
25 | 0.0029602 | 0.00074189

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1