## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_154-39_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_154-39_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_154-39_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_154-39_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_154-39_0_2_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_154-39_0_2_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_154-39_0_2_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_154-39_0_2_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_154-39_0_2_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_154-39_0_2_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_154-39_0_2_node_56 | 0.4 | n |  | TRUE
11 | bus_LV_154-39_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_154-39_0_2_node_53 | 0.4 | n |  | TRUE
13 | bus_LV_154-39_0_2_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_154-39_0_2_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_154-39_0_2_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_154-39_0_2_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_154-39_0_2_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_154-39_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_154-39_0_2_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_154-39_0_2_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_154-39_0_2_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_154-39_0_2_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_154-39_0_2_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_154-39_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_154-39_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_154-39_0_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_154-39_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_154-39_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_154-39_0_2_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_154-39_0_2_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_154-39_0_2_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_154-39_0_2_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_154-39_0_2_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_154-39_0_2_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_154-39_0_2_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_154-39_0_2_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_154-39_0_2_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_154-39_0_2_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_154-39_0_2_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_154-39_0_2_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_154-39_0_2_node_55 | 0.4 | n |  | TRUE
42 | bus_LV_154-39_0_2_node_61 | 0.4 | n |  | TRUE
43 | bus_LV_154-39_0_2_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_154-39_0_2_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_154-39_0_2_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_154-39_0_2_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_154-39_0_2_node_51 | 0.4 | n |  | TRUE
48 | bus_LV_154-39_0_2_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_154-39_0_2_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_154-39_0_2_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_154-39_0_2_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_154-39_0_2_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_154-39_0_2_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_154-39_0_2_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_154-39_0_2_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_154-39_0_2_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_154-39_0_2_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_154-39_0_2_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_154-39_0_2_node_47 | 0.4 | n |  | TRUE
60 | bus_MV_364_0_node_124 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_154-39_0_2_load_0 | 0 | 0.0011601 | 0.00029075 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_154-39_0_2_load_3 | 2 | 0.0047453 | 0.0011893 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_154-39_0_2_load_18 | 4 | 0.011503 | 0.002883 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_154-39_0_2_load_60 | 9 | 0.010201 | 0.0025566 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_154-39_0_2_load_53 | 12 | 0.0028991 | 0.00072659 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_154-39_0_2_load_44 | 15 | 0.0011534 | 0.00028907 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_154-39_0_2_load_9 | 17 | 0.0031284 | 0.00078405 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_154-39_0_2_load_12 | 18 | 0.00024631 | 6.1731e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_154-39_0_2_load_10 | 20 | 0.0011617 | 0.00029114 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_154-39_0_2_load_43 | 21 | 0.0043828 | 0.0010984 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_154-39_0_2_load_13 | 23 | 0.004421 | 0.001108 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_154-39_0_2_load_15 | 25 | 0.0079353 | 0.0019888 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_154-39_0_2_load_26 | 26 | 0.0019964 | 0.00050034 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_154-39_0_2_load_24 | 28 | 0.0016225 | 0.00040663 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_154-39_0_2_load_63 | 29 | 0.0097013 | 0.0024314 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_154-39_0_2_load_22 | 30 | 0.010527 | 0.0026382 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_154-39_0_2_load_49 | 31 | 0.0014344 | 0.00035949 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_154-39_0_2_load_50 | 32 | 0.0015524 | 0.00038906 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_154-39_0_2_load_62 | 33 | 0.0076005 | 0.0019049 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_154-39_0_2_load_58 | 35 | 0.0099844 | 0.0025023 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_154-39_0_2_load_23 | 36 | 0.0065186 | 0.0016337 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_154-39_0_2_load_27 | 38 | 0.0017646 | 0.00044226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_154-39_0_2_load_28 | 39 | 0.0017624 | 0.00044171 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_154-39_0_2_load_55 | 41 | 0.0039645 | 0.00099361 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_154-39_0_2_load_61 | 42 | 0.0088132 | 0.0022088 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_154-39_0_2_load_35 | 43 | 0.0069998 | 0.0017543 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_154-39_0_2_load_29 | 44 | 0.0069409 | 0.0017396 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_154-39_0_2_load_51 | 47 | 0.0018972 | 0.00047548 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_154-39_0_2_load_41 | 49 | 0.0012664 | 0.00031739 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_154-39_0_2_load_52 | 50 | 0.0047796 | 0.0011979 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_154-39_0_2_load_36 | 52 | 0.0012344 | 0.00030937 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_154-39_0_2_load_42 | 53 | 0.0053597 | 0.0013433 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_154-39_0_2_load_37 | 54 | 0.0013267 | 0.00033251 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_154-39_0_2_load_39 | 55 | 0.0011643 | 0.00029179 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_154-39_0_2_load_48 | 56 | 0.0012561 | 0.00031481 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_154-39_0_2_load_45 | 57 | 0.0039196 | 0.00098234 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_154-39_0_2_load_46 | 58 | 0.0021851 | 0.00054765 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_154-39_0_2_load_47 | 59 | 0.0019918 | 0.00049919 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_154-39_0_2_line_0 |  | 0 | 1 | 0.016332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_154-39_0_2_line_1 |  | 1 | 2 | 0.017057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_154-39_0_2_line_2 |  | 1 | 3 | 0.042926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_154-39_0_2_line_3 |  | 3 | 11 | 0.012093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_154-39_0_2_line_4 |  | 3 | 12 | 0.025018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_154-39_0_2_line_5 |  | 4 | 5 | 0.0069561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_154-39_0_2_line_6 |  | 4 | 6 | 0.0051892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_154-39_0_2_line_7 |  | 5 | 7 | 0.032783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_154-39_0_2_line_8 |  | 5 | 8 | 0.0373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_154-39_0_2_line_9 |  | 6 | 30 | 0.009986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_154-39_0_2_line_10 |  | 7 | 9 | 0.007255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_154-39_0_2_line_11 |  | 7 | 10 | 0.08047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_154-39_0_2_line_12 |  | 8 | 29 | 0.014953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_154-39_0_2_line_13 |  | 8 | 24 | 0.041355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_154-39_0_2_line_14 |  | 10 | 34 | 0.043546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_154-39_0_2_line_15 |  | 10 | 35 | 0.01774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_154-39_0_2_line_16 |  | 11 | 15 | 0.016542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_154-39_0_2_line_17 |  | 11 | 13 | 0.02842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_154-39_0_2_line_18 |  | 12 | 16 | 0.018951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_154-39_0_2_line_19 |  | 13 | 14 | 0.027044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_154-39_0_2_line_20 |  | 14 | 17 | 0.019155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_154-39_0_2_line_21 |  | 16 | 47 | 0.054112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_154-39_0_2_line_22 |  | 16 | 22 | 0.048198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_154-39_0_2_line_23 |  | 16 | 45 | 0.046512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_154-39_0_2_line_24 |  | 17 | 20 | 0.0014248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_154-39_0_2_line_25 |  | 18 | 19 | 0.0275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_154-39_0_2_line_26 |  | 19 | 20 | 0.033463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_154-39_0_2_line_27 |  | 21 | 22 | 0.01506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_154-39_0_2_line_28 |  | 23 | 24 | 0.023884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_154-39_0_2_line_29 |  | 24 | 25 | 0.0095482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_154-39_0_2_line_30 |  | 25 | 27 | 0.084601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_154-39_0_2_line_31 |  | 26 | 27 | 0.07126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_154-39_0_2_line_32 |  | 26 | 28 | 0.0415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_154-39_0_2_line_33 |  | 28 | 36 | 0.0099101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_154-39_0_2_line_34 |  | 31 | 32 | 0.016568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_154-39_0_2_line_35 |  | 31 | 33 | 0.13921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_154-39_0_2_line_36 |  | 32 | 38 | 0.00010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_154-39_0_2_line_37 |  | 34 | 42 | 0.012125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_154-39_0_2_line_38 |  | 36 | 37 | 0.021238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_154-39_0_2_line_39 |  | 37 | 38 | 0.019009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_154-39_0_2_line_40 |  | 37 | 39 | 0.014007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_154-39_0_2_line_41 |  | 39 | 40 | 0.0080423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_154-39_0_2_line_42 |  | 40 | 43 | 0.011631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_154-39_0_2_line_43 |  | 40 | 44 | 0.023933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_154-39_0_2_line_44 |  | 41 | 42 | 0.040278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_154-39_0_2_line_45 |  | 44 | 45 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_154-39_0_2_line_46 |  | 45 | 46 | 0.19075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_154-39_0_2_line_47 |  | 46 | 48 | 0.073835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_154-39_0_2_line_48 |  | 46 | 49 | 0.027364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_154-39_0_2_line_49 |  | 47 | 50 | 0.0093945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_154-39_0_2_line_50 |  | 48 | 51 | 0.035506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_154-39_0_2_line_51 |  | 48 | 52 | 0.011246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_154-39_0_2_line_52 |  | 49 | 53 | 0.051645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_154-39_0_2_line_53 |  | 51 | 56 | 0.017294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_154-39_0_2_line_54 |  | 51 | 57 | 0.01401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_154-39_0_2_line_55 |  | 52 | 54 | 0.0089812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_154-39_0_2_line_56 |  | 54 | 55 | 0.0087897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_154-39_0_2_line_57 |  | 57 | 58 | 0.024004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_154-39_0_2_line_58 |  | 58 | 59 | 0.005521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_154-39_0_2_trafo_17 | 0.63 MVA 20/0.4 kV | 60 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2688255.4512 | 1242701.7302 | 2688267.408 | 1242710.5589 | 2688268.6077 | 1242711.407
1 | 2688255.4512 | 1242701.7302 | 2688255.9242 | 1242684.6802
2 | 2688223.4157 | 1242687.8103 | 2688228.9352 | 1242680.6427 | 2688255.4512 | 1242701.7302
3 | 2688223.4157 | 1242687.8103 | 2688214.5882 | 1242679.5175
4 | 2688223.4157 | 1242687.8103 | 2688208.593 | 1242707.9642
5 | 2688441.0131 | 1242859.9867 | 2688434.0579 | 1242860.0995
6 | 2688428.8694 | 1242860.1837 | 2688434.0579 | 1242860.0995
7 | 2688471.5842 | 1242849.846 | 2688464.323 | 1242849.6042 | 2688441.0131 | 1242859.9867
8 | 2688441.0131 | 1242859.9867 | 2688429.4651 | 1242879.0398 | 2688417.9285 | 1242888.7194
9 | 2688428.8694 | 1242860.1837 | 2688419.92 | 1242864.6647
10 | 2688471.5842 | 1242849.846 | 2688470.8491 | 1242857.0626
11 | 2688471.5842 | 1242849.846 | 2688481.0988 | 1242845.9961 | 2688491.2938 | 1242852.7753 | 2688497.5189 | 1242864.6991 | 2688492.7034 | 1242893.5819 | 2688487.3651 | 1242907.8462
12 | 2688417.9285 | 1242888.7194 | 2688414.3805 | 1242894.4708 | 2688413.586 | 1242902.6317
13 | 2688417.9285 | 1242888.7194 | 2688402.6246 | 1242891.4824 | 2688393.2636 | 1242897.7142 | 2688391.8342 | 1242901.3067 | 2688385.2005 | 1242909.6918
14 | 2688487.3651 | 1242907.8462 | 2688484.8784 | 1242923.5318 | 2688473.2393 | 1242931.4641 | 2688461.0601 | 1242937.5982
15 | 2688487.3651 | 1242907.8462 | 2688472.9971 | 1242918.3063
16 | 2688214.5882 | 1242679.5175 | 2688200.1962 | 1242671.3628
17 | 2688203.901 | 1242661.0562 | 2688219.8635 | 1242672.5018 | 2688214.5882 | 1242679.5175
18 | 2688197.6138 | 1242723.4086 | 2688203.8715 | 1242714.3838 | 2688208.593 | 1242707.9642
19 | 2688203.901 | 1242661.0562 | 2688189.8661 | 1242652.1633 | 2688197.5237 | 1242645.083
20 | 2688197.5237 | 1242645.083 | 2688213.1813 | 1242634.048
21 | 2688197.6138 | 1242723.4086 | 2688231.619 | 1242765.5005
22 | 2688162.1833 | 1242725.2947 | 2688187.4845 | 1242739.6256 | 2688197.6138 | 1242723.4086
23 | 2688175.0113 | 1242764.0026 | 2688180.9092 | 1242751.7145 | 2688187.4845 | 1242739.6256 | 2688197.6138 | 1242723.4086
24 | 2688213.1813 | 1242634.048 | 2688214.3459 | 1242633.2272
25 | 2688241.6981 | 1242613.95 | 2688253.3099 | 1242628.7002 | 2688249.4355 | 1242630.4772 | 2688245.8031 | 1242633.0738
26 | 2688241.6981 | 1242613.95 | 2688214.3459 | 1242633.2272
27 | 2688162.1833 | 1242725.2947 | 2688169.2379 | 1242711.9897
28 | 2688385.2005 | 1242909.6918 | 2688387.6949 | 1242926.9528 | 2688386.8792 | 1242933.3447
29 | 2688385.2005 | 1242909.6918 | 2688375.6862 | 1242910.4952
30 | 2688297.4291 | 1242894.7966 | 2688309.0408 | 1242896.3038 | 2688318.3193 | 1242898.1433 | 2688323.268 | 1242898.3281 | 2688329.445 | 1242898.2756 | 2688332.6767 | 1242899.0354 | 2688341.9034 | 1242904.8548 | 2688343.2789 | 1242906.3986 | 2688346.5556 | 1242911.7513 | 2688348.5031 | 1242912.959 | 2688350.3218 | 1242913.1751 | 2688364.6223 | 1242912.8099 | 2688375.6862 | 1242910.4952
31 | 2688235.3411 | 1242859.8253 | 2688297.4291 | 1242894.7966
32 | 2688235.3411 | 1242859.8253 | 2688235.0353 | 1242851.926 | 2688231.0312 | 1242846.6737 | 2688221.4925 | 1242847.5882 | 2688213.4879 | 1242846.5017 | 2688210.8199 | 1242837.5611
33 | 2688210.8617 | 1242828.7798 | 2688208.5659 | 1242833.8415 | 2688210.7948 | 1242837.4773 | 2688210.8199 | 1242837.5611
34 | 2688239.5545 | 1242825.468 | 2688238.9008 | 1242817.2024 | 2688232.8838 | 1242811.5195
35 | 2688239.5545 | 1242825.468 | 2688377.9715 | 1242840.3331
36 | 2688232.8838 | 1242811.5195 | 2688232.8082 | 1242811.4481
37 | 2688461.0601 | 1242937.5982 | 2688454.1606 | 1242947.5805
38 | 2688216.1411 | 1242808.402 | 2688214.1465 | 1242821.5376 | 2688210.8617 | 1242828.7798
39 | 2688216.1411 | 1242808.402 | 2688223.862 | 1242805.6926 | 2688228.8292 | 1242807.6901 | 2688232.8082 | 1242811.4481
40 | 2688216.1411 | 1242808.402 | 2688207.0865 | 1242797.7148
41 | 2688202.404 | 1242791.1963 | 2688205.0641 | 1242795.3278 | 2688207.0865 | 1242797.7148
42 | 2688202.404 | 1242791.1963 | 2688192.0066 | 1242796.4679
43 | 2688202.404 | 1242791.1963 | 2688200.797 | 1242784.8789 | 2688187.9695 | 1242773.1018
44 | 2688454.1606 | 1242947.5805 | 2688429.7196 | 1242979.5954
45 | 2688175.0113 | 1242764.0026 | 2688187.9695 | 1242773.1018
46 | 2688120.3679 | 1242945.747 | 2688125.3889 | 1242913.5979 | 2688127.5326 | 1242901.0983 | 2688139.2404 | 1242850.8685 | 2688158.7272 | 1242802.1777 | 2688166.2998 | 1242784.0213 | 2688175.0113 | 1242764.0026
47 | 2688120.3679 | 1242945.747 | 2688119.7491 | 1242950.7637 | 2688116.8455 | 1242980.8316 | 2688120.4131 | 1242980.8624 | 2688120.2477 | 1243005.7338 | 2688121.5652 | 1243008.1329 | 2688128.9599 | 1243008.0204
48 | 2688120.3679 | 1242945.747 | 2688133.3138 | 1242948.5301 | 2688145.201 | 1242956.1541
49 | 2688239.0748 | 1242759.785 | 2688231.619 | 1242765.5005
50 | 2688152.3383 | 1243031.6071 | 2688135.3944 | 1243007.927 | 2688128.9599 | 1243008.0204
51 | 2688128.9599 | 1243008.0204 | 2688138.1107 | 1243001.4838
52 | 2688181.482 | 1242979.6018 | 2688172.0988 | 1242985.8337 | 2688165.7591 | 1242975.9878 | 2688149.0388 | 1242958.6155 | 2688145.201 | 1242956.1541
53 | 2688152.3383 | 1243031.6071 | 2688166.3685 | 1243021.4414
54 | 2688152.3383 | 1243031.6071 | 2688160.4891 | 1243043.0024
55 | 2688138.1107 | 1243001.4838 | 2688145.4189 | 1242996.2634
56 | 2688145.4189 | 1242996.2634 | 2688152.5713 | 1242991.1543
57 | 2688160.4891 | 1243043.0024 | 2688166.3421 | 1243051.1851 | 2688177.7096 | 1243043.1099
58 | 2688182.2105 | 1243039.9126 | 2688177.7096 | 1243043.1099

## bus_geodata
| x | y | coords
0 | 2688268.6077 | 1242711.407
1 | 2688255.4512 | 1242701.7302
2 | 2688255.9242 | 1242684.6802
3 | 2688223.4157 | 1242687.8103
4 | 2688434.0579 | 1242860.0995
5 | 2688441.0131 | 1242859.9867
6 | 2688428.8694 | 1242860.1837
7 | 2688471.5842 | 1242849.846
8 | 2688417.9285 | 1242888.7195
9 | 2688470.8491 | 1242857.0626
10 | 2688487.3651 | 1242907.8462
11 | 2688214.5882 | 1242679.5175
12 | 2688208.593 | 1242707.9642
13 | 2688203.901 | 1242661.0562
14 | 2688197.5237 | 1242645.083
15 | 2688200.1962 | 1242671.3628
16 | 2688197.6138 | 1242723.4086
17 | 2688213.1813 | 1242634.048
18 | 2688245.8031 | 1242633.0738
19 | 2688241.6981 | 1242613.95
20 | 2688214.3459 | 1242633.2272
21 | 2688169.2379 | 1242711.9897
22 | 2688162.1833 | 1242725.2947
23 | 2688386.8792 | 1242933.3447
24 | 2688385.2005 | 1242909.6918
25 | 2688375.6862 | 1242910.4952
26 | 2688235.3411 | 1242859.8253
27 | 2688297.4291 | 1242894.7966
28 | 2688210.8199 | 1242837.5611
29 | 2688413.586 | 1242902.6317
30 | 2688419.92 | 1242864.6647
31 | 2688239.5545 | 1242825.468
32 | 2688232.8838 | 1242811.5195
33 | 2688377.9715 | 1242840.3331
34 | 2688461.0601 | 1242937.5982
35 | 2688472.9971 | 1242918.3063
36 | 2688210.8617 | 1242828.7798
37 | 2688216.1411 | 1242808.402
38 | 2688232.8082 | 1242811.4481
39 | 2688207.0865 | 1242797.7148
40 | 2688202.404 | 1242791.1963
41 | 2688429.7196 | 1242979.5954
42 | 2688454.1606 | 1242947.5805
43 | 2688192.0066 | 1242796.4679
44 | 2688187.9695 | 1242773.1018
45 | 2688175.0113 | 1242764.0026
46 | 2688120.3679 | 1242945.747
47 | 2688231.619 | 1242765.5005
48 | 2688128.9599 | 1243008.0204
49 | 2688145.201 | 1242956.1541
50 | 2688239.0747 | 1242759.785
51 | 2688152.3383 | 1243031.6071
52 | 2688138.1107 | 1243001.4838
53 | 2688181.482 | 1242979.6018
54 | 2688145.4189 | 1242996.2634
55 | 2688152.5713 | 1242991.1543
56 | 2688166.3685 | 1243021.4414
57 | 2688160.4891 | 1243043.0024
58 | 2688177.7096 | 1243043.1099
59 | 2688182.2105 | 1243039.9126
60 | 2688385.2005 | 1242909.6918

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98435 | -0.30111 | 0.0011601 | 0.00029075
1 | 0.98437 | -0.30077 | 0 | 0
2 | 0.98429 | -0.30223 | 0.0047453 | 0.0011893
3 | 0.9846 | -0.29621 | 0 | 0
4 | 0.98893 | -0.21256 | 0.011503 | 0.002883
5 | 0.98907 | -0.20983 | 0 | 0
6 | 0.98888 | -0.21353 | 0 | 0
7 | 0.98808 | -0.22911 | 0 | 0
8 | 0.99096 | -0.17335 | 0 | 0
9 | 0.98801 | -0.23043 | 0.010201 | 0.0025566
10 | 0.9864 | -0.26187 | 0 | 0
11 | 0.98454 | -0.29745 | 0 | 0
12 | 0.98487 | -0.29099 | 0.0028991 | 0.00072659
13 | 0.98442 | -0.29977 | 0 | 0
14 | 0.98431 | -0.30198 | 0 | 0
15 | 0.98452 | -0.29779 | 0.0011534 | 0.00028907
16 | 0.98512 | -0.28606 | 0 | 0
17 | 0.98423 | -0.30354 | 0.0031284 | 0.00078405
18 | 0.98421 | -0.30385 | 0.00024631 | 6.1731e-05
19 | 0.98422 | -0.30373 | 0 | 0
20 | 0.98422 | -0.30358 | 0.0011617 | 0.00029114
21 | 0.98487 | -0.29104 | 0.0043828 | 0.0010984
22 | 0.98493 | -0.28985 | 0 | 0
23 | 0.99332 | -0.12784 | 0.004421 | 0.001108
24 | 0.99341 | -0.12597 | 0 | 0
25 | 0.99402 | -0.11432 | 0.0079353 | 0.0019888
26 | 0.99453 | -0.10427 | 0.0019964 | 0.00050034
27 | 1 | 0 | -0.16404 | -0.041409
28 | 0.99141 | -0.16405 | 0.0016225 | 0.00040663
29 | 0.99082 | -0.17592 | 0.0097013 | 0.0024314
30 | 0.98879 | -0.21541 | 0.010527 | 0.0026382
31 | 0.9889 | -0.21268 | 0.0014344 | 0.00035949
32 | 0.98904 | -0.21001 | 0.0015524 | 0.00038906
33 | 0.98793 | -0.23156 | 0.0076005 | 0.0019049
34 | 0.98588 | -0.27184 | 0 | 0
35 | 0.98623 | -0.26504 | 0.0099844 | 0.0025023
36 | 0.99069 | -0.1781 | 0.0065186 | 0.0016337
37 | 0.98925 | -0.20581 | 0 | 0
38 | 0.98904 | -0.20999 | 0.0017646 | 0.00044226
39 | 0.98847 | -0.22103 | 0.0017624 | 0.00044171
40 | 0.98803 | -0.22954 | 0 | 0
41 | 0.9856 | -0.27749 | 0.0039645 | 0.00099361
42 | 0.98574 | -0.27462 | 0.0088132 | 0.0022088
43 | 0.98795 | -0.23099 | 0.0069998 | 0.0017543
44 | 0.98688 | -0.25188 | 0.0069409 | 0.0017396
45 | 0.98621 | -0.26472 | 0 | 0
46 | 0.98274 | -0.33235 | 0 | 0
47 | 0.98479 | -0.29255 | 0.0018972 | 0.00047548
48 | 0.98185 | -0.3498 | 0 | 0
49 | 0.98258 | -0.33563 | 0.0012664 | 0.00031739
50 | 0.98475 | -0.29336 | 0.0047796 | 0.0011979
51 | 0.98155 | -0.35581 | 0 | 0
52 | 0.98181 | -0.35056 | 0.0012344 | 0.00030937
53 | 0.98232 | -0.34063 | 0.0053597 | 0.0013433
54 | 0.98179 | -0.35096 | 0.0013267 | 0.00033251
55 | 0.98178 | -0.35115 | 0.0011643 | 0.00029179
56 | 0.98153 | -0.3562 | 0.0012561 | 0.00031481
57 | 0.98144 | -0.35786 | 0.0039196 | 0.00098234
58 | 0.98135 | -0.35968 | 0.0021851 | 0.00054765
59 | 0.98134 | -0.35988 | 0.0019918 | 0.00049919
60 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0011601 | -0.00029075 | 0.0011601 | 0.00029055 | 1.8835e-08 | -1.9556e-07 | 0.0017537 | 0.0017536 | 0.0017537 | 0.98435 | -0.30111 | 0.98437 | -0.30077 | 0.48178
1 | 0.0047456 | 0.0011893 | -0.0047453 | -0.0011893 | 3.2916e-07 | -6.1466e-09 | 0.0071737 | 0.0071738 | 0.0071738 | 0.98437 | -0.30077 | 0.98429 | -0.30223 | 1.9708
2 | -0.0059057 | -0.0014798 | 0.005907 | 0.0014801 | 1.2829e-06 | 2.7522e-07 | 0.0089273 | 0.0089271 | 0.0089273 | 0.98437 | -0.30077 | 0.9846 | -0.29621 | 2.4526
3 | 0.0056914 | 0.0014249 | -0.0056911 | -0.0014249 | 3.3547e-07 | 6.0907e-08 | 0.0086009 | 0.0086009 | 0.0086009 | 0.9846 | -0.29621 | 0.98454 | -0.29745 | 2.3629
4 | -0.011598 | -0.0029051 | 0.011601 | 0.0029066 | 2.8823e-06 | 1.5264e-06 | 0.017528 | 0.017528 | 0.017528 | 0.9846 | -0.29621 | 0.98487 | -0.29099 | 4.8154
5 | -0.022032 | -0.005522 | 0.022034 | 0.0055237 | 2.8666e-06 | 1.7454e-06 | 0.03315 | 0.03315 | 0.03315 | 0.98893 | -0.21256 | 0.98907 | -0.20983 | 9.1072
6 | 0.010528 | 0.002639 | -0.010528 | -0.0026387 | 4.8835e-07 | 2.4596e-07 | 0.015842 | 0.015842 | 0.015842 | 0.98893 | -0.21256 | 0.98888 | -0.21353 | 4.3521
7 | 0.033039 | 0.0083073 | -0.033009 | -0.0082882 | 3.0386e-05 | 1.9027e-05 | 0.049716 | 0.049716 | 0.049716 | 0.98907 | -0.20983 | 0.98808 | -0.22911 | 13.6583
8 | -0.055074 | -0.013831 | 0.05517 | 0.013892 | 9.6049e-05 | 6.0992e-05 | 0.082866 | 0.082866 | 0.082866 | 0.98907 | -0.20983 | 0.99096 | -0.17335 | 22.7654
9 | 0.010528 | 0.0026387 | -0.010527 | -0.0026382 | 9.3976e-07 | 4.7335e-07 | 0.015842 | 0.015842 | 0.015842 | 0.98888 | -0.21353 | 0.98879 | -0.21541 | 4.3521
10 | 0.010201 | 0.0025569 | -0.010201 | -0.0025566 | 6.4214e-07 | 3.1805e-07 | 0.015363 | 0.015363 | 0.015363 | 0.98808 | -0.22911 | 0.98801 | -0.23043 | 4.2207
11 | 0.022808 | 0.0057313 | -0.022772 | -0.0057096 | 3.5612e-05 | 2.1763e-05 | 0.034353 | 0.034353 | 0.034353 | 0.98808 | -0.22911 | 0.9864 | -0.26187 | 9.4377
12 | 0.0097025 | 0.0024319 | -0.0097013 | -0.0024314 | 1.1902e-06 | 5.6914e-07 | 0.014569 | 0.014569 | 0.014569 | 0.99096 | -0.17335 | 0.99082 | -0.17592 | 4.0026
13 | -0.064872 | -0.016324 | 0.06502 | 0.016418 | 0.00014723 | 9.3692e-05 | 0.097435 | 0.097435 | 0.097435 | 0.99096 | -0.17335 | 0.99341 | -0.12597 | 26.7679
14 | 0.012786 | 0.0032065 | -0.01278 | -0.0032032 | 6.0758e-06 | 3.333e-06 | 0.019289 | 0.019289 | 0.019289 | 0.9864 | -0.26187 | 0.98588 | -0.27184 | 5.2992
15 | 0.0099859 | 0.0025031 | -0.0099844 | -0.0025023 | 1.5097e-06 | 7.3978e-07 | 0.015064 | 0.015064 | 0.015064 | 0.9864 | -0.26187 | 0.98623 | -0.26504 | 4.1386
16 | 0.0011534 | 0.00028887 | -0.0011534 | -0.00028907 | 1.885e-08 | -1.9829e-07 | 0.0017432 | 0.0017432 | 0.0017432 | 0.98454 | -0.29745 | 0.98452 | -0.29779 | 0.47891
17 | 0.0045377 | 0.001136 | -0.0045372 | -0.0011361 | 5.0121e-07 | -4.0585e-08 | 0.0068577 | 0.0068579 | 0.0068579 | 0.98454 | -0.29745 | 0.98442 | -0.29977 | 1.884
18 | -0.0145 | -0.0036332 | 0.014504 | 0.0036351 | 3.4109e-06 | 1.9418e-06 | 0.021908 | 0.021908 | 0.021908 | 0.98487 | -0.29099 | 0.98512 | -0.28606 | 6.0187
19 | 0.0045372 | 0.0011361 | -0.0045367 | -0.0011361 | 4.7697e-07 | -3.8529e-08 | 0.0068579 | 0.006858 | 0.006858 | 0.98442 | -0.29977 | 0.98431 | -0.30198 | 1.8841
20 | 0.0045367 | 0.0011361 | -0.0045364 | -0.0011361 | 3.3785e-07 | -2.7236e-08 | 0.006858 | 0.0068581 | 0.0068581 | 0.98431 | -0.30198 | 0.98423 | -0.30354 | 1.8841
21 | 0.0066791 | 0.001674 | -0.006677 | -0.0016734 | 2.0654e-06 | 6.3315e-07 | 0.010089 | 0.010089 | 0.010089 | 0.98512 | -0.28606 | 0.98479 | -0.29255 | 2.7717
22 | 0.0043838 | 0.0010983 | -0.004383 | -0.0010984 | 7.925e-07 | -1.0633e-07 | 0.0066216 | 0.0066218 | 0.0066218 | 0.98512 | -0.28606 | 0.98493 | -0.28985 | 1.8192
23 | -0.025567 | -0.0064074 | 0.025593 | 0.0064234 | 2.6012e-05 | 1.6055e-05 | 0.038618 | 0.038618 | 0.038618 | 0.98512 | -0.28606 | 0.98621 | -0.26472 | 10.6094
24 | 0.001408 | 0.00035208 | -0.001408 | -0.0003521 | 2.4205e-09 | -1.6558e-08 | 0.0021284 | 0.0021284 | 0.0021284 | 0.98423 | -0.30354 | 0.98422 | -0.30358 | 0.58473
25 | -0.00024631 | -6.1731e-05 | 0.00024631 | 6.1383e-05 | 1.4296e-09 | -3.4856e-07 | 0.00037239 | 0.00037227 | 0.00037239 | 0.98421 | -0.30385 | 0.98422 | -0.30373 | 0.10231
26 | -0.00024631 | -6.1383e-05 | 0.00024631 | 6.0958e-05 | 1.7383e-09 | -4.2415e-07 | 0.00037227 | 0.00037212 | 0.00037227 | 0.98422 | -0.30373 | 0.98422 | -0.30358 | 0.10227
27 | -0.0043828 | -0.0010984 | 0.004383 | 0.0010984 | 2.4763e-07 | -3.3165e-08 | 0.0066219 | 0.0066218 | 0.0066219 | 0.98487 | -0.29104 | 0.98493 | -0.28985 | 1.8192
28 | -0.004421 | -0.001108 | 0.0044214 | 0.001108 | 3.9284e-07 | -5.7778e-08 | 0.0066228 | 0.0066227 | 0.0066228 | 0.99332 | -0.12784 | 0.99341 | -0.12597 | 1.8195
29 | -0.069441 | -0.017526 | 0.06948 | 0.01755 | 3.877e-05 | 2.4689e-05 | 0.10406 | 0.10406 | 0.10406 | 0.99341 | -0.12597 | 0.99402 | -0.11432 | 28.5873
30 | -0.077415 | -0.019539 | 0.077842 | 0.019811 | 0.00042643 | 0.00027181 | 0.11594 | 0.11594 | 0.11594 | 0.99402 | -0.11432 | 1 | 0 | 31.8507
31 | -0.084121 | -0.021328 | 0.084545 | 0.021598 | 0.0004239 | 0.00027037 | 0.12595 | 0.12595 | 0.12595 | 0.99453 | -0.10427 | 1 | 0 | 34.6014
32 | 0.082125 | 0.020827 | -0.081889 | -0.020677 | 0.0002353 | 0.00015006 | 0.12296 | 0.12296 | 0.12296 | 0.99453 | -0.10427 | 0.99141 | -0.16405 | 33.7809
33 | 0.080267 | 0.020271 | -0.080213 | -0.020236 | 5.3986e-05 | 3.4423e-05 | 0.12053 | 0.12053 | 0.12053 | 0.99141 | -0.16405 | 0.99069 | -0.1781 | 33.1119
34 | -0.0090417 | -0.002267 | 0.0090429 | 0.0022675 | 1.1501e-06 | 5.2347e-07 | 0.013606 | 0.013606 | 0.013606 | 0.9889 | -0.21268 | 0.98904 | -0.21001 | 3.7378
35 | 0.0076074 | 0.0019075 | -0.0076005 | -0.0019049 | 6.8413e-06 | 2.5941e-06 | 0.011447 | 0.011448 | 0.011448 | 0.9889 | -0.21268 | 0.98793 | -0.23156 | 3.145
36 | -0.010595 | -0.0026565 | 0.010595 | 0.0026565 | 9.9103e-09 | 5.0073e-09 | 0.015941 | 0.015941 | 0.015941 | 0.98904 | -0.21001 | 0.98904 | -0.20999 | 4.3794
37 | 0.01278 | 0.0032032 | -0.012778 | -0.0032022 | 1.6918e-06 | 9.2815e-07 | 0.019289 | 0.019289 | 0.019289 | 0.98588 | -0.27184 | 0.98574 | -0.27462 | 5.2993
38 | 0.073694 | 0.018603 | -0.073596 | -0.01854 | 9.7664e-05 | 6.2232e-05 | 0.11074 | 0.11074 | 0.11074 | 0.99069 | -0.1781 | 0.98925 | -0.20581 | 30.4221
39 | 0.012362 | 0.0031001 | -0.01236 | -0.0030988 | 2.4651e-06 | 1.3337e-06 | 0.018596 | 0.018596 | 0.018596 | 0.98925 | -0.20581 | 0.98904 | -0.20999 | 5.1088
40 | 0.061234 | 0.01544 | -0.061189 | -0.015412 | 4.4595e-05 | 2.8361e-05 | 0.09214 | 0.092141 | 0.092141 | 0.98925 | -0.20581 | 0.98847 | -0.22103 | 25.3133
41 | 0.059427 | 0.01497 | -0.059403 | -0.014955 | 2.4151e-05 | 1.5354e-05 | 0.089487 | 0.089487 | 0.089487 | 0.98847 | -0.22103 | 0.98803 | -0.22954 | 24.5845
42 | 0.0070003 | 0.0017545 | -0.0069998 | -0.0017543 | 4.848e-07 | 1.6132e-07 | 0.010543 | 0.010543 | 0.010543 | 0.98803 | -0.22954 | 0.98795 | -0.23099 | 2.8964
43 | 0.052403 | 0.0132 | -0.052347 | -0.013165 | 5.5933e-05 | 3.5491e-05 | 0.078945 | 0.078945 | 0.078945 | 0.98803 | -0.22954 | 0.98688 | -0.25188 | 21.6881
44 | -0.0039645 | -0.00099361 | 0.0039651 | 0.00099344 | 5.4112e-07 | -1.6707e-07 | 0.0059855 | 0.0059854 | 0.0059855 | 0.9856 | -0.27749 | 0.98574 | -0.27462 | 1.6444
45 | 0.045406 | 0.011425 | -0.045378 | -0.011408 | 2.7844e-05 | 1.7618e-05 | 0.068479 | 0.068479 | 0.068479 | 0.98688 | -0.25188 | 0.98621 | -0.26472 | 18.813
46 | 0.019785 | 0.0049842 | -0.019721 | -0.0049458 | 6.3785e-05 | 3.8397e-05 | 0.029861 | 0.029862 | 0.029862 | 0.98621 | -0.26472 | 0.98274 | -0.33235 | 8.2039
47 | 0.013093 | 0.0032847 | -0.013082 | -0.0032787 | 1.0883e-05 | 6.0307e-06 | 0.019826 | 0.019826 | 0.019826 | 0.98274 | -0.33235 | 0.98185 | -0.3498 | 5.4467
48 | 0.0066284 | 0.0016611 | -0.0066274 | -0.0016608 | 1.0336e-06 | 3.1487e-07 | 0.010036 | 0.010036 | 0.010036 | 0.98274 | -0.33235 | 0.98258 | -0.33563 | 2.7573
49 | 0.0047798 | 0.0011979 | -0.0047796 | -0.0011979 | 1.8376e-07 | -1.9155e-09 | 0.0072223 | 0.0072223 | 0.0072223 | 0.98479 | -0.29255 | 0.98475 | -0.29336 | 1.9842
50 | 0.0093565 | 0.0023452 | -0.0093538 | -0.002344 | 2.6773e-06 | 1.2645e-06 | 0.01418 | 0.01418 | 0.01418 | 0.98185 | -0.3498 | 0.98155 | -0.35581 | 3.8957
51 | 0.0037256 | 0.00093342 | -0.0037254 | -0.00093348 | 1.3444e-07 | -5.6184e-08 | 0.0056461 | 0.0056461 | 0.0056461 | 0.98185 | -0.3498 | 0.98181 | -0.35056 | 1.5511
52 | 0.005361 | 0.0013434 | -0.0053597 | -0.0013433 | 1.2766e-06 | 1.6302e-07 | 0.0081186 | 0.0081189 | 0.0081189 | 0.98258 | -0.33563 | 0.98232 | -0.34063 | 2.2305
53 | 0.0012561 | 0.00031461 | -0.0012561 | -0.00031481 | 2.3517e-08 | -2.0353e-07 | 0.0019042 | 0.0019043 | 0.0019043 | 0.98155 | -0.35581 | 0.98153 | -0.3562 | 0.52316
54 | 0.0080977 | 0.0020294 | -0.0080969 | -0.002029 | 7.9176e-07 | 3.2966e-07 | 0.012276 | 0.012276 | 0.012276 | 0.98155 | -0.35581 | 0.98144 | -0.35786 | 3.3725
55 | 0.002491 | 0.00062411 | -0.002491 | -0.00062419 | 4.8004e-08 | -8.2856e-08 | 0.0037753 | 0.0037753 | 0.0037753 | 0.98181 | -0.35056 | 0.98179 | -0.35096 | 1.0372
56 | 0.0011643 | 0.00029169 | -0.0011643 | -0.00029179 | 1.0263e-08 | -1.0458e-07 | 0.0017646 | 0.0017646 | 0.0017646 | 0.98179 | -0.35096 | 0.98178 | -0.35115 | 0.48478
57 | 0.0041773 | 0.0010467 | -0.0041769 | -0.0010468 | 3.6107e-07 | -7.2223e-08 | 0.0063333 | 0.0063335 | 0.0063335 | 0.98144 | -0.35786 | 0.98135 | -0.35968 | 1.74
58 | 0.0019918 | 0.00049913 | -0.0019918 | -0.00049919 | 1.8884e-08 | -5.7668e-08 | 0.0030201 | 0.0030202 | 0.0030202 | 0.98135 | -0.35968 | 0.98134 | -0.35988 | 0.82971

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16404 | 0.041409

## res_load
| p_mw | q_mvar
0 | 0.0011601 | 0.00029075
1 | 0.0047453 | 0.0011893
2 | 0.011503 | 0.002883
3 | 0.010201 | 0.0025566
4 | 0.0028991 | 0.00072659
5 | 0.0011534 | 0.00028907
6 | 0.0031284 | 0.00078405
7 | 0.00024631 | 6.1731e-05
8 | 0.0011617 | 0.00029114
9 | 0.0043828 | 0.0010984
10 | 0.004421 | 0.001108
11 | 0.0079353 | 0.0019888
12 | 0.0019964 | 0.00050034
13 | 0.0016225 | 0.00040663
14 | 0.0097013 | 0.0024314
15 | 0.010527 | 0.0026382
16 | 0.0014344 | 0.00035949
17 | 0.0015524 | 0.00038906
18 | 0.0076005 | 0.0019049
19 | 0.0099844 | 0.0025023
20 | 0.0065186 | 0.0016337
21 | 0.0017646 | 0.00044226
22 | 0.0017624 | 0.00044171
23 | 0.0039645 | 0.00099361
24 | 0.0088132 | 0.0022088
25 | 0.0069998 | 0.0017543
26 | 0.0069409 | 0.0017396
27 | 0.0018972 | 0.00047548
28 | 0.0012664 | 0.00031739
29 | 0.0047796 | 0.0011979
30 | 0.0012344 | 0.00030937
31 | 0.0053597 | 0.0013433
32 | 0.0013267 | 0.00033251
33 | 0.0011643 | 0.00029179
34 | 0.0012561 | 0.00031481
35 | 0.0039196 | 0.00098234
36 | 0.0021851 | 0.00054765
37 | 0.0019918 | 0.00049919

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1