## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_154-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_154-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_154-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_154-5_0_4_node_122 | 0.4 | n |  | TRUE
4 | bus_LV_154-5_0_4_node_117 | 0.4 | n |  | TRUE
5 | bus_LV_154-5_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_154-5_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_154-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_154-5_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_154-5_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_154-5_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_154-5_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_154-5_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_154-5_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_154-5_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_154-5_0_4_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_154-5_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_154-5_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_154-5_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_154-5_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_154-5_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_154-5_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_154-5_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_154-5_0_4_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_154-5_0_4_node_143 | 0.4 | n |  | TRUE
25 | bus_LV_154-5_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_154-5_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_154-5_0_4_node_66 | 0.4 | n |  | TRUE
28 | bus_LV_154-5_0_4_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_154-5_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_154-5_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_154-5_0_4_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_154-5_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_154-5_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_154-5_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_154-5_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_154-5_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_154-5_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_154-5_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_154-5_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_154-5_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_154-5_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_154-5_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_154-5_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_154-5_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_154-5_0_4_node_99 | 0.4 | n |  | TRUE
46 | bus_LV_154-5_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_154-5_0_4_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_154-5_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_154-5_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_154-5_0_4_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_154-5_0_4_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_154-5_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_154-5_0_4_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_154-5_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_154-5_0_4_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_154-5_0_4_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_154-5_0_4_node_83 | 0.4 | n |  | TRUE
58 | bus_LV_154-5_0_4_node_62 | 0.4 | n |  | TRUE
59 | bus_LV_154-5_0_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_154-5_0_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_154-5_0_4_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_154-5_0_4_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_154-5_0_4_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_154-5_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_154-5_0_4_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_154-5_0_4_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_154-5_0_4_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_154-5_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_154-5_0_4_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_154-5_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_154-5_0_4_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_154-5_0_4_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_154-5_0_4_node_89 | 0.4 | n |  | TRUE
74 | bus_LV_154-5_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_154-5_0_4_node_87 | 0.4 | n |  | TRUE
76 | bus_LV_154-5_0_4_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_154-5_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_154-5_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_154-5_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_154-5_0_4_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_154-5_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_154-5_0_4_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_154-5_0_4_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_154-5_0_4_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_154-5_0_4_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_154-5_0_4_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_154-5_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_154-5_0_4_node_139 | 0.4 | n |  | TRUE
89 | bus_LV_154-5_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_154-5_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_154-5_0_4_node_140 | 0.4 | n |  | TRUE
92 | bus_LV_154-5_0_4_node_137 | 0.4 | n |  | TRUE
93 | bus_LV_154-5_0_4_node_138 | 0.4 | n |  | TRUE
94 | bus_LV_154-5_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_154-5_0_4_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_154-5_0_4_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_154-5_0_4_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_154-5_0_4_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_154-5_0_4_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_154-5_0_4_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_154-5_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_154-5_0_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_154-5_0_4_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_154-5_0_4_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_154-5_0_4_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_154-5_0_4_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_154-5_0_4_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_154-5_0_4_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_154-5_0_4_node_120 | 0.4 | n |  | TRUE
110 | bus_LV_154-5_0_4_node_119 | 0.4 | n |  | TRUE
111 | bus_LV_154-5_0_4_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_154-5_0_4_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_154-5_0_4_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_154-5_0_4_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_154-5_0_4_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_154-5_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_154-5_0_4_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_154-5_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_154-5_0_4_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_154-5_0_4_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_154-5_0_4_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_154-5_0_4_node_114 | 0.4 | n |  | TRUE
123 | bus_LV_154-5_0_4_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_154-5_0_4_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_154-5_0_4_node_136 | 0.4 | n |  | TRUE
126 | bus_LV_154-5_0_4_node_134 | 0.4 | n |  | TRUE
127 | bus_LV_154-5_0_4_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_154-5_0_4_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_154-5_0_4_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_154-5_0_4_node_127 | 0.4 | n |  | TRUE
131 | bus_LV_154-5_0_4_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_154-5_0_4_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_154-5_0_4_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_154-5_0_4_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_154-5_0_4_node_130 | 0.4 | n |  | TRUE
136 | bus_LV_154-5_0_4_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_154-5_0_4_node_132 | 0.4 | n |  | TRUE
138 | bus_LV_154-5_0_4_node_141 | 0.4 | n |  | TRUE
139 | bus_LV_154-5_0_4_node_142 | 0.4 | n |  | TRUE
140 | bus_MV_492_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_154-5_0_4_load_0 | 0 | 0.0026355 | 0.00066051 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_154-5_0_4_load_1 | 1 | 0.002874 | 0.0007203 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_154-5_0_4_load_122 | 3 | 0.0047118 | 0.0011809 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_154-5_0_4_load_117 | 4 | 0.0068843 | 0.0017254 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_154-5_0_4_load_3 | 5 | 0.010575 | 0.0026503 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_154-5_0_4_load_4 | 6 | 0.0019811 | 0.00049652 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_154-5_0_4_load_5 | 7 | 0.0015359 | 0.00038494 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_154-5_0_4_load_6 | 8 | 0.0020688 | 0.00051848 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_154-5_0_4_load_7 | 9 | 0.0020698 | 0.00051874 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_154-5_0_4_load_9 | 11 | 0.011718 | 0.0029368 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_154-5_0_4_load_18 | 12 | 0.0018454 | 0.00046251 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_154-5_0_4_load_16 | 13 | 0.011353 | 0.0028453 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_154-5_0_4_load_19 | 14 | 0.0020298 | 0.00050872 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_154-5_0_4_load_39 | 15 | 0.013869 | 0.0034758 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_154-5_0_4_load_13 | 16 | 0.011379 | 0.0028519 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_154-5_0_4_load_20 | 17 | 0.0023112 | 0.00057925 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_154-5_0_4_load_10 | 18 | 0.009938 | 0.0024907 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_154-5_0_4_load_11 | 19 | 0.0089708 | 0.0022483 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_154-5_0_4_load_14 | 21 | 0.0020783 | 0.00052087 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_154-5_0_4_load_65 | 23 | 0.0033439 | 0.00083806 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_154-5_0_4_load_143 | 24 | 0.013023 | 0.0032638 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_154-5_0_4_load_22 | 25 | 0.003908 | 0.00097943 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_154-5_0_4_load_40 | 28 | 0.0023103 | 0.00057903 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_154-5_0_4_load_21 | 29 | 0.0020636 | 0.00051718 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_154-5_0_4_load_38 | 30 | 0.0020718 | 0.00051924 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_154-5_0_4_load_25 | 33 | 0.0039805 | 0.00099761 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_154-5_0_4_load_36 | 34 | 0.0025579 | 0.00064106 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_154-5_0_4_load_26 | 35 | 0.0044174 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_154-5_0_4_load_27 | 36 | 0.0024826 | 0.00062219 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_154-5_0_4_load_30 | 38 | 0.0014263 | 0.00035747 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_154-5_0_4_load_31 | 39 | 0.0036865 | 0.00092392 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_154-5_0_4_load_33 | 40 | 0.001558 | 0.00039048 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_154-5_0_4_load_34 | 41 | 0.00092384 | 0.00023154 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_154-5_0_4_load_32 | 42 | 0.0026418 | 0.0006621 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_154-5_0_4_load_35 | 43 | 0.0026353 | 0.00066046 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_154-5_0_4_load_43 | 44 | 0.0012162 | 0.0003048 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_154-5_0_4_load_99 | 45 | 0.0047838 | 0.0011989 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_154-5_0_4_load_44 | 46 | 0.0045762 | 0.0011469 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_154-5_0_4_load_100 | 47 | 0.0022868 | 0.00057313 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_154-5_0_4_load_41 | 48 | 0.0037943 | 0.00095093 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_154-5_0_4_load_47 | 50 | 0.0044809 | 0.001123 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_154-5_0_4_load_49 | 51 | 0.0030942 | 0.00077548 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_154-5_0_4_load_46 | 52 | 0.0029315 | 0.0007347 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_154-5_0_4_load_48 | 53 | 0.0010866 | 0.00027232 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_154-5_0_4_load_50 | 54 | 0.0011501 | 0.00028824 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_154-5_0_4_load_51 | 55 | 0.0049825 | 0.0012487 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_154-5_0_4_load_45 | 56 | 0.0084915 | 0.0021282 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_154-5_0_4_load_83 | 57 | 0.0027031 | 0.00067747 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_154-5_0_4_load_62 | 58 | 0.0025642 | 0.00064264 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_154-5_0_4_load_84 | 59 | 0.0011656 | 0.00029212 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_154-5_0_4_load_59 | 60 | 0.0031291 | 0.00078422 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_154-5_0_4_load_52 | 61 | 0.0040017 | 0.0010029 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_154-5_0_4_load_53 | 62 | 0.0083553 | 0.002094 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_154-5_0_4_load_54 | 63 | 0.0053043 | 0.0013294 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_154-5_0_4_load_55 | 64 | 0.002671 | 0.00066941 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_154-5_0_4_load_56 | 65 | 0.0091324 | 0.0022888 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_154-5_0_4_load_58 | 67 | 0.0045492 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_154-5_0_4_load_60 | 68 | 0.0015699 | 0.00039344 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_154-5_0_4_load_61 | 69 | 0.002231 | 0.00055915 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_154-5_0_4_load_63 | 70 | 0.0031346 | 0.0007856 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_154-5_0_4_load_64 | 71 | 0.0027548 | 0.00069042 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_154-5_0_4_load_71 | 72 | 0.0041269 | 0.0010343 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_154-5_0_4_load_89 | 73 | 0.0031241 | 0.00078297 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_154-5_0_4_load_87 | 75 | 0.007959 | 0.0019947 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_154-5_0_4_load_67 | 76 | 0.0024669 | 0.00061826 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_154-5_0_4_load_68 | 77 | 0.0036155 | 0.00090612 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_154-5_0_4_load_70 | 79 | 0.0033758 | 0.00084606 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_154-5_0_4_load_77 | 80 | 0.0078209 | 0.0019601 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_154-5_0_4_load_78 | 81 | 0.0031083 | 0.00077901 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_154-5_0_4_load_73 | 82 | 0.002928 | 0.00073382 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_154-5_0_4_load_74 | 83 | 0.0034155 | 0.00085599 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_154-5_0_4_load_79 | 87 | 0.0041137 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_154-5_0_4_load_139 | 88 | 0.0020899 | 0.00052377 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_154-5_0_4_load_81 | 89 | 0.0033328 | 0.00083529 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_154-5_0_4_load_82 | 90 | 0.0022352 | 0.00056019 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_154-5_0_4_load_140 | 91 | 0.0018369 | 0.00046037 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_154-5_0_4_load_137 | 92 | 0.0022074 | 0.00055324 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_154-5_0_4_load_138 | 93 | 0.0037064 | 0.00092892 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_154-5_0_4_load_85 | 94 | 0.0079137 | 0.0019834 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_154-5_0_4_load_101 | 95 | 0.0081351 | 0.0020388 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_154-5_0_4_load_97 | 96 | 0.0044652 | 0.0011191 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_154-5_0_4_load_86 | 97 | 0.004984 | 0.0012491 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_154-5_0_4_load_88 | 98 | 0.0012615 | 0.00031616 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_154-5_0_4_load_90 | 99 | 0.0033441 | 0.00083811 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_154-5_0_4_load_91 | 100 | 0.0023944 | 0.0006001 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_154-5_0_4_load_102 | 101 | 0.0035681 | 0.00089425 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_154-5_0_4_load_92 | 103 | 0.0017617 | 0.00044152 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_154-5_0_4_load_93 | 104 | 0.0028777 | 0.00072123 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_154-5_0_4_load_94 | 105 | 0.0015495 | 0.00038834 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_154-5_0_4_load_95 | 106 | 0.0058477 | 0.0014656 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_154-5_0_4_load_96 | 107 | 0.0046041 | 0.0011539 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_154-5_0_4_load_120 | 109 | 0.001484 | 0.00037192 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_154-5_0_4_load_119 | 110 | 0.0010511 | 0.00026342 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_154-5_0_4_load_109 | 111 | 0.00096731 | 0.00024243 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_154-5_0_4_load_107 | 112 | 0.0011339 | 0.00028419 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_154-5_0_4_load_105 | 113 | 0.0035719 | 0.0008952 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_154-5_0_4_load_112 | 114 | 0.0024438 | 0.00061248 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_154-5_0_4_load_110 | 115 | 0.0033933 | 0.00085044 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_154-5_0_4_load_115 | 116 | 0.0028775 | 0.00072117 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_154-5_0_4_load_104 | 118 | 0.0048408 | 0.0012132 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_154-5_0_4_load_106 | 119 | 0.0049282 | 0.0012351 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_154-5_0_4_load_108 | 120 | 0.0074235 | 0.0018605 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_154-5_0_4_load_114 | 122 | 0.001054 | 0.00026415 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_154-5_0_4_load_116 | 123 | 0.0010918 | 0.00027362 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_154-5_0_4_load_118 | 124 | 0.0010108 | 0.00025334 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_154-5_0_4_load_136 | 125 | 0.0015656 | 0.00039237 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_154-5_0_4_load_134 | 126 | 0.0011059 | 0.00027716 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_154-5_0_4_load_123 | 127 | 0.0021332 | 0.00053464 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_154-5_0_4_load_126 | 129 | 0.0012919 | 0.00032378 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_154-5_0_4_load_127 | 130 | 0.00080163 | 0.00020091 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_154-5_0_4_load_129 | 132 | 0.0025079 | 0.00062853 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_154-5_0_4_load_135 | 133 | 0.0014449 | 0.00036212 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_154-5_0_4_load_133 | 134 | 0.0040874 | 0.0010244 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_154-5_0_4_load_130 | 135 | 0.0012678 | 0.00031775 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_154-5_0_4_load_131 | 136 | 0.0016081 | 0.00040303 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_154-5_0_4_load_132 | 137 | 0.0039556 | 0.00099137 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_154-5_0_4_load_141 | 138 | 0.0017149 | 0.00042979 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_154-5_0_4_load_142 | 139 | 0.0022066 | 0.00055302 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_154-5_0_4_line_0 |  | 0 | 1 | 0.040459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_154-5_0_4_line_1 |  | 1 | 2 | 0.080187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_154-5_0_4_line_2 |  | 2 | 3 | 0.67343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_154-5_0_4_line_3 |  | 3 | 4 | 0.044882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_154-5_0_4_line_4 |  | 4 | 121 | 0.026978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_154-5_0_4_line_5 |  | 5 | 6 | 0.005431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_154-5_0_4_line_6 |  | 5 | 7 | 0.020377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_154-5_0_4_line_7 |  | 6 | 8 | 0.011207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_154-5_0_4_line_8 |  | 7 | 9 | 0.002882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_154-5_0_4_line_9 |  | 8 | 10 | 0.029398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_154-5_0_4_line_10 |  | 9 | 11 | 0.0069059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_154-5_0_4_line_11 |  | 10 | 12 | 0.013896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_154-5_0_4_line_12 |  | 10 | 13 | 0.012804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_154-5_0_4_line_13 |  | 11 | 14 | 0.019701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_154-5_0_4_line_14 |  | 12 | 15 | 0.0047676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_154-5_0_4_line_15 |  | 13 | 16 | 0.0089103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_154-5_0_4_line_16 |  | 14 | 17 | 0.0046962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_154-5_0_4_line_17 |  | 15 | 28 | 0.027281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_154-5_0_4_line_18 |  | 16 | 19 | 0.029267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_154-5_0_4_line_19 |  | 17 | 29 | 0.0010137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_154-5_0_4_line_20 |  | 18 | 19 | 0.0071621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_154-5_0_4_line_21 |  | 18 | 20 | 0.020039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_154-5_0_4_line_22 |  | 20 | 21 | 0.0026932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_154-5_0_4_line_23 |  | 22 | 23 | 0.023556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_154-5_0_4_line_24 |  | 22 | 24 | 0.054374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_154-5_0_4_line_25 |  | 23 | 27 | 0.05578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_154-5_0_4_line_26 |  | 25 | 26 | 0.061205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_154-5_0_4_line_27 |  | 26 | 32 | 0.023255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_154-5_0_4_line_28 |  | 27 | 67 | 0.019767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_154-5_0_4_line_29 |  | 28 | 48 | 0.0075939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_154-5_0_4_line_30 |  | 29 | 30 | 0.037422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_154-5_0_4_line_31 |  | 30 | 31 | 0.019652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_154-5_0_4_line_32 |  | 31 | 34 | 0.015877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_154-5_0_4_line_33 |  | 31 | 33 | 0.017091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_154-5_0_4_line_34 |  | 32 | 33 | 0.042518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_154-5_0_4_line_35 |  | 34 | 43 | 0.047363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_154-5_0_4_line_36 |  | 35 | 36 | 0.02629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_154-5_0_4_line_37 |  | 35 | 37 | 0.0023686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_154-5_0_4_line_38 |  | 37 | 38 | 0.028838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_154-5_0_4_line_39 |  | 37 | 39 | 0.019313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_154-5_0_4_line_40 |  | 38 | 40 | 0.00069298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_154-5_0_4_line_41 |  | 39 | 41 | 0.02406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_154-5_0_4_line_42 |  | 40 | 44 | 0.00090664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_154-5_0_4_line_43 |  | 41 | 45 | 0.0014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_154-5_0_4_line_44 |  | 42 | 43 | 0.0081289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_154-5_0_4_line_45 |  | 44 | 46 | 0.00067277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_154-5_0_4_line_46 |  | 45 | 47 | 0.0033888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_154-5_0_4_line_47 |  | 46 | 56 | 0.040688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_154-5_0_4_line_48 |  | 47 | 112 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_154-5_0_4_line_49 |  | 48 | 49 | 0.027175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_154-5_0_4_line_50 |  | 49 | 50 | 0.024688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_154-5_0_4_line_51 |  | 49 | 51 | 0.03087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_154-5_0_4_line_52 |  | 50 | 52 | 0.015639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_154-5_0_4_line_53 |  | 51 | 55 | 0.014922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_154-5_0_4_line_54 |  | 52 | 56 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_154-5_0_4_line_55 |  | 53 | 54 | 0.0059638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_154-5_0_4_line_56 |  | 54 | 57 | 0.0034696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_154-5_0_4_line_57 |  | 55 | 58 | 0.0021189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_154-5_0_4_line_58 |  | 57 | 59 | 0.0026396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_154-5_0_4_line_59 |  | 58 | 60 | 0.034454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_154-5_0_4_line_60 |  | 59 | 94 | 0.02991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_154-5_0_4_line_61 |  | 60 | 66 | 0.021318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_154-5_0_4_line_62 |  | 61 | 62 | 0.0040949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_154-5_0_4_line_63 |  | 61 | 63 | 0.029062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_154-5_0_4_line_64 |  | 62 | 64 | 0.029034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_154-5_0_4_line_65 |  | 63 | 65 | 0.0041024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_154-5_0_4_line_66 |  | 64 | 66 | 0.046574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_154-5_0_4_line_67 |  | 65 | 67 | 0.046052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_154-5_0_4_line_68 |  | 66 | 68 | 0.035645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_154-5_0_4_line_69 |  | 66 | 69 | 0.024025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_154-5_0_4_line_70 |  | 68 | 70 | 0.0014859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_154-5_0_4_line_71 |  | 69 | 71 | 0.011316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_154-5_0_4_line_72 |  | 70 | 72 | 0.012538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_154-5_0_4_line_73 |  | 71 | 73 | 0.017392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_154-5_0_4_line_74 |  | 72 | 74 | 0.041868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_154-5_0_4_line_75 |  | 73 | 75 | 0.018187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_154-5_0_4_line_76 |  | 74 | 82 | 0.0027788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_154-5_0_4_line_77 |  | 74 | 83 | 0.025362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_154-5_0_4_line_78 |  | 75 | 97 | 0.014083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_154-5_0_4_line_79 |  | 76 | 77 | 0.034127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_154-5_0_4_line_80 |  | 77 | 78 | 0.018466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_154-5_0_4_line_81 |  | 78 | 79 | 0.034432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_154-5_0_4_line_82 |  | 79 | 80 | 0.012544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_154-5_0_4_line_83 |  | 80 | 81 | 0.033884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_154-5_0_4_line_84 |  | 81 | 87 | 0.0037709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_154-5_0_4_line_85 |  | 82 | 84 | 0.021625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_154-5_0_4_line_86 |  | 83 | 85 | 0.022257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_154-5_0_4_line_87 |  | 84 | 86 | 0.00888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_154-5_0_4_line_88 |  | 84 | 87 | 0.042443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_154-5_0_4_line_89 |  | 85 | 88 | 0.018483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_154-5_0_4_line_90 |  | 86 | 89 | 0.037741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_154-5_0_4_line_91 |  | 86 | 90 | 0.022241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_154-5_0_4_line_92 |  | 88 | 91 | 0.024523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_154-5_0_4_line_93 |  | 90 | 92 | 0.030612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_154-5_0_4_line_94 |  | 91 | 138 | 0.015808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_154-5_0_4_line_95 |  | 92 | 93 | 0.031172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_154-5_0_4_line_96 |  | 94 | 95 | 0.00055359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_154-5_0_4_line_97 |  | 95 | 96 | 0.015567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_154-5_0_4_line_98 |  | 96 | 106 | 0.020764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_154-5_0_4_line_99 |  | 97 | 98 | 0.0020598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_154-5_0_4_line_100 |  | 98 | 99 | 0.020918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_154-5_0_4_line_101 |  | 99 | 100 | 0.0064153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_154-5_0_4_line_102 |  | 100 | 101 | 0.0041903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_154-5_0_4_line_103 |  | 101 | 102 | 0.0059619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_154-5_0_4_line_104 |  | 102 | 114 | 0.018213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_154-5_0_4_line_105 |  | 102 | 115 | 0.035791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_154-5_0_4_line_106 |  | 103 | 104 | 0.016168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_154-5_0_4_line_107 |  | 103 | 105 | 0.0037134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_154-5_0_4_line_108 |  | 104 | 106 | 0.021836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_154-5_0_4_line_109 |  | 105 | 107 | 0.010552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_154-5_0_4_line_110 |  | 107 | 108 | 0.0085196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_154-5_0_4_line_111 |  | 108 | 109 | 0.020211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_154-5_0_4_line_112 |  | 108 | 110 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_154-5_0_4_line_113 |  | 110 | 111 | 0.007602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_154-5_0_4_line_114 |  | 111 | 120 | 0.024425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_154-5_0_4_line_115 |  | 112 | 113 | 0.0067757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_154-5_0_4_line_116 |  | 113 | 118 | 0.033062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_154-5_0_4_line_117 |  | 114 | 116 | 0.0096871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_154-5_0_4_line_118 |  | 115 | 117 | 0.0061261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_154-5_0_4_line_119 |  | 116 | 125 | 0.013394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_154-5_0_4_line_120 |  | 117 | 121 | 0.001967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_154-5_0_4_line_121 |  | 117 | 122 | 0.048695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_154-5_0_4_line_122 |  | 118 | 119 | 0.009211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_154-5_0_4_line_123 |  | 119 | 120 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_154-5_0_4_line_124 |  | 121 | 123 | 0.015953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_154-5_0_4_line_125 |  | 122 | 124 | 0.029107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_154-5_0_4_line_126 |  | 125 | 126 | 0.0096708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_154-5_0_4_line_127 |  | 126 | 137 | 0.025406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_154-5_0_4_line_128 |  | 127 | 128 | 0.027801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_154-5_0_4_line_129 |  | 128 | 129 | 0.0096487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_154-5_0_4_line_130 |  | 129 | 130 | 0.04829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_154-5_0_4_line_131 |  | 130 | 131 | 0.029556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_154-5_0_4_line_132 |  | 131 | 132 | 0.039877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_154-5_0_4_line_133 |  | 132 | 133 | 0.0030028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_154-5_0_4_line_134 |  | 133 | 134 | 0.025487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_154-5_0_4_line_135 |  | 134 | 136 | 0.0033647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_154-5_0_4_line_136 |  | 135 | 136 | 0.031919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_154-5_0_4_line_137 |  | 135 | 137 | 0.0014859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_154-5_0_4_line_138 |  | 138 | 139 | 0.0094819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_154-5_0_4_trafo_49 | 0.63 MVA 20/0.4 kV | 140 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2688464.7271 | 1241433.719 | 2688471.076 | 1241449.9768 | 2688480.0246 | 1241471.1703
1 | 2688497.9621 | 1241547.9493 | 2688499.777 | 1241536.2789 | 2688497.893 | 1241525.2094 | 2688493.1525 | 1241502.8779 | 2688486.3839 | 1241486.2315 | 2688480.0246 | 1241471.1703
2 | 2687904.37 | 1241865.9941 | 2688497.9621 | 1241547.9493
3 | 2687904.37 | 1241865.9941 | 2687906.1025 | 1241871.4477 | 2687911.1337 | 1241887.5563 | 2687912.7739 | 1241895.7532 | 2687913.3488 | 1241905.4244 | 2687913.02 | 1241909.6481
4 | 2687905.7511 | 1241935.4672 | 2687910.1989 | 1241924.1025 | 2687912.6485 | 1241914.4206 | 2687913.02 | 1241909.6481
5 | 2687652.7252 | 1242005.8561 | 2687647.703 | 1242003.7888
6 | 2687628.8598 | 1241996.0322 | 2687647.703 | 1242003.7888
7 | 2687652.7252 | 1242005.8561 | 2687663.0887 | 1242010.1221
8 | 2687628.8598 | 1241996.0322 | 2687628.2343 | 1241995.7747 | 2687626.1062 | 1241995.1952
9 | 2687686.7065 | 1242027.6282 | 2687663.0887 | 1242010.1221 | 2687663.0887 | 1242010.1221
10 | 2687626.1062 | 1241995.1952 | 2687619.4429 | 1241993.3807
11 | 2687686.7065 | 1242027.6282 | 2687696.1187 | 1242017.4053
12 | 2687686.7065 | 1242027.6282 | 2687678.8094 | 1242037.7067
13 | 2687600.4344 | 1241988.2045 | 2687619.4429 | 1241993.3807
14 | 2687699.348 | 1242013.8979 | 2687696.1187 | 1242017.4053
15 | 2687678.8094 | 1242037.7067 | 2687673.3138 | 1242044.7204
16 | 2687595.9032 | 1241986.9706 | 2687600.4344 | 1241988.2045
17 | 2687699.348 | 1242013.8979 | 2687714.4614 | 1241997.4828 | 2687717.9777 | 1241993.9733
18 | 2687655.9801 | 1242068.2892 | 2687665.4071 | 1242054.8113 | 2687673.3138 | 1242044.7204
19 | 2687595.9032 | 1241986.9706 | 2687594.9251 | 1241986.7042
20 | 2687655.9801 | 1242068.2892 | 2687651.8751 | 1242074.1582
21 | 2687640.3898 | 1242090.5791 | 2687651.8751 | 1242074.1582
22 | 2687640.3898 | 1242090.5791 | 2687638.8398 | 1242092.7816
23 | 2687602.881 | 1242143.8756 | 2687608.8086 | 1242146.932 | 2687620.2838 | 1242152.6722 | 2687623.7766 | 1242154.7348
24 | 2687602.881 | 1242143.8756 | 2687559.8922 | 1242110.5808
25 | 2687671.0925 | 1242184.2345 | 2687650.8563 | 1242170.7257 | 2687623.7766 | 1242154.7348
26 | 2687542.4092 | 1242046.2341 | 2687548.1179 | 1242040.5698 | 2687547.3207 | 1242034.1311 | 2687543.6183 | 1242017.5866 | 2687556.8013 | 1242022.896 | 2687572.1717 | 1242024.9687
27 | 2687526.0506 | 1242029.6586 | 2687542.4092 | 1242046.2341
28 | 2687671.0925 | 1242184.2345 | 2687683.2533 | 1242170.1816 | 2687684.0735 | 1242169.3293
29 | 2687723.3525 | 1241988.6087 | 2687717.9777 | 1241993.9733
30 | 2687594.9251 | 1241986.7042 | 2687558.8183 | 1241976.872
31 | 2687539.8573 | 1241971.7086 | 2687558.8183 | 1241976.872
32 | 2687539.8573 | 1241971.7086 | 2687543.849 | 1241956.3414
33 | 2687539.8573 | 1241971.7086 | 2687536.2281 | 1241988.4097
34 | 2687526.0506 | 1242029.6586 | 2687531.064 | 1242012.709 | 2687532.8894 | 1242003.7738 | 2687536.2281 | 1241988.4097
35 | 2687557.9796 | 1241911.1747 | 2687548.5869 | 1241938.1017 | 2687543.849 | 1241956.3414
36 | 2687644.764 | 1241893.0879 | 2687621.6687 | 1241880.5265
37 | 2687646.8447 | 1241894.2196 | 2687644.764 | 1241893.0879
38 | 2687646.8447 | 1241894.2196 | 2687672.2928 | 1241907.7844
39 | 2687646.8447 | 1241894.2196 | 2687656.8422 | 1241877.6957
40 | 2687672.2928 | 1241907.7844 | 2687672.9043 | 1241908.1103
41 | 2687656.8422 | 1241877.6957 | 2687657.4934 | 1241876.6195 | 2687668.2545 | 1241861.6452 | 2687670.7604 | 1241858.0747
42 | 2687672.9043 | 1241908.1103 | 2687673.7044 | 1241908.5368
43 | 2687671.601 | 1241856.8769 | 2687670.7604 | 1241858.0747
44 | 2687557.9796 | 1241911.1747 | 2687558.5502 | 1241909.5388 | 2687561.0445 | 1241903.6489
45 | 2687673.7044 | 1241908.5368 | 2687674.2981 | 1241908.8533
46 | 2687671.601 | 1241856.8769 | 2687673.5477 | 1241854.1031
47 | 2687674.2981 | 1241908.8533 | 2687685.1634 | 1241914.6449 | 2687709.3658 | 1241929.4577 | 2687709.3658 | 1241929.4577
48 | 2687673.5477 | 1241854.1031 | 2687679.8321 | 1241845.1486 | 2687682.3453 | 1241842.8659
49 | 2687742.5865 | 1241969.4113 | 2687723.3525 | 1241988.6087
50 | 2687742.5865 | 1241969.4113 | 2687728.287 | 1241949.2863
51 | 2687742.5865 | 1241969.4113 | 2687758.8133 | 1241995.6729
52 | 2687717.4924 | 1241937.9703 | 2687728.2623 | 1241949.2515 | 2687728.287 | 1241949.2863
53 | 2687766.6567 | 1242008.3668 | 2687758.8133 | 1241995.6729
54 | 2687717.4924 | 1241937.9703 | 2687709.3658 | 1241929.4577
55 | 2687776.4115 | 1241937.2701 | 2687772.0882 | 1241941.3782
56 | 2687776.4115 | 1241937.2701 | 2687778.9267 | 1241934.8802
57 | 2687767.7705 | 1242010.1693 | 2687766.6567 | 1242008.3668
58 | 2687780.8402 | 1241933.0619 | 2687778.9267 | 1241934.8802
59 | 2687785.881 | 1242039.4797 | 2687767.7705 | 1242010.1693
60 | 2687800.5849 | 1241910.6703 | 2687787.9155 | 1241926.3389 | 2687780.8402 | 1241933.0619
61 | 2687797.0867 | 1242057.6151 | 2687785.881 | 1242039.4797
62 | 2687740.1392 | 1242113.3773 | 2687743.065 | 1242110.5123
63 | 2687740.1392 | 1242113.3773 | 2687719.3742 | 1242133.71
64 | 2687763.8097 | 1242090.1994 | 2687743.065 | 1242110.5123
65 | 2687716.443 | 1242136.5802 | 2687719.3742 | 1242133.71
66 | 2687797.0867 | 1242057.6151 | 2687763.8097 | 1242090.1994
67 | 2687684.0735 | 1242169.3293 | 2687701.6202 | 1242151.0945 | 2687716.443 | 1242136.5802
68 | 2687797.0867 | 1242057.6151 | 2687814.2591 | 1242088.851
69 | 2687797.0867 | 1242057.6151 | 2687814.5752 | 1242041.142
70 | 2687814.2591 | 1242088.851 | 2687814.975 | 1242090.1531
71 | 2687822.8124 | 1242033.383 | 2687814.5752 | 1242041.142
72 | 2687821.0929 | 1242101.0974 | 2687817.7086 | 1242095.1254 | 2687814.975 | 1242090.1531
73 | 2687822.8124 | 1242033.383 | 2687835.4724 | 1242021.4581
74 | 2687841.7357 | 1242137.5231 | 2687821.0929 | 1242101.0974
75 | 2687848.7801 | 1242009.0617 | 2687838.4609 | 1242018.6431 | 2687835.4724 | 1242021.4581
76 | 2687841.7357 | 1242137.5231 | 2687843.1196 | 1242139.9328
77 | 2687841.7357 | 1242137.5231 | 2687859.9127 | 1242119.8365
78 | 2687859.1001 | 1241999.4795 | 2687848.7801 | 1242009.0617
79 | 2687715.0944 | 1242213.5645 | 2687743.5975 | 1242232.3324
80 | 2687759.0205 | 1242242.4877 | 2687743.5975 | 1242232.3324
81 | 2687759.0205 | 1242242.4877 | 2687779.3822 | 1242219.394 | 2687782.029 | 1242216.89
82 | 2687791.1415 | 1242208.2691 | 2687782.029 | 1242216.89
83 | 2687791.1415 | 1242208.2691 | 2687801.3811 | 1242198.5819 | 2687816.5668 | 1242185.8944
84 | 2687816.5668 | 1242185.8944 | 2687817.5181 | 1242185.0997 | 2687819.5136 | 1242183.5422
85 | 2687853.8895 | 1242158.6852 | 2687843.1196 | 1242139.9328
86 | 2687875.8644 | 1242104.3151 | 2687859.9127 | 1242119.8365
87 | 2687853.8895 | 1242158.6852 | 2687858.4108 | 1242166.3355
88 | 2687853.8895 | 1242158.6852 | 2687834.0167 | 1242172.2232 | 2687819.5136 | 1242183.5422
89 | 2687875.8644 | 1242104.3151 | 2687875.4883 | 1242102.1412 | 2687886.895 | 1242090.5296
90 | 2687858.4108 | 1242166.3355 | 2687878.6652 | 1242198.1807
91 | 2687858.4108 | 1242166.3355 | 2687873.9855 | 1242150.4581
92 | 2687886.895 | 1242090.5296 | 2687893.4357 | 1242083.8714 | 2687905.1708 | 1242074.2276
93 | 2687895.4219 | 1242128.6049 | 2687873.9855 | 1242150.4581
94 | 2687917.3836 | 1242064.1913 | 2687905.1708 | 1242074.2276
95 | 2687917.251 | 1242106.3516 | 2687895.4219 | 1242128.6049
96 | 2687800.5849 | 1241910.6703 | 2687800.5849 | 1241910.6703 | 2687800.8038 | 1241910.1619
97 | 2687800.8038 | 1241910.1619 | 2687806.9599 | 1241895.8634
98 | 2687811.203 | 1241875.6691 | 2687808.9239 | 1241891.3017 | 2687806.9599 | 1241895.8634
99 | 2687859.1001 | 1241999.4795 | 2687860.6096 | 1241998.078
100 | 2687875.9388 | 1241983.8448 | 2687860.6096 | 1241998.078
101 | 2687875.9388 | 1241983.8448 | 2687880.6401 | 1241979.4797
102 | 2687880.6401 | 1241979.4797 | 2687882.6638 | 1241977.6007 | 2687883.8272 | 1241976.7714
103 | 2687889.3834 | 1241975.1761 | 2687885.5217 | 1241975.5637 | 2687883.8272 | 1241976.7714
104 | 2687889.3834 | 1241975.1761 | 2687894.32 | 1241977.7622 | 2687904.6279 | 1241985.0771
105 | 2687889.3834 | 1241975.1761 | 2687897.864 | 1241951.3621 | 2687902.4412 | 1241941.8989
106 | 2687801.0244 | 1241840.1484 | 2687801.1506 | 1241840.2716 | 2687809.0882 | 1241854.1547
107 | 2687801.0244 | 1241840.1484 | 2687798.3679 | 1241837.5538
108 | 2687809.0882 | 1241854.1547 | 2687809.0882 | 1241854.1547 | 2687812.0039 | 1241870.1763 | 2687811.203 | 1241875.6691
109 | 2687798.3679 | 1241837.5538 | 2687790.8187 | 1241830.1807
110 | 2687784.7238 | 1241824.228 | 2687790.8187 | 1241830.1807
111 | 2687784.7238 | 1241824.228 | 2687797.8156 | 1241808.8302
112 | 2687784.7238 | 1241824.228 | 2687771.498 | 1241819.326
113 | 2687771.498 | 1241819.326 | 2687764.3698 | 1241816.684
114 | 2687740.0717 | 1241814.4077 | 2687763.8191 | 1241816.4799 | 2687764.3698 | 1241816.684
115 | 2687687.3609 | 1241838.3102 | 2687682.3453 | 1241842.8659
116 | 2687715.2201 | 1241820.9388 | 2687694.7688 | 1241831.5815 | 2687687.3609 | 1241838.3102
117 | 2687904.6279 | 1241985.0771 | 2687912.5279 | 1241990.6832
118 | 2687906.3737 | 1241937.3333 | 2687903.3161 | 1241940.0901 | 2687902.4412 | 1241941.8989
119 | 2687923.2586 | 1241998.695 | 2687916.2124 | 1241993.2978 | 2687912.5279 | 1241990.6832
120 | 2687906.3737 | 1241937.3333 | 2687905.7511 | 1241935.4672
121 | 2687906.3737 | 1241937.3333 | 2687910.9831 | 1241937.0014 | 2687915.1532 | 1241939.2759 | 2687918.9336 | 1241942.8456 | 2687928.604 | 1241952.5182 | 2687944.6571 | 1241962.6078 | 2687945.9154 | 1241963.3979
122 | 2687715.2201 | 1241820.9388 | 2687716.4388 | 1241820.3046 | 2687724.0256 | 1241818.3392
123 | 2687740.0717 | 1241814.4077 | 2687739.4213 | 1241814.351 | 2687724.0256 | 1241818.3392
124 | 2687905.7511 | 1241935.4672 | 2687916.9679 | 1241924.1237
125 | 2687970.8892 | 1241978.3352 | 2687967.4677 | 1241976.3893 | 2687958.0061 | 1241970.9895 | 2687945.9154 | 1241963.3979
126 | 2687930.936 | 1242004.5756 | 2687923.2586 | 1241998.695
127 | 2687930.936 | 1242004.5756 | 2687934.8496 | 1242007.5733 | 2687950.3137 | 1242020.9954
128 | 2687964.4081 | 1242151.5946 | 2687954.7306 | 1242155.6764 | 2687942.0722 | 1242167.4653
129 | 2687964.4081 | 1242151.5946 | 2687971.2098 | 1242144.751
130 | 2688005.9352 | 1242111.2245 | 2687994.1182 | 1242121.7019 | 2687971.2098 | 1242144.751
131 | 2688028.0504 | 1242091.6163 | 2688005.9352 | 1242111.2245
132 | 2688028.0504 | 1242091.6163 | 2688014.25 | 1242076.4895 | 2687999.598 | 1242063.7722
133 | 2687999.598 | 1242063.7722 | 2687997.3303 | 1242061.8039
134 | 2687978.0824 | 1242045.0975 | 2687997.3303 | 1242061.8039
135 | 2687975.5413 | 1242042.892 | 2687978.0824 | 1242045.0975
136 | 2687975.5413 | 1242042.892 | 2687951.4358 | 1242021.9694
137 | 2687950.3137 | 1242020.9954 | 2687951.4358 | 1242021.9694
138 | 2687924.7092 | 1242058.1712 | 2687917.3836 | 1242064.1913

## bus_geodata
| x | y | coords
0 | 2688464.7271 | 1241433.719
1 | 2688480.0246 | 1241471.1703
2 | 2688497.9621 | 1241547.9493
3 | 2687904.37 | 1241865.9941
4 | 2687913.02 | 1241909.6481
5 | 2687647.703 | 1242003.7888
6 | 2687652.7252 | 1242005.8561
7 | 2687628.8598 | 1241996.0322
8 | 2687663.0887 | 1242010.1221
9 | 2687626.1062 | 1241995.1952
10 | 2687686.7065 | 1242027.6282
11 | 2687619.4429 | 1241993.3807
12 | 2687696.1187 | 1242017.4053
13 | 2687678.8094 | 1242037.7067
14 | 2687600.4344 | 1241988.2045
15 | 2687699.348 | 1242013.8979
16 | 2687673.3138 | 1242044.7204
17 | 2687595.9032 | 1241986.9706
18 | 2687651.8751 | 1242074.1582
19 | 2687655.9801 | 1242068.2892
20 | 2687640.3898 | 1242090.5791
21 | 2687638.8398 | 1242092.7816
22 | 2687602.881 | 1242143.8756
23 | 2687623.7766 | 1242154.7348
24 | 2687559.8922 | 1242110.5808
25 | 2687572.1717 | 1242024.9687
26 | 2687542.4092 | 1242046.2341
27 | 2687671.0925 | 1242184.2345
28 | 2687717.9777 | 1241993.9733
29 | 2687594.9251 | 1241986.7042
30 | 2687558.8183 | 1241976.8719
31 | 2687539.8573 | 1241971.7086
32 | 2687526.0506 | 1242029.6586
33 | 2687536.2281 | 1241988.4097
34 | 2687543.849 | 1241956.3414
35 | 2687644.764 | 1241893.0879
36 | 2687621.6687 | 1241880.5265
37 | 2687646.8447 | 1241894.2196
38 | 2687672.2928 | 1241907.7844
39 | 2687656.8422 | 1241877.6957
40 | 2687672.9043 | 1241908.1103
41 | 2687670.7604 | 1241858.0747
42 | 2687561.0445 | 1241903.6489
43 | 2687557.9796 | 1241911.1747
44 | 2687673.7044 | 1241908.5368
45 | 2687671.601 | 1241856.8769
46 | 2687674.2981 | 1241908.8533
47 | 2687673.5477 | 1241854.1031
48 | 2687723.3525 | 1241988.6087
49 | 2687742.5865 | 1241969.4113
50 | 2687728.287 | 1241949.2863
51 | 2687758.8133 | 1241995.6729
52 | 2687717.4924 | 1241937.9703
53 | 2687772.0882 | 1241941.3782
54 | 2687776.4115 | 1241937.2701
55 | 2687766.6567 | 1242008.3668
56 | 2687709.3658 | 1241929.4577
57 | 2687778.9267 | 1241934.8802
58 | 2687767.7705 | 1242010.1693
59 | 2687780.8402 | 1241933.0619
60 | 2687785.881 | 1242039.4797
61 | 2687740.1392 | 1242113.3773
62 | 2687743.065 | 1242110.5123
63 | 2687719.3742 | 1242133.71
64 | 2687763.8097 | 1242090.1994
65 | 2687716.443 | 1242136.5802
66 | 2687797.0867 | 1242057.6151
67 | 2687684.0735 | 1242169.3293
68 | 2687814.2591 | 1242088.8511
69 | 2687814.5752 | 1242041.142
70 | 2687814.975 | 1242090.1531
71 | 2687822.8124 | 1242033.383
72 | 2687821.0929 | 1242101.0974
73 | 2687835.4724 | 1242021.4581
74 | 2687841.7357 | 1242137.5231
75 | 2687848.7801 | 1242009.0617
76 | 2687715.0944 | 1242213.5645
77 | 2687743.5975 | 1242232.3324
78 | 2687759.0205 | 1242242.4877
79 | 2687782.029 | 1242216.89
80 | 2687791.1415 | 1242208.2691
81 | 2687816.5668 | 1242185.8944
82 | 2687843.1196 | 1242139.9328
83 | 2687859.9127 | 1242119.8365
84 | 2687853.8895 | 1242158.6852
85 | 2687875.8644 | 1242104.3151
86 | 2687858.4108 | 1242166.3355
87 | 2687819.5136 | 1242183.5422
88 | 2687886.895 | 1242090.5296
89 | 2687878.6652 | 1242198.1807
90 | 2687873.9855 | 1242150.4581
91 | 2687905.1708 | 1242074.2276
92 | 2687895.4219 | 1242128.6049
93 | 2687917.251 | 1242106.3516
94 | 2687800.5849 | 1241910.6703
95 | 2687800.8038 | 1241910.1619
96 | 2687806.9599 | 1241895.8634
97 | 2687859.1001 | 1241999.4795
98 | 2687860.6096 | 1241998.078
99 | 2687875.9388 | 1241983.8448
100 | 2687880.6401 | 1241979.4797
101 | 2687883.8272 | 1241976.7714
102 | 2687889.3834 | 1241975.1761
103 | 2687801.0244 | 1241840.1484
104 | 2687809.0882 | 1241854.1547
105 | 2687798.3679 | 1241837.5538
106 | 2687811.203 | 1241875.6691
107 | 2687790.8187 | 1241830.1807
108 | 2687784.7238 | 1241824.228
109 | 2687797.8156 | 1241808.8302
110 | 2687771.498 | 1241819.326
111 | 2687764.3698 | 1241816.684
112 | 2687682.3453 | 1241842.8659
113 | 2687687.3609 | 1241838.3102
114 | 2687904.6279 | 1241985.0771
115 | 2687902.4412 | 1241941.8989
116 | 2687912.5279 | 1241990.6832
117 | 2687906.3737 | 1241937.3333
118 | 2687715.2201 | 1241820.9388
119 | 2687724.0256 | 1241818.3392
120 | 2687740.0717 | 1241814.4077
121 | 2687905.7511 | 1241935.4672
122 | 2687945.9154 | 1241963.3979
123 | 2687916.9679 | 1241924.1237
124 | 2687970.8892 | 1241978.3352
125 | 2687923.2586 | 1241998.695
126 | 2687930.936 | 1242004.5756
127 | 2687942.0722 | 1242167.4653
128 | 2687964.4081 | 1242151.5946
129 | 2687971.2098 | 1242144.751
130 | 2688005.9352 | 1242111.2245
131 | 2688028.0504 | 1242091.6163
132 | 2687999.598 | 1242063.7722
133 | 2687997.3303 | 1242061.8039
134 | 2687978.0824 | 1242045.0975
135 | 2687951.4358 | 1242021.9694
136 | 2687975.5413 | 1242042.892
137 | 2687950.3137 | 1242020.9954
138 | 2687917.3836 | 1242064.1913
139 | 2687924.7092 | 1242058.1712
140 | 2687742.5865 | 1241969.4113

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97964 | -0.39355 | 0.0026355 | 0.00066051
1 | 0.97973 | -0.39161 | 0.002874 | 0.0007203
2 | 0.98014 | -0.38359 | 0 | 0
3 | 0.98358 | -0.31633 | 0.0047118 | 0.0011809
4 | 0.984 | -0.30805 | 0.0068843 | 0.0017254
5 | 0.98611 | -0.26674 | 0.010575 | 0.0026503
6 | 0.98636 | -0.26187 | 0.0019811 | 0.00049652
7 | 0.98537 | -0.28119 | 0.0015359 | 0.00038494
8 | 0.9869 | -0.25141 | 0.0020688 | 0.00051848
9 | 0.98527 | -0.28316 | 0.0020698 | 0.00051874
10 | 0.98836 | -0.22296 | 0 | 0
11 | 0.98504 | -0.28761 | 0.011718 | 0.0029368
12 | 0.98961 | -0.19872 | 0.0018454 | 0.00046251
13 | 0.98785 | -0.23296 | 0.011353 | 0.0028453
14 | 0.9846 | -0.29619 | 0.0020298 | 0.00050872
15 | 0.99005 | -0.19027 | 0.013869 | 0.0034758
16 | 0.98758 | -0.23811 | 0.011379 | 0.0028519
17 | 0.9845 | -0.29806 | 0.0023112 | 0.00057925
18 | 0.98694 | -0.25063 | 0.009938 | 0.0024907
19 | 0.98702 | -0.24909 | 0.0089708 | 0.0022483
20 | 0.9869 | -0.25138 | 0 | 0
21 | 0.9869 | -0.25148 | 0.0020783 | 0.00052087
22 | 0.98652 | -0.25927 | 0 | 0
23 | 0.9868 | -0.25378 | 0.0033439 | 0.00083806
24 | 0.98587 | -0.27196 | 0.013023 | 0.0032638
25 | 0.983 | -0.32736 | 0.003908 | 0.00097943
26 | 0.98322 | -0.32304 | 0 | 0
27 | 0.98764 | -0.23745 | 0 | 0
28 | 0.9929 | -0.13532 | 0.0023103 | 0.00057903
29 | 0.98448 | -0.29842 | 0.0020636 | 0.00051718
30 | 0.98387 | -0.31041 | 0.0020718 | 0.00051924
31 | 0.98358 | -0.31598 | 0 | 0
32 | 0.98331 | -0.3214 | 0 | 0
33 | 0.98346 | -0.31841 | 0.0039805 | 0.00099761
34 | 0.98347 | -0.31822 | 0.0025579 | 0.00064106
35 | 0.98527 | -0.28117 | 0.0044174 | 0.0011071
36 | 0.98521 | -0.28234 | 0.0024826 | 0.00062219
37 | 0.98528 | -0.28087 | 0 | 0
38 | 0.98762 | -0.2358 | 0.0014263 | 0.00035747
39 | 0.98384 | -0.30877 | 0.0036865 | 0.00092392
40 | 0.98768 | -0.2347 | 0.001558 | 0.00039048
41 | 0.98212 | -0.34205 | 0.00092384 | 0.00023154
42 | 0.98322 | -0.32311 | 0.0026418 | 0.0006621
43 | 0.98324 | -0.32272 | 0.0026353 | 0.00066046
44 | 0.98775 | -0.23324 | 0.0012162 | 0.0003048
45 | 0.98202 | -0.34405 | 0.0047838 | 0.0011989
46 | 0.98781 | -0.23214 | 0.0045762 | 0.0011469
47 | 0.9818 | -0.3484 | 0.0022868 | 0.00057313
48 | 0.99371 | -0.11977 | 0.0037943 | 0.00095093
49 | 0.9967 | -0.062524 | 0 | 0
50 | 0.99414 | -0.11113 | 0.0044809 | 0.001123
51 | 1 | 0 | -0.44164 | -0.11254
52 | 0.99258 | -0.14082 | 0.0029315 | 0.0007347
53 | 0.97208 | -0.53888 | 0.0010866 | 0.00027232
54 | 0.97209 | -0.53876 | 0.0011501 | 0.00028824
55 | 0.99861 | -0.02637 | 0.0049825 | 0.0012487
56 | 0.99144 | -0.16261 | 0.0084915 | 0.0021282
57 | 0.9721 | -0.53862 | 0.0027031 | 0.00067747
58 | 0.99842 | -0.030029 | 0.0025642 | 0.00064264
59 | 0.97211 | -0.53838 | 0.0011656 | 0.00029212
60 | 0.99533 | -0.088935 | 0.0031291 | 0.00078422
61 | 0.98988 | -0.19398 | 0.0040017 | 0.0010029
62 | 0.99003 | -0.19111 | 0.0083553 | 0.002094
63 | 0.98894 | -0.21228 | 0.0053043 | 0.0013294
64 | 0.9913 | -0.16651 | 0.002671 | 0.00066941
65 | 0.98882 | -0.21448 | 0.0091324 | 0.0022888
66 | 0.99345 | -0.12498 | 0 | 0
67 | 0.98794 | -0.23167 | 0.0045492 | 0.0011401
68 | 0.99152 | -0.1622 | 0.0015699 | 0.00039344
69 | 0.99163 | -0.16001 | 0.002231 | 0.00055915
70 | 0.99144 | -0.16372 | 0.0031346 | 0.0007856
71 | 0.9908 | -0.1761 | 0.0027548 | 0.00069042
72 | 0.99082 | -0.1758 | 0.0041269 | 0.0010343
73 | 0.98956 | -0.20004 | 0.0031241 | 0.00078297
74 | 0.98889 | -0.21318 | 0 | 0
75 | 0.98831 | -0.22412 | 0.007959 | 0.0019947
76 | 0.98603 | -0.26884 | 0.0024669 | 0.00061826
77 | 0.98611 | -0.26733 | 0.0036155 | 0.00090612
78 | 0.98621 | -0.26532 | 0 | 0
79 | 0.9864 | -0.26156 | 0.0033758 | 0.00084606
80 | 0.98651 | -0.25944 | 0.0078209 | 0.0019601
81 | 0.98705 | -0.24896 | 0.0031083 | 0.00077901
82 | 0.98879 | -0.21511 | 0.002928 | 0.00073382
83 | 0.98863 | -0.21827 | 0.0034155 | 0.00085599
84 | 0.98808 | -0.22899 | 0 | 0
85 | 0.98847 | -0.22139 | 0 | 0
86 | 0.98798 | -0.23081 | 0 | 0
87 | 0.98712 | -0.24758 | 0.0041137 | 0.001031
88 | 0.98833 | -0.22398 | 0.0020899 | 0.00052377
89 | 0.98787 | -0.23306 | 0.0033328 | 0.00083529
90 | 0.98782 | -0.23405 | 0.0022352 | 0.00056019
91 | 0.9882 | -0.2265 | 0.0018369 | 0.00046037
92 | 0.98765 | -0.23729 | 0.0022074 | 0.00055324
93 | 0.98754 | -0.23935 | 0.0037064 | 0.00092892
94 | 0.97228 | -0.53501 | 0.0079137 | 0.0019834
95 | 0.97229 | -0.53487 | 0.0081351 | 0.0020388
96 | 0.97261 | -0.52851 | 0.0044652 | 0.0011191
97 | 0.98745 | -0.24081 | 0.004984 | 0.0012491
98 | 0.98734 | -0.24307 | 0.0012615 | 0.00031616
99 | 0.98618 | -0.26557 | 0.0033441 | 0.00083811
100 | 0.98584 | -0.2721 | 0.0023944 | 0.0006001
101 | 0.98563 | -0.27618 | 0.0035681 | 0.00089425
102 | 0.98535 | -0.28162 | 0 | 0
103 | 0.97432 | -0.49479 | 0.0017617 | 0.00044152
104 | 0.97378 | -0.50529 | 0.0028777 | 0.00072123
105 | 0.97444 | -0.49226 | 0.0015495 | 0.00038834
106 | 0.97312 | -0.51833 | 0.0058477 | 0.0014656
107 | 0.97482 | -0.48477 | 0.0046041 | 0.0011539
108 | 0.97517 | -0.47802 | 0 | 0
109 | 0.97514 | -0.47857 | 0.001484 | 0.00037192
110 | 0.97576 | -0.46645 | 0.0010511 | 0.00026342
111 | 0.97608 | -0.46008 | 0.00096731 | 0.00024243
112 | 0.98088 | -0.36621 | 0.0011339 | 0.00028419
113 | 0.98046 | -0.3745 | 0.0035719 | 0.0008952
114 | 0.9849 | -0.29048 | 0.0024438 | 0.00061248
115 | 0.98457 | -0.29685 | 0.0033933 | 0.00085044
116 | 0.98468 | -0.29478 | 0.0028775 | 0.00072117
117 | 0.98446 | -0.29909 | 0 | 0
118 | 0.97849 | -0.41292 | 0.0048408 | 0.0012132
119 | 0.97798 | -0.42284 | 0.0049282 | 0.0012351
120 | 0.97715 | -0.43921 | 0.0074235 | 0.0018605
121 | 0.98443 | -0.29973 | 0 | 0
122 | 0.98437 | -0.3009 | 0.001054 | 0.00026415
123 | 0.98441 | -0.30004 | 0.0010918 | 0.00027362
124 | 0.98434 | -0.30143 | 0.0010108 | 0.00025334
125 | 0.98441 | -0.30002 | 0.0015656 | 0.00039237
126 | 0.98423 | -0.30354 | 0.0011059 | 0.00027716
127 | 0.98261 | -0.33526 | 0.0021332 | 0.00053464
128 | 0.98266 | -0.33419 | 0 | 0
129 | 0.98268 | -0.33382 | 0.0012919 | 0.00032378
130 | 0.98283 | -0.33083 | 0.00080163 | 0.00020091
131 | 0.98295 | -0.32858 | 0 | 0
132 | 0.9831 | -0.32553 | 0.0025079 | 0.00062853
133 | 0.98312 | -0.32517 | 0.0014449 | 0.00036212
134 | 0.98331 | -0.32141 | 0.0040874 | 0.0010244
135 | 0.98376 | -0.31268 | 0.0012678 | 0.00031775
136 | 0.98335 | -0.32066 | 0.0016081 | 0.00040303
137 | 0.98378 | -0.31228 | 0.0039556 | 0.00099137
138 | 0.98815 | -0.22761 | 0.0017149 | 0.00042979
139 | 0.98813 | -0.22798 | 0.0022066 | 0.00055302
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0026355 | -0.00066051 | 0.0026357 | 0.00066016 | 2.4312e-07 | -3.5384e-07 | 0.0040032 | 0.004003 | 0.0040032 | 0.97964 | -0.39355 | 0.97973 | -0.39161 | 1.0998
1 | -0.0055097 | -0.0013805 | 0.0055118 | 0.0013808 | 2.1055e-06 | 3.3733e-07 | 0.008368 | 0.0083677 | 0.008368 | 0.97973 | -0.39161 | 0.98014 | -0.38359 | 2.2989
2 | -0.0055118 | -0.0013808 | 0.0055295 | 0.0013836 | 1.7676e-05 | 2.795e-06 | 0.0083677 | 0.0083646 | 0.0083677 | 0.98014 | -0.38359 | 0.98358 | -0.31633 | 2.2988
3 | -0.010241 | -0.0025645 | 0.010245 | 0.0025665 | 4.0399e-06 | 2.0156e-06 | 0.015493 | 0.015493 | 0.015493 | 0.98358 | -0.31633 | 0.984 | -0.30805 | 4.2563
4 | -0.01713 | -0.0042919 | 0.017136 | 0.0042959 | 6.7881e-06 | 4.0015e-06 | 0.025903 | 0.025903 | 0.025903 | 0.984 | -0.30805 | 0.98443 | -0.29973 | 7.1163
5 | -0.050168 | -0.012596 | 0.05018 | 0.012604 | 1.1674e-05 | 7.4022e-06 | 0.075711 | 0.075711 | 0.075711 | 0.98611 | -0.26674 | 0.98636 | -0.26187 | 20.7996
6 | 0.039593 | 0.0099459 | -0.039566 | -0.0099287 | 2.7284e-05 | 1.7202e-05 | 0.059753 | 0.059753 | 0.059753 | 0.98611 | -0.26674 | 0.98537 | -0.28119 | 16.4158
7 | -0.052161 | -0.0131 | 0.052187 | 0.013117 | 2.603e-05 | 1.6516e-05 | 0.078699 | 0.078699 | 0.078699 | 0.98636 | -0.26187 | 0.9869 | -0.25141 | 21.6207
8 | 0.03803 | 0.0095438 | -0.038026 | -0.0095415 | 3.5651e-06 | 2.2449e-06 | 0.057434 | 0.057434 | 0.057434 | 0.98537 | -0.28119 | 0.98527 | -0.28316 | 15.7786
9 | -0.054256 | -0.013635 | 0.054329 | 0.013682 | 7.38e-05 | 4.6856e-05 | 0.081819 | 0.081818 | 0.081819 | 0.9869 | -0.25141 | 0.98836 | -0.22296 | 22.4776
10 | 0.035957 | 0.0090228 | -0.035949 | -0.009018 | 7.638e-06 | 4.8004e-06 | 0.054308 | 0.054308 | 0.054308 | 0.98527 | -0.28316 | 0.98504 | -0.28761 | 14.9198
11 | -0.098089 | -0.024664 | 0.098203 | 0.024737 | 0.00011369 | 7.2582e-05 | 0.14771 | 0.14771 | 0.14771 | 0.98836 | -0.22296 | 0.98961 | -0.19872 | 40.5785
12 | 0.04376 | 0.010982 | -0.043739 | -0.010969 | 2.0844e-05 | 1.3176e-05 | 0.065887 | 0.065887 | 0.065887 | 0.98836 | -0.22296 | 0.98785 | -0.23296 | 18.1009
13 | 0.024231 | 0.0060812 | -0.024221 | -0.0060751 | 9.9001e-06 | 6.0854e-06 | 0.036607 | 0.036607 | 0.036607 | 0.98504 | -0.28761 | 0.9846 | -0.29619 | 10.0568
14 | -0.10005 | -0.025199 | 0.10009 | 0.025225 | 4.0485e-05 | 2.5849e-05 | 0.15048 | 0.15048 | 0.15048 | 0.98961 | -0.19872 | 0.99005 | -0.19027 | 41.3408
15 | 0.032386 | 0.0081236 | -0.032378 | -0.0081187 | 7.9529e-06 | 4.9758e-06 | 0.048787 | 0.048787 | 0.048787 | 0.98785 | -0.23296 | 0.98758 | -0.23811 | 13.4029
16 | 0.022191 | 0.0055664 | -0.022189 | -0.0055652 | 1.981e-06 | 1.2081e-06 | 0.033539 | 0.033539 | 0.033539 | 0.9846 | -0.29619 | 0.9845 | -0.29806 | 9.2141
17 | -0.11396 | -0.028701 | 0.11426 | 0.028893 | 0.00030028 | 0.00019183 | 0.17132 | 0.17132 | 0.17132 | 0.99005 | -0.19027 | 0.9929 | -0.13532 | 47.0672
18 | 0.020999 | 0.0052668 | -0.020988 | -0.0052601 | 1.0988e-05 | 6.6581e-06 | 0.031641 | 0.031641 | 0.031641 | 0.98758 | -0.23811 | 0.98702 | -0.24909 | 8.6927
19 | 0.019878 | 0.004986 | -0.019878 | -0.0049858 | 3.4316e-07 | 2.0673e-07 | 0.030046 | 0.030046 | 0.030046 | 0.9845 | -0.29806 | 0.98448 | -0.29842 | 8.2544
20 | -0.012016 | -0.0030113 | 0.012017 | 0.0030118 | 8.8156e-07 | 4.7266e-07 | 0.018117 | 0.018117 | 0.018117 | 0.98694 | -0.25063 | 0.98702 | -0.24909 | 4.9772
21 | 0.0020784 | 0.00052063 | -0.0020783 | -0.00052084 | 7.3786e-08 | -2.0884e-07 | 0.0031335 | 0.0031336 | 0.0031336 | 0.98694 | -0.25063 | 0.9869 | -0.25138 | 0.86087
22 | 0.0020783 | 0.00052084 | -0.0020783 | -0.00052087 | 9.917e-09 | -2.8066e-08 | 0.0031336 | 0.0031336 | 0.0031336 | 0.9869 | -0.25138 | 0.9869 | -0.25148 | 0.86087
23 | -0.013031 | -0.0032681 | 0.013034 | 0.00327 | 3.4127e-06 | 1.8833e-06 | 0.019655 | 0.019655 | 0.019655 | 0.98652 | -0.25927 | 0.9868 | -0.25378 | 5.3998
24 | 0.013031 | 0.0032681 | -0.013023 | -0.0032638 | 7.8776e-06 | 4.3479e-06 | 0.019655 | 0.019656 | 0.019656 | 0.98652 | -0.25927 | 0.98587 | -0.27196 | 5.3999
25 | -0.016378 | -0.0041081 | 0.016391 | 0.0041155 | 1.2759e-05 | 7.4525e-06 | 0.024698 | 0.024697 | 0.024698 | 0.9868 | -0.25378 | 0.98764 | -0.23745 | 6.7851
26 | -0.003908 | -0.00097943 | 0.0039088 | 0.00097917 | 8.0317e-07 | -2.6205e-07 | 0.0059157 | 0.0059154 | 0.0059157 | 0.983 | -0.32736 | 0.98322 | -0.32304 | 1.6252
27 | -0.0039088 | -0.00097917 | 0.0039091 | 0.00097907 | 3.0515e-07 | -9.9669e-08 | 0.0059154 | 0.0059153 | 0.0059154 | 0.98322 | -0.32304 | 0.98331 | -0.3214 | 1.6251
28 | -0.016391 | -0.0041155 | 0.016395 | 0.0041182 | 4.5214e-06 | 2.6407e-06 | 0.024697 | 0.024697 | 0.024697 | 0.98764 | -0.23745 | 0.98794 | -0.23167 | 6.785
29 | -0.11657 | -0.029472 | 0.11666 | 0.029527 | 8.6999e-05 | 5.5581e-05 | 0.17479 | 0.17479 | 0.17479 | 0.9929 | -0.13532 | 0.99371 | -0.11977 | 48.0184
30 | 0.017814 | 0.0044686 | -0.017804 | -0.0044625 | 1.0175e-05 | 6.0364e-06 | 0.026927 | 0.026927 | 0.026927 | 0.98448 | -0.29842 | 0.98387 | -0.31041 | 7.3976
31 | 0.015732 | 0.0039433 | -0.015728 | -0.0039409 | 4.1721e-06 | 2.4207e-06 | 0.023794 | 0.023794 | 0.023794 | 0.98387 | -0.31041 | 0.98358 | -0.31598 | 6.5368
32 | 0.007837 | 0.001964 | -0.0078362 | -0.0019637 | 8.3694e-07 | 3.3415e-07 | 0.011856 | 0.011856 | 0.011856 | 0.98358 | -0.31598 | 0.98347 | -0.31822 | 3.2572
33 | 0.007891 | 0.0019769 | -0.0078901 | -0.0019765 | 9.1335e-07 | 3.6765e-07 | 0.011938 | 0.011938 | 0.011938 | 0.98358 | -0.31598 | 0.98346 | -0.31841 | 3.2796
34 | -0.0039091 | -0.00097907 | 0.0039096 | 0.00097889 | 5.5788e-07 | -1.8238e-07 | 0.0059153 | 0.0059151 | 0.0059153 | 0.98331 | -0.3214 | 0.98346 | -0.31841 | 1.6251
35 | 0.0052783 | 0.0013226 | -0.0052771 | -0.0013225 | 1.1328e-06 | 1.2413e-07 | 0.0079861 | 0.0079863 | 0.0079863 | 0.98347 | -0.31822 | 0.98324 | -0.32272 | 2.194
36 | 0.0024827 | 0.00062194 | -0.0024826 | -0.00062219 | 1.386e-07 | -2.461e-07 | 0.0037494 | 0.0037496 | 0.0037496 | 0.98527 | -0.28117 | 0.98521 | -0.28234 | 1.0301
37 | -0.0069001 | -0.001729 | 0.0069002 | 0.0017291 | 9.6456e-08 | 3.1566e-08 | 0.010421 | 0.010421 | 0.010421 | 0.98527 | -0.28117 | 0.98528 | -0.28087 | 2.8629
38 | -0.087948 | -0.022312 | 0.088139 | 0.022434 | 0.00019106 | 0.00012191 | 0.13292 | 0.13292 | 0.13292 | 0.98528 | -0.28087 | 0.98762 | -0.2358 | 36.5163
39 | 0.081048 | 0.020583 | -0.080939 | -0.020514 | 0.00010868 | 6.9308e-05 | 0.1225 | 0.1225 | 0.1225 | 0.98528 | -0.28087 | 0.98384 | -0.30877 | 33.6534
40 | -0.089565 | -0.022792 | 0.08957 | 0.022795 | 4.7408e-06 | 3.0253e-06 | 0.13507 | 0.13507 | 0.13507 | 0.98762 | -0.2358 | 0.98768 | -0.2347 | 37.1066
41 | 0.077252 | 0.01959 | -0.077129 | -0.019511 | 0.00012335 | 7.8636e-05 | 0.11692 | 0.11692 | 0.11692 | 0.98384 | -0.30877 | 0.98212 | -0.34205 | 32.1217
42 | -0.091128 | -0.023185 | 0.091134 | 0.023189 | 6.42e-06 | 4.0972e-06 | 0.13742 | 0.13742 | 0.13742 | 0.98768 | -0.2347 | 0.98775 | -0.23324 | 37.7515
43 | 0.076205 | 0.01928 | -0.076198 | -0.019275 | 7.3232e-06 | 4.6683e-06 | 0.11552 | 0.11552 | 0.11552 | 0.98212 | -0.34205 | 0.98202 | -0.34405 | 31.7372
44 | -0.0026418 | -0.0006621 | 0.0026419 | 0.00066203 | 4.8728e-08 | -7.1912e-08 | 0.0039982 | 0.0039981 | 0.0039982 | 0.98322 | -0.32311 | 0.98324 | -0.32272 | 1.0984
45 | -0.09235 | -0.023494 | 0.092355 | 0.023497 | 4.8918e-06 | 3.1222e-06 | 0.13925 | 0.13925 | 0.13925 | 0.98775 | -0.23324 | 0.98781 | -0.23214 | 38.2548
46 | 0.071414 | 0.018076 | -0.071399 | -0.018067 | 1.4898e-05 | 9.4918e-06 | 0.10827 | 0.10827 | 0.10827 | 0.98202 | -0.34405 | 0.9818 | -0.3484 | 29.7458
47 | -0.096932 | -0.024644 | 0.097257 | 0.024852 | 0.00032587 | 0.00020803 | 0.14614 | 0.14614 | 0.14614 | 0.98781 | -0.23214 | 0.99144 | -0.16261 | 40.1486
48 | 0.069112 | 0.017493 | -0.069053 | -0.017456 | 5.905e-05 | 3.7611e-05 | 0.10481 | 0.10481 | 0.10481 | 0.9818 | -0.3484 | 0.98088 | -0.36621 | 28.7936
49 | -0.12045 | -0.030478 | 0.12078 | 0.03069 | 0.0003319 | 0.00021206 | 0.18047 | 0.18047 | 0.18047 | 0.99371 | -0.11977 | 0.9967 | -0.062524 | 49.5793
50 | 0.1137 | 0.02918 | -0.11343 | -0.029009 | 0.00026751 | 0.00017089 | 0.16999 | 0.16999 | 0.16999 | 0.9967 | -0.062524 | 0.99414 | -0.11113 | 46.6996
51 | -0.23448 | -0.05987 | 0.23519 | 0.060324 | 0.0007109 | 0.00045417 | 0.35045 | 0.35045 | 0.35045 | 0.9967 | -0.062524 | 1 | 0 | 48.1394
52 | 0.10895 | 0.027886 | -0.10879 | -0.027786 | 0.00015636 | 9.9865e-05 | 0.16328 | 0.16328 | 0.16328 | 0.99414 | -0.11113 | 0.99258 | -0.14082 | 44.8571
53 | 0.2048 | 0.052218 | -0.20454 | -0.052052 | 0.00026036 | 0.00016624 | 0.30506 | 0.30506 | 0.30506 | 1 | 0 | 0.99861 | -0.02637 | 41.9036
54 | 0.10586 | 0.027051 | -0.10575 | -0.02698 | 0.00011141 | 7.1152e-05 | 0.15889 | 0.15889 | 0.15889 | 0.99258 | -0.14082 | 0.99144 | -0.16261 | 43.6498
55 | -0.0010866 | -0.00027232 | 0.0010866 | 0.00027225 | 6.1872e-09 | -6.9974e-08 | 0.0016633 | 0.0016633 | 0.0016633 | 0.97208 | -0.53888 | 0.97209 | -0.53876 | 0.45695
56 | -0.0022367 | -0.0005605 | 0.0022367 | 0.00056047 | 1.5252e-08 | -3.3252e-08 | 0.0034238 | 0.0034238 | 0.0034238 | 0.97209 | -0.53876 | 0.9721 | -0.53862 | 0.9406
57 | 0.19956 | 0.050803 | -0.19952 | -0.050781 | 3.5195e-05 | 2.2469e-05 | 0.29763 | 0.29763 | 0.29763 | 0.99861 | -0.02637 | 0.99842 | -0.030029 | 40.8838
58 | -0.0049399 | -0.0012379 | 0.0049399 | 0.0012379 | 5.6597e-08 | 3.4975e-09 | 0.0075616 | 0.0075615 | 0.0075616 | 0.9721 | -0.53862 | 0.97211 | -0.53838 | 2.0773
59 | 0.19696 | 0.050138 | -0.1964 | -0.049782 | 0.00055768 | 0.00035602 | 0.29381 | 0.29381 | 0.29381 | 0.99842 | -0.030029 | 0.99533 | -0.088935 | 40.3589
60 | -0.0061055 | -0.0015301 | 0.0061065 | 0.0015303 | 9.7963e-07 | 2.5608e-07 | 0.0093457 | 0.0093455 | 0.0093457 | 0.97211 | -0.53838 | 0.97228 | -0.53501 | 2.5675
61 | 0.19327 | 0.048998 | -0.19293 | -0.048785 | 0.00033416 | 0.00021331 | 0.28913 | 0.28913 | 0.28913 | 0.99533 | -0.088935 | 0.99345 | -0.12498 | 39.7163
62 | -0.039434 | -0.0099112 | 0.039439 | 0.0099146 | 5.3977e-06 | 3.4019e-06 | 0.059288 | 0.059288 | 0.059288 | 0.98988 | -0.19398 | 0.99003 | -0.19111 | 16.288
63 | 0.035432 | 0.0089083 | -0.035401 | -0.0088889 | 3.0929e-05 | 1.9422e-05 | 0.053273 | 0.053273 | 0.053273 | 0.98988 | -0.19398 | 0.98894 | -0.21228 | 14.6354
64 | -0.047795 | -0.012009 | 0.047851 | 0.012044 | 5.6201e-05 | 3.5595e-05 | 0.071846 | 0.071846 | 0.071846 | 0.99003 | -0.19111 | 0.9913 | -0.16651 | 19.738
65 | 0.030097 | 0.0075595 | -0.030094 | -0.0075575 | 3.1558e-06 | 1.9671e-06 | 0.045292 | 0.045292 | 0.045292 | 0.98894 | -0.21228 | 0.98882 | -0.21448 | 12.4428
66 | -0.050522 | -0.012714 | 0.050622 | 0.012777 | 0.00010049 | 6.3715e-05 | 0.075855 | 0.075855 | 0.075855 | 0.9913 | -0.16651 | 0.99345 | -0.12498 | 20.8394
67 | 0.020962 | 0.0052687 | -0.020944 | -0.0052583 | 1.7189e-05 | 1.0411e-05 | 0.031549 | 0.031549 | 0.031549 | 0.98882 | -0.21448 | 0.98794 | -0.23167 | 8.6674
68 | 0.059309 | 0.014975 | -0.059203 | -0.014908 | 0.00010558 | 6.7109e-05 | 0.088873 | 0.088873 | 0.088873 | 0.99345 | -0.12498 | 0.99152 | -0.1622 | 24.4157
69 | 0.083004 | 0.021032 | -0.082864 | -0.020943 | 0.00013944 | 8.8931e-05 | 0.12441 | 0.12441 | 0.12441 | 0.99345 | -0.12498 | 0.99163 | -0.16001 | 34.1777
70 | 0.057633 | 0.014514 | -0.057629 | -0.014512 | 4.1708e-06 | 2.6502e-06 | 0.086517 | 0.086517 | 0.086517 | 0.99152 | -0.1622 | 0.99144 | -0.16372 | 23.7684
71 | 0.080633 | 0.020384 | -0.080571 | -0.020345 | 6.219e-05 | 3.9656e-05 | 0.12106 | 0.12106 | 0.12106 | 0.99163 | -0.16001 | 0.9908 | -0.1761 | 33.258
72 | 0.054494 | 0.013726 | -0.054463 | -0.013706 | 3.1471e-05 | 1.998e-05 | 0.081813 | 0.081813 | 0.081813 | 0.99144 | -0.16372 | 0.99082 | -0.1758 | 22.476
73 | 0.077816 | 0.019654 | -0.077727 | -0.019597 | 8.916e-05 | 5.6839e-05 | 0.11692 | 0.11692 | 0.11692 | 0.9908 | -0.1761 | 0.98956 | -0.20004 | 32.1214
74 | 0.050336 | 0.012672 | -0.050246 | -0.012615 | 8.977e-05 | 5.6915e-05 | 0.075615 | 0.075615 | 0.075615 | 0.99082 | -0.1758 | 0.98889 | -0.21318 | 20.7734
75 | 0.074603 | 0.018814 | -0.074517 | -0.01876 | 8.5894e-05 | 5.4739e-05 | 0.11222 | 0.11222 | 0.11222 | 0.98956 | -0.20004 | 0.98831 | -0.22412 | 30.8308
76 | 0.038977 | 0.0097899 | -0.038973 | -0.0097876 | 3.5853e-06 | 2.259e-06 | 0.058657 | 0.058657 | 0.058657 | 0.98889 | -0.21318 | 0.98879 | -0.21511 | 16.1146
77 | 0.011269 | 0.0028252 | -0.011267 | -0.0028237 | 2.735e-06 | 1.4251e-06 | 0.016958 | 0.016958 | 0.016958 | 0.98889 | -0.21318 | 0.98863 | -0.21827 | 4.6588
78 | 0.066558 | 0.016765 | -0.066505 | -0.016731 | 5.3065e-05 | 3.3781e-05 | 0.10024 | 0.10024 | 0.10024 | 0.98831 | -0.22412 | 0.98745 | -0.24081 | 27.5387
79 | -0.0024669 | -0.00061826 | 0.0024671 | 0.00061794 | 1.7736e-07 | -3.2183e-07 | 0.0037228 | 0.0037226 | 0.0037228 | 0.98603 | -0.26884 | 0.98611 | -0.26733 | 1.0227
80 | -0.0060825 | -0.0015241 | 0.0060831 | 0.0015242 | 5.8335e-07 | 1.3774e-07 | 0.0091783 | 0.0091782 | 0.0091783 | 0.98611 | -0.26733 | 0.98621 | -0.26532 | 2.5215
81 | -0.0060831 | -0.0015242 | 0.0060842 | 0.0015245 | 1.0877e-06 | 2.5668e-07 | 0.0091782 | 0.0091781 | 0.0091782 | 0.98621 | -0.26532 | 0.9864 | -0.26156 | 2.5215
82 | -0.00946 | -0.0023705 | 0.009461 | 0.002371 | 9.5797e-07 | 4.5296e-07 | 0.014271 | 0.01427 | 0.014271 | 0.9864 | -0.26156 | 0.98651 | -0.25944 | 3.9205
83 | -0.017282 | -0.0043311 | 0.017291 | 0.0043362 | 8.6341e-06 | 5.093e-06 | 0.026067 | 0.026067 | 0.026067 | 0.98651 | -0.25944 | 0.98705 | -0.24896 | 7.1613
84 | -0.020399 | -0.0051152 | 0.0204 | 0.005116 | 1.3374e-06 | 8.0771e-07 | 0.030753 | 0.030753 | 0.030753 | 0.98705 | -0.24896 | 0.98712 | -0.24758 | 8.4486
85 | 0.036045 | 0.0090538 | -0.036021 | -0.0090388 | 2.3867e-05 | 1.4998e-05 | 0.054251 | 0.054251 | 0.054251 | 0.98879 | -0.21511 | 0.98808 | -0.22899 | 14.9041
86 | 0.0078513 | 0.0019678 | -0.0078501 | -0.0019673 | 1.1656e-06 | 4.6061e-07 | 0.011817 | 0.011817 | 0.011817 | 0.98863 | -0.21827 | 0.98847 | -0.22139 | 3.2465
87 | 0.011486 | 0.0028784 | -0.011485 | -0.0028779 | 9.9631e-07 | 5.2391e-07 | 0.017297 | 0.017297 | 0.017297 | 0.98808 | -0.22899 | 0.98798 | -0.23081 | 4.752
88 | 0.024536 | 0.0061603 | -0.024514 | -0.006147 | 2.1735e-05 | 1.3367e-05 | 0.036954 | 0.036954 | 0.036954 | 0.98808 | -0.22899 | 0.98712 | -0.24758 | 10.1522
89 | 0.0078501 | 0.0019673 | -0.0078492 | -0.0019669 | 9.6794e-07 | 3.8259e-07 | 0.011817 | 0.011817 | 0.011817 | 0.98847 | -0.22139 | 0.98833 | -0.22398 | 3.2465
90 | 0.0033332 | 0.00083503 | -0.0033328 | -0.00083529 | 3.5667e-07 | -2.5497e-07 | 0.00502 | 0.0050202 | 0.0050202 | 0.98798 | -0.23081 | 0.98787 | -0.23306 | 1.3792
91 | 0.0081515 | 0.0020429 | -0.0081503 | -0.0020424 | 1.2571e-06 | 5.1981e-07 | 0.012277 | 0.012277 | 0.012277 | 0.98798 | -0.23081 | 0.98782 | -0.23405 | 3.3729
92 | 0.0057593 | 0.0014431 | -0.0057586 | -0.001443 | 6.9142e-07 | 1.2829e-07 | 0.008671 | 0.0086711 | 0.0086711 | 0.98833 | -0.22398 | 0.9882 | -0.2265 | 2.3822
93 | 0.0059151 | 0.0014822 | -0.0059142 | -0.001482 | 9.114e-07 | 1.9148e-07 | 0.0089103 | 0.0089104 | 0.0089104 | 0.98782 | -0.23405 | 0.98765 | -0.23729 | 2.4479
94 | 0.0039217 | 0.00098264 | -0.0039215 | -0.00098271 | 2.0671e-07 | -7.0215e-08 | 0.0059051 | 0.0059052 | 0.0059052 | 0.9882 | -0.2265 | 0.98815 | -0.22761 | 1.6223
95 | 0.0037068 | 0.00092875 | -0.0037064 | -0.00092892 | 3.6459e-07 | -1.6554e-07 | 0.0055846 | 0.0055848 | 0.0055848 | 0.98765 | -0.23729 | 0.98754 | -0.23935 | 1.5343
96 | -0.01402 | -0.0035137 | 0.01402 | 0.0035137 | 9.5578e-08 | 5.4304e-08 | 0.021457 | 0.021457 | 0.021457 | 0.97228 | -0.53501 | 0.97229 | -0.53487 | 5.8948
97 | -0.022155 | -0.0055526 | 0.022162 | 0.0055567 | 6.7116e-06 | 4.1023e-06 | 0.033907 | 0.033907 | 0.033907 | 0.97229 | -0.53487 | 0.97261 | -0.52851 | 9.3151
98 | -0.026627 | -0.0066758 | 0.02664 | 0.0066838 | 1.2923e-05 | 8.0128e-06 | 0.040739 | 0.040738 | 0.040739 | 0.97261 | -0.52851 | 0.97312 | -0.51833 | 11.1919
99 | 0.061521 | 0.015482 | -0.061515 | -0.015478 | 6.6421e-06 | 4.2246e-06 | 0.09273 | 0.09273 | 0.09273 | 0.98745 | -0.24081 | 0.98734 | -0.24307 | 25.4754
100 | 0.060253 | 0.015162 | -0.060188 | -0.015121 | 6.4715e-05 | 4.1151e-05 | 0.090829 | 0.090829 | 0.090829 | 0.98734 | -0.24307 | 0.98618 | -0.26557 | 24.9531
101 | 0.056844 | 0.014282 | -0.056827 | -0.014271 | 1.7703e-05 | 1.1248e-05 | 0.085784 | 0.085784 | 0.085784 | 0.98618 | -0.26557 | 0.98584 | -0.2721 | 23.5669
102 | 0.054432 | 0.013671 | -0.054422 | -0.013664 | 1.061e-05 | 6.7367e-06 | 0.082169 | 0.08217 | 0.08217 | 0.98584 | -0.2721 | 0.98563 | -0.27618 | 22.574
103 | 0.050853 | 0.01277 | -0.05084 | -0.012762 | 1.3181e-05 | 8.3597e-06 | 0.076783 | 0.076783 | 0.076783 | 0.98563 | -0.27618 | 0.98535 | -0.28162 | 21.0942
104 | 0.027134 | 0.0068132 | -0.027122 | -0.0068061 | 1.147e-05 | 7.1087e-06 | 0.04098 | 0.04098 | 0.04098 | 0.98535 | -0.28162 | 0.9849 | -0.29048 | 11.2583
105 | 0.023706 | 0.0059485 | -0.023689 | -0.005938 | 1.7204e-05 | 1.0555e-05 | 0.035802 | 0.035803 | 0.035803 | 0.98535 | -0.28162 | 0.98457 | -0.29685 | 9.8359
106 | 0.035404 | 0.0088944 | -0.035386 | -0.0088832 | 1.7731e-05 | 1.1147e-05 | 0.054077 | 0.054078 | 0.054078 | 0.97432 | -0.49479 | 0.97378 | -0.50529 | 14.8565
107 | -0.037165 | -0.0093359 | 0.03717 | 0.0093387 | 4.4876e-06 | 2.8258e-06 | 0.056768 | 0.056768 | 0.056768 | 0.97432 | -0.49479 | 0.97444 | -0.49226 | 15.5956
108 | 0.032508 | 0.008162 | -0.032488 | -0.0081493 | 2.021e-05 | 1.2663e-05 | 0.04968 | 0.04968 | 0.04968 | 0.97378 | -0.50529 | 0.97312 | -0.51833 | 13.6484
109 | -0.038719 | -0.0097271 | 0.038733 | 0.0097358 | 1.3837e-05 | 8.7244e-06 | 0.059134 | 0.059134 | 0.059134 | 0.97444 | -0.49226 | 0.97482 | -0.48477 | 16.2456
110 | -0.043337 | -0.01089 | 0.043351 | 0.010899 | 1.3985e-05 | 8.8442e-06 | 0.066162 | 0.066162 | 0.066162 | 0.97482 | -0.48477 | 0.97517 | -0.47802 | 18.1763
111 | 0.001484 | 0.00037169 | -0.001484 | -0.00037192 | 3.8862e-08 | -2.2727e-07 | 0.0022644 | 0.0022645 | 0.0022645 | 0.97517 | -0.47802 | 0.97514 | -0.47857 | 0.6221
112 | -0.044835 | -0.01127 | 0.04486 | 0.011286 | 2.4766e-05 | 1.5674e-05 | 0.068426 | 0.068426 | 0.068426 | 0.97517 | -0.47802 | 0.97576 | -0.46645 | 18.7984
113 | -0.045911 | -0.011549 | 0.045925 | 0.011558 | 1.398e-05 | 8.8523e-06 | 0.070029 | 0.070029 | 0.070029 | 0.97576 | -0.46645 | 0.97608 | -0.46008 | 19.2387
114 | -0.046892 | -0.011801 | 0.046939 | 0.01183 | 4.683e-05 | 2.9665e-05 | 0.071504 | 0.071503 | 0.071504 | 0.97608 | -0.46008 | 0.97715 | -0.43921 | 19.6438
115 | 0.067919 | 0.017172 | -0.067892 | -0.017154 | 2.7003e-05 | 1.7196e-05 | 0.10309 | 0.10309 | 0.10309 | 0.98088 | -0.36621 | 0.98046 | -0.3745 | 28.321
116 | 0.06432 | 0.016259 | -0.064202 | -0.016184 | 0.00011827 | 7.5276e-05 | 0.097668 | 0.097668 | 0.097668 | 0.98046 | -0.3745 | 0.97849 | -0.41292 | 26.8318
117 | 0.024679 | 0.0061936 | -0.024673 | -0.0061905 | 5.0509e-06 | 3.1093e-06 | 0.037288 | 0.037288 | 0.037288 | 0.9849 | -0.29048 | 0.98468 | -0.29478 | 10.244
118 | 0.020296 | 0.0050875 | -0.020294 | -0.0050862 | 2.1615e-06 | 1.3055e-06 | 0.030674 | 0.030674 | 0.030674 | 0.98457 | -0.29685 | 0.98446 | -0.29909 | 8.427
119 | 0.021796 | 0.0054693 | -0.021791 | -0.005466 | 5.4497e-06 | 3.3175e-06 | 0.03294 | 0.03294 | 0.03294 | 0.98468 | -0.29478 | 0.98441 | -0.30002 | 9.0494
120 | 0.018229 | 0.0045696 | -0.018228 | -0.0045693 | 5.5999e-07 | 3.3339e-07 | 0.027553 | 0.027553 | 0.027553 | 0.98446 | -0.29909 | 0.98443 | -0.29973 | 7.5696
121 | 0.002065 | 0.00051663 | -0.0020648 | -0.00051713 | 1.7788e-07 | -5.0524e-07 | 0.0031209 | 0.0031212 | 0.0031212 | 0.98446 | -0.29909 | 0.98437 | -0.3009 | 0.85746
122 | 0.059361 | 0.014971 | -0.059333 | -0.014953 | 2.8169e-05 | 1.7913e-05 | 0.090306 | 0.090306 | 0.090306 | 0.97849 | -0.41292 | 0.97798 | -0.42284 | 24.8094
123 | 0.054405 | 0.013718 | -0.054362 | -0.013691 | 4.2575e-05 | 2.704e-05 | 0.082808 | 0.082808 | 0.082808 | 0.97798 | -0.42284 | 0.97715 | -0.43921 | 22.7495
124 | 0.0010918 | 0.00027343 | -0.0010918 | -0.00027362 | 1.6292e-08 | -1.9239e-07 | 0.0016502 | 0.0016503 | 0.0016503 | 0.98443 | -0.29973 | 0.98441 | -0.30004 | 0.45338
125 | 0.0010109 | 0.00025298 | -0.0010108 | -0.00025334 | 2.5484e-08 | -3.5369e-07 | 0.0015279 | 0.0015281 | 0.0015281 | 0.98437 | -0.3009 | 0.98434 | -0.30143 | 0.4198
126 | 0.020225 | 0.0050736 | -0.020222 | -0.0050716 | 3.3899e-06 | 2.0466e-06 | 0.030573 | 0.030573 | 0.030573 | 0.98441 | -0.30002 | 0.98423 | -0.30354 | 8.3993
127 | 0.019116 | 0.0047944 | -0.019108 | -0.0047897 | 7.9582e-06 | 4.7705e-06 | 0.028902 | 0.028902 | 0.028902 | 0.98423 | -0.30354 | 0.98378 | -0.31228 | 7.94
128 | -0.0021332 | -0.00053464 | 0.0021333 | 0.00053436 | 1.0879e-07 | -2.8254e-07 | 0.0032305 | 0.0032304 | 0.0032305 | 0.98261 | -0.33526 | 0.98266 | -0.33419 | 0.8875
129 | -0.0021333 | -0.00053436 | 0.0021334 | 0.00053426 | 3.7757e-08 | -9.8071e-08 | 0.0032304 | 0.0032303 | 0.0032304 | 0.98266 | -0.33419 | 0.98268 | -0.33382 | 0.88746
130 | -0.0034253 | -0.00085804 | 0.0034258 | 0.00085774 | 4.8711e-07 | -3.0012e-07 | 0.0051865 | 0.0051863 | 0.0051865 | 0.98268 | -0.33382 | 0.98283 | -0.33083 | 1.4249
131 | -0.0042274 | -0.0010586 | 0.0042278 | 0.0010586 | 4.5397e-07 | -8.4058e-08 | 0.0064 | 0.0063999 | 0.0064 | 0.98283 | -0.33083 | 0.98295 | -0.32858 | 1.7582
132 | -0.0042278 | -0.0010586 | 0.0042285 | 0.0010584 | 6.1247e-07 | -1.1357e-07 | 0.0063999 | 0.0063997 | 0.0063999 | 0.98295 | -0.32858 | 0.9831 | -0.32553 | 1.7582
133 | -0.0067363 | -0.001687 | 0.0067365 | 0.001687 | 1.1705e-07 | 3.6839e-08 | 0.010196 | 0.010196 | 0.010196 | 0.9831 | -0.32553 | 0.98312 | -0.32517 | 2.801
134 | -0.0081813 | -0.0020491 | 0.0081828 | 0.0020497 | 1.4654e-06 | 6.1462e-07 | 0.012382 | 0.012382 | 0.012382 | 0.98312 | -0.32517 | 0.98331 | -0.32141 | 3.4018
135 | -0.01227 | -0.0030742 | 0.012271 | 0.0030744 | 4.35e-07 | 2.3572e-07 | 0.018568 | 0.018568 | 0.018568 | 0.98331 | -0.32141 | 0.98335 | -0.32066 | 5.101
136 | 0.013884 | 0.0034804 | -0.013879 | -0.0034774 | 5.2791e-06 | 2.9735e-06 | 0.021001 | 0.021001 | 0.021001 | 0.98376 | -0.31268 | 0.98335 | -0.32066 | 5.7695
137 | -0.015152 | -0.0037981 | 0.015152 | 0.0037983 | 2.9268e-07 | 1.6845e-07 | 0.022919 | 0.022919 | 0.022919 | 0.98376 | -0.31268 | 0.98378 | -0.31228 | 6.2963
138 | 0.0022066 | 0.00055292 | -0.0022066 | -0.00055302 | 3.9259e-08 | -9.6336e-08 | 0.0033228 | 0.0033228 | 0.0033228 | 0.98815 | -0.22761 | 0.98813 | -0.22798 | 0.91287

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44473 | 0.11332

## res_load
| p_mw | q_mvar
0 | 0.0026355 | 0.00066051
1 | 0.002874 | 0.0007203
2 | 0.0047118 | 0.0011809
3 | 0.0068843 | 0.0017254
4 | 0.010575 | 0.0026503
5 | 0.0019811 | 0.00049652
6 | 0.0015359 | 0.00038494
7 | 0.0020688 | 0.00051848
8 | 0.0020698 | 0.00051874
9 | 0.011718 | 0.0029368
10 | 0.0018454 | 0.00046251
11 | 0.011353 | 0.0028453
12 | 0.0020298 | 0.00050872
13 | 0.013869 | 0.0034758
14 | 0.011379 | 0.0028519
15 | 0.0023112 | 0.00057925
16 | 0.009938 | 0.0024907
17 | 0.0089708 | 0.0022483
18 | 0.0020783 | 0.00052087
19 | 0.0033439 | 0.00083806
20 | 0.013023 | 0.0032638
21 | 0.003908 | 0.00097943
22 | 0.0023103 | 0.00057903
23 | 0.0020636 | 0.00051718
24 | 0.0020718 | 0.00051924
25 | 0.0039805 | 0.00099761
26 | 0.0025579 | 0.00064106
27 | 0.0044174 | 0.0011071
28 | 0.0024826 | 0.00062219
29 | 0.0014263 | 0.00035747
30 | 0.0036865 | 0.00092392
31 | 0.001558 | 0.00039048
32 | 0.00092384 | 0.00023154
33 | 0.0026418 | 0.0006621
34 | 0.0026353 | 0.00066046
35 | 0.0012162 | 0.0003048
36 | 0.0047838 | 0.0011989
37 | 0.0045762 | 0.0011469
38 | 0.0022868 | 0.00057313
39 | 0.0037943 | 0.00095093
40 | 0.0044809 | 0.001123
41 | 0.0030942 | 0.00077548
42 | 0.0029315 | 0.0007347
43 | 0.0010866 | 0.00027232
44 | 0.0011501 | 0.00028824
45 | 0.0049825 | 0.0012487
46 | 0.0084915 | 0.0021282
47 | 0.0027031 | 0.00067747
48 | 0.0025642 | 0.00064264
49 | 0.0011656 | 0.00029212
50 | 0.0031291 | 0.00078422
51 | 0.0040017 | 0.0010029
52 | 0.0083553 | 0.002094
53 | 0.0053043 | 0.0013294
54 | 0.002671 | 0.00066941
55 | 0.0091324 | 0.0022888
56 | 0.0045492 | 0.0011401
57 | 0.0015699 | 0.00039344
58 | 0.002231 | 0.00055915
59 | 0.0031346 | 0.0007856
60 | 0.0027548 | 0.00069042
61 | 0.0041269 | 0.0010343
62 | 0.0031241 | 0.00078297
63 | 0.007959 | 0.0019947
64 | 0.0024669 | 0.00061826
65 | 0.0036155 | 0.00090612
66 | 0.0033758 | 0.00084606
67 | 0.0078209 | 0.0019601
68 | 0.0031083 | 0.00077901
69 | 0.002928 | 0.00073382
70 | 0.0034155 | 0.00085599
71 | 0.0041137 | 0.001031
72 | 0.0020899 | 0.00052377
73 | 0.0033328 | 0.00083529
74 | 0.0022352 | 0.00056019
75 | 0.0018369 | 0.00046037
76 | 0.0022074 | 0.00055324
77 | 0.0037064 | 0.00092892
78 | 0.0079137 | 0.0019834
79 | 0.0081351 | 0.0020388
80 | 0.0044652 | 0.0011191
81 | 0.004984 | 0.0012491
82 | 0.0012615 | 0.00031616
83 | 0.0033441 | 0.00083811
84 | 0.0023944 | 0.0006001
85 | 0.0035681 | 0.00089425
86 | 0.0017617 | 0.00044152
87 | 0.0028777 | 0.00072123
88 | 0.0015495 | 0.00038834
89 | 0.0058477 | 0.0014656
90 | 0.0046041 | 0.0011539
91 | 0.001484 | 0.00037192
92 | 0.0010511 | 0.00026342
93 | 0.00096731 | 0.00024243
94 | 0.0011339 | 0.00028419
95 | 0.0035719 | 0.0008952
96 | 0.0024438 | 0.00061248
97 | 0.0033933 | 0.00085044
98 | 0.0028775 | 0.00072117
99 | 0.0048408 | 0.0012132
100 | 0.0049282 | 0.0012351
101 | 0.0074235 | 0.0018605
102 | 0.001054 | 0.00026415
103 | 0.0010918 | 0.00027362
104 | 0.0010108 | 0.00025334
105 | 0.0015656 | 0.00039237
106 | 0.0011059 | 0.00027716
107 | 0.0021332 | 0.00053464
108 | 0.0012919 | 0.00032378
109 | 0.00080163 | 0.00020091
110 | 0.0025079 | 0.00062853
111 | 0.0014449 | 0.00036212
112 | 0.0040874 | 0.0010244
113 | 0.0012678 | 0.00031775
114 | 0.0016081 | 0.00040303
115 | 0.0039556 | 0.00099137
116 | 0.0017149 | 0.00042979
117 | 0.0022066 | 0.00055302

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1