## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_154-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_154-6_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_154-6_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_154-6_0_4_node_257 | 0.4 | n |  | TRUE
4 | bus_LV_154-6_0_4_node_256 | 0.4 | n |  | TRUE
5 | bus_LV_154-6_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_154-6_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_154-6_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_154-6_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_154-6_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_154-6_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_154-6_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_154-6_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_154-6_0_4_node_214 | 0.4 | n |  | TRUE
14 | bus_LV_154-6_0_4_node_213 | 0.4 | n |  | TRUE
15 | bus_LV_154-6_0_4_node_215 | 0.4 | n |  | TRUE
16 | bus_LV_154-6_0_4_node_210 | 0.4 | n |  | TRUE
17 | bus_LV_154-6_0_4_node_216 | 0.4 | n |  | TRUE
18 | bus_LV_154-6_0_4_node_209 | 0.4 | n |  | TRUE
19 | bus_LV_154-6_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_154-6_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_154-6_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_154-6_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_154-6_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_154-6_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_154-6_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_154-6_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_154-6_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_154-6_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_154-6_0_4_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_154-6_0_4_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_154-6_0_4_node_87 | 0.4 | n |  | TRUE
32 | bus_LV_154-6_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_154-6_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_154-6_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_154-6_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_154-6_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_154-6_0_4_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_154-6_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_154-6_0_4_node_91 | 0.4 | n |  | TRUE
40 | bus_LV_154-6_0_4_node_93 | 0.4 | n |  | TRUE
41 | bus_LV_154-6_0_4_node_89 | 0.4 | n |  | TRUE
42 | bus_LV_154-6_0_4_node_67 | 0.4 | n |  | TRUE
43 | bus_LV_154-6_0_4_node_68 | 0.4 | n |  | TRUE
44 | bus_LV_154-6_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_154-6_0_4_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_154-6_0_4_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_154-6_0_4_node_76 | 0.4 | n |  | TRUE
48 | bus_LV_154-6_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_154-6_0_4_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_154-6_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_154-6_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_154-6_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_154-6_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_154-6_0_4_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_154-6_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_154-6_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_154-6_0_4_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_154-6_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_154-6_0_4_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_154-6_0_4_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_154-6_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_154-6_0_4_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_154-6_0_4_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_154-6_0_4_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_154-6_0_4_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_154-6_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_154-6_0_4_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_154-6_0_4_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_154-6_0_4_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_154-6_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_154-6_0_4_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_154-6_0_4_node_247 | 0.4 | n |  | TRUE
73 | bus_LV_154-6_0_4_node_243 | 0.4 | n |  | TRUE
74 | bus_LV_154-6_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_154-6_0_4_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_154-6_0_4_node_225 | 0.4 | n |  | TRUE
77 | bus_LV_154-6_0_4_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_154-6_0_4_node_263 | 0.4 | n |  | TRUE
79 | bus_LV_154-6_0_4_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_154-6_0_4_node_244 | 0.4 | n |  | TRUE
81 | bus_LV_154-6_0_4_node_245 | 0.4 | n |  | TRUE
82 | bus_LV_154-6_0_4_node_242 | 0.4 | n |  | TRUE
83 | bus_LV_154-6_0_4_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_154-6_0_4_node_84 | 0.4 | n |  | TRUE
85 | bus_LV_154-6_0_4_node_48 | 0.4 | n |  | TRUE
86 | bus_LV_154-6_0_4_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_154-6_0_4_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_154-6_0_4_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_154-6_0_4_node_55 | 0.4 | n |  | TRUE
90 | bus_LV_154-6_0_4_node_52 | 0.4 | n |  | TRUE
91 | bus_LV_154-6_0_4_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_154-6_0_4_node_54 | 0.4 | n |  | TRUE
93 | bus_LV_154-6_0_4_node_56 | 0.4 | n |  | TRUE
94 | bus_LV_154-6_0_4_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_154-6_0_4_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_154-6_0_4_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_154-6_0_4_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_154-6_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_154-6_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_154-6_0_4_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_154-6_0_4_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_154-6_0_4_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_154-6_0_4_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_154-6_0_4_node_226 | 0.4 | n |  | TRUE
105 | bus_LV_154-6_0_4_node_241 | 0.4 | n |  | TRUE
106 | bus_LV_154-6_0_4_node_236 | 0.4 | n |  | TRUE
107 | bus_LV_154-6_0_4_node_264 | 0.4 | n |  | TRUE
108 | bus_LV_154-6_0_4_node_246 | 0.4 | n |  | TRUE
109 | bus_LV_154-6_0_4_node_262 | 0.4 | n |  | TRUE
110 | bus_LV_154-6_0_4_node_260 | 0.4 | n |  | TRUE
111 | bus_LV_154-6_0_4_node_248 | 0.4 | n |  | TRUE
112 | bus_LV_154-6_0_4_node_249 | 0.4 | n |  | TRUE
113 | bus_LV_154-6_0_4_node_233 | 0.4 | n |  | TRUE
114 | bus_LV_154-6_0_4_node_224 | 0.4 | n |  | TRUE
115 | bus_LV_154-6_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_154-6_0_4_node_94 | 0.4 | n |  | TRUE
117 | bus_LV_154-6_0_4_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_154-6_0_4_node_231 | 0.4 | n |  | TRUE
119 | bus_LV_154-6_0_4_node_222 | 0.4 | n |  | TRUE
120 | bus_LV_154-6_0_4_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_154-6_0_4_node_98 | 0.4 | n |  | TRUE
122 | bus_LV_154-6_0_4_node_85 | 0.4 | n |  | TRUE
123 | bus_LV_154-6_0_4_node_95 | 0.4 | n |  | TRUE
124 | bus_LV_154-6_0_4_node_96 | 0.4 | n |  | TRUE
125 | bus_LV_154-6_0_4_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_154-6_0_4_node_102 | 0.4 | n |  | TRUE
127 | bus_LV_154-6_0_4_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_154-6_0_4_node_103 | 0.4 | n |  | TRUE
129 | bus_LV_154-6_0_4_node_145 | 0.4 | n |  | TRUE
130 | bus_LV_154-6_0_4_node_105 | 0.4 | n |  | TRUE
131 | bus_LV_154-6_0_4_node_146 | 0.4 | n |  | TRUE
132 | bus_LV_154-6_0_4_node_144 | 0.4 | n |  | TRUE
133 | bus_LV_154-6_0_4_node_106 | 0.4 | n |  | TRUE
134 | bus_LV_154-6_0_4_node_107 | 0.4 | n |  | TRUE
135 | bus_LV_154-6_0_4_node_130 | 0.4 | n |  | TRUE
136 | bus_LV_154-6_0_4_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_154-6_0_4_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_154-6_0_4_node_109 | 0.4 | n |  | TRUE
139 | bus_LV_154-6_0_4_node_110 | 0.4 | n |  | TRUE
140 | bus_LV_154-6_0_4_node_111 | 0.4 | n |  | TRUE
141 | bus_LV_154-6_0_4_node_112 | 0.4 | n |  | TRUE
142 | bus_LV_154-6_0_4_node_113 | 0.4 | n |  | TRUE
143 | bus_LV_154-6_0_4_node_114 | 0.4 | n |  | TRUE
144 | bus_LV_154-6_0_4_node_128 | 0.4 | n |  | TRUE
145 | bus_LV_154-6_0_4_node_117 | 0.4 | n |  | TRUE
146 | bus_LV_154-6_0_4_node_118 | 0.4 | n |  | TRUE
147 | bus_LV_154-6_0_4_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_154-6_0_4_node_119 | 0.4 | n |  | TRUE
149 | bus_LV_154-6_0_4_node_120 | 0.4 | n |  | TRUE
150 | bus_LV_154-6_0_4_node_133 | 0.4 | n |  | TRUE
151 | bus_LV_154-6_0_4_node_198 | 0.4 | n |  | TRUE
152 | bus_LV_154-6_0_4_node_126 | 0.4 | n |  | TRUE
153 | bus_LV_154-6_0_4_node_199 | 0.4 | n |  | TRUE
154 | bus_LV_154-6_0_4_node_121 | 0.4 | n |  | TRUE
155 | bus_LV_154-6_0_4_node_122 | 0.4 | n |  | TRUE
156 | bus_LV_154-6_0_4_node_123 | 0.4 | n |  | TRUE
157 | bus_LV_154-6_0_4_node_124 | 0.4 | n |  | TRUE
158 | bus_LV_154-6_0_4_node_125 | 0.4 | n |  | TRUE
159 | bus_LV_154-6_0_4_node_127 | 0.4 | n |  | TRUE
160 | bus_LV_154-6_0_4_node_134 | 0.4 | n |  | TRUE
161 | bus_LV_154-6_0_4_node_135 | 0.4 | n |  | TRUE
162 | bus_LV_154-6_0_4_node_136 | 0.4 | n |  | TRUE
163 | bus_LV_154-6_0_4_node_195 | 0.4 | n |  | TRUE
164 | bus_LV_154-6_0_4_node_193 | 0.4 | n |  | TRUE
165 | bus_LV_154-6_0_4_node_132 | 0.4 | n |  | TRUE
166 | bus_LV_154-6_0_4_node_142 | 0.4 | n |  | TRUE
167 | bus_LV_154-6_0_4_node_143 | 0.4 | n |  | TRUE
168 | bus_LV_154-6_0_4_node_137 | 0.4 | n |  | TRUE
169 | bus_LV_154-6_0_4_node_138 | 0.4 | n |  | TRUE
170 | bus_LV_154-6_0_4_node_167 | 0.4 | n |  | TRUE
171 | bus_LV_154-6_0_4_node_139 | 0.4 | n |  | TRUE
172 | bus_LV_154-6_0_4_node_154 | 0.4 | n |  | TRUE
173 | bus_LV_154-6_0_4_node_140 | 0.4 | n |  | TRUE
174 | bus_LV_154-6_0_4_node_141 | 0.4 | n |  | TRUE
175 | bus_LV_154-6_0_4_node_147 | 0.4 | n |  | TRUE
176 | bus_LV_154-6_0_4_node_158 | 0.4 | n |  | TRUE
177 | bus_LV_154-6_0_4_node_270 | 0.4 | n |  | TRUE
178 | bus_LV_154-6_0_4_node_159 | 0.4 | n |  | TRUE
179 | bus_LV_154-6_0_4_node_148 | 0.4 | n |  | TRUE
180 | bus_LV_154-6_0_4_node_149 | 0.4 | n |  | TRUE
181 | bus_LV_154-6_0_4_node_150 | 0.4 | n |  | TRUE
182 | bus_LV_154-6_0_4_node_152 | 0.4 | n |  | TRUE
183 | bus_LV_154-6_0_4_node_153 | 0.4 | n |  | TRUE
184 | bus_LV_154-6_0_4_node_151 | 0.4 | n |  | TRUE
185 | bus_LV_154-6_0_4_node_155 | 0.4 | n |  | TRUE
186 | bus_LV_154-6_0_4_node_156 | 0.4 | n |  | TRUE
187 | bus_LV_154-6_0_4_node_157 | 0.4 | n |  | TRUE
188 | bus_LV_154-6_0_4_node_168 | 0.4 | n |  | TRUE
189 | bus_LV_154-6_0_4_node_161 | 0.4 | n |  | TRUE
190 | bus_LV_154-6_0_4_node_177 | 0.4 | n |  | TRUE
191 | bus_LV_154-6_0_4_node_164 | 0.4 | n |  | TRUE
192 | bus_LV_154-6_0_4_node_171 | 0.4 | n |  | TRUE
193 | bus_LV_154-6_0_4_node_160 | 0.4 | n |  | TRUE
194 | bus_LV_154-6_0_4_node_179 | 0.4 | n |  | TRUE
195 | bus_LV_154-6_0_4_node_175 | 0.4 | n |  | TRUE
196 | bus_LV_154-6_0_4_node_162 | 0.4 | n |  | TRUE
197 | bus_LV_154-6_0_4_node_163 | 0.4 | n |  | TRUE
198 | bus_LV_154-6_0_4_node_165 | 0.4 | n |  | TRUE
199 | bus_LV_154-6_0_4_node_166 | 0.4 | n |  | TRUE
200 | bus_LV_154-6_0_4_node_197 | 0.4 | n |  | TRUE
201 | bus_LV_154-6_0_4_node_196 | 0.4 | n |  | TRUE
202 | bus_LV_154-6_0_4_node_201 | 0.4 | n |  | TRUE
203 | bus_LV_154-6_0_4_node_202 | 0.4 | n |  | TRUE
204 | bus_LV_154-6_0_4_node_173 | 0.4 | n |  | TRUE
205 | bus_LV_154-6_0_4_node_169 | 0.4 | n |  | TRUE
206 | bus_LV_154-6_0_4_node_170 | 0.4 | n |  | TRUE
207 | bus_LV_154-6_0_4_node_172 | 0.4 | n |  | TRUE
208 | bus_LV_154-6_0_4_node_174 | 0.4 | n |  | TRUE
209 | bus_LV_154-6_0_4_node_184 | 0.4 | n |  | TRUE
210 | bus_LV_154-6_0_4_node_182 | 0.4 | n |  | TRUE
211 | bus_LV_154-6_0_4_node_176 | 0.4 | n |  | TRUE
212 | bus_LV_154-6_0_4_node_178 | 0.4 | n |  | TRUE
213 | bus_LV_154-6_0_4_node_180 | 0.4 | n |  | TRUE
214 | bus_LV_154-6_0_4_node_181 | 0.4 | n |  | TRUE
215 | bus_LV_154-6_0_4_node_183 | 0.4 | n |  | TRUE
216 | bus_LV_154-6_0_4_node_203 | 0.4 | n |  | TRUE
217 | bus_LV_154-6_0_4_node_190 | 0.4 | n |  | TRUE
218 | bus_LV_154-6_0_4_node_185 | 0.4 | n |  | TRUE
219 | bus_LV_154-6_0_4_node_186 | 0.4 | n |  | TRUE
220 | bus_LV_154-6_0_4_node_187 | 0.4 | n |  | TRUE
221 | bus_LV_154-6_0_4_node_188 | 0.4 | n |  | TRUE
222 | bus_LV_154-6_0_4_node_189 | 0.4 | n |  | TRUE
223 | bus_LV_154-6_0_4_node_191 | 0.4 | n |  | TRUE
224 | bus_LV_154-6_0_4_node_211 | 0.4 | n |  | TRUE
225 | bus_LV_154-6_0_4_node_212 | 0.4 | n |  | TRUE
226 | bus_LV_154-6_0_4_node_192 | 0.4 | n |  | TRUE
227 | bus_LV_154-6_0_4_node_194 | 0.4 | n |  | TRUE
228 | bus_LV_154-6_0_4_node_200 | 0.4 | n |  | TRUE
229 | bus_LV_154-6_0_4_node_230 | 0.4 | n |  | TRUE
230 | bus_LV_154-6_0_4_node_228 | 0.4 | n |  | TRUE
231 | bus_LV_154-6_0_4_node_208 | 0.4 | n |  | TRUE
232 | bus_LV_154-6_0_4_node_205 | 0.4 | n |  | TRUE
233 | bus_LV_154-6_0_4_node_204 | 0.4 | n |  | TRUE
234 | bus_LV_154-6_0_4_node_206 | 0.4 | n |  | TRUE
235 | bus_LV_154-6_0_4_node_207 | 0.4 | n |  | TRUE
236 | bus_LV_154-6_0_4_node_217 | 0.4 | n |  | TRUE
237 | bus_LV_154-6_0_4_node_218 | 0.4 | n |  | TRUE
238 | bus_LV_154-6_0_4_node_219 | 0.4 | n |  | TRUE
239 | bus_LV_154-6_0_4_node_220 | 0.4 | n |  | TRUE
240 | bus_LV_154-6_0_4_node_221 | 0.4 | n |  | TRUE
241 | bus_LV_154-6_0_4_node_223 | 0.4 | n |  | TRUE
242 | bus_LV_154-6_0_4_node_269 | 0.4 | n |  | TRUE
243 | bus_LV_154-6_0_4_node_235 | 0.4 | n |  | TRUE
244 | bus_LV_154-6_0_4_node_227 | 0.4 | n |  | TRUE
245 | bus_LV_154-6_0_4_node_229 | 0.4 | n |  | TRUE
246 | bus_LV_154-6_0_4_node_232 | 0.4 | n |  | TRUE
247 | bus_LV_154-6_0_4_node_234 | 0.4 | n |  | TRUE
248 | bus_LV_154-6_0_4_node_237 | 0.4 | n |  | TRUE
249 | bus_LV_154-6_0_4_node_239 | 0.4 | n |  | TRUE
250 | bus_LV_154-6_0_4_node_268 | 0.4 | n |  | TRUE
251 | bus_LV_154-6_0_4_node_240 | 0.4 | n |  | TRUE
252 | bus_LV_154-6_0_4_node_265 | 0.4 | n |  | TRUE
253 | bus_LV_154-6_0_4_node_267 | 0.4 | n |  | TRUE
254 | bus_LV_154-6_0_4_node_266 | 0.4 | n |  | TRUE
255 | bus_LV_154-6_0_4_node_261 | 0.4 | n |  | TRUE
256 | bus_LV_154-6_0_4_node_255 | 0.4 | n |  | TRUE
257 | bus_LV_154-6_0_4_node_259 | 0.4 | n |  | TRUE
258 | bus_LV_154-6_0_4_node_253 | 0.4 | n |  | TRUE
259 | bus_LV_154-6_0_4_node_250 | 0.4 | n |  | TRUE
260 | bus_LV_154-6_0_4_node_251 | 0.4 | n |  | TRUE
261 | bus_LV_154-6_0_4_node_252 | 0.4 | n |  | TRUE
262 | bus_LV_154-6_0_4_node_254 | 0.4 | n |  | TRUE
263 | bus_LV_154-6_0_4_node_258 | 0.4 | n |  | TRUE
264 | bus_MV_492_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_154-6_0_4_load_0 | 0 | 0.001346 | 0.00033733 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_154-6_0_4_load_3 | 2 | 0.0018035 | 0.00045199 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_154-6_0_4_load_257 | 3 | 0.0012315 | 0.00030864 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_154-6_0_4_load_256 | 4 | 0.0012769 | 0.00032001 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_154-6_0_4_load_6 | 5 | 0.0048811 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_154-6_0_4_load_5 | 8 | 0.0025549 | 0.00064032 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_154-6_0_4_load_11 | 11 | 0.0020131 | 0.00050454 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_154-6_0_4_load_214 | 13 | 0.0022583 | 0.00056598 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_154-6_0_4_load_213 | 14 | 0.00021777 | 5.4578e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_154-6_0_4_load_215 | 15 | 0.0007559 | 0.00018945 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_154-6_0_4_load_210 | 16 | 0.0016859 | 0.00042253 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_154-6_0_4_load_216 | 17 | 0.00040851 | 0.00010238 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_154-6_0_4_load_209 | 18 | 0.0015096 | 0.00037834 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_154-6_0_4_load_12 | 19 | 0.0051415 | 0.0012886 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_154-6_0_4_load_13 | 20 | 0.0019201 | 0.00048123 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_154-6_0_4_load_15 | 22 | 0.00083162 | 0.00020842 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_154-6_0_4_load_22 | 26 | 0.0052572 | 0.0013176 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_154-6_0_4_load_90 | 29 | 0.0021267 | 0.00053299 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_154-6_0_4_load_88 | 30 | 0.0031739 | 0.00079546 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_154-6_0_4_load_87 | 31 | 0.003707 | 0.00092907 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_154-6_0_4_load_24 | 33 | 0.0002772 | 6.9473e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_154-6_0_4_load_25 | 34 | 0.0023555 | 0.00059034 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_154-6_0_4_load_26 | 35 | 0.0017898 | 0.00044856 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_154-6_0_4_load_23 | 36 | 0.0014546 | 0.00036455 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_154-6_0_4_load_63 | 37 | 0.0048631 | 0.0012188 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_154-6_0_4_load_31 | 38 | 0.0037962 | 0.00095142 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_154-6_0_4_load_91 | 39 | 0.0025929 | 0.00064984 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_154-6_0_4_load_93 | 40 | 0.0024682 | 0.0006186 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_154-6_0_4_load_89 | 41 | 0.002655 | 0.0006654 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_154-6_0_4_load_68 | 43 | 0.0033855 | 0.00084849 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_154-6_0_4_load_27 | 44 | 0.0011252 | 0.000282 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_154-6_0_4_load_62 | 45 | 0.0046783 | 0.0011725 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_154-6_0_4_load_76 | 47 | 0.0024517 | 0.00061446 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_154-6_0_4_load_28 | 48 | 0.0027787 | 0.0006964 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_154-6_0_4_load_29 | 49 | 0.002478 | 0.00062104 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_154-6_0_4_load_32 | 51 | 0.0010888 | 0.00027288 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_154-6_0_4_load_33 | 52 | 0.0026476 | 0.00066356 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_154-6_0_4_load_34 | 53 | 0.0012778 | 0.00032024 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_154-6_0_4_load_35 | 54 | 0.001388 | 0.00034787 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_154-6_0_4_load_42 | 55 | 0.0016451 | 0.00041231 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_154-6_0_4_load_49 | 56 | 0.0019363 | 0.00048529 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_154-6_0_4_load_50 | 58 | 0.0025609 | 0.00064183 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_154-6_0_4_load_36 | 59 | 0.0034532 | 0.00086546 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_154-6_0_4_load_37 | 60 | 0.001453 | 0.00036416 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_154-6_0_4_load_38 | 61 | 0.0021676 | 0.00054324 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_154-6_0_4_load_41 | 63 | 0.003387 | 0.00084885 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_154-6_0_4_load_43 | 64 | 0.003597 | 0.00090149 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_154-6_0_4_load_51 | 66 | 0.0020111 | 0.00050402 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_154-6_0_4_load_46 | 67 | 0.0019211 | 0.00048148 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_154-6_0_4_load_86 | 68 | 0.00071121 | 0.00017825 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_154-6_0_4_load_77 | 69 | 0.0033869 | 0.00084883 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_154-6_0_4_load_47 | 70 | 0.0018533 | 0.00046447 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_154-6_0_4_load_243 | 73 | 0.0013709 | 0.00034357 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_154-6_0_4_load_225 | 76 | 0.00067413 | 0.00016895 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_154-6_0_4_load_263 | 78 | 0.0020352 | 0.00051008 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_154-6_0_4_load_244 | 80 | 0.0034516 | 0.00086505 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_154-6_0_4_load_245 | 81 | 0.002917 | 0.00073106 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_154-6_0_4_load_242 | 82 | 0.0029274 | 0.00073367 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_154-6_0_4_load_69 | 83 | 0.0022321 | 0.00055941 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_154-6_0_4_load_84 | 84 | 0.0015641 | 0.000392 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_154-6_0_4_load_48 | 85 | 0.0013591 | 0.00034062 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_154-6_0_4_load_64 | 86 | 0.0019335 | 0.00048458 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_154-6_0_4_load_58 | 87 | 0.0011222 | 0.00028124 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_154-6_0_4_load_57 | 88 | 0.0035831 | 0.00089802 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_154-6_0_4_load_55 | 89 | 0.0021974 | 0.00055072 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_154-6_0_4_load_52 | 90 | 0.0017556 | 0.00044001 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_154-6_0_4_load_53 | 91 | 0.0018427 | 0.00046183 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_154-6_0_4_load_54 | 92 | 0.0067908 | 0.0017019 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_154-6_0_4_load_56 | 93 | 0.0010797 | 0.0002706 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_154-6_0_4_load_59 | 94 | 0.0040282 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_154-6_0_4_load_60 | 95 | 0.0056616 | 0.0014189 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_154-6_0_4_load_61 | 96 | 0.002914 | 0.00073033 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_154-6_0_4_load_78 | 97 | 0.00071163 | 0.00017835 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_154-6_0_4_load_79 | 98 | 0.00064104 | 0.00016066 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_154-6_0_4_load_80 | 99 | 0.0005003 | 0.00012539 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_154-6_0_4_load_81 | 101 | 0.0017832 | 0.0004469 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_154-6_0_4_load_82 | 102 | 0.0030356 | 0.00076078 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_154-6_0_4_load_83 | 103 | 0.0016433 | 0.00041186 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_154-6_0_4_load_241 | 105 | 0.0020356 | 0.00051016 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_154-6_0_4_load_264 | 107 | 0.0020355 | 0.00051014 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_154-6_0_4_load_262 | 109 | 0.0013402 | 0.00033589 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_154-6_0_4_load_260 | 110 | 0.0010607 | 0.00026585 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_154-6_0_4_load_248 | 111 | 0.0036518 | 0.00091523 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_154-6_0_4_load_249 | 112 | 0.0021907 | 0.00054904 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_154-6_0_4_load_224 | 114 | 0.0013906 | 0.00034851 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_154-6_0_4_load_115 | 115 | 0.0019652 | 0.00049253 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_154-6_0_4_load_94 | 116 | 0.0025729 | 0.00064484 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_154-6_0_4_load_101 | 117 | 0.0012722 | 0.00031885 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_154-6_0_4_load_231 | 118 | 0.0011302 | 0.00028326 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_154-6_0_4_load_222 | 119 | 0.0016646 | 0.00041718 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_154-6_0_4_load_98 | 121 | 0.0021827 | 0.00054704 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_154-6_0_4_load_85 | 122 | 0.0010762 | 0.00026972 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_154-6_0_4_load_95 | 123 | 0.0026479 | 0.00066363 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_154-6_0_4_load_99 | 125 | 0.0017801 | 0.00044614 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_154-6_0_4_load_102 | 126 | 0.0016593 | 0.00041586 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_154-6_0_4_load_104 | 127 | 0.0016383 | 0.00041059 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_154-6_0_4_load_103 | 128 | 0.0014102 | 0.00035344 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_154-6_0_4_load_105 | 130 | 0.0014914 | 0.00037379 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_154-6_0_4_load_144 | 132 | 0.0060935 | 0.0015272 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_154-6_0_4_load_106 | 133 | 0.0022937 | 0.00057484 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_154-6_0_4_load_107 | 134 | 0.0020474 | 0.00051312 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_154-6_0_4_load_130 | 135 | 0.00089535 | 0.00022439 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_154-6_0_4_load_131 | 136 | 0.0025895 | 0.00064898 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_154-6_0_4_load_108 | 137 | 0.0011157 | 0.00027962 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_154-6_0_4_load_109 | 138 | 0.0011527 | 0.0002889 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_154-6_0_4_load_110 | 139 | 0.0020511 | 0.00051405 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_154-6_0_4_load_111 | 140 | 0.0013703 | 0.00034344 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_154-6_0_4_load_112 | 141 | 0.0036628 | 0.00091799 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_154-6_0_4_load_113 | 142 | 0.0013396 | 0.00033574 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_154-6_0_4_load_114 | 143 | 0.0017989 | 0.00045085 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_154-6_0_4_load_128 | 144 | 0.0015566 | 0.00039013 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_154-6_0_4_load_117 | 145 | 0.0016824 | 0.00042165 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_154-6_0_4_load_118 | 146 | 0.0032571 | 0.00081632 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_154-6_0_4_load_129 | 147 | 0.003516 | 0.0008812 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_154-6_0_4_load_119 | 148 | 0.0011801 | 0.00029576 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_154-6_0_4_load_120 | 149 | 0.0029805 | 0.00074697 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_154-6_0_4_load_133 | 150 | 0.0020154 | 0.00050511 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_154-6_0_4_load_198 | 151 | 0.0020693 | 0.00051861 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_154-6_0_4_load_126 | 152 | 0.0016321 | 0.00040904 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_154-6_0_4_load_199 | 153 | 0.0014331 | 0.00035916 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_154-6_0_4_load_121 | 154 | 0.0023644 | 0.00059257 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_154-6_0_4_load_122 | 155 | 0.003345 | 0.00083834 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_154-6_0_4_load_123 | 156 | 0.0018523 | 0.00046423 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_154-6_0_4_load_124 | 157 | 0.0013375 | 0.00033522 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_154-6_0_4_load_125 | 158 | 0.0045396 | 0.0011377 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_154-6_0_4_load_127 | 159 | 0.0012125 | 0.00030389 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_154-6_0_4_load_135 | 161 | 0.0024401 | 0.00061155 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_154-6_0_4_load_136 | 162 | 0.0010063 | 0.00025219 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_154-6_0_4_load_195 | 163 | 0.001119 | 0.00028046 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_154-6_0_4_load_193 | 164 | 0.0013938 | 0.00034931 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_154-6_0_4_load_132 | 165 | 0.0017946 | 0.00044977 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_154-6_0_4_load_143 | 167 | 0.0034702 | 0.00086971 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_154-6_0_4_load_137 | 168 | 0.0024494 | 0.00061387 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_154-6_0_4_load_138 | 169 | 0.00098728 | 0.00024744 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_154-6_0_4_load_167 | 170 | 0.0024715 | 0.00061941 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_154-6_0_4_load_139 | 171 | 0.0025889 | 0.00064883 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_154-6_0_4_load_154 | 172 | 0.0032758 | 0.00082098 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_154-6_0_4_load_140 | 173 | 0.0026739 | 0.00067013 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_154-6_0_4_load_141 | 174 | 0.0015042 | 0.000377 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_154-6_0_4_load_147 | 175 | 0.0015783 | 0.00039555 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_154-6_0_4_load_158 | 176 | 0.0018954 | 0.00047502 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_154-6_0_4_load_270 | 177 | 0.0034889 | 0.0008744 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_154-6_0_4_load_159 | 178 | 0.00086392 | 0.00021652 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_154-6_0_4_load_148 | 179 | 0.0020239 | 0.00050723 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_154-6_0_4_load_149 | 180 | 0.0016386 | 0.00041066 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_154-6_0_4_load_152 | 182 | 0.0036454 | 0.00091362 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_154-6_0_4_load_153 | 183 | 0.003003 | 0.00075261 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_154-6_0_4_load_156 | 186 | 0.0023005 | 0.00057657 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_154-6_0_4_load_157 | 187 | 0.0018785 | 0.00047079 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_154-6_0_4_load_168 | 188 | 0.0019753 | 0.00049507 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_154-6_0_4_load_161 | 189 | 0.0016043 | 0.00040209 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_154-6_0_4_load_164 | 191 | 0.0022049 | 0.00055261 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_154-6_0_4_load_171 | 192 | 0.00087041 | 0.00021815 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_154-6_0_4_load_160 | 193 | 0.0024422 | 0.00061208 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_154-6_0_4_load_175 | 195 | 0.002116 | 0.00053032 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_154-6_0_4_load_162 | 196 | 0.0014667 | 0.00036759 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_154-6_0_4_load_163 | 197 | 0.0026044 | 0.00065272 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_154-6_0_4_load_165 | 198 | 0.0024728 | 0.00061975 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_154-6_0_4_load_197 | 200 | 0.0015002 | 0.00037598 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_154-6_0_4_load_196 | 201 | 0.0020607 | 0.00051646 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_154-6_0_4_load_201 | 202 | 0.0033214 | 0.00083243 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_154-6_0_4_load_173 | 204 | 0.0018769 | 0.0004704 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_154-6_0_4_load_169 | 205 | 0.00087842 | 0.00022015 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_154-6_0_4_load_170 | 206 | 0.00087557 | 0.00021944 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_154-6_0_4_load_172 | 207 | 0.0017707 | 0.00044378 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_154-6_0_4_load_174 | 208 | 0.0021253 | 0.00053264 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_154-6_0_4_load_184 | 209 | 0.0036454 | 0.00091362 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_154-6_0_4_load_182 | 210 | 0.0021564 | 0.00054045 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_154-6_0_4_load_176 | 211 | 0.0020864 | 0.00052289 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_154-6_0_4_load_178 | 212 | 0.0021009 | 0.00052654 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_154-6_0_4_load_180 | 213 | 0.0036454 | 0.00091362 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_154-6_0_4_load_181 | 214 | 0.0018814 | 0.00047152 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_154-6_0_4_load_183 | 215 | 0.0023237 | 0.00058238 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_154-6_0_4_load_203 | 216 | 0.0026926 | 0.00067483 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_154-6_0_4_load_190 | 217 | 0.0025717 | 0.00064452 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_154-6_0_4_load_185 | 218 | 0.0023817 | 0.00059692 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_154-6_0_4_load_186 | 219 | 0.0027692 | 0.00069402 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_154-6_0_4_load_187 | 220 | 0.0027374 | 0.00068606 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_154-6_0_4_load_188 | 221 | 0.0027591 | 0.00069149 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_154-6_0_4_load_189 | 222 | 0.0023038 | 0.00057739 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_154-6_0_4_load_191 | 223 | 0.0026912 | 0.00067449 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_154-6_0_4_load_211 | 224 | 0.0026597 | 0.00066658 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_154-6_0_4_load_212 | 225 | 0.0026463 | 0.00066321 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_154-6_0_4_load_192 | 226 | 0.001409 | 0.00035313 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_154-6_0_4_load_194 | 227 | 0.001596 | 0.0004 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_154-6_0_4_load_200 | 228 | 0.0014968 | 0.00037514 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_154-6_0_4_load_230 | 229 | 0.0016471 | 0.0004128 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_154-6_0_4_load_228 | 230 | 0.00061749 | 0.00015476 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_154-6_0_4_load_208 | 231 | 0.0015804 | 0.0003961 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_154-6_0_4_load_205 | 232 | 0.0015021 | 0.00037645 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_154-6_0_4_load_204 | 233 | 0.00086558 | 0.00021694 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_154-6_0_4_load_206 | 234 | 0.002721 | 0.00068194 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_154-6_0_4_load_207 | 235 | 0.0026614 | 0.000667 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_154-6_0_4_load_217 | 236 | 0.00072505 | 0.00018172 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_154-6_0_4_load_218 | 237 | 0.0035836 | 0.00089813 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_154-6_0_4_load_219 | 238 | 0.0016816 | 0.00042145 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_154-6_0_4_load_220 | 239 | 0.0014892 | 0.00037324 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_154-6_0_4_load_221 | 240 | 0.0015601 | 0.00039101 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_154-6_0_4_load_223 | 241 | 0.0014453 | 0.00036222 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_154-6_0_4_load_235 | 243 | 0.00080297 | 0.00020124 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_154-6_0_4_load_227 | 244 | 0.0013185 | 0.00033045 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_154-6_0_4_load_232 | 246 | 0.0005798 | 0.00014531 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_154-6_0_4_load_234 | 247 | 0.00055598 | 0.00013934 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_154-6_0_4_load_237 | 248 | 0.00061646 | 0.0001545 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_154-6_0_4_load_239 | 249 | 0.0020355 | 0.00051014 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_154-6_0_4_load_240 | 251 | 0.0020927 | 0.00052449 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_154-6_0_4_load_265 | 252 | 0.0020927 | 0.00052447 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_154-6_0_4_load_267 | 253 | 0.0020354 | 0.00051012 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_154-6_0_4_load_266 | 254 | 0.0020927 | 0.00052448 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_154-6_0_4_load_261 | 255 | 0.0011836 | 0.00029663 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_154-6_0_4_load_255 | 256 | 0.0033467 | 0.00083877 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_154-6_0_4_load_259 | 257 | 0.0012938 | 0.00032426 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_154-6_0_4_load_253 | 258 | 0.0046323 | 0.001161 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_154-6_0_4_load_250 | 259 | 0.0055793 | 0.0013983 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_154-6_0_4_load_251 | 260 | 0.0028083 | 0.00070384 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_154-6_0_4_load_252 | 261 | 0.0030526 | 0.00076506 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_154-6_0_4_load_254 | 262 | 0.0029667 | 0.00074354 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_154-6_0_4_load_258 | 263 | 0.0011112 | 0.00027849 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 248 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_154-6_0_4_line_0 |  | 0 | 1 | 0.026161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_154-6_0_4_line_1 |  | 1 | 2 | 0.044059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_154-6_0_4_line_2 |  | 1 | 3 | 0.4549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_154-6_0_4_line_3 |  | 2 | 7 | 0.0068386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_154-6_0_4_line_4 |  | 3 | 4 | 0.0017922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_154-6_0_4_line_5 |  | 4 | 263 | 0.0085121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_154-6_0_4_line_6 |  | 5 | 6 | 0.052935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_154-6_0_4_line_7 |  | 6 | 9 | 0.10521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_154-6_0_4_line_8 |  | 7 | 8 | 0.069221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_154-6_0_4_line_9 |  | 9 | 10 | 0.058588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_154-6_0_4_line_10 |  | 9 | 11 | 0.040419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_154-6_0_4_line_11 |  | 10 | 15 | 0.021228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_154-6_0_4_line_12 |  | 10 | 14 | 0.03031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_154-6_0_4_line_13 |  | 11 | 16 | 0.032445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_154-6_0_4_line_14 |  | 12 | 13 | 0.02674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_154-6_0_4_line_15 |  | 12 | 14 | 0.0404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_154-6_0_4_line_16 |  | 13 | 17 | 0.061409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_154-6_0_4_line_17 |  | 16 | 18 | 0.018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_154-6_0_4_line_18 |  | 17 | 236 | 0.080696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_154-6_0_4_line_19 |  | 18 | 231 | 0.017161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_154-6_0_4_line_20 |  | 19 | 20 | 0.0273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_154-6_0_4_line_21 |  | 19 | 21 | 0.031424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_154-6_0_4_line_22 |  | 20 | 22 | 0.0086061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_154-6_0_4_line_23 |  | 21 | 23 | 0.002387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_154-6_0_4_line_24 |  | 22 | 24 | 0.039063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_154-6_0_4_line_25 |  | 23 | 25 | 0.02794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_154-6_0_4_line_26 |  | 23 | 26 | 0.025194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_154-6_0_4_line_27 |  | 24 | 36 | 0.024279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_154-6_0_4_line_28 |  | 24 | 32 | 0.043774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_154-6_0_4_line_29 |  | 25 | 37 | 0.015578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_154-6_0_4_line_30 |  | 25 | 38 | 0.013188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_154-6_0_4_line_31 |  | 26 | 31 | 0.036715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_154-6_0_4_line_32 |  | 27 | 28 | 0.041511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_154-6_0_4_line_33 |  | 27 | 29 | 0.09784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_154-6_0_4_line_34 |  | 28 | 30 | 0.042758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_154-6_0_4_line_35 |  | 28 | 31 | 0.027752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_154-6_0_4_line_36 |  | 30 | 41 | 0.016461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_154-6_0_4_line_37 |  | 32 | 33 | 0.016241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_154-6_0_4_line_38 |  | 32 | 34 | 0.028038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_154-6_0_4_line_39 |  | 32 | 35 | 0.027177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_154-6_0_4_line_40 |  | 33 | 42 | 0.019069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_154-6_0_4_line_41 |  | 34 | 43 | 0.0067699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_154-6_0_4_line_42 |  | 36 | 44 | 0.022225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_154-6_0_4_line_43 |  | 37 | 45 | 0.023699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_154-6_0_4_line_44 |  | 39 | 40 | 0.03059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_154-6_0_4_line_45 |  | 40 | 116 | 0.017212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_154-6_0_4_line_46 |  | 42 | 46 | 0.003058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_154-6_0_4_line_47 |  | 43 | 47 | 0.017085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_154-6_0_4_line_48 |  | 45 | 95 | 0.00048105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_154-6_0_4_line_49 |  | 46 | 97 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_154-6_0_4_line_50 |  | 46 | 98 | 0.012553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_154-6_0_4_line_51 |  | 46 | 99 | 0.022876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_154-6_0_4_line_52 |  | 47 | 69 | 0.013356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_154-6_0_4_line_53 |  | 48 | 49 | 0.001885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_154-6_0_4_line_54 |  | 48 | 50 | 0.03587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_154-6_0_4_line_55 |  | 50 | 51 | 0.00095351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_154-6_0_4_line_56 |  | 50 | 52 | 0.014568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_154-6_0_4_line_57 |  | 51 | 53 | 0.023332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_154-6_0_4_line_58 |  | 52 | 54 | 0.0051579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_154-6_0_4_line_59 |  | 53 | 55 | 0.025321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_154-6_0_4_line_60 |  | 54 | 56 | 0.020824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_154-6_0_4_line_61 |  | 55 | 57 | 0.0050406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_154-6_0_4_line_62 |  | 56 | 58 | 0.015205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_154-6_0_4_line_63 |  | 57 | 63 | 0.022634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_154-6_0_4_line_64 |  | 57 | 60 | 0.0037956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_154-6_0_4_line_65 |  | 58 | 88 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_154-6_0_4_line_66 |  | 59 | 60 | 0.01347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_154-6_0_4_line_67 |  | 59 | 61 | 0.0094665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_154-6_0_4_line_68 |  | 61 | 62 | 0.0097925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_154-6_0_4_line_69 |  | 62 | 64 | 0.018353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_154-6_0_4_line_70 |  | 62 | 65 | 0.14349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_154-6_0_4_line_71 |  | 63 | 66 | 0.017425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_154-6_0_4_line_72 |  | 64 | 67 | 0.021444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_154-6_0_4_line_73 |  | 65 | 68 | 0.051623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_154-6_0_4_line_74 |  | 66 | 69 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_154-6_0_4_line_75 |  | 67 | 70 | 0.005106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_154-6_0_4_line_76 |  | 68 | 84 | 0.014504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_154-6_0_4_line_77 |  | 70 | 85 | 0.0060717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_154-6_0_4_line_78 |  | 71 | 72 | 0.054192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_154-6_0_4_line_79 |  | 71 | 73 | 0.0368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_154-6_0_4_line_80 |  | 72 | 78 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_154-6_0_4_line_81 |  | 72 | 107 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_154-6_0_4_line_82 |  | 73 | 82 | 0.01136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_154-6_0_4_line_83 |  | 74 | 75 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_154-6_0_4_line_84 |  | 74 | 76 | 0.02941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_154-6_0_4_line_85 |  | 74 | 77 | 0.0086169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_154-6_0_4_line_86 |  | 75 | 78 | 0.017267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_154-6_0_4_line_87 |  | 76 | 98 | 0.02546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_154-6_0_4_line_88 |  | 77 | 83 | 0.023456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_154-6_0_4_line_89 |  | 79 | 80 | 0.044725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_154-6_0_4_line_90 |  | 79 | 81 | 0.028058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_154-6_0_4_line_91 |  | 79 | 82 | 0.0078534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_154-6_0_4_line_92 |  | 80 | 111 | 0.012396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_154-6_0_4_line_93 |  | 81 | 112 | 0.025649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_154-6_0_4_line_94 |  | 84 | 122 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_154-6_0_4_line_95 |  | 85 | 86 | 0.0037478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_154-6_0_4_line_96 |  | 86 | 87 | 0.014959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_154-6_0_4_line_97 |  | 87 | 93 | 0.0019048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_154-6_0_4_line_98 |  | 88 | 89 | 0.0083924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_154-6_0_4_line_99 |  | 89 | 91 | 0.023343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_154-6_0_4_line_100 |  | 90 | 91 | 0.0002256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_154-6_0_4_line_101 |  | 90 | 92 | 0.0022156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_154-6_0_4_line_102 |  | 94 | 95 | 0.027537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_154-6_0_4_line_103 |  | 94 | 96 | 0.0032282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_154-6_0_4_line_104 |  | 97 | 113 | 0.019313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_154-6_0_4_line_105 |  | 99 | 114 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_154-6_0_4_line_106 |  | 100 | 101 | 0.011325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_154-6_0_4_line_107 |  | 100 | 102 | 0.050465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_154-6_0_4_line_108 |  | 100 | 103 | 0.055402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_154-6_0_4_line_109 |  | 101 | 115 | 0.024806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_154-6_0_4_line_110 |  | 102 | 116 | 0.026536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_154-6_0_4_line_111 |  | 103 | 117 | 0.014367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_154-6_0_4_line_112 |  | 104 | 105 | 0.0080231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_154-6_0_4_line_113 |  | 104 | 106 | 0.025104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_154-6_0_4_line_114 |  | 105 | 242 | 0.011314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_154-6_0_4_line_115 |  | 106 | 243 | 0.0020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_154-6_0_4_line_116 |  | 107 | 242 | 0.023022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_154-6_0_4_line_117 |  | 108 | 109 | 0.023564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_154-6_0_4_line_118 |  | 108 | 110 | 0.012788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_154-6_0_4_line_119 |  | 109 | 255 | 0.010398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_154-6_0_4_line_120 |  | 110 | 257 | 0.0066846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_154-6_0_4_line_121 |  | 111 | 255 | 0.05209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_154-6_0_4_line_122 |  | 112 | 256 | 0.025237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_154-6_0_4_line_123 |  | 113 | 118 | 0.027577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_154-6_0_4_line_124 |  | 114 | 119 | 0.022281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_154-6_0_4_line_125 |  | 115 | 120 | 0.019513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_154-6_0_4_line_126 |  | 117 | 121 | 0.014376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_154-6_0_4_line_127 |  | 118 | 245 | 0.019508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_154-6_0_4_line_128 |  | 119 | 239 | 0.020818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_154-6_0_4_line_129 |  | 120 | 145 | 0.015511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_154-6_0_4_line_130 |  | 120 | 146 | 0.021314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_154-6_0_4_line_131 |  | 121 | 124 | 0.023183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_154-6_0_4_line_132 |  | 123 | 124 | 0.018289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_154-6_0_4_line_133 |  | 125 | 126 | 0.0046092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_154-6_0_4_line_134 |  | 126 | 127 | 0.0075311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_154-6_0_4_line_135 |  | 127 | 130 | 0.014063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_154-6_0_4_line_136 |  | 128 | 129 | 0.023483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_154-6_0_4_line_137 |  | 129 | 131 | 0.19477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_154-6_0_4_line_138 |  | 129 | 132 | 0.041948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_154-6_0_4_line_139 |  | 130 | 133 | 0.01634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_154-6_0_4_line_140 |  | 131 | 177 | 0.093227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_154-6_0_4_line_141 |  | 132 | 166 | 0.01655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_154-6_0_4_line_142 |  | 133 | 134 | 0.0068915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_154-6_0_4_line_143 |  | 134 | 135 | 0.021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_154-6_0_4_line_144 |  | 135 | 136 | 0.012907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_154-6_0_4_line_145 |  | 136 | 165 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_154-6_0_4_line_146 |  | 137 | 138 | 0.0091844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_154-6_0_4_line_147 |  | 137 | 139 | 0.025687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_154-6_0_4_line_148 |  | 138 | 140 | 0.02452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_154-6_0_4_line_149 |  | 139 | 141 | 0.015376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_154-6_0_4_line_150 |  | 140 | 142 | 0.0084722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_154-6_0_4_line_151 |  | 141 | 143 | 0.02483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_154-6_0_4_line_152 |  | 143 | 144 | 0.0069374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_154-6_0_4_line_153 |  | 144 | 147 | 0.0067717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_154-6_0_4_line_154 |  | 145 | 148 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_154-6_0_4_line_155 |  | 146 | 149 | 0.0081669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_154-6_0_4_line_156 |  | 147 | 163 | 0.0073919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_154-6_0_4_line_157 |  | 148 | 150 | 0.0052284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_154-6_0_4_line_158 |  | 149 | 151 | 0.019617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
159 | LV_154-6_0_4_line_159 |  | 150 | 152 | 0.010353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
160 | LV_154-6_0_4_line_160 |  | 151 | 153 | 0.0092006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
161 | LV_154-6_0_4_line_161 |  | 152 | 157 | 0.0044033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
162 | LV_154-6_0_4_line_162 |  | 153 | 228 | 0.0090358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
163 | LV_154-6_0_4_line_163 |  | 154 | 155 | 0.014365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
164 | LV_154-6_0_4_line_164 |  | 154 | 156 | 0.016211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
165 | LV_154-6_0_4_line_165 |  | 155 | 157 | 0.02474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
166 | LV_154-6_0_4_line_166 |  | 156 | 158 | 0.0091485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
167 | LV_154-6_0_4_line_167 |  | 158 | 159 | 0.012773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_154-6_0_4_line_168 |  | 159 | 160 | 0.014358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
169 | LV_154-6_0_4_line_169 |  | 160 | 161 | 0.011548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
170 | LV_154-6_0_4_line_170 |  | 160 | 162 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_154-6_0_4_line_171 |  | 161 | 168 | 0.00057986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
172 | LV_154-6_0_4_line_172 |  | 162 | 169 | 0.0081457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_154-6_0_4_line_173 |  | 163 | 164 | 0.0076263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_154-6_0_4_line_174 |  | 164 | 226 | 0.0032889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_154-6_0_4_line_175 |  | 165 | 166 | 0.025392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_154-6_0_4_line_176 |  | 166 | 167 | 0.019749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_154-6_0_4_line_177 |  | 167 | 175 | 0.026206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_154-6_0_4_line_178 |  | 168 | 170 | 0.036422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
179 | LV_154-6_0_4_line_179 |  | 169 | 171 | 0.0066755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_154-6_0_4_line_180 |  | 170 | 172 | 0.0077777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
181 | LV_154-6_0_4_line_181 |  | 171 | 173 | 0.01772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_154-6_0_4_line_182 |  | 172 | 184 | 0.018129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
183 | LV_154-6_0_4_line_183 |  | 173 | 174 | 0.0070854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_154-6_0_4_line_184 |  | 175 | 176 | 0.0021694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_154-6_0_4_line_185 |  | 176 | 178 | 0.0088646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_154-6_0_4_line_186 |  | 178 | 193 | 0.022891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_154-6_0_4_line_187 |  | 179 | 180 | 0.0033391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_154-6_0_4_line_188 |  | 179 | 181 | 0.018287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_154-6_0_4_line_189 |  | 181 | 182 | 0.0241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
190 | LV_154-6_0_4_line_190 |  | 181 | 183 | 0.0074893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
191 | LV_154-6_0_4_line_191 |  | 182 | 186 | 0.017413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
192 | LV_154-6_0_4_line_192 |  | 183 | 187 | 0.0087619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
193 | LV_154-6_0_4_line_193 |  | 184 | 185 | 0.024206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
194 | LV_154-6_0_4_line_194 |  | 185 | 188 | 0.019712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
195 | LV_154-6_0_4_line_195 |  | 185 | 189 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_154-6_0_4_line_196 |  | 186 | 190 | 0.011077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
197 | LV_154-6_0_4_line_197 |  | 187 | 191 | 0.012124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
198 | LV_154-6_0_4_line_198 |  | 188 | 192 | 0.019335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
199 | LV_154-6_0_4_line_199 |  | 189 | 193 | 0.0057295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_154-6_0_4_line_200 |  | 190 | 194 | 0.015027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
201 | LV_154-6_0_4_line_201 |  | 190 | 195 | 0.008924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
202 | LV_154-6_0_4_line_202 |  | 191 | 196 | 0.0020319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
203 | LV_154-6_0_4_line_203 |  | 192 | 204 | 0.0086356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
204 | LV_154-6_0_4_line_204 |  | 192 | 205 | 0.013154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_154-6_0_4_line_205 |  | 194 | 214 | 0.013456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
206 | LV_154-6_0_4_line_206 |  | 195 | 211 | 0.0085987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
207 | LV_154-6_0_4_line_207 |  | 196 | 197 | 0.021733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
208 | LV_154-6_0_4_line_208 |  | 197 | 198 | 0.0023083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
209 | LV_154-6_0_4_line_209 |  | 198 | 199 | 0.019248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
210 | LV_154-6_0_4_line_210 |  | 199 | 200 | 0.028759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
211 | LV_154-6_0_4_line_211 |  | 200 | 201 | 0.023394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
212 | LV_154-6_0_4_line_212 |  | 201 | 227 | 0.010737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
213 | LV_154-6_0_4_line_213 |  | 202 | 203 | 0.024655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_154-6_0_4_line_214 |  | 203 | 231 | 0.035721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
215 | LV_154-6_0_4_line_215 |  | 203 | 232 | 0.026068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
216 | LV_154-6_0_4_line_216 |  | 204 | 208 | 0.014888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
217 | LV_154-6_0_4_line_217 |  | 205 | 206 | 0.0077243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_154-6_0_4_line_218 |  | 206 | 207 | 0.0070881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_154-6_0_4_line_219 |  | 208 | 209 | 0.0096096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
220 | LV_154-6_0_4_line_220 |  | 209 | 210 | 0.0030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
221 | LV_154-6_0_4_line_221 |  | 210 | 215 | 0.013804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
222 | LV_154-6_0_4_line_222 |  | 211 | 212 | 0.01428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
223 | LV_154-6_0_4_line_223 |  | 212 | 213 | 0.0084073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
224 | LV_154-6_0_4_line_224 |  | 213 | 215 | 0.00026527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
225 | LV_154-6_0_4_line_225 |  | 214 | 216 | 0.0025527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
226 | LV_154-6_0_4_line_226 |  | 216 | 217 | 0.013748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
227 | LV_154-6_0_4_line_227 |  | 217 | 221 | 0.010071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
228 | LV_154-6_0_4_line_228 |  | 218 | 219 | 0.00038641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
229 | LV_154-6_0_4_line_229 |  | 218 | 220 | 0.0098644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
230 | LV_154-6_0_4_line_230 |  | 219 | 221 | 0.012208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
231 | LV_154-6_0_4_line_231 |  | 220 | 222 | 0.015138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
232 | LV_154-6_0_4_line_232 |  | 222 | 223 | 1.7739e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
233 | LV_154-6_0_4_line_233 |  | 223 | 224 | 0.010081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
234 | LV_154-6_0_4_line_234 |  | 224 | 225 | 0.0041085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
235 | LV_154-6_0_4_line_235 |  | 225 | 235 | 0.0079393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
236 | LV_154-6_0_4_line_236 |  | 226 | 227 | 0.0045225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_154-6_0_4_line_237 |  | 228 | 229 | 0.0040379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
238 | LV_154-6_0_4_line_238 |  | 229 | 230 | 0.025397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
239 | LV_154-6_0_4_line_239 |  | 230 | 244 | 0.0041645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
240 | LV_154-6_0_4_line_240 |  | 232 | 233 | 0.018094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
241 | LV_154-6_0_4_line_241 |  | 233 | 234 | 0.0042362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
242 | LV_154-6_0_4_line_242 |  | 234 | 235 | 0.010161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
243 | LV_154-6_0_4_line_243 |  | 236 | 237 | 0.17551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
244 | LV_154-6_0_4_line_244 |  | 238 | 239 | 0.021377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_154-6_0_4_line_245 |  | 238 | 240 | 0.021655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_154-6_0_4_line_246 |  | 240 | 241 | 0.02759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_154-6_0_4_line_247 |  | 242 | 250 | 0.024505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_154-6_0_4_line_248 |  | 244 | 245 | 0.021723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
249 | LV_154-6_0_4_line_249 |  | 245 | 246 | 0.018619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
250 | LV_154-6_0_4_line_250 |  | 246 | 247 | 0.022704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
251 | LV_154-6_0_4_line_251 |  | 247 | 248 | 0.0035212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
252 | LV_154-6_0_4_line_252 |  | 249 | 250 | 0.01586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_154-6_0_4_line_253 |  | 250 | 253 | 0.01938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_154-6_0_4_line_254 |  | 251 | 252 | 0.0089336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_154-6_0_4_line_255 |  | 252 | 254 | 0.037053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_154-6_0_4_line_256 |  | 253 | 254 | 0.011418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_154-6_0_4_line_257 |  | 256 | 258 | 0.0091873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_154-6_0_4_line_258 |  | 257 | 263 | 0.0024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_154-6_0_4_line_259 |  | 258 | 260 | 0.015401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_154-6_0_4_line_260 |  | 259 | 260 | 0.02653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_154-6_0_4_line_261 |  | 259 | 261 | 0.00029712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_154-6_0_4_line_262 |  | 261 | 262 | 0.0016467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_154-6_0_4_trafo_237 | 0.63 MVA 20/0.4 kV | 264 | 248 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2688378.8102 | 1241227.2616 | 2688391.9516 | 1241204.6406
1 | 2688378.8102 | 1241227.2616 | 2688401.1047 | 1241236.2223 | 2688408.6571 | 1241231.2645 | 2688418.3951 | 1241236.3732
2 | 2687958.8564 | 1241052.4088 | 2688378.8102 | 1241227.2616
3 | 2688424.4509 | 1241239.5502 | 2688418.3951 | 1241236.3732
4 | 2687957.8686 | 1241053.9042 | 2687958.8564 | 1241052.4088
5 | 2687957.8686 | 1241053.9042 | 2687953.1771 | 1241061.0067
6 | 2688032.127 | 1240830.454 | 2688042.1975 | 1240856.6002 | 2688049.5793 | 1240880.3976
7 | 2687927.9359 | 1240827.8526 | 2687966.445 | 1240821.0625 | 2687993.5368 | 1240825.8897 | 2688014.4348 | 1240829.213 | 2688018.076 | 1240829.4672 | 2688032.127 | 1240830.454
8 | 2688470.5519 | 1241196.1164 | 2688463.1384 | 1241196.8286 | 2688440.436 | 1241205.5857 | 2688424.4509 | 1241239.5502
9 | 2687927.9359 | 1240827.8526 | 2687927.9991 | 1240815.9337 | 2687931.2768 | 1240788.6735 | 2687934.0005 | 1240779.407 | 2687939.9345 | 1240771.9117
10 | 2687927.9359 | 1240827.8526 | 2687888.0251 | 1240834.242
11 | 2687939.9345 | 1240771.9117 | 2687939.0966 | 1240759.0566 | 2687935.9518 | 1240751.3266 | 2687935.9518 | 1240751.3266
12 | 2687939.9345 | 1240771.9117 | 2687957.3065 | 1240758.5482 | 2687962.9611 | 1240756.6417 | 2687965.2359 | 1240757.4836
13 | 2687888.0251 | 1240834.242 | 2687855.9881 | 1240839.3709
14 | 2687994.2497 | 1240784.9593 | 2688001.5074 | 1240771.8462 | 2688012.2086 | 1240766.9876
15 | 2687994.2497 | 1240784.9593 | 2687989.12 | 1240779.5238 | 2687977.09 | 1240765.6465 | 2687968.9704 | 1240758.8657 | 2687965.2359 | 1240757.4836
16 | 2688046.4967 | 1240721.3993 | 2688032.4626 | 1240757.8949 | 2688025.6321 | 1240762.0856 | 2688013.2703 | 1240766.5056 | 2688012.2086 | 1240766.9876
17 | 2687837.8729 | 1240842.271 | 2687855.9881 | 1240839.3709
18 | 2688070.7254 | 1240644.4463 | 2688049.5708 | 1240713.4051 | 2688046.4967 | 1240721.3993
19 | 2687820.9281 | 1240844.9837 | 2687837.8729 | 1240842.271
20 | 2687500.0171 | 1241216.6223 | 2687472.725 | 1241215.9686
21 | 2687441.4917 | 1241212.6042 | 2687470.1093 | 1241215.906 | 2687472.725 | 1241215.9686
22 | 2687500.0171 | 1241216.6223 | 2687508.6207 | 1241216.8284
23 | 2687439.1139 | 1241212.3246 | 2687441.4917 | 1241212.6042
24 | 2687547.5659 | 1241214.2132 | 2687514.8133 | 1241216.9767 | 2687508.6207 | 1241216.8284
25 | 2687439.1139 | 1241212.3246 | 2687429.7727 | 1241238.6618
26 | 2687439.1139 | 1241212.3246 | 2687414.5764 | 1241206.6091
27 | 2687547.5659 | 1241214.2132 | 2687547.4896 | 1241225.0199 | 2687544.3841 | 1241235.1037 | 2687543.4021 | 1241237.8542
28 | 2687591.2135 | 1241209.498 | 2687556.8734 | 1241213.2497 | 2687547.5659 | 1241214.2132
29 | 2687429.7727 | 1241238.6618 | 2687423.5838 | 1241248.6446 | 2687421.9433 | 1241252.1082
30 | 2687429.7727 | 1241238.6618 | 2687438.2945 | 1241248.7266
31 | 2687414.5764 | 1241206.6091 | 2687385.7075 | 1241199.8847 | 2687378.8178 | 1241198.2813
32 | 2687310.7336 | 1241185.9936 | 2687342.9457 | 1241190.1594 | 2687351.7886 | 1241191.9908
33 | 2687310.7336 | 1241185.9936 | 2687302.4663 | 1241278.1281 | 2687299.9396 | 1241282.8277
34 | 2687351.7886 | 1241191.9908 | 2687344.4855 | 1241234.121
35 | 2687351.7886 | 1241191.9908 | 2687378.8178 | 1241198.2813
36 | 2687341.674 | 1241250.3401 | 2687344.4855 | 1241234.121
37 | 2687591.2135 | 1241209.498 | 2687592.737 | 1241203.6162 | 2687594.7157 | 1241198.1525 | 2687596.0354 | 1241194.003
38 | 2687591.2135 | 1241209.498 | 2687589.2355 | 1241218.4976 | 2687587.8324 | 1241222.8801 | 2687584.0983 | 1241234.5669 | 2687583.5205 | 1241236.4329
39 | 2687591.2135 | 1241209.498 | 2687618.2367 | 1241206.6111
40 | 2687603.5313 | 1241176.7336 | 2687600.1397 | 1241181.0979 | 2687596.0354 | 1241194.003
41 | 2687581.5178 | 1241242.8998 | 2687583.5205 | 1241236.4329
42 | 2687535.9286 | 1241258.7852 | 2687543.4021 | 1241237.8542
43 | 2687412.5023 | 1241273.7551 | 2687413.04 | 1241270.9055 | 2687421.9433 | 1241252.1082
44 | 2687380.2224 | 1241107.3431 | 2687401.2668 | 1241085.1415
45 | 2687401.2668 | 1241085.1415 | 2687411.4745 | 1241074.3725 | 2687413.5148 | 1241073.1592
46 | 2687605.7032 | 1241174.5752 | 2687603.5313 | 1241176.7336
47 | 2687581.5178 | 1241242.8998 | 2687576.4638 | 1241259.2201
48 | 2687412.4131 | 1241274.2279 | 2687412.5023 | 1241273.7551
49 | 2687605.7032 | 1241174.5752 | 2687607.9827 | 1241172.2961 | 2687612.1182 | 1241158.3827
50 | 2687605.7032 | 1241174.5752 | 2687613.994 | 1241184.0013
51 | 2687605.7032 | 1241174.5752 | 2687590.9744 | 1241157.0713
52 | 2687572.5129 | 1241271.9781 | 2687576.4638 | 1241259.2201
53 | 2687475.3376 | 1241279.0033 | 2687476.9615 | 1241279.9604
54 | 2687507.8998 | 1241298.1118 | 2687494.9823 | 1241290.5826 | 2687476.9615 | 1241279.9604
55 | 2687507.8998 | 1241298.1118 | 2687508.7575 | 1241298.5283
56 | 2687507.8998 | 1241298.1118 | 2687502.6957 | 1241311.7186
57 | 2687508.7575 | 1241298.5283 | 2687523.6061 | 1241305.7378 | 2687529.7292 | 1241308.7547
58 | 2687502.6957 | 1241311.7186 | 2687502.009 | 1241313.514 | 2687500.8695 | 1241316.5424
59 | 2687552.4433 | 1241319.9461 | 2687529.7292 | 1241308.7547
60 | 2687500.8695 | 1241316.5424 | 2687493.5359 | 1241336.0322
61 | 2687556.975 | 1241322.153 | 2687555.3155 | 1241321.3612 | 2687552.4433 | 1241319.9461
62 | 2687494.2322 | 1241350.8281 | 2687493.1593 | 1241348.0421 | 2687492.5099 | 1241338.7591 | 2687493.5359 | 1241336.0322
63 | 2687556.975 | 1241322.153 | 2687563.6706 | 1241300.5316
64 | 2687556.975 | 1241322.153 | 2687560.3954 | 1241323.7983
65 | 2687494.2322 | 1241350.8281 | 2687496.036 | 1241355.5122 | 2687503.3804 | 1241361.8276
66 | 2687560.3954 | 1241323.7983 | 2687572.5344 | 1241329.6374
67 | 2687581.0653 | 1241333.741 | 2687572.5344 | 1241329.6374
68 | 2687589.891 | 1241337.9834 | 2687582.4203 | 1241334.3928 | 2687581.0653 | 1241333.741
69 | 2687589.891 | 1241337.9834 | 2687592.7502 | 1241342.5289 | 2687591.9873 | 1241348.1106 | 2687588.7836 | 1241354.7254
70 | 2687589.891 | 1241337.9834 | 2687597.4337 | 1241338.7508 | 2687619.8498 | 1241347.7104 | 2687630.7025 | 1241352.185 | 2687665.5599 | 1241361.4731 | 2687645.7651 | 1241422.2919
71 | 2687563.6706 | 1241300.5316 | 2687568.8252 | 1241283.8865
72 | 2687579.4362 | 1241374.0254 | 2687588.7836 | 1241354.7254
73 | 2687645.7651 | 1241422.2919 | 2687636.7223 | 1241421.2243 | 2687609.0088 | 1241417.7015 | 2687596.4311 | 1241425.0769
74 | 2687572.5129 | 1241271.9781 | 2687568.8252 | 1241283.8865
75 | 2687579.4362 | 1241374.0254 | 2687577.2105 | 1241378.6209
76 | 2687596.4311 | 1241425.0769 | 2687596.4311 | 1241425.0769 | 2687587.447 | 1241436.4636
77 | 2687574.564 | 1241384.0854 | 2687577.2105 | 1241378.6209
78 | 2687758.5561 | 1241158.2209 | 2687753.9084 | 1241160.0757 | 2687737.2526 | 1241167.0458 | 2687714.7248 | 1241176.3419 | 2687708.3785 | 1241179.039
79 | 2687758.5561 | 1241158.2209 | 2687768.4751 | 1241154.2646 | 2687785.1425 | 1241147.5395 | 2687792.6556 | 1241144.3872
80 | 2687708.3785 | 1241179.039 | 2687694.289 | 1241184.6395
81 | 2687708.3785 | 1241179.039 | 2687709.0903 | 1241164.1386
82 | 2687803.1386 | 1241140.0113 | 2687800.604 | 1241141.0523 | 2687792.6556 | 1241144.3872
83 | 2687678.2201 | 1241190.9577 | 2687669.7097 | 1241193.7452 | 2687662.2853 | 1241195.7148
84 | 2687662.2853 | 1241195.7148 | 2687647.2704 | 1241199.6293 | 2687640.4792 | 1241200.7076 | 2687635.2636 | 1241200.0634 | 2687633.5892 | 1241199.5169
85 | 2687659.4283 | 1241201.2544 | 2687663.1145 | 1241200.4972 | 2687662.2853 | 1241195.7148
86 | 2687678.2201 | 1241190.9577 | 2687686.5328 | 1241187.7226 | 2687694.289 | 1241184.6395
87 | 2687633.5892 | 1241199.5169 | 2687630.4473 | 1241198.4912 | 2687625.6031 | 1241195.7399 | 2687621.8782 | 1241192.9718 | 2687616.1668 | 1241186.4717 | 2687613.994 | 1241184.0013
88 | 2687659.4283 | 1241201.2544 | 2687660.9395 | 1241209.0046 | 2687662.539 | 1241213.854 | 2687668.6304 | 1241222.349
89 | 2687810.4032 | 1241137.0276 | 2687814.7315 | 1241135.2903 | 2687831.2644 | 1241128.4633 | 2687850.6012 | 1241120.21 | 2687851.6438 | 1241119.7268
90 | 2687810.4032 | 1241137.0276 | 2687822.76 | 1241111.8372
91 | 2687810.4032 | 1241137.0276 | 2687803.1386 | 1241140.0113
92 | 2687851.6438 | 1241119.7268 | 2687862.8903 | 1241114.5142
93 | 2687822.76 | 1241111.8372 | 2687834.0557 | 1241088.8099
94 | 2687587.447 | 1241436.4636 | 2687580.3219 | 1241445.4941
95 | 2687574.564 | 1241384.0854 | 2687572.9303 | 1241387.4584
96 | 2687561.565 | 1241394.091 | 2687562.0871 | 1241394.3477 | 2687566.8882 | 1241394.3741 | 2687570.6954 | 1241392.0731 | 2687572.9303 | 1241387.4584
97 | 2687561.565 | 1241394.091 | 2687559.8558 | 1241393.2503
98 | 2687503.3804 | 1241361.8276 | 2687509.7437 | 1241367.2994
99 | 2687530.0409 | 1241378.5857 | 2687513.2842 | 1241370.3439 | 2687509.7437 | 1241367.2994
100 | 2687530.0409 | 1241378.5857 | 2687530.2433 | 1241378.6853
101 | 2687530.2433 | 1241378.6853 | 2687532.2315 | 1241379.6632
102 | 2687407.3067 | 1241301.2868 | 2687412.4131 | 1241274.2279
103 | 2687406.7081 | 1241304.459 | 2687407.3067 | 1241301.2868
104 | 2687617.3252 | 1241139.788 | 2687615.0804 | 1241148.4167 | 2687612.1182 | 1241158.3827
105 | 2687590.9744 | 1241157.0713 | 2687589.3319 | 1241155.1195 | 2687577.7684 | 1241141.7915
106 | 2687482.4667 | 1241039.4038 | 2687492.9089 | 1241035.0209
107 | 2687482.4667 | 1241039.4038 | 2687462.4201 | 1241047.0918 | 2687444.4458 | 1241054.766 | 2687436.3228 | 1241059.5963
108 | 2687482.4667 | 1241039.4038 | 2687470.5633 | 1241030.7443 | 2687440.4714 | 1241010.4307 | 2687437.1147 | 1241007.6236
109 | 2687492.9089 | 1241035.0209 | 2687502.3262 | 1241031.0682 | 2687515.7036 | 1241025.2377
110 | 2687413.5148 | 1241073.1592 | 2687436.3228 | 1241059.5963
111 | 2687426.0932 | 1240998.4071 | 2687437.1147 | 1241007.6236
112 | 2687675.6079 | 1241152.3021 | 2687683.3625 | 1241150.2438
113 | 2687675.6079 | 1241152.3021 | 2687666.9967 | 1241148.6055 | 2687651.1961 | 1241148.372
114 | 2687694.2983 | 1241147.3412 | 2687683.3625 | 1241150.2438
115 | 2687651.1961 | 1241148.372 | 2687649.2302 | 1241147.681
116 | 2687694.2983 | 1241147.3412 | 2687699.9204 | 1241150.6711 | 2687704.0549 | 1241158.9716 | 2687709.0903 | 1241164.1386
117 | 2687941.1026 | 1241079.2867 | 2687931.8633 | 1241082.7746 | 2687918.992 | 1241087.4318
118 | 2687941.1026 | 1241079.2867 | 2687948.1509 | 1241068.616
119 | 2687918.992 | 1241087.4318 | 2687909.3445 | 1241091.3094
120 | 2687948.1509 | 1241068.616 | 2687951.8352 | 1241063.0384
121 | 2687909.3445 | 1241091.3094 | 2687906.425 | 1241092.4828 | 2687900.4439 | 1241097.0531 | 2687884.8085 | 1241104.5382 | 2687868.0602 | 1241112.118 | 2687862.8903 | 1241114.5142
122 | 2687834.0557 | 1241088.8099 | 2687845.1704 | 1241066.1517
123 | 2687617.3252 | 1241139.788 | 2687624.2651 | 1241113.099
124 | 2687577.7684 | 1241141.7915 | 2687570.6472 | 1241133.5837 | 2687563.2153 | 1241124.9206
125 | 2687533.5916 | 1241017.4413 | 2687515.7036 | 1241025.2377
126 | 2687426.0932 | 1240998.4071 | 2687415.0647 | 1240989.1847
127 | 2687629.1746 | 1241094.2185 | 2687624.2651 | 1241113.099
128 | 2687549.6734 | 1241109.1097 | 2687550.6871 | 1241110.3167 | 2687563.2153 | 1241124.9206
129 | 2687533.5916 | 1241017.4413 | 2687525.7924 | 1241004.0339
130 | 2687533.5916 | 1241017.4413 | 2687550.3458 | 1241030.6161
131 | 2687397.2804 | 1240974.3128 | 2687415.0647 | 1240989.1847
132 | 2687397.2804 | 1240974.3128 | 2687385.1366 | 1240960.6377
133 | 2687436.451 | 1240914.5761 | 2687434.937 | 1240918.5266 | 2687434.7427 | 1240918.8514
134 | 2687439.1462 | 1240907.5438 | 2687436.451 | 1240914.5761
135 | 2687439.1462 | 1240907.5438 | 2687444.1788 | 1240894.4123
136 | 2687421.0559 | 1240804.9172 | 2687408.2915 | 1240812.5793 | 2687402.8714 | 1240819.2508
137 | 2687354.2012 | 1240706.6394 | 2687335.6628 | 1240727.9155 | 2687310.9023 | 1240756.283 | 2687337.8754 | 1240778.9852 | 2687352.5663 | 1240788.9197 | 2687359.2978 | 1240781.6467 | 2687421.0559 | 1240804.9172
138 | 2687421.0559 | 1240804.9172 | 2687434.2728 | 1240798.8852 | 2687458.4236 | 1240797.5399 | 2687461.5573 | 1240798.3291
139 | 2687444.1788 | 1240894.4123 | 2687450.0265 | 1240879.1541
140 | 2687354.2012 | 1240706.6394 | 2687364.4511 | 1240715.6857 | 2687366.4534 | 1240713.747 | 2687379.2176 | 1240725.1098 | 2687386.2952 | 1240729.2615 | 2687392.5922 | 1240727.8865 | 2687394.9108 | 1240729.633 | 2687390.2071 | 1240739.382 | 2687401.1554 | 1240748.75 | 2687407.6965 | 1240747.7455 | 2687412.0422 | 1240745.3522 | 2687415.7914 | 1240741.36
141 | 2687477.6058 | 1240802.3705 | 2687461.5573 | 1240798.3291
142 | 2687452.4927 | 1240872.7191 | 2687450.0265 | 1240879.1541
143 | 2687452.4927 | 1240872.7191 | 2687456.5567 | 1240862.115 | 2687459.9924 | 1240852.3634
144 | 2687464.2815 | 1240840.1895 | 2687459.9924 | 1240852.3634
145 | 2687464.2815 | 1240840.1895 | 2687469.1682 | 1240826.3194
146 | 2687603.6437 | 1240976.169 | 2687595.9008 | 1240981.1087
147 | 2687603.6437 | 1240976.169 | 2687604.482 | 1240975.6343 | 2687624.4588 | 1240961.1199
148 | 2687575.0433 | 1240993.9905 | 2687582.3361 | 1240989.7623 | 2687595.9008 | 1240981.1087
149 | 2687636.8979 | 1240952.0822 | 2687624.4588 | 1240961.1199
150 | 2687567.7139 | 1240998.2399 | 2687575.0433 | 1240993.9905
151 | 2687656.4811 | 1240936.839 | 2687646.9293 | 1240944.7938 | 2687636.8979 | 1240952.0822
152 | 2687656.4811 | 1240936.839 | 2687661.8119 | 1240932.3995
153 | 2687666.9545 | 1240927.9955 | 2687665.1512 | 1240929.6185 | 2687661.8119 | 1240932.3995
154 | 2687513.3996 | 1240981.9339 | 2687516.7399 | 1240988.4718 | 2687525.7924 | 1241004.0339
155 | 2687556.7655 | 1241035.6643 | 2687550.3458 | 1241030.6161
156 | 2687666.9545 | 1240927.9955 | 2687672.449 | 1240923.0507
157 | 2687513.3996 | 1240981.9339 | 2687511.0208 | 1240977.2779
158 | 2687556.7655 | 1241035.6643 | 2687572.1857 | 1241047.79
159 | 2687511.0208 | 1240977.2779 | 2687506.3106 | 1240968.0587 | 2687506.3106 | 1240968.0587
160 | 2687572.1857 | 1241047.79 | 2687579.418 | 1241053.4772
161 | 2687508.7512 | 1240964.3937 | 2687506.3106 | 1240968.0587
162 | 2687579.418 | 1241053.4772 | 2687586.5208 | 1241059.0625
163 | 2687535.7801 | 1240936.4114 | 2687525.2306 | 1240946.161
164 | 2687535.7801 | 1240936.4114 | 2687539.3887 | 1240933.0764 | 2687548.8037 | 1240926.8321
165 | 2687525.2306 | 1240946.161 | 2687513.9511 | 1240956.5852 | 2687508.7512 | 1240964.3937
166 | 2687556.4277 | 1240921.7755 | 2687548.8037 | 1240926.8321
167 | 2687556.4277 | 1240921.7755 | 2687567.0721 | 1240914.7157
168 | 2687574.5354 | 1240902.4502 | 2687567.0721 | 1240914.7157
169 | 2687574.5354 | 1240902.4502 | 2687579.1647 | 1240891.871
170 | 2687574.5354 | 1240902.4502 | 2687586.88 | 1240907.3033
171 | 2687579.1647 | 1240891.871 | 2687579.3971 | 1240891.3398
172 | 2687594.4609 | 1240910.2837 | 2687586.88 | 1240907.3033
173 | 2687678.1177 | 1240917.9491 | 2687672.449 | 1240923.0507
174 | 2687680.5623 | 1240915.749 | 2687678.1177 | 1240917.9491
175 | 2687477.6058 | 1240802.3705 | 2687469.1682 | 1240826.3194
176 | 2687477.6058 | 1240802.3705 | 2687495.9168 | 1240806.788 | 2687496.8011 | 1240807.0141
177 | 2687522.19 | 1240813.5059 | 2687496.8011 | 1240807.0141
178 | 2687592.187 | 1240857.2428 | 2687580.7572 | 1240888.2316 | 2687579.3971 | 1240891.3398
179 | 2687594.4609 | 1240910.2837 | 2687600.6735 | 1240912.7261
180 | 2687592.187 | 1240857.2428 | 2687594.8784 | 1240849.9456
181 | 2687617.1645 | 1240919.2093 | 2687600.6735 | 1240912.7261
182 | 2687601.1519 | 1240832.9367 | 2687594.8784 | 1240849.9456
183 | 2687623.7586 | 1240921.8017 | 2687617.1645 | 1240919.2093
184 | 2687522.19 | 1240813.5059 | 2687524.2918 | 1240814.0434
185 | 2687532.8801 | 1240816.2393 | 2687524.2918 | 1240814.0434
186 | 2687532.8801 | 1240816.2393 | 2687555.0574 | 1240821.91
187 | 2687644.6494 | 1240844.0401 | 2687647.8848 | 1240844.866
188 | 2687665.6032 | 1240849.3889 | 2687647.8848 | 1240844.866
189 | 2687665.6032 | 1240849.3889 | 2687670.8613 | 1240825.8692
190 | 2687665.6032 | 1240849.3889 | 2687672.8404 | 1240851.3156
191 | 2687670.8613 | 1240825.8692 | 2687674.6605 | 1240808.8754
192 | 2687681.3074 | 1240853.5697 | 2687672.8404 | 1240851.3156
193 | 2687601.1519 | 1240832.9367 | 2687577.4623 | 1240827.6388
194 | 2687577.4623 | 1240827.6388 | 2687582.9566 | 1240808.7076
195 | 2687577.4623 | 1240827.6388 | 2687560.6083 | 1240823.3294
196 | 2687677.0773 | 1240798.0653 | 2687674.6605 | 1240808.8754
197 | 2687681.3074 | 1240853.5697 | 2687693.023 | 1240856.6886
198 | 2687588.3458 | 1240790.1387 | 2687582.9566 | 1240808.7076
199 | 2687560.6083 | 1240823.3294 | 2687555.0574 | 1240821.91
200 | 2687681.3285 | 1240783.6509 | 2687677.0773 | 1240798.0653
201 | 2687677.0773 | 1240798.0653 | 2687668.1843 | 1240798.8083
202 | 2687693.023 | 1240856.6886 | 2687694.9865 | 1240857.2114
203 | 2687588.3458 | 1240790.1387 | 2687596.5569 | 1240792.8132
204 | 2687588.3458 | 1240790.1387 | 2687575.9881 | 1240785.6311
205 | 2687681.3285 | 1240783.6509 | 2687694.5171 | 1240786.319
206 | 2687659.6155 | 1240799.5242 | 2687668.1843 | 1240798.8083
207 | 2687715.9883 | 1240862.8025 | 2687694.9865 | 1240857.2114
208 | 2687718.1798 | 1240863.5127 | 2687717.2988 | 1240863.1514 | 2687715.9883 | 1240862.8025
209 | 2687733.6395 | 1240874.4677 | 2687724.9205 | 1240866.2774 | 2687718.1798 | 1240863.5127
210 | 2687733.6395 | 1240874.4677 | 2687722.4435 | 1240881.3962 | 2687709.7916 | 1240890.5101
211 | 2687691.9045 | 1240905.5415 | 2687703.8545 | 1240894.7869 | 2687709.7916 | 1240890.5101
212 | 2687683.9239 | 1240912.7237 | 2687691.9045 | 1240905.5415
213 | 2687785.6567 | 1240850.6304 | 2687762.544 | 1240859.2143
214 | 2687785.6567 | 1240850.6304 | 2687820.9281 | 1240844.9837
215 | 2687785.6567 | 1240850.6304 | 2687789.9119 | 1240824.9116
216 | 2687610.7126 | 1240797.4239 | 2687596.5569 | 1240792.8132
217 | 2687568.7314 | 1240782.9842 | 2687575.9881 | 1240785.6311
218 | 2687562.0724 | 1240780.5553 | 2687568.7314 | 1240782.9842
219 | 2687619.8497 | 1240800.4 | 2687619.8497 | 1240800.4 | 2687610.7126 | 1240797.4239
220 | 2687619.8497 | 1240800.4 | 2687622.8912 | 1240800.3895
221 | 2687636.6951 | 1240800.3421 | 2687622.8912 | 1240800.3895
222 | 2687659.6155 | 1240799.5242 | 2687650.3875 | 1240800.2951 | 2687645.3676 | 1240800.3123
223 | 2687636.9603 | 1240800.3412 | 2687645.3676 | 1240800.3123
224 | 2687636.6951 | 1240800.3421 | 2687636.9603 | 1240800.3412
225 | 2687697.0191 | 1240786.8252 | 2687694.5171 | 1240786.319
226 | 2687697.0191 | 1240786.8252 | 2687706.7071 | 1240788.7851 | 2687710.4868 | 1240789.5868
227 | 2687710.4868 | 1240789.5868 | 2687720.3387 | 1240791.6766
228 | 2687732.6587 | 1240794.2899 | 2687732.2807 | 1240794.2097
229 | 2687732.6587 | 1240794.2899 | 2687742.3084 | 1240796.3367
230 | 2687732.2807 | 1240794.2097 | 2687720.3387 | 1240791.6766
231 | 2687757.1166 | 1240799.4778 | 2687742.3084 | 1240796.3367
232 | 2687757.134 | 1240799.4815 | 2687757.1166 | 1240799.4778
233 | 2687757.134 | 1240799.4815 | 2687766.9955 | 1240801.5733
234 | 2687771.0146 | 1240802.4258 | 2687766.9955 | 1240801.5733
235 | 2687778.7811 | 1240804.0732 | 2687771.0146 | 1240802.4258
236 | 2687680.5623 | 1240915.749 | 2687683.9239 | 1240912.7237
237 | 2687589.6949 | 1241061.5584 | 2687586.5208 | 1241059.0625
238 | 2687609.6589 | 1241077.2572 | 2687589.6949 | 1241061.5584
239 | 2687612.9325 | 1241079.8314 | 2687609.6589 | 1241077.2572
240 | 2687792.8654 | 1240807.0607 | 2687789.9119 | 1240824.9116
241 | 2687788.7214 | 1240806.1817 | 2687792.8654 | 1240807.0607 | 2687792.8654 | 1240807.0607
242 | 2687788.7214 | 1240806.1817 | 2687778.7811 | 1240804.0732
243 | 2688070.7254 | 1240644.4463 | 2688018.6884 | 1240476.8319
244 | 2687535.9252 | 1241092.7404 | 2687549.6734 | 1241109.1097
245 | 2687535.9252 | 1241092.7404 | 2687534.3755 | 1241090.8954 | 2687521.7324 | 1241076.3853
246 | 2687503.6405 | 1241055.5556 | 2687505.2932 | 1241057.5423 | 2687518.0536 | 1241072.1633 | 2687521.7324 | 1241076.3853
247 | 2687694.2983 | 1241147.3412 | 2687701.6178 | 1241138.1537 | 2687703.355 | 1241125.5034
248 | 2687629.1746 | 1241094.2185 | 2687619.8544 | 1241085.2745 | 2687612.9325 | 1241079.8314
249 | 2687629.1746 | 1241094.2185 | 2687637.3145 | 1241077.4735
250 | 2687637.3145 | 1241077.4735 | 2687647.2404 | 1241057.0543
251 | 2687648.7798 | 1241053.8874 | 2687647.2404 | 1241057.0543
252 | 2687703.355 | 1241125.5034 | 2687691.2867 | 1241117.8084 | 2687689.7457 | 1241117.6742
253 | 2687703.355 | 1241125.5034 | 2687703.7364 | 1241122.7182 | 2687714.4635 | 1241110.0901
254 | 2687708.3719 | 1241066.8537 | 2687708.2231 | 1241067.3107 | 2687704.1199 | 1241074.701
255 | 2687704.1199 | 1241074.701 | 2687699.9261 | 1241082.2546 | 2687717.2871 | 1241094.0863 | 2687720.7901 | 1241100.6095 | 2687720.7901 | 1241100.6095
256 | 2687720.7901 | 1241100.6095 | 2687716.0496 | 1241108.2228 | 2687714.4635 | 1241110.0901
257 | 2687849.2165 | 1241057.9033 | 2687845.1704 | 1241066.1517
258 | 2687953.1771 | 1241061.0067 | 2687951.8352 | 1241063.0384
259 | 2687849.2165 | 1241057.9033 | 2687855.9994 | 1241044.0759
260 | 2687867.6832 | 1241020.2575 | 2687855.9994 | 1241044.0759
261 | 2687867.6832 | 1241020.2575 | 2687867.8141 | 1241019.9907
262 | 2687868.5393 | 1241018.5123 | 2687867.8141 | 1241019.9907

## bus_geodata
| x | y | coords
0 | 2688391.9516 | 1241204.6406
1 | 2688378.8102 | 1241227.2616
2 | 2688418.3951 | 1241236.3732
3 | 2687958.8564 | 1241052.4088
4 | 2687957.8686 | 1241053.9042
5 | 2688049.5793 | 1240880.3976
6 | 2688032.127 | 1240830.454
7 | 2688424.4509 | 1241239.5502
8 | 2688470.5519 | 1241196.1164
9 | 2687927.9359 | 1240827.8526
10 | 2687939.9345 | 1240771.9117
11 | 2687888.0251 | 1240834.242
12 | 2687994.2497 | 1240784.9593
13 | 2688012.2086 | 1240766.9876
14 | 2687965.2359 | 1240757.4836
15 | 2687935.9518 | 1240751.3266
16 | 2687855.9881 | 1240839.3709
17 | 2688046.4967 | 1240721.3993
18 | 2687837.8729 | 1240842.271
19 | 2687472.725 | 1241215.9686
20 | 2687500.0171 | 1241216.6223
21 | 2687441.4917 | 1241212.6042
22 | 2687508.6207 | 1241216.8284
23 | 2687439.1139 | 1241212.3246
24 | 2687547.5659 | 1241214.2132
25 | 2687429.7727 | 1241238.6618
26 | 2687414.5764 | 1241206.6091
27 | 2687310.7336 | 1241185.9936
28 | 2687351.7886 | 1241191.9908
29 | 2687299.9396 | 1241282.8277
30 | 2687344.4855 | 1241234.121
31 | 2687378.8178 | 1241198.2813
32 | 2687591.2135 | 1241209.498
33 | 2687596.0354 | 1241194.003
34 | 2687583.5205 | 1241236.4329
35 | 2687618.2367 | 1241206.6111
36 | 2687543.4021 | 1241237.8542
37 | 2687421.9433 | 1241252.1082
38 | 2687438.2945 | 1241248.7266
39 | 2687380.2224 | 1241107.3431
40 | 2687401.2668 | 1241085.1415
41 | 2687341.674 | 1241250.3401
42 | 2687603.5313 | 1241176.7336
43 | 2687581.5178 | 1241242.8998
44 | 2687535.9286 | 1241258.7852
45 | 2687412.5023 | 1241273.7551
46 | 2687605.7032 | 1241174.5752
47 | 2687576.4638 | 1241259.2201
48 | 2687476.9615 | 1241279.9604
49 | 2687475.3376 | 1241279.0033
50 | 2687507.8998 | 1241298.1118
51 | 2687508.7575 | 1241298.5283
52 | 2687502.6957 | 1241311.7186
53 | 2687529.7292 | 1241308.7547
54 | 2687500.8695 | 1241316.5424
55 | 2687552.4433 | 1241319.9461
56 | 2687493.5359 | 1241336.0322
57 | 2687556.975 | 1241322.153
58 | 2687494.2322 | 1241350.8281
59 | 2687572.5344 | 1241329.6374
60 | 2687560.3954 | 1241323.7983
61 | 2687581.0653 | 1241333.741
62 | 2687589.891 | 1241337.9834
63 | 2687563.6706 | 1241300.5316
64 | 2687588.7836 | 1241354.7254
65 | 2687645.7651 | 1241422.2919
66 | 2687568.8252 | 1241283.8865
67 | 2687579.4362 | 1241374.0254
68 | 2687596.4311 | 1241425.0769
69 | 2687572.5129 | 1241271.9781
70 | 2687577.2105 | 1241378.6209
71 | 2687758.5561 | 1241158.2209
72 | 2687708.3785 | 1241179.039
73 | 2687792.6556 | 1241144.3872
74 | 2687662.2853 | 1241195.7148
75 | 2687678.2201 | 1241190.9577
76 | 2687633.5892 | 1241199.5169
77 | 2687659.4283 | 1241201.2544
78 | 2687694.289 | 1241184.6395
79 | 2687810.4032 | 1241137.0276
80 | 2687851.6438 | 1241119.7268
81 | 2687822.76 | 1241111.8372
82 | 2687803.1386 | 1241140.0113
83 | 2687668.6304 | 1241222.349
84 | 2687587.447 | 1241436.4636
85 | 2687574.564 | 1241384.0854
86 | 2687572.9303 | 1241387.4584
87 | 2687561.565 | 1241394.091
88 | 2687503.3804 | 1241361.8276
89 | 2687509.7437 | 1241367.2994
90 | 2687530.2433 | 1241378.6853
91 | 2687530.0409 | 1241378.5857
92 | 2687532.2315 | 1241379.6632
93 | 2687559.8558 | 1241393.2503
94 | 2687407.3067 | 1241301.2868
95 | 2687412.4131 | 1241274.2279
96 | 2687406.7081 | 1241304.459
97 | 2687612.1182 | 1241158.3827
98 | 2687613.994 | 1241184.0013
99 | 2687590.9744 | 1241157.0713
100 | 2687482.4667 | 1241039.4038
101 | 2687492.9089 | 1241035.0209
102 | 2687436.3228 | 1241059.5963
103 | 2687437.1147 | 1241007.6236
104 | 2687675.6079 | 1241152.3021
105 | 2687683.3625 | 1241150.2438
106 | 2687651.1961 | 1241148.372
107 | 2687709.0903 | 1241164.1386
108 | 2687941.1026 | 1241079.2867
109 | 2687918.992 | 1241087.4318
110 | 2687948.1509 | 1241068.616
111 | 2687862.8903 | 1241114.5142
112 | 2687834.0557 | 1241088.8099
113 | 2687617.3252 | 1241139.788
114 | 2687577.7684 | 1241141.7915
115 | 2687515.7036 | 1241025.2377
116 | 2687413.5148 | 1241073.1592
117 | 2687426.0932 | 1240998.4071
118 | 2687624.2651 | 1241113.099
119 | 2687563.2153 | 1241124.9206
120 | 2687533.5916 | 1241017.4413
121 | 2687415.0647 | 1240989.1847
122 | 2687580.3219 | 1241445.4941
123 | 2687385.1366 | 1240960.6377
124 | 2687397.2804 | 1240974.3128
125 | 2687434.7427 | 1240918.8514
126 | 2687436.451 | 1240914.5761
127 | 2687439.1462 | 1240907.5438
128 | 2687402.8714 | 1240819.2508
129 | 2687421.0559 | 1240804.9172
130 | 2687444.1788 | 1240894.4123
131 | 2687354.2012 | 1240706.6394
132 | 2687461.5573 | 1240798.3291
133 | 2687450.0265 | 1240879.1541
134 | 2687452.4927 | 1240872.7191
135 | 2687459.9924 | 1240852.3634
136 | 2687464.2815 | 1240840.1895
137 | 2687603.6437 | 1240976.169
138 | 2687595.9008 | 1240981.1087
139 | 2687624.4588 | 1240961.1199
140 | 2687575.0433 | 1240993.9905
141 | 2687636.8979 | 1240952.0822
142 | 2687567.7139 | 1240998.2399
143 | 2687656.4811 | 1240936.839
144 | 2687661.8119 | 1240932.3995
145 | 2687525.7924 | 1241004.0339
146 | 2687550.3458 | 1241030.6161
147 | 2687666.9545 | 1240927.9955
148 | 2687513.3996 | 1240981.9339
149 | 2687556.7655 | 1241035.6643
150 | 2687511.0208 | 1240977.2779
151 | 2687572.1857 | 1241047.79
152 | 2687506.3106 | 1240968.0587
153 | 2687579.418 | 1241053.4772
154 | 2687535.7801 | 1240936.4114
155 | 2687525.2306 | 1240946.161
156 | 2687548.8037 | 1240926.8321
157 | 2687508.7512 | 1240964.3937
158 | 2687556.4277 | 1240921.7755
159 | 2687567.0721 | 1240914.7157
160 | 2687574.5354 | 1240902.4502
161 | 2687579.1647 | 1240891.871
162 | 2687586.88 | 1240907.3033
163 | 2687672.449 | 1240923.0507
164 | 2687678.1177 | 1240917.9491
165 | 2687469.1682 | 1240826.3194
166 | 2687477.6058 | 1240802.3705
167 | 2687496.8011 | 1240807.0141
168 | 2687579.3971 | 1240891.3398
169 | 2687594.4609 | 1240910.2837
170 | 2687592.187 | 1240857.2428
171 | 2687600.6735 | 1240912.7261
172 | 2687594.8784 | 1240849.9456
173 | 2687617.1645 | 1240919.2093
174 | 2687623.7586 | 1240921.8017
175 | 2687522.19 | 1240813.5059
176 | 2687524.2918 | 1240814.0434
177 | 2687415.7914 | 1240741.36
178 | 2687532.8801 | 1240816.2394
179 | 2687647.8848 | 1240844.866
180 | 2687644.6494 | 1240844.0401
181 | 2687665.6032 | 1240849.3889
182 | 2687670.8613 | 1240825.8692
183 | 2687672.8404 | 1240851.3156
184 | 2687601.1519 | 1240832.9367
185 | 2687577.4623 | 1240827.6388
186 | 2687674.6605 | 1240808.8754
187 | 2687681.3074 | 1240853.5697
188 | 2687582.9566 | 1240808.7076
189 | 2687560.6083 | 1240823.3294
190 | 2687677.0773 | 1240798.0653
191 | 2687693.023 | 1240856.6886
192 | 2687588.3458 | 1240790.1387
193 | 2687555.0574 | 1240821.91
194 | 2687681.3285 | 1240783.6509
195 | 2687668.1843 | 1240798.8083
196 | 2687694.9865 | 1240857.2114
197 | 2687715.9883 | 1240862.8025
198 | 2687718.1798 | 1240863.5127
199 | 2687733.6395 | 1240874.4677
200 | 2687709.7916 | 1240890.5101
201 | 2687691.9045 | 1240905.5415
202 | 2687762.544 | 1240859.2143
203 | 2687785.6567 | 1240850.6304
204 | 2687596.5569 | 1240792.8132
205 | 2687575.9881 | 1240785.6311
206 | 2687568.7314 | 1240782.9842
207 | 2687562.0724 | 1240780.5553
208 | 2687610.7126 | 1240797.4239
209 | 2687619.8497 | 1240800.4
210 | 2687622.8912 | 1240800.3895
211 | 2687659.6155 | 1240799.5242
212 | 2687645.3676 | 1240800.3123
213 | 2687636.9603 | 1240800.3412
214 | 2687694.5171 | 1240786.319
215 | 2687636.6951 | 1240800.3421
216 | 2687697.0191 | 1240786.8252
217 | 2687710.4868 | 1240789.5868
218 | 2687732.6587 | 1240794.2899
219 | 2687732.2807 | 1240794.2097
220 | 2687742.3084 | 1240796.3367
221 | 2687720.3387 | 1240791.6766
222 | 2687757.1166 | 1240799.4778
223 | 2687757.134 | 1240799.4815
224 | 2687766.9955 | 1240801.5733
225 | 2687771.0146 | 1240802.4258
226 | 2687680.5623 | 1240915.749
227 | 2687683.9239 | 1240912.7237
228 | 2687586.5208 | 1241059.0625
229 | 2687589.6949 | 1241061.5584
230 | 2687609.6589 | 1241077.2572
231 | 2687820.9281 | 1240844.9837
232 | 2687789.9119 | 1240824.9116
233 | 2687792.8654 | 1240807.0607
234 | 2687788.7214 | 1240806.1817
235 | 2687778.7811 | 1240804.0732
236 | 2688070.7254 | 1240644.4463
237 | 2688018.6884 | 1240476.8319
238 | 2687535.9252 | 1241092.7404
239 | 2687549.6734 | 1241109.1097
240 | 2687521.7324 | 1241076.3853
241 | 2687503.6405 | 1241055.5556
242 | 2687694.2983 | 1241147.3412
243 | 2687649.2302 | 1241147.681
244 | 2687612.9325 | 1241079.8314
245 | 2687629.1746 | 1241094.2185
246 | 2687637.3145 | 1241077.4735
247 | 2687647.2404 | 1241057.0543
248 | 2687648.7798 | 1241053.8874
249 | 2687689.7457 | 1241117.6742
250 | 2687703.355 | 1241125.5034
251 | 2687708.3719 | 1241066.8537
252 | 2687704.1199 | 1241074.701
253 | 2687714.4635 | 1241110.0901
254 | 2687720.7901 | 1241100.6095
255 | 2687909.3445 | 1241091.3094
256 | 2687845.1704 | 1241066.1517
257 | 2687951.8352 | 1241063.0384
258 | 2687849.2165 | 1241057.9033
259 | 2687867.6832 | 1241020.2575
260 | 2687855.9994 | 1241044.0759
261 | 2687867.8141 | 1241019.9907
262 | 2687868.5393 | 1241018.5123
263 | 2687953.1771 | 1241061.0067
264 | 2687653.4369 | 1241044.307

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97198 | -0.5409 | 0.001346 | 0.00033733
1 | 0.97201 | -0.54025 | 0 | 0
2 | 0.97183 | -0.54379 | 0.0018035 | 0.00045199
3 | 0.97443 | -0.4924 | 0.0012315 | 0.00030864
4 | 0.97444 | -0.49217 | 0.0012769 | 0.00032001
5 | 0.97013 | -0.57656 | 0.0048811 | 0.0012233
6 | 0.97037 | -0.57177 | 0 | 0
7 | 0.97181 | -0.54412 | 0 | 0
8 | 0.97165 | -0.54738 | 0.0025549 | 0.00064032
9 | 0.97061 | -0.56701 | 0 | 0
10 | 0.9705 | -0.56918 | 0 | 0
11 | 0.97073 | -0.5646 | 0.0020131 | 0.00050454
12 | 0.97039 | -0.57151 | 0 | 0
13 | 0.97034 | -0.57238 | 0.0022583 | 0.00056598
14 | 0.97045 | -0.5702 | 0.00021777 | 5.4578e-05
15 | 0.97049 | -0.56948 | 0.0007559 | 0.00018945
16 | 0.97085 | -0.56236 | 0.0016859 | 0.00042253
17 | 0.97028 | -0.57373 | 0.00040851 | 0.00010238
18 | 0.97092 | -0.56096 | 0.0015096 | 0.00037834
19 | 0.97982 | -0.38683 | 0.0051415 | 0.0012886
20 | 0.98104 | -0.36306 | 0.0019201 | 0.00048123
21 | 0.97857 | -0.41132 | 0 | 0
22 | 0.98144 | -0.35528 | 0.00083162 | 0.00020842
23 | 0.97848 | -0.41318 | 0 | 0
24 | 0.98327 | -0.31946 | 0 | 0
25 | 0.9778 | -0.42639 | 0 | 0
26 | 0.97808 | -0.42095 | 0.0052572 | 0.0013176
27 | 0.9774 | -0.4344 | 0 | 0
28 | 0.97748 | -0.43279 | 0 | 0
29 | 0.9772 | -0.4382 | 0.0021267 | 0.00053299
30 | 0.97725 | -0.43734 | 0.0031739 | 0.00079546
31 | 0.97768 | -0.42876 | 0.003707 | 0.00092907
32 | 0.98544 | -0.27745 | 0 | 0
33 | 0.98739 | -0.2398 | 0.0002772 | 6.9473e-05
34 | 0.98351 | -0.3149 | 0.0023555 | 0.00059034
35 | 0.98539 | -0.27832 | 0.0017898 | 0.00044856
36 | 0.98322 | -0.32059 | 0.0014546 | 0.00036455
37 | 0.97748 | -0.43268 | 0.0048631 | 0.0012188
38 | 0.97776 | -0.4273 | 0.0037962 | 0.00095142
39 | 0.98616 | -0.26356 | 0.0025929 | 0.00064984
40 | 0.98623 | -0.26214 | 0.0024682 | 0.0006186
41 | 0.97721 | -0.43814 | 0.002655 | 0.0006654
42 | 0.98968 | -0.1957 | 0 | 0
43 | 0.98306 | -0.32367 | 0.0033855 | 0.00084849
44 | 0.98319 | -0.32104 | 0.0011252 | 0.000282
45 | 0.9771 | -0.44016 | 0.0046783 | 0.0011725
46 | 0.99005 | -0.18864 | 0 | 0
47 | 0.98197 | -0.34481 | 0.0024517 | 0.00061446
48 | 0.97645 | -0.45294 | 0.0027787 | 0.0006964
49 | 0.97644 | -0.45303 | 0.002478 | 0.00062104
50 | 0.97662 | -0.4495 | 0 | 0
51 | 0.97665 | -0.44898 | 0.0010888 | 0.00027288
52 | 0.97629 | -0.45608 | 0.0026476 | 0.00066356
53 | 0.97732 | -0.43575 | 0.0012778 | 0.00032024
54 | 0.97618 | -0.45816 | 0.001388 | 0.00034787
55 | 0.97808 | -0.42082 | 0.0016451 | 0.00041231
56 | 0.97578 | -0.46603 | 0.0019363 | 0.00048529
57 | 0.97824 | -0.4177 | 0 | 0
58 | 0.97552 | -0.47125 | 0.0025609 | 0.00064183
59 | 0.97789 | -0.42467 | 0.0034532 | 0.00086546
60 | 0.97816 | -0.41931 | 0.001453 | 0.00036416
61 | 0.97772 | -0.42785 | 0.0021676 | 0.00054324
62 | 0.97758 | -0.43074 | 0 | 0
63 | 0.97944 | -0.39411 | 0.003387 | 0.00084885
64 | 0.97736 | -0.43505 | 0.003597 | 0.00090149
65 | 0.97713 | -0.43953 | 0 | 0
66 | 0.98043 | -0.37493 | 0.0020111 | 0.00050402
67 | 0.97717 | -0.43868 | 0.0019211 | 0.00048148
68 | 0.97697 | -0.44269 | 0.00071121 | 0.00017825
69 | 0.98115 | -0.36077 | 0.0033869 | 0.00084883
70 | 0.97714 | -0.43936 | 0.0018533 | 0.00046447
71 | 0.97962 | -0.39051 | 0 | 0
72 | 0.98229 | -0.33836 | 0 | 0
73 | 0.9778 | -0.42608 | 0.0013709 | 0.00034357
74 | 0.98547 | -0.27672 | 0 | 0
75 | 0.98439 | -0.29777 | 0 | 0
76 | 0.98746 | -0.23846 | 0.00067413 | 0.00016895
77 | 0.98546 | -0.27707 | 0 | 0
78 | 0.98326 | -0.31965 | 0.0020352 | 0.00051008
79 | 0.9769 | -0.44381 | 0 | 0
80 | 0.97601 | -0.46124 | 0.0034516 | 0.00086505
81 | 0.97618 | -0.45791 | 0.002917 | 0.00073106
82 | 0.97725 | -0.4368 | 0.0029274 | 0.00073367
83 | 0.98541 | -0.27801 | 0.0022321 | 0.00055941
84 | 0.97693 | -0.44339 | 0.0015641 | 0.000392
85 | 0.97711 | -0.43997 | 0.0013591 | 0.00034062
86 | 0.97709 | -0.44026 | 0.0019335 | 0.00048458
87 | 0.97706 | -0.44086 | 0.0011222 | 0.00028124
88 | 0.97529 | -0.4756 | 0.0035831 | 0.00089802
89 | 0.9752 | -0.47754 | 0.0021974 | 0.00055072
90 | 0.97497 | -0.48202 | 0.0017556 | 0.00044001
91 | 0.97497 | -0.48199 | 0.0018427 | 0.00046183
92 | 0.97495 | -0.4823 | 0.0067908 | 0.0017019
93 | 0.97706 | -0.4409 | 0.0010797 | 0.0002706
94 | 0.97692 | -0.44376 | 0.0040282 | 0.0010096
95 | 0.9771 | -0.44027 | 0.0056616 | 0.0014189
96 | 0.97691 | -0.44393 | 0.002914 | 0.00073033
97 | 0.99181 | -0.15505 | 0.00071163 | 0.00017835
98 | 0.98919 | -0.20516 | 0.00064104 | 0.00016066
99 | 0.98985 | -0.1926 | 0.0005003 | 0.00012539
100 | 0.987 | -0.24731 | 0 | 0
101 | 0.98719 | -0.24357 | 0.0017832 | 0.0004469
102 | 0.9865 | -0.25695 | 0.0030356 | 0.00076078
103 | 0.9866 | -0.25499 | 0.0016433 | 0.00041186
104 | 0.98177 | -0.34865 | 0 | 0
105 | 0.98177 | -0.34853 | 0.0020356 | 0.00051016
106 | 0.98175 | -0.34901 | 0 | 0
107 | 0.98208 | -0.34246 | 0.0020355 | 0.00051014
108 | 0.97473 | -0.48641 | 0 | 0
109 | 0.97499 | -0.48136 | 0.0013402 | 0.00033589
110 | 0.97459 | -0.48916 | 0.0010607 | 0.00026585
111 | 0.9758 | -0.4653 | 0.0036518 | 0.00091523
112 | 0.97559 | -0.46944 | 0.0021907 | 0.00054904
113 | 0.99277 | -0.13676 | 0 | 0
114 | 0.98968 | -0.19592 | 0.0013906 | 0.00034851
115 | 0.98765 | -0.23461 | 0.0019652 | 0.00049253
116 | 0.98631 | -0.26058 | 0.0025729 | 0.00064484
117 | 0.98652 | -0.25656 | 0.0012722 | 0.00031885
118 | 0.99414 | -0.11069 | 0.0011302 | 0.00028326
119 | 0.98952 | -0.19903 | 0.0016646 | 0.00041718
120 | 0.98805 | -0.22688 | 0 | 0
121 | 0.98646 | -0.2578 | 0.0021827 | 0.00054704
122 | 0.97692 | -0.44362 | 0.0010762 | 0.00026972
123 | 0.98636 | -0.25977 | 0.0026479 | 0.00066363
124 | 0.9864 | -0.2589 | 0 | 0
125 | 0.97216 | -0.53623 | 0.0017801 | 0.00044614
126 | 0.97217 | -0.53608 | 0.0016593 | 0.00041586
127 | 0.9722 | -0.5356 | 0.0016383 | 0.00041059
128 | 0.97297 | -0.52029 | 0.0014102 | 0.00035344
129 | 0.973 | -0.51968 | 0 | 0
130 | 0.97226 | -0.53428 | 0.0014914 | 0.00037379
131 | 0.97237 | -0.53222 | 0 | 0
132 | 0.97319 | -0.51589 | 0.0060935 | 0.0015272
133 | 0.97236 | -0.5323 | 0.0022937 | 0.00057484
134 | 0.97242 | -0.53118 | 0.0020474 | 0.00051312
135 | 0.97264 | -0.52681 | 0.00089535 | 0.00022439
136 | 0.97278 | -0.52401 | 0.0025895 | 0.00064898
137 | 0.97016 | -0.57578 | 0.0011157 | 0.00027962
138 | 0.97013 | -0.57643 | 0.0011527 | 0.0002889
139 | 0.97028 | -0.57341 | 0.0020511 | 0.00051405
140 | 0.97007 | -0.57766 | 0.0013703 | 0.00034344
141 | 0.97038 | -0.57141 | 0.0036628 | 0.00091799
142 | 0.97006 | -0.57787 | 0.0013396 | 0.00033574
143 | 0.97063 | -0.56649 | 0.0017989 | 0.00045085
144 | 0.97071 | -0.56489 | 0.0015566 | 0.00039013
145 | 0.98726 | -0.24191 | 0.0016824 | 0.00042165
146 | 0.98923 | -0.20417 | 0.0032571 | 0.00081632
147 | 0.9708 | -0.56313 | 0.003516 | 0.0008812
148 | 0.98599 | -0.26633 | 0.0011801 | 0.00029576
149 | 0.98969 | -0.19536 | 0.0029805 | 0.00074697
150 | 0.98573 | -0.27135 | 0.0020154 | 0.00050511
151 | 0.99081 | -0.17397 | 0.0020693 | 0.00051861
152 | 0.98522 | -0.2812 | 0.0016321 | 0.00040904
153 | 0.99134 | -0.16387 | 0.0014331 | 0.00035916
154 | 0.98311 | -0.32193 | 0.0023644 | 0.00059257
155 | 0.9838 | -0.30861 | 0.003345 | 0.00083834
156 | 0.98235 | -0.3368 | 0.0018523 | 0.00046423
157 | 0.985 | -0.28536 | 0.0013375 | 0.00033522
158 | 0.98192 | -0.34513 | 0.0045396 | 0.0011377
159 | 0.98133 | -0.3565 | 0.0012125 | 0.00030389
160 | 0.98068 | -0.36923 | 0 | 0
161 | 0.98017 | -0.37902 | 0.0024401 | 0.00061155
162 | 0.98057 | -0.37133 | 0.0010063 | 0.00025219
163 | 0.97092 | -0.56073 | 0.001119 | 0.00028046
164 | 0.97106 | -0.55809 | 0.0013938 | 0.00034931
165 | 0.97298 | -0.52011 | 0.0017946 | 0.00044977
166 | 0.97336 | -0.51254 | 0 | 0
167 | 0.97386 | -0.50266 | 0.0034702 | 0.00086971
168 | 0.98015 | -0.3795 | 0.0024494 | 0.00061387
169 | 0.98051 | -0.37248 | 0.00098728 | 0.00024744
170 | 0.9786 | -0.40963 | 0.0024715 | 0.00061941
171 | 0.98047 | -0.3733 | 0.0025889 | 0.00064883
172 | 0.97828 | -0.41599 | 0.0032758 | 0.00082098
173 | 0.9804 | -0.37464 | 0.0026739 | 0.00067013
174 | 0.98039 | -0.37483 | 0.0015042 | 0.000377
175 | 0.97461 | -0.4879 | 0.0015783 | 0.00039555
176 | 0.97468 | -0.48662 | 0.0018954 | 0.00047502
177 | 0.97207 | -0.53822 | 0.0034889 | 0.0008744
178 | 0.97496 | -0.48107 | 0.00086392 | 0.00021652
179 | 0.97214 | -0.53672 | 0.0020239 | 0.00050723
180 | 0.97213 | -0.53682 | 0.0016386 | 0.00041066
181 | 0.9722 | -0.53548 | 0 | 0
182 | 0.97245 | -0.5306 | 0.0036454 | 0.00091362
183 | 0.97213 | -0.53687 | 0.003003 | 0.00075261
184 | 0.97753 | -0.43055 | 0 | 0
185 | 0.97654 | -0.45003 | 0 | 0
186 | 0.97264 | -0.52678 | 0.0023005 | 0.00057657
187 | 0.97205 | -0.53838 | 0.0018785 | 0.00047079
188 | 0.97591 | -0.46241 | 0.0019753 | 0.00049507
189 | 0.97591 | -0.46246 | 0.0016043 | 0.00040209
190 | 0.97277 | -0.52423 | 0 | 0
191 | 0.97195 | -0.54036 | 0.0022049 | 0.00055261
192 | 0.9753 | -0.47438 | 0.00087041 | 0.00021815
193 | 0.97571 | -0.46639 | 0.0024422 | 0.00061208
194 | 0.97256 | -0.52831 | 0 | 0
195 | 0.973 | -0.51976 | 0.002116 | 0.00053032
196 | 0.97194 | -0.54067 | 0.0014667 | 0.00036759
197 | 0.97178 | -0.54385 | 0.0026044 | 0.00065272
198 | 0.97176 | -0.54416 | 0.0024728 | 0.00061975
199 | 0.97164 | -0.54653 | 0 | 0
200 | 0.97146 | -0.55007 | 0.0015002 | 0.00037598
201 | 0.97132 | -0.55279 | 0.0020607 | 0.00051646
202 | 0.97108 | -0.55778 | 0.0033214 | 0.00083243
203 | 0.97115 | -0.55627 | 0 | 0
204 | 0.97504 | -0.47956 | 0.0018769 | 0.0004704
205 | 0.97526 | -0.47523 | 0.00087842 | 0.00022015
206 | 0.97524 | -0.47561 | 0.00087557 | 0.00021944
207 | 0.97522 | -0.47584 | 0.0017707 | 0.00044378
208 | 0.97459 | -0.48837 | 0.0021253 | 0.00053264
209 | 0.9743 | -0.49396 | 0.0036454 | 0.00091362
210 | 0.97422 | -0.49568 | 0.0021564 | 0.00054045
211 | 0.97322 | -0.51537 | 0.0020864 | 0.00052289
212 | 0.97359 | -0.50795 | 0.0021009 | 0.00052654
213 | 0.97382 | -0.50351 | 0.0036454 | 0.00091362
214 | 0.97238 | -0.53196 | 0.0018814 | 0.00047152
215 | 0.97383 | -0.50336 | 0.0023237 | 0.00058238
216 | 0.97234 | -0.53263 | 0.0026926 | 0.00067483
217 | 0.97217 | -0.53607 | 0.0025717 | 0.00064452
218 | 0.97191 | -0.54132 | 0.0023817 | 0.00059692
219 | 0.97191 | -0.54123 | 0.0027692 | 0.00069402
220 | 0.97181 | -0.54331 | 0.0027374 | 0.00068606
221 | 0.97205 | -0.53848 | 0.0027591 | 0.00069149
222 | 0.97166 | -0.54618 | 0.0023038 | 0.00057739
223 | 0.97166 | -0.54618 | 0.0026912 | 0.00067449
224 | 0.97158 | -0.54786 | 0.0026597 | 0.00066658
225 | 0.97154 | -0.5485 | 0.0026463 | 0.00066321
226 | 0.97112 | -0.55687 | 0.001409 | 0.00035313
227 | 0.97121 | -0.55508 | 0.001596 | 0.0004
228 | 0.99186 | -0.15391 | 0.0014968 | 0.00037514
229 | 0.9921 | -0.14943 | 0.0016471 | 0.0004128
230 | 0.99358 | -0.12114 | 0.00061749 | 0.00015476
231 | 0.97099 | -0.55952 | 0.0015804 | 0.0003961
232 | 0.97129 | -0.55349 | 0.0015021 | 0.00037645
233 | 0.9714 | -0.55144 | 0.00086558 | 0.00021694
234 | 0.97142 | -0.55095 | 0.002721 | 0.00068194
235 | 0.97149 | -0.54963 | 0.0026614 | 0.000667
236 | 0.9702 | -0.57535 | 0.00072505 | 0.00018172
237 | 0.97005 | -0.57827 | 0.0035836 | 0.00089813
238 | 0.98931 | -0.20311 | 0.0016816 | 0.00042145
239 | 0.9894 | -0.20132 | 0.0014892 | 0.00037324
240 | 0.98925 | -0.20427 | 0.0015601 | 0.00039101
241 | 0.98921 | -0.20498 | 0.0014453 | 0.00036222
242 | 0.9818 | -0.34795 | 0 | 0
243 | 0.98175 | -0.34904 | 0.00080297 | 0.00020124
244 | 0.99383 | -0.1165 | 0.0013185 | 0.00033045
245 | 0.99511 | -0.092198 | 0 | 0
246 | 0.99714 | -0.05384 | 0.0005798 | 0.00014531
247 | 0.99962 | -0.0072185 | 0.00055598 | 0.00013934
248 | 1 | 0 | -0.48166 | -0.12409
249 | 0.98154 | -0.35312 | 0.0020355 | 0.00051014
250 | 0.98157 | -0.35254 | 0 | 0
251 | 0.98119 | -0.3599 | 0.0020927 | 0.00052449
252 | 0.98121 | -0.35956 | 0.0020927 | 0.00052447
253 | 0.98142 | -0.35546 | 0.0020354 | 0.00051012
254 | 0.98136 | -0.35675 | 0.0020927 | 0.00052448
255 | 0.97511 | -0.47887 | 0.0011836 | 0.00029663
256 | 0.97507 | -0.4798 | 0.0033467 | 0.00083877
257 | 0.97453 | -0.49046 | 0.0012938 | 0.00032426
258 | 0.9749 | -0.483 | 0.0046323 | 0.001161
259 | 0.97441 | -0.49272 | 0.0055793 | 0.0013983
260 | 0.9747 | -0.48708 | 0.0028083 | 0.00070384
261 | 0.97441 | -0.49276 | 0.0030526 | 0.00076506
262 | 0.97441 | -0.49284 | 0.0029667 | 0.00074354
263 | 0.97451 | -0.49088 | 0.0011112 | 0.00027849
264 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.001346 | -0.00033733 | 0.001346 | 0.00033704 | 4.1653e-08 | -2.976e-07 | 0.0020606 | 0.0020605 | 0.0020606 | 0.97198 | -0.5409 | 0.97201 | -0.54025 | 0.56609
1 | 0.0043596 | 0.0010916 | -0.0043588 | -0.0010917 | 7.3585e-07 | -7.5073e-08 | 0.0066735 | 0.0066737 | 0.0066737 | 0.97201 | -0.54025 | 0.97183 | -0.54379 | 1.8334
2 | -0.0057056 | -0.0014286 | 0.0057186 | 0.0014313 | 1.301e-05 | 2.6737e-06 | 0.008734 | 0.008732 | 0.008734 | 0.97201 | -0.54025 | 0.97443 | -0.4924 | 2.3994
3 | 0.0025554 | 0.00063966 | -0.0025553 | -0.00063972 | 3.9254e-08 | -5.9611e-08 | 0.0039124 | 0.0039124 | 0.0039124 | 0.97183 | -0.54379 | 0.97181 | -0.54412 | 1.0748
4 | -0.0069501 | -0.0017399 | 0.0069501 | 0.0017399 | 7.5691e-08 | 2.6117e-08 | 0.010612 | 0.010612 | 0.010612 | 0.97443 | -0.4924 | 0.97444 | -0.49217 | 2.9155
5 | -0.008227 | -0.00206 | 0.0082275 | 0.0020602 | 5.0374e-07 | 2.1635e-07 | 0.012562 | 0.012562 | 0.012562 | 0.97444 | -0.49217 | 0.97451 | -0.49088 | 3.4512
6 | -0.0048811 | -0.0012233 | 0.0048822 | 0.0012234 | 1.1126e-06 | 5.8302e-08 | 0.0074867 | 0.0074865 | 0.0074867 | 0.97013 | -0.57656 | 0.97037 | -0.57177 | 2.0568
7 | -0.0048822 | -0.0012234 | 0.0048833 | 0.0012215 | 1.1055e-06 | -1.8926e-06 | 0.0074865 | 0.0074855 | 0.0074865 | 0.97037 | -0.57177 | 0.97061 | -0.56701 | 1.0284
8 | 0.0025553 | 0.00063972 | -0.0025549 | -0.00064032 | 3.9736e-07 | -6.032e-07 | 0.0039124 | 0.0039127 | 0.0039127 | 0.97181 | -0.54412 | 0.97165 | -0.54738 | 1.0749
9 | 0.0079521 | 0.0019705 | -0.0079513 | -0.0019729 | 8.1533e-07 | -2.3744e-06 | 0.012183 | 0.012184 | 0.012184 | 0.97061 | -0.56701 | 0.9705 | -0.56918 | 0.83682
10 | -0.012835 | -0.003192 | 0.012837 | 0.0031909 | 1.4658e-06 | -1.0604e-06 | 0.019669 | 0.019668 | 0.019669 | 0.97061 | -0.56701 | 0.97073 | -0.5646 | 1.3509
11 | 0.00075592 | 0.00018919 | -0.0007559 | -0.00018945 | 1.0692e-08 | -2.5546e-07 | 0.0011589 | 0.001159 | 0.001159 | 0.9705 | -0.56918 | 0.97049 | -0.56948 | 0.31841
12 | 0.0071954 | 0.0017837 | -0.0071951 | -0.001785 | 3.4543e-07 | -1.277e-06 | 0.011025 | 0.011026 | 0.011026 | 0.9705 | -0.56918 | 0.97045 | -0.5702 | 0.75726
13 | -0.01485 | -0.0036955 | 0.014852 | 0.0036949 | 1.5748e-06 | -5.9676e-07 | 0.022754 | 0.022753 | 0.022754 | 0.97073 | -0.5646 | 0.97085 | -0.56236 | 1.5628
14 | 0.0069769 | 0.0017321 | -0.0069766 | -0.0017332 | 2.8663e-07 | -1.1379e-06 | 0.010693 | 0.010693 | 0.010693 | 0.97039 | -0.57151 | 0.97034 | -0.57238 | 0.73441
15 | -0.0069769 | -0.0017321 | 0.0069773 | 0.0017304 | 4.33e-07 | -1.7194e-06 | 0.010693 | 0.010692 | 0.010693 | 0.97039 | -0.57151 | 0.97045 | -0.5702 | 0.73438
16 | 0.0047183 | 0.0011673 | -0.004718 | -0.0011701 | 3.0098e-07 | -2.8414e-06 | 0.00723 | 0.007231 | 0.007231 | 0.97034 | -0.57238 | 0.97028 | -0.57373 | 0.49664
17 | -0.016538 | -0.0041174 | 0.016539 | 0.0041172 | 1.1041e-06 | -2.0085e-07 | 0.025337 | 0.025337 | 0.025337 | 0.97085 | -0.56236 | 0.97092 | -0.56096 | 1.7402
18 | 0.0043095 | 0.0010677 | -0.0043091 | -0.0010715 | 3.3007e-07 | -3.7751e-06 | 0.0066046 | 0.006606 | 0.006606 | 0.97028 | -0.57373 | 0.9702 | -0.57535 | 0.45371
19 | -0.018048 | -0.0044955 | 0.018049 | 0.0044955 | 1.23e-06 | -6.1786e-08 | 0.02765 | 0.02765 | 0.02765 | 0.97092 | -0.56096 | 0.97099 | -0.55952 | 1.8991
20 | -0.048101 | -0.012088 | 0.048156 | 0.012123 | 5.4647e-05 | 3.463e-05 | 0.073062 | 0.073061 | 0.073062 | 0.97982 | -0.38683 | 0.98104 | -0.36306 | 20.0719
21 | 0.04296 | 0.0108 | -0.04291 | -0.010768 | 5.0176e-05 | 3.1717e-05 | 0.065253 | 0.065253 | 0.065253 | 0.97982 | -0.38683 | 0.97857 | -0.41132 | 17.9268
22 | -0.050076 | -0.012604 | 0.050095 | 0.012616 | 1.8628e-05 | 1.1813e-05 | 0.075974 | 0.075974 | 0.075974 | 0.98104 | -0.36306 | 0.98144 | -0.35528 | 20.8719
23 | 0.04291 | 0.010768 | -0.042906 | -0.010766 | 3.8115e-06 | 2.4093e-06 | 0.065253 | 0.065253 | 0.065253 | 0.97857 | -0.41132 | 0.97848 | -0.41318 | 17.9268
24 | -0.050926 | -0.012824 | 0.051014 | 0.01288 | 8.7382e-05 | 5.543e-05 | 0.077235 | 0.077234 | 0.077235 | 0.98144 | -0.35528 | 0.98327 | -0.31946 | 21.2183
25 | 0.025972 | 0.0065197 | -0.025956 | -0.0065096 | 1.6348e-05 | 1.0112e-05 | 0.039501 | 0.039501 | 0.039501 | 0.97848 | -0.41318 | 0.9778 | -0.42639 | 10.8519
26 | 0.016934 | 0.0042459 | -0.016928 | -0.0042422 | 6.266e-06 | 3.6939e-06 | 0.025753 | 0.025753 | 0.025753 | 0.97848 | -0.41318 | 0.97808 | -0.42095 | 7.075
27 | 0.0025799 | 0.00064606 | -0.0025798 | -0.00064628 | 1.3877e-07 | -2.1912e-07 | 0.0039041 | 0.0039042 | 0.0039042 | 0.98327 | -0.31946 | 0.98322 | -0.32059 | 1.0726
28 | -0.053594 | -0.013526 | 0.053702 | 0.013594 | 0.00010807 | 6.8608e-05 | 0.081139 | 0.081138 | 0.081139 | 0.98327 | -0.31946 | 0.98544 | -0.27745 | 22.2908
29 | 0.022159 | 0.0055582 | -0.022153 | -0.0055542 | 6.6437e-06 | 4.0567e-06 | 0.033724 | 0.033724 | 0.033724 | 0.9778 | -0.42639 | 0.97748 | -0.43268 | 9.2647
30 | 0.0037964 | 0.00095136 | -0.0037962 | -0.00095142 | 1.6507e-07 | -5.9771e-08 | 0.0057773 | 0.0057773 | 0.0057773 | 0.9778 | -0.42639 | 0.97776 | -0.4273 | 1.5872
31 | 0.01167 | 0.0029246 | -0.011666 | -0.0029223 | 4.3403e-06 | 2.3172e-06 | 0.017755 | 0.017755 | 0.017755 | 0.97808 | -0.42095 | 0.97768 | -0.42876 | 4.8777
32 | -0.002127 | -0.00053201 | 0.0021272 | 0.0005316 | 1.6319e-07 | -4.1586e-07 | 0.0032379 | 0.0032377 | 0.0032379 | 0.9774 | -0.4344 | 0.97748 | -0.43279 | 0.88953
33 | 0.002127 | 0.00053201 | -0.0021267 | -0.00053299 | 3.8471e-07 | -9.7977e-07 | 0.0032379 | 0.0032383 | 0.0032383 | 0.9774 | -0.4344 | 0.9772 | -0.4382 | 0.88965
34 | 0.0058303 | 0.001461 | -0.005829 | -0.0014607 | 1.2631e-06 | 2.7253e-07 | 0.0088754 | 0.0088756 | 0.0088756 | 0.97748 | -0.43279 | 0.97725 | -0.43734 | 2.4383
35 | -0.0079575 | -0.0019926 | 0.007959 | 0.0019932 | 1.5269e-06 | 6.2931e-07 | 0.012113 | 0.012113 | 0.012113 | 0.97748 | -0.43279 | 0.97768 | -0.42876 | 3.3278
36 | 0.0026551 | 0.00066526 | -0.002655 | -0.0006654 | 1.0089e-07 | -1.4166e-07 | 0.0040427 | 0.0040428 | 0.0040428 | 0.97725 | -0.43734 | 0.97721 | -0.43814 | 1.1107
37 | -0.13028 | -0.03299 | 0.13051 | 0.033141 | 0.00023598 | 0.00015082 | 0.19684 | 0.19684 | 0.19684 | 0.98544 | -0.27745 | 0.98739 | -0.2398 | 54.077
38 | 0.074786 | 0.018947 | -0.074651 | -0.018862 | 0.00013426 | 8.5568e-05 | 0.113 | 0.113 | 0.113 | 0.98544 | -0.27745 | 0.98351 | -0.3149 | 31.0439
39 | 0.0017899 | 0.00044826 | -0.0017898 | -0.00044856 | 7.444e-08 | -2.9858e-07 | 0.0027026 | 0.0027027 | 0.0027027 | 0.98544 | -0.27745 | 0.98539 | -0.27832 | 0.7425
40 | -0.13079 | -0.033211 | 0.13107 | 0.033388 | 0.00027825 | 0.00017783 | 0.19726 | 0.19726 | 0.19726 | 0.98739 | -0.2398 | 0.98968 | -0.1957 | 54.1918
41 | 0.072296 | 0.018272 | -0.072265 | -0.018252 | 3.0404e-05 | 1.9373e-05 | 0.10944 | 0.10944 | 0.10944 | 0.98351 | -0.3149 | 0.98306 | -0.32367 | 30.0648
42 | 0.0011252 | 0.00028174 | -0.0011252 | -0.000282 | 2.4168e-08 | -2.664e-07 | 0.0017028 | 0.0017029 | 0.0017029 | 0.98322 | -0.32059 | 0.98319 | -0.32104 | 0.46784
43 | 0.01729 | 0.0043354 | -0.017283 | -0.0043317 | 6.1568e-06 | 3.6434e-06 | 0.026321 | 0.026321 | 0.026321 | 0.97748 | -0.43268 | 0.9771 | -0.44016 | 7.231
44 | -0.0025929 | -0.00064984 | 0.0025931 | 0.00064957 | 1.7559e-07 | -2.7795e-07 | 0.0039124 | 0.0039123 | 0.0039124 | 0.98616 | -0.26356 | 0.98623 | -0.26214 | 1.0748
45 | -0.0050613 | -0.0012682 | 0.0050617 | 0.0012682 | 3.7638e-07 | 2.123e-08 | 0.0076363 | 0.0076362 | 0.0076363 | 0.98623 | -0.26214 | 0.98631 | -0.26058 | 2.0979
46 | -0.13107 | -0.033388 | 0.13111 | 0.033417 | 4.4621e-05 | 2.8518e-05 | 0.19726 | 0.19726 | 0.19726 | 0.98968 | -0.1957 | 0.99005 | -0.18864 | 54.1918
47 | 0.06888 | 0.017404 | -0.06881 | -0.017359 | 6.9713e-05 | 4.44e-05 | 0.10431 | 0.10431 | 0.10431 | 0.98306 | -0.32367 | 0.98197 | -0.34481 | 28.657
48 | 0.012605 | 0.0031592 | -0.012605 | -0.0031592 | 6.6474e-08 | 3.6518e-08 | 0.019196 | 0.019196 | 0.019196 | 0.9771 | -0.44016 | 0.9771 | -0.44027 | 5.2737
49 | -0.21566 | -0.05494 | 0.21601 | 0.055164 | 0.0003501 | 0.00022361 | 0.32444 | 0.32444 | 0.32444 | 0.99005 | -0.18864 | 0.99181 | -0.15505 | 44.5665
50 | 0.074806 | 0.019083 | -0.074747 | -0.019045 | 5.9634e-05 | 3.8005e-05 | 0.11255 | 0.11255 | 0.11255 | 0.99005 | -0.18864 | 0.98919 | -0.20516 | 30.9206
51 | 0.0097375 | 0.0024407 | -0.0097356 | -0.0024398 | 1.8375e-06 | 8.8185e-07 | 0.014635 | 0.014635 | 0.014635 | 0.99005 | -0.18864 | 0.98985 | -0.1926 | 4.0207
52 | 0.066358 | 0.016745 | -0.066308 | -0.016713 | 5.0683e-05 | 3.2268e-05 | 0.1006 | 0.1006 | 0.1006 | 0.98197 | -0.34481 | 0.98115 | -0.36077 | 27.6364
53 | 0.002478 | 0.00062102 | -0.002478 | -0.00062104 | 1.008e-08 | -1.7127e-08 | 0.0037762 | 0.0037762 | 0.0037762 | 0.97645 | -0.45294 | 0.97644 | -0.45303 | 1.0374
54 | -0.0052566 | -0.0013174 | 0.0052575 | 0.0013175 | 8.6316e-07 | 1.0366e-07 | 0.0080107 | 0.0080105 | 0.0080107 | 0.97645 | -0.45294 | 0.97662 | -0.4495 | 2.2007
55 | -0.029989 | -0.007526 | 0.02999 | 0.0075264 | 7.4666e-07 | 4.6593e-07 | 0.045696 | 0.045696 | 0.045696 | 0.97662 | -0.4495 | 0.97665 | -0.44898 | 12.554
56 | 0.024732 | 0.0062084 | -0.024724 | -0.0062037 | 7.7588e-06 | 4.7834e-06 | 0.037686 | 0.037686 | 0.037686 | 0.97662 | -0.4495 | 0.97629 | -0.45608 | 10.3533
57 | -0.031079 | -0.0077993 | 0.031099 | 0.0078116 | 1.9621e-05 | 1.2265e-05 | 0.047355 | 0.047355 | 0.047355 | 0.97665 | -0.44898 | 0.97732 | -0.43575 | 13.0097
58 | 0.022076 | 0.0055401 | -0.022074 | -0.0055388 | 2.1902e-06 | 1.3373e-06 | 0.033651 | 0.033651 | 0.033651 | 0.97629 | -0.45608 | 0.97618 | -0.45816 | 9.2447
59 | -0.032376 | -0.0081318 | 0.032399 | 0.0081463 | 2.3079e-05 | 1.4453e-05 | 0.049301 | 0.049301 | 0.049301 | 0.97732 | -0.43575 | 0.97808 | -0.42082 | 13.5441
60 | 0.020686 | 0.0051909 | -0.020678 | -0.0051862 | 7.7656e-06 | 4.7098e-06 | 0.031535 | 0.031535 | 0.031535 | 0.97618 | -0.45816 | 0.97578 | -0.46603 | 8.6634
61 | -0.034044 | -0.0085586 | 0.03405 | 0.0085618 | 5.0726e-06 | 3.1832e-06 | 0.051803 | 0.051803 | 0.051803 | 0.97808 | -0.42082 | 0.97824 | -0.4177 | 14.2317
62 | 0.018742 | 0.0047009 | -0.018737 | -0.0046981 | 4.658e-06 | 2.7913e-06 | 0.028582 | 0.028582 | 0.028582 | 0.97578 | -0.46603 | 0.97552 | -0.47125 | 7.8523
63 | -0.05736 | -0.014407 | 0.057424 | 0.014448 | 6.4633e-05 | 4.108e-05 | 0.087262 | 0.087262 | 0.087262 | 0.97824 | -0.4177 | 0.97944 | -0.39411 | 23.9731
64 | 0.02331 | 0.0058454 | -0.023308 | -0.0058443 | 1.7896e-06 | 1.0977e-06 | 0.035459 | 0.035459 | 0.035459 | 0.97824 | -0.4177 | 0.97816 | -0.41931 | 9.7414
65 | 0.016177 | 0.0040563 | -0.016173 | -0.0040543 | 3.3579e-06 | 1.9655e-06 | 0.024676 | 0.024676 | 0.024676 | 0.97552 | -0.47125 | 0.97529 | -0.4756 | 6.7791
66 | -0.02185 | -0.0054768 | 0.021855 | 0.0054802 | 5.5841e-06 | 3.4048e-06 | 0.033249 | 0.033248 | 0.033249 | 0.97789 | -0.42467 | 0.97816 | -0.41931 | 9.1342
67 | 0.018397 | 0.0046113 | -0.018394 | -0.0046097 | 2.7819e-06 | 1.6617e-06 | 0.027994 | 0.027994 | 0.027994 | 0.97789 | -0.42467 | 0.97772 | -0.42785 | 7.6906
68 | 0.016226 | 0.0040664 | -0.016224 | -0.0040651 | 2.2395e-06 | 1.3105e-06 | 0.024695 | 0.024695 | 0.024695 | 0.97772 | -0.42785 | 0.97758 | -0.43074 | 6.7844
69 | 0.012871 | 0.0032266 | -0.012868 | -0.0032252 | 2.6416e-06 | 1.4606e-06 | 0.019591 | 0.019591 | 0.019591 | 0.97758 | -0.43074 | 0.97736 | -0.43505 | 5.3822
70 | 0.0033535 | 0.00083848 | -0.0033521 | -0.00083938 | 1.4019e-06 | -9.0104e-07 | 0.0051038 | 0.0051044 | 0.0051044 | 0.97758 | -0.43074 | 0.97713 | -0.43953 | 1.4023
71 | -0.060811 | -0.015297 | 0.060867 | 0.015333 | 5.5798e-05 | 3.5491e-05 | 0.092408 | 0.092408 | 0.092408 | 0.97944 | -0.39411 | 0.98043 | -0.37493 | 25.3867
72 | 0.009271 | 0.0023237 | -0.0092694 | -0.0023229 | 1.6022e-06 | 7.567e-07 | 0.014115 | 0.014115 | 0.014115 | 0.97736 | -0.43505 | 0.97717 | -0.43868 | 3.8778
73 | 0.0033521 | 0.00083938 | -0.0033516 | -0.0008397 | 5.0442e-07 | -3.237e-07 | 0.0051044 | 0.0051047 | 0.0051047 | 0.97713 | -0.43953 | 0.97697 | -0.44269 | 1.4024
74 | -0.062878 | -0.015837 | 0.062921 | 0.015864 | 4.26e-05 | 2.7107e-05 | 0.09546 | 0.09546 | 0.09546 | 0.98043 | -0.37493 | 0.98115 | -0.36077 | 26.2253
75 | 0.0073482 | 0.0018414 | -0.007348 | -0.0018414 | 2.3975e-07 | 8.9475e-08 | 0.01119 | 0.01119 | 0.01119 | 0.97717 | -0.43868 | 0.97714 | -0.43936 | 3.0741
76 | 0.0026404 | 0.00066145 | -0.0026403 | -0.00066158 | 8.7962e-08 | -1.2532e-07 | 0.0040214 | 0.0040215 | 0.0040215 | 0.97697 | -0.44269 | 0.97693 | -0.44339 | 1.1048
77 | 0.0054947 | 0.0013769 | -0.0054946 | -0.0013769 | 1.5941e-07 | 2.5972e-08 | 0.0083675 | 0.0083675 | 0.0083675 | 0.97714 | -0.43936 | 0.97711 | -0.43997 | 2.2988
78 | -0.053335 | -0.013447 | 0.053469 | 0.013532 | 0.00013348 | 8.474e-05 | 0.081044 | 0.081043 | 0.081044 | 0.97962 | -0.39051 | 0.98229 | -0.33836 | 22.2647
79 | 0.053335 | 0.013447 | -0.053244 | -0.01339 | 9.0638e-05 | 5.7546e-05 | 0.081044 | 0.081044 | 0.081044 | 0.97962 | -0.39051 | 0.9778 | -0.42608 | 22.2648
80 | -0.068703 | -0.017352 | 0.068764 | 0.017391 | 6.1639e-05 | 3.9257e-05 | 0.10412 | 0.10412 | 0.10412 | 0.98229 | -0.33836 | 0.98326 | -0.31965 | 28.6047
81 | 0.015234 | 0.0038197 | -0.015231 | -0.003818 | 2.9793e-06 | 1.7179e-06 | 0.023078 | 0.023078 | 0.023078 | 0.98229 | -0.33836 | 0.98208 | -0.34246 | 6.34
82 | 0.051874 | 0.013046 | -0.051847 | -0.01303 | 2.6558e-05 | 1.6854e-05 | 0.078958 | 0.078958 | 0.078958 | 0.9778 | -0.42608 | 0.97725 | -0.4368 | 21.6917
83 | 0.070945 | 0.017994 | -0.070874 | -0.017949 | 7.1695e-05 | 4.5673e-05 | 0.1072 | 0.1072 | 0.1072 | 0.98547 | -0.27672 | 0.98439 | -0.29777 | 29.4508
84 | -0.073178 | -0.018553 | 0.073313 | 0.018639 | 0.00013484 | 8.5919e-05 | 0.11057 | 0.11057 | 0.11057 | 0.98547 | -0.27672 | 0.98746 | -0.23846 | 30.3767
85 | 0.0022322 | 0.00055909 | -0.0022322 | -0.00055918 | 3.6707e-08 | -8.6292e-08 | 0.0033704 | 0.0033705 | 0.0033705 | 0.98547 | -0.27672 | 0.98546 | -0.27707 | 0.92595
86 | 0.070874 | 0.017949 | -0.070799 | -0.017901 | 7.4411e-05 | 4.7403e-05 | 0.1072 | 0.1072 | 0.1072 | 0.98439 | -0.29777 | 0.98326 | -0.31965 | 29.4508
87 | -0.073987 | -0.018808 | 0.074106 | 0.018884 | 0.00011888 | 7.5757e-05 | 0.11159 | 0.11159 | 0.11159 | 0.98746 | -0.23846 | 0.98919 | -0.20516 | 30.6557
88 | 0.0022322 | 0.00055918 | -0.0022321 | -0.00055941 | 9.9924e-08 | -2.3487e-07 | 0.0033705 | 0.0033706 | 0.0033706 | 0.98546 | -0.27707 | 0.98541 | -0.27801 | 0.92598
89 | 0.021358 | 0.0053633 | -0.02134 | -0.0053525 | 1.7754e-05 | 1.0803e-05 | 0.032536 | 0.032536 | 0.032536 | 0.9769 | -0.44381 | 0.97601 | -0.46124 | 8.9385
90 | 0.027546 | 0.0069222 | -0.027527 | -0.0069107 | 1.8529e-05 | 1.1508e-05 | 0.041965 | 0.041965 | 0.041965 | 0.9769 | -0.44381 | 0.97618 | -0.45791 | 11.5287
91 | -0.048903 | -0.012285 | 0.04892 | 0.012296 | 1.6346e-05 | 1.0363e-05 | 0.0745 | 0.0745 | 0.0745 | 0.9769 | -0.44381 | 0.97725 | -0.4368 | 20.4671
92 | 0.017888 | 0.0044874 | -0.017885 | -0.0044854 | 3.4577e-06 | 2.0581e-06 | 0.027274 | 0.027274 | 0.027274 | 0.97601 | -0.46124 | 0.9758 | -0.4653 | 7.4928
93 | 0.02461 | 0.0061796 | -0.024597 | -0.0061713 | 1.3539e-05 | 8.3444e-06 | 0.037518 | 0.037518 | 0.037518 | 0.97618 | -0.45791 | 0.97559 | -0.46944 | 10.3072
94 | 0.0010762 | 0.00026958 | -0.0010762 | -0.00026972 | 1.159e-08 | -1.3661e-07 | 0.0016392 | 0.0016392 | 0.0016392 | 0.97693 | -0.44339 | 0.97692 | -0.44362 | 0.45033
95 | 0.0041355 | 0.0010362 | -0.0041354 | -0.0010363 | 5.5742e-08 | -1.1267e-08 | 0.0062978 | 0.0062978 | 0.0062978 | 0.97711 | -0.43997 | 0.97709 | -0.44026 | 1.7302
96 | 0.0022019 | 0.00055167 | -0.0022019 | -0.00055182 | 6.3077e-08 | -1.4699e-07 | 0.0033532 | 0.0033533 | 0.0033533 | 0.97709 | -0.44026 | 0.97706 | -0.44086 | 0.92124
97 | 0.0010797 | 0.00027058 | -0.0010797 | -0.0002706 | 1.9314e-09 | -2.2621e-08 | 0.0016443 | 0.0016443 | 0.0016443 | 0.97706 | -0.44086 | 0.97706 | -0.4409 | 0.45174
98 | 0.01259 | 0.0031563 | -0.012589 | -0.0031557 | 1.1613e-06 | 6.3849e-07 | 0.019209 | 0.019209 | 0.019209 | 0.97529 | -0.4756 | 0.9752 | -0.47754 | 5.2772
99 | 0.010391 | 0.0026049 | -0.010389 | -0.0026038 | 2.2009e-06 | 1.1174e-06 | 0.015856 | 0.015856 | 0.015856 | 0.9752 | -0.47754 | 0.97497 | -0.48199 | 4.3561
100 | -0.0085466 | -0.002142 | 0.0085466 | 0.002142 | 1.4394e-08 | 6.3994e-09 | 0.013044 | 0.013044 | 0.013044 | 0.97497 | -0.48202 | 0.97497 | -0.48199 | 3.5835
101 | 0.0067909 | 0.001702 | -0.0067908 | -0.0017019 | 8.9252e-08 | 2.9491e-08 | 0.010364 | 0.010364 | 0.010364 | 0.97497 | -0.48202 | 0.97495 | -0.4823 | 2.8474
102 | -0.0069423 | -0.0017399 | 0.0069434 | 0.0017403 | 1.1546e-06 | 3.941e-07 | 0.010574 | 0.010574 | 0.010574 | 0.97692 | -0.44376 | 0.9771 | -0.44027 | 2.905
103 | 0.0029141 | 0.0007303 | -0.002914 | -0.00073033 | 2.385e-08 | -2.5155e-08 | 0.0044386 | 0.0044386 | 0.0044386 | 0.97692 | -0.44376 | 0.97691 | -0.44393 | 1.2194
104 | -0.21672 | -0.055342 | 0.21691 | 0.055464 | 0.00019184 | 0.00012178 | 0.32551 | 0.32551 | 0.32551 | 0.99181 | -0.15505 | 0.99277 | -0.13676 | 22.3566
105 | 0.0092353 | 0.0023144 | -0.0092339 | -0.0023137 | 1.4598e-06 | 6.7468e-07 | 0.013883 | 0.013883 | 0.013883 | 0.98985 | -0.1926 | 0.98968 | -0.19592 | 3.8141
106 | -0.018426 | -0.004619 | 0.01843 | 0.004621 | 3.2775e-06 | 1.9528e-06 | 0.02778 | 0.02778 | 0.02778 | 0.987 | -0.24731 | 0.98719 | -0.24357 | 7.632
107 | 0.010676 | 0.0026768 | -0.010672 | -0.0026743 | 4.9032e-06 | 2.4934e-06 | 0.016096 | 0.016097 | 0.016097 | 0.987 | -0.24731 | 0.9865 | -0.25695 | 4.4221
108 | 0.00775 | 0.0019422 | -0.0077472 | -0.0019411 | 2.8363e-06 | 1.1075e-06 | 0.011684 | 0.011684 | 0.011684 | 0.987 | -0.24731 | 0.9866 | -0.25499 | 3.21
109 | -0.020213 | -0.0050679 | 0.020221 | 0.0050731 | 8.6353e-06 | 5.2093e-06 | 0.030468 | 0.030468 | 0.030468 | 0.98719 | -0.24357 | 0.98765 | -0.23461 | 8.3704
110 | 0.007636 | 0.0019135 | -0.0076346 | -0.001913 | 1.3201e-06 | 5.0614e-07 | 0.011518 | 0.011518 | 0.011518 | 0.9865 | -0.25695 | 0.98631 | -0.26058 | 3.1643
111 | 0.0061038 | 0.0015293 | -0.0061034 | -0.0015291 | 4.5659e-07 | 1.0876e-07 | 0.0092058 | 0.0092059 | 0.0092059 | 0.9866 | -0.25499 | 0.98652 | -0.25656 | 2.5291
112 | -0.00080299 | -0.00020091 | 0.00080299 | 0.00020081 | 4.4554e-09 | -9.8604e-08 | 0.0012169 | 0.0012169 | 0.0012169 | 0.98177 | -0.34865 | 0.98177 | -0.34853 | 0.33432
113 | 0.00080299 | 0.00020091 | -0.00080297 | -0.00020122 | 1.3943e-08 | -3.0852e-07 | 0.0012169 | 0.001217 | 0.001217 | 0.98177 | -0.34865 | 0.98175 | -0.34901 | 0.33435
114 | -0.0028385 | -0.00071097 | 0.0028386 | 0.00071087 | 7.8525e-08 | -9.2824e-08 | 0.004302 | 0.004302 | 0.004302 | 0.98177 | -0.34853 | 0.9818 | -0.34795 | 1.1819
115 | 0.00080297 | 0.00020122 | -0.00080297 | -0.00020124 | 1.1574e-09 | -2.5608e-08 | 0.001217 | 0.001217 | 0.001217 | 0.98175 | -0.34901 | 0.98175 | -0.34904 | 0.33435
116 | 0.013196 | 0.0033079 | -0.013192 | -0.003306 | 3.4512e-06 | 1.9175e-06 | 0.019994 | 0.019994 | 0.019994 | 0.98208 | -0.34246 | 0.9818 | -0.34795 | 5.4928
117 | -0.011696 | -0.00293 | 0.011698 | 0.0029315 | 2.8167e-06 | 1.5089e-06 | 0.017854 | 0.017854 | 0.017854 | 0.97473 | -0.48641 | 0.97499 | -0.48136 | 4.9049
118 | 0.011696 | 0.00293 | -0.011694 | -0.0029292 | 1.5287e-06 | 8.1898e-07 | 0.017854 | 0.017854 | 0.017854 | 0.97473 | -0.48641 | 0.97459 | -0.48916 | 4.905
119 | -0.013039 | -0.0032674 | 0.01304 | 0.0032683 | 1.544e-06 | 8.5845e-07 | 0.019899 | 0.019899 | 0.019899 | 0.97499 | -0.48136 | 0.97511 | -0.47887 | 5.4668
120 | 0.010633 | 0.0026634 | -0.010633 | -0.002663 | 6.6066e-07 | 3.3953e-07 | 0.016234 | 0.016234 | 0.016234 | 0.97459 | -0.48916 | 0.97453 | -0.49046 | 4.46
121 | 0.014233 | 0.0035701 | -0.014224 | -0.0035649 | 9.2028e-06 | 5.2395e-06 | 0.021705 | 0.021705 | 0.021705 | 0.9758 | -0.4653 | 0.97511 | -0.47887 | 5.963
122 | 0.022406 | 0.0056222 | -0.022395 | -0.0056155 | 1.1055e-05 | 6.76e-06 | 0.034177 | 0.034177 | 0.034177 | 0.97559 | -0.46944 | 0.97507 | -0.4798 | 9.3893
123 | -0.21691 | -0.055464 | 0.21718 | 0.055638 | 0.00027393 | 0.00017389 | 0.32551 | 0.32551 | 0.32551 | 0.99277 | -0.13676 | 0.99414 | -0.11069 | 22.3565
124 | 0.0078433 | 0.0019652 | -0.0078421 | -0.0019647 | 1.1619e-06 | 4.5737e-07 | 0.011792 | 0.011793 | 0.011793 | 0.98968 | -0.19592 | 0.98952 | -0.19903 | 3.2397
125 | -0.022187 | -0.0055656 | 0.022195 | 0.0055706 | 8.1772e-06 | 4.9836e-06 | 0.033429 | 0.033429 | 0.033429 | 0.98765 | -0.23461 | 0.98805 | -0.22688 | 9.1838
126 | 0.0048311 | 0.0012103 | -0.0048309 | -0.0012103 | 2.8627e-07 | -3.3682e-10 | 0.0072869 | 0.0072869 | 0.0072869 | 0.98652 | -0.25656 | 0.98646 | -0.2578 | 2.0019
127 | -0.21831 | -0.055921 | 0.21851 | 0.056045 | 0.0001958 | 0.0001243 | 0.3272 | 0.3272 | 0.3272 | 0.99414 | -0.11069 | 0.99511 | -0.092198 | 22.4727
128 | 0.0061776 | 0.0015476 | -0.0061769 | -0.0015474 | 6.7367e-07 | 1.6377e-07 | 0.0092895 | 0.0092896 | 0.0092896 | 0.98952 | -0.19903 | 0.9894 | -0.20132 | 2.5521
129 | 0.21956 | 0.056057 | -0.2194 | -0.055956 | 0.00015935 | 0.00010119 | 0.33103 | 0.33104 | 0.33104 | 0.98805 | -0.22688 | 0.98726 | -0.24191 | 22.7359
130 | -0.24176 | -0.061628 | 0.24202 | 0.061797 | 0.00026542 | 0.00016878 | 0.36446 | 0.36446 | 0.36446 | 0.98805 | -0.22688 | 0.98923 | -0.20417 | 25.0318
131 | 0.0026482 | 0.00066326 | -0.002648 | -0.00066347 | 1.3872e-07 | -2.0717e-07 | 0.0039945 | 0.0039946 | 0.0039946 | 0.98646 | -0.2578 | 0.9864 | -0.2589 | 1.0974
132 | -0.0026479 | -0.00066363 | 0.002648 | 0.00066347 | 1.0944e-07 | -1.634e-07 | 0.0039946 | 0.0039946 | 0.0039946 | 0.98636 | -0.25977 | 0.9864 | -0.2589 | 1.0974
133 | -0.0017801 | -0.00044614 | 0.0017801 | 0.00044609 | 1.2832e-08 | -4.8938e-08 | 0.0027247 | 0.0027247 | 0.0027247 | 0.97216 | -0.53623 | 0.97217 | -0.53608 | 0.74855
134 | -0.0034394 | -0.00086195 | 0.0034395 | 0.00086191 | 7.8268e-08 | -4.3291e-08 | 0.0052644 | 0.0052644 | 0.0052644 | 0.97217 | -0.53608 | 0.9722 | -0.5356 | 1.4463
135 | -0.0050778 | -0.0012725 | 0.0050781 | 0.0012725 | 3.1853e-07 | 2.9471e-08 | 0.0077719 | 0.0077718 | 0.0077719 | 0.9722 | -0.5356 | 0.97226 | -0.53428 | 2.1351
136 | -0.0014102 | -0.00035344 | 0.0014103 | 0.00035318 | 4.0961e-08 | -2.6545e-07 | 0.0021568 | 0.0021567 | 0.0021568 | 0.97297 | -0.52029 | 0.973 | -0.51968 | 0.59252
137 | 0.003492 | 0.00087279 | -0.0034899 | -0.00087388 | 2.0826e-06 | -1.0847e-06 | 0.0053394 | 0.0053403 | 0.0053403 | 0.973 | -0.51968 | 0.97237 | -0.53222 | 1.4671
138 | -0.0049023 | -0.001226 | 0.0049031 | 0.001226 | 8.8389e-07 | 4.4575e-08 | 0.0074961 | 0.0074959 | 0.0074961 | 0.973 | -0.51968 | 0.97319 | -0.51589 | 2.0594
139 | -0.0065695 | -0.0016463 | 0.0065702 | 0.0016465 | 6.1944e-07 | 1.9378e-07 | 0.010054 | 0.010054 | 0.010054 | 0.97226 | -0.53428 | 0.97236 | -0.5323 | 2.7622
140 | 0.0034899 | 0.00087388 | -0.0034889 | -0.0008744 | 9.9709e-07 | -5.1791e-07 | 0.0053403 | 0.0053407 | 0.0053407 | 0.97237 | -0.53222 | 0.97207 | -0.53822 | 1.4672
141 | -0.010997 | -0.0027532 | 0.010998 | 0.0027541 | 1.7543e-06 | 9.1708e-07 | 0.016813 | 0.016813 | 0.016813 | 0.97319 | -0.51589 | 0.97336 | -0.51254 | 4.6189
142 | -0.0088638 | -0.0022214 | 0.0088643 | 0.0022216 | 4.7549e-07 | 2.1882e-07 | 0.013564 | 0.013564 | 0.013564 | 0.97236 | -0.5323 | 0.97242 | -0.53118 | 3.7265
143 | -0.010912 | -0.0027347 | 0.010914 | 0.0027359 | 2.2682e-06 | 1.1825e-06 | 0.016697 | 0.016697 | 0.016697 | 0.97242 | -0.53118 | 0.97264 | -0.52681 | 4.5872
144 | -0.011809 | -0.0029603 | 0.011811 | 0.0029611 | 1.5799e-06 | 8.5093e-07 | 0.018067 | 0.018067 | 0.018067 | 0.97264 | -0.52681 | 0.97278 | -0.52401 | 4.9634
145 | -0.0144 | -0.0036101 | 0.014403 | 0.0036116 | 2.6758e-06 | 1.5299e-06 | 0.022028 | 0.022028 | 0.022028 | 0.97278 | -0.52401 | 0.97298 | -0.52011 | 6.0516
146 | 0.003863 | 0.00096775 | -0.0038629 | -0.00096778 | 1.209e-07 | -3.6029e-08 | 0.0059248 | 0.0059248 | 0.0059248 | 0.97016 | -0.57578 | 0.97013 | -0.57643 | 1.6277
147 | -0.0049787 | -0.0012474 | 0.0049792 | 0.0012474 | 5.6167e-07 | 4.2237e-08 | 0.007636 | 0.0076359 | 0.007636 | 0.97016 | -0.57578 | 0.97028 | -0.57341 | 2.0978
148 | 0.0027101 | 0.00067888 | -0.00271 | -0.00067908 | 1.5888e-07 | -2.0105e-07 | 0.0041567 | 0.0041568 | 0.0041568 | 0.97013 | -0.57643 | 0.97007 | -0.57766 | 1.142
149 | -0.0070303 | -0.0017615 | 0.007031 | 0.0017617 | 6.7022e-07 | 2.3901e-07 | 0.010781 | 0.010781 | 0.010781 | 0.97028 | -0.57341 | 0.97038 | -0.57141 | 2.9619
150 | 0.0013396 | 0.00033564 | -0.0013396 | -0.00033574 | 1.3415e-08 | -9.6009e-08 | 0.0020548 | 0.0020549 | 0.0020549 | 0.97007 | -0.57766 | 0.97006 | -0.57787 | 0.56453
151 | -0.010694 | -0.0026797 | 0.010696 | 0.002681 | 2.5037e-06 | 1.2956e-06 | 0.016398 | 0.016398 | 0.016398 | 0.97038 | -0.57141 | 0.97063 | -0.56649 | 4.505
152 | -0.012495 | -0.0031318 | 0.012496 | 0.0031324 | 9.546e-07 | 5.2519e-07 | 0.019156 | 0.019156 | 0.019156 | 0.97063 | -0.56649 | 0.97071 | -0.56489 | 5.2626
153 | -0.014053 | -0.0035225 | 0.014054 | 0.0035232 | 1.1784e-06 | 6.7046e-07 | 0.021542 | 0.021542 | 0.021542 | 0.97071 | -0.56489 | 0.9708 | -0.56313 | 5.9181
154 | 0.21772 | 0.055535 | -0.21746 | -0.055372 | 0.00025641 | 0.00016281 | 0.3285 | 0.3285 | 0.3285 | 0.98726 | -0.24191 | 0.98599 | -0.26633 | 22.5618
155 | -0.24528 | -0.062613 | 0.24538 | 0.06268 | 0.00010446 | 6.6432e-05 | 0.36936 | 0.36936 | 0.36936 | 0.98923 | -0.20417 | 0.98969 | -0.19536 | 25.3683
156 | -0.01757 | -0.0044044 | 0.017572 | 0.0044055 | 2.0105e-06 | 1.1953e-06 | 0.026931 | 0.026931 | 0.026931 | 0.9708 | -0.56313 | 0.97092 | -0.56073 | 7.3987
157 | 0.21628 | 0.055076 | -0.21623 | -0.055043 | 5.2323e-05 | 3.322e-05 | 0.32672 | 0.32672 | 0.32672 | 0.98599 | -0.26633 | 0.98573 | -0.27135 | 22.4395
158 | -0.24836 | -0.063427 | 0.24862 | 0.06359 | 0.00025703 | 0.00016349 | 0.37384 | 0.37384 | 0.37384 | 0.98969 | -0.19536 | 0.99081 | -0.17397 | 25.6761
159 | 0.21422 | 0.054538 | -0.21411 | -0.054473 | 0.00010168 | 6.455e-05 | 0.32368 | 0.32368 | 0.32368 | 0.98573 | -0.27135 | 0.98522 | -0.2812 | 22.2305
160 | -0.25069 | -0.064109 | 0.25081 | 0.064187 | 0.00012256 | 7.7965e-05 | 0.37695 | 0.37695 | 0.37695 | 0.99081 | -0.17397 | 0.99134 | -0.16387 | 25.8895
161 | 0.21248 | 0.054064 | -0.21244 | -0.054037 | 4.2592e-05 | 2.7035e-05 | 0.32121 | 0.32121 | 0.32121 | 0.98522 | -0.2812 | 0.985 | -0.28536 | 22.0613
162 | -0.25225 | -0.064546 | 0.25237 | 0.064623 | 0.00012174 | 7.745e-05 | 0.3791 | 0.3791 | 0.3791 | 0.99134 | -0.16387 | 0.99186 | -0.15391 | 26.0372
163 | -0.20739 | -0.052629 | 0.20752 | 0.052714 | 0.00013289 | 8.4321e-05 | 0.31413 | 0.31413 | 0.31413 | 0.98311 | -0.32193 | 0.9838 | -0.30861 | 21.575
164 | 0.20502 | 0.052037 | -0.20488 | -0.051944 | 0.00014658 | 9.2987e-05 | 0.31055 | 0.31055 | 0.31055 | 0.98311 | -0.32193 | 0.98235 | -0.3368 | 21.3293
165 | -0.21087 | -0.053552 | 0.2111 | 0.053702 | 0.00023631 | 0.00014998 | 0.31919 | 0.31919 | 0.31919 | 0.9838 | -0.30861 | 0.985 | -0.28536 | 21.9225
166 | 0.20303 | 0.051479 | -0.20294 | -0.051428 | 8.1229e-05 | 5.1523e-05 | 0.30775 | 0.30775 | 0.30775 | 0.98235 | -0.3368 | 0.98192 | -0.34513 | 21.1366
167 | 0.1984 | 0.05029 | -0.1983 | -0.050221 | 0.0001084 | 6.8728e-05 | 0.30087 | 0.30087 | 0.30087 | 0.98192 | -0.34513 | 0.98133 | -0.3565 | 20.6641
168 | 0.19708 | 0.049918 | -0.19696 | -0.049841 | 0.00012036 | 7.6307e-05 | 0.29903 | 0.29903 | 0.29903 | 0.98133 | -0.3565 | 0.98068 | -0.36923 | 20.5379
169 | 0.1882 | 0.047645 | -0.18811 | -0.047589 | 8.8388e-05 | 5.5986e-05 | 0.28574 | 0.28574 | 0.28574 | 0.98068 | -0.36923 | 0.98017 | -0.37902 | 19.6247
170 | 0.0087623 | 0.0021961 | -0.0087615 | -0.0021957 | 8.7927e-07 | 3.9539e-07 | 0.013295 | 0.013296 | 0.013296 | 0.98068 | -0.36923 | 0.98057 | -0.37133 | 3.6526
171 | 0.18567 | 0.046978 | -0.18567 | -0.046975 | 4.3241e-06 | 2.7382e-06 | 0.28203 | 0.28203 | 0.28203 | 0.98017 | -0.37902 | 0.98015 | -0.3795 | 19.3703
172 | 0.0077552 | 0.0019435 | -0.0077548 | -0.0019433 | 4.2306e-07 | 1.6801e-07 | 0.011768 | 0.011769 | 0.011769 | 0.98057 | -0.37133 | 0.98051 | -0.37248 | 3.2331
173 | -0.018691 | -0.004686 | 0.018693 | 0.0046874 | 2.3468e-06 | 1.4076e-06 | 0.028646 | 0.028646 | 0.028646 | 0.97092 | -0.56073 | 0.97106 | -0.55809 | 7.8698
174 | -0.020087 | -0.0050367 | 0.020088 | 0.0050374 | 1.1686e-06 | 7.0722e-07 | 0.030782 | 0.030782 | 0.030782 | 0.97106 | -0.55809 | 0.97112 | -0.55687 | 8.4565
175 | -0.016198 | -0.0040614 | 0.016203 | 0.0040648 | 5.8433e-06 | 3.4242e-06 | 0.024772 | 0.024772 | 0.024772 | 0.97298 | -0.52011 | 0.97336 | -0.51254 | 6.8056
176 | -0.027202 | -0.006819 | 0.027215 | 0.0068269 | 1.2807e-05 | 7.951e-06 | 0.041585 | 0.041585 | 0.041585 | 0.97336 | -0.51254 | 0.97386 | -0.50266 | 11.4245
177 | -0.030685 | -0.0076966 | 0.030706 | 0.0077101 | 2.1604e-05 | 1.35e-05 | 0.046887 | 0.046887 | 0.046887 | 0.97386 | -0.50266 | 0.97461 | -0.4879 | 12.8811
178 | 0.18322 | 0.046361 | -0.18295 | -0.046194 | 0.00026449 | 0.00016744 | 0.27831 | 0.27831 | 0.27831 | 0.98015 | -0.3795 | 0.9786 | -0.40963 | 19.115
179 | 0.0067675 | 0.0016959 | -0.0067672 | -0.0016958 | 2.6404e-07 | 8.4795e-08 | 0.01027 | 0.01027 | 0.01027 | 0.98051 | -0.37248 | 0.98047 | -0.3733 | 2.8215
180 | 0.18048 | 0.045574 | -0.18043 | -0.045539 | 5.4965e-05 | 3.4787e-05 | 0.27456 | 0.27456 | 0.27456 | 0.9786 | -0.40963 | 0.97828 | -0.41599 | 18.8569
181 | 0.0041784 | 0.001047 | -0.0041781 | -0.001047 | 2.672e-07 | -5.2449e-08 | 0.0063413 | 0.0063414 | 0.0063414 | 0.98047 | -0.3733 | 0.9804 | -0.37464 | 1.7421
182 | 0.17715 | 0.044718 | -0.17703 | -0.04464 | 0.00012351 | 7.8136e-05 | 0.26957 | 0.26957 | 0.26957 | 0.97828 | -0.41599 | 0.97753 | -0.43055 | 18.5147
183 | 0.0015043 | 0.00037692 | -0.0015042 | -0.000377 | 1.385e-08 | -8.0482e-08 | 0.0022831 | 0.0022831 | 0.0022831 | 0.9804 | -0.37464 | 0.98039 | -0.37483 | 0.62723
184 | -0.032285 | -0.0081057 | 0.032287 | 0.0081069 | 1.977e-06 | 1.2382e-06 | 0.049297 | 0.049297 | 0.049297 | 0.97461 | -0.4879 | 0.97468 | -0.48662 | 13.5431
185 | -0.034182 | -0.0085819 | 0.034191 | 0.0085876 | 9.0546e-06 | 5.6845e-06 | 0.05219 | 0.05219 | 0.05219 | 0.97468 | -0.48662 | 0.97496 | -0.48107 | 14.338
186 | -0.035055 | -0.0088041 | 0.03508 | 0.0088196 | 2.4578e-05 | 1.5444e-05 | 0.053509 | 0.053509 | 0.053509 | 0.97496 | -0.48107 | 0.97571 | -0.46639 | 14.7003
187 | 0.0016386 | 0.00041063 | -0.0016386 | -0.00041066 | 7.8768e-09 | -3.6358e-08 | 0.0025081 | 0.0025081 | 0.0025081 | 0.97214 | -0.53672 | 0.97213 | -0.53682 | 0.68904
188 | -0.0036624 | -0.00091786 | 0.0036627 | 0.00091777 | 2.1551e-07 | -8.8816e-08 | 0.005606 | 0.0056059 | 0.005606 | 0.97214 | -0.53672 | 0.9722 | -0.53548 | 1.5401
189 | -0.043977 | -0.011029 | 0.043987 | 0.011035 | 1.0237e-05 | 5.356e-06 | 0.067312 | 0.067312 | 0.067312 | 0.9722 | -0.53548 | 0.97245 | -0.5306 | 4.6231
190 | 0.040314 | 0.010111 | -0.040311 | -0.01011 | 2.6734e-06 | 1.3396e-06 | 0.061706 | 0.061706 | 0.061706 | 0.9722 | -0.53548 | 0.97213 | -0.53687 | 4.2381
191 | -0.047632 | -0.011948 | 0.047641 | 0.011953 | 8.6732e-06 | 4.6866e-06 | 0.07289 | 0.072889 | 0.07289 | 0.97245 | -0.5306 | 0.97264 | -0.52678 | 5.0062
192 | 0.037308 | 0.0093575 | -0.037306 | -0.0093562 | 2.6791e-06 | 1.2801e-06 | 0.05711 | 0.05711 | 0.05711 | 0.97213 | -0.53687 | 0.97205 | -0.53838 | 3.9224
193 | 0.17703 | 0.04464 | -0.17686 | -0.044536 | 0.00016491 | 0.00010433 | 0.26957 | 0.26957 | 0.26957 | 0.97753 | -0.43055 | 0.97654 | -0.45003 | 18.5147
194 | 0.13771 | 0.034683 | -0.13763 | -0.034632 | 8.1417e-05 | 5.1121e-05 | 0.20989 | 0.20989 | 0.20989 | 0.97654 | -0.45003 | 0.97591 | -0.46241 | 14.4159
195 | 0.039157 | 0.0098528 | -0.039133 | -0.0098382 | 2.3235e-05 | 1.4653e-05 | 0.059679 | 0.05968 | 0.05968 | 0.97654 | -0.45003 | 0.97591 | -0.46246 | 16.3955
196 | -0.049942 | -0.012529 | 0.049948 | 0.012533 | 6.0629e-06 | 3.3302e-06 | 0.076409 | 0.076409 | 0.076409 | 0.97264 | -0.52678 | 0.97277 | -0.52423 | 5.2479
197 | 0.035427 | 0.0088854 | -0.035424 | -0.0088839 | 3.3432e-06 | 1.5385e-06 | 0.054234 | 0.054235 | 0.054235 | 0.97205 | -0.53838 | 0.97195 | -0.54036 | 3.7249
198 | 0.13565 | 0.034137 | -0.13557 | -0.034088 | 7.7583e-05 | 4.8688e-05 | 0.20688 | 0.20688 | 0.20688 | 0.97591 | -0.46241 | 0.9753 | -0.47438 | 14.209
199 | 0.037529 | 0.0094361 | -0.037522 | -0.0094317 | 7.0379e-06 | 4.4327e-06 | 0.057233 | 0.057233 | 0.057233 | 0.97591 | -0.46246 | 0.97571 | -0.46639 | 15.7235
200 | 0.058867 | 0.014742 | -0.058855 | -0.014736 | 1.1422e-05 | 6.564e-06 | 0.090042 | 0.090043 | 0.090043 | 0.97277 | -0.52423 | 0.97256 | -0.52831 | 6.1842
201 | -0.10881 | -0.027275 | 0.10884 | 0.027289 | 2.3179e-05 | 1.4392e-05 | 0.16645 | 0.16645 | 0.16645 | 0.97277 | -0.52423 | 0.973 | -0.51976 | 11.4321
202 | 0.033219 | 0.0083313 | -0.033219 | -0.008331 | 4.9272e-07 | 2.1461e-07 | 0.050859 | 0.050859 | 0.050859 | 0.97195 | -0.54036 | 0.97194 | -0.54067 | 3.4931
203 | 0.13118 | 0.032987 | -0.13114 | -0.032967 | 3.2441e-05 | 2.0331e-05 | 0.20018 | 0.20018 | 0.20018 | 0.9753 | -0.47438 | 0.97504 | -0.47956 | 13.7485
204 | 0.0035249 | 0.00088316 | -0.0035248 | -0.00088323 | 1.4267e-07 | -7.284e-08 | 0.0053779 | 0.0053779 | 0.0053779 | 0.9753 | -0.47438 | 0.97526 | -0.47523 | 1.4775
205 | 0.058855 | 0.014736 | -0.058845 | -0.01473 | 1.0228e-05 | 5.8779e-06 | 0.090043 | 0.090043 | 0.090043 | 0.97256 | -0.52831 | 0.97238 | -0.53196 | 6.1843
206 | -0.11095 | -0.02782 | 0.11098 | 0.027834 | 2.3211e-05 | 1.4428e-05 | 0.16969 | 0.16969 | 0.16969 | 0.973 | -0.51976 | 0.97322 | -0.51537 | 11.6543
207 | 0.031752 | 0.0079635 | -0.031747 | -0.0079615 | 4.8152e-06 | 2.0045e-06 | 0.048613 | 0.048614 | 0.048614 | 0.97194 | -0.54067 | 0.97178 | -0.54385 | 3.3389
208 | 0.029143 | 0.0073087 | -0.029142 | -0.0073086 | 4.3096e-07 | 1.6142e-07 | 0.044626 | 0.044626 | 0.044626 | 0.97178 | -0.54385 | 0.97176 | -0.54416 | 3.065
209 | 0.026669 | 0.0066888 | -0.026666 | -0.0066879 | 3.0097e-06 | 9.7249e-07 | 0.040839 | 0.04084 | 0.04084 | 0.97176 | -0.54416 | 0.97164 | -0.54653 | 2.8049
210 | 0.026666 | 0.0066879 | -0.026662 | -0.0066864 | 4.497e-06 | 1.4535e-06 | 0.04084 | 0.04084 | 0.04084 | 0.97164 | -0.54653 | 0.97146 | -0.55007 | 2.805
211 | 0.025162 | 0.0063104 | -0.025158 | -0.0063095 | 3.2581e-06 | 9.2674e-07 | 0.038542 | 0.038543 | 0.038543 | 0.97146 | -0.55007 | 0.97132 | -0.55279 | 2.6472
212 | 0.023098 | 0.005793 | -0.023095 | -0.0057917 | 2.5207e-06 | 1.3475e-06 | 0.035386 | 0.035386 | 0.035386 | 0.97132 | -0.55279 | 0.97121 | -0.55508 | 4.8607
213 | -0.0033214 | -0.00083243 | 0.0033217 | 0.00083228 | 2.3949e-07 | -1.5177e-07 | 0.0050895 | 0.0050894 | 0.0050895 | 0.97108 | -0.55778 | 0.97115 | -0.55627 | 1.3982
214 | 0.019633 | 0.0048917 | -0.01963 | -0.0048916 | 3.0284e-06 | 1.7053e-07 | 0.030072 | 0.030072 | 0.030072 | 0.97115 | -0.55627 | 0.97099 | -0.55952 | 2.0654
215 | -0.022955 | -0.005724 | 0.022958 | 0.0057247 | 3.0214e-06 | 6.4327e-07 | 0.035161 | 0.03516 | 0.035161 | 0.97115 | -0.55627 | 0.97129 | -0.55349 | 2.4149
216 | 0.12927 | 0.032496 | -0.12921 | -0.032462 | 5.4339e-05 | 3.4035e-05 | 0.19731 | 0.19731 | 0.19731 | 0.97504 | -0.47956 | 0.97459 | -0.48837 | 13.5518
217 | 0.0026463 | 0.00066308 | -0.0026463 | -0.00066314 | 4.7223e-08 | -6.616e-08 | 0.0040377 | 0.0040377 | 0.0040377 | 0.97526 | -0.47523 | 0.97524 | -0.47561 | 1.1093
218 | 0.0017707 | 0.00044371 | -0.0017707 | -0.00044378 | 1.9403e-08 | -7.6024e-08 | 0.0027017 | 0.0027018 | 0.0027018 | 0.97524 | -0.47561 | 0.97522 | -0.47584 | 0.74225
219 | 0.12709 | 0.03193 | -0.12705 | -0.031908 | 3.393e-05 | 2.1237e-05 | 0.19407 | 0.19407 | 0.19407 | 0.97459 | -0.48837 | 0.9743 | -0.49396 | 13.3289
220 | 0.12341 | 0.030995 | -0.1234 | -0.030988 | 1.0132e-05 | 6.3329e-06 | 0.1885 | 0.1885 | 0.1885 | 0.9743 | -0.49396 | 0.97422 | -0.49568 | 12.9465
221 | 0.12124 | 0.030448 | -0.1212 | -0.03042 | 4.4391e-05 | 2.7723e-05 | 0.18521 | 0.18521 | 0.18521 | 0.97422 | -0.49568 | 0.97383 | -0.50336 | 12.7203
222 | -0.11306 | -0.028357 | 0.1131 | 0.028382 | 4.001e-05 | 2.4897e-05 | 0.17288 | 0.17288 | 0.17288 | 0.97322 | -0.51537 | 0.97359 | -0.50795 | 11.8734
223 | -0.1152 | -0.028908 | 0.11523 | 0.028924 | 2.4439e-05 | 1.5223e-05 | 0.17609 | 0.17609 | 0.17609 | 0.97359 | -0.50795 | 0.97382 | -0.50351 | 12.0939
224 | -0.11887 | -0.029837 | 0.11887 | 0.029838 | 8.2065e-07 | 5.1202e-07 | 0.18166 | 0.18166 | 0.18166 | 0.97382 | -0.50351 | 0.97383 | -0.50336 | 12.4765
225 | 0.056963 | 0.014258 | -0.056962 | -0.014257 | 1.8182e-06 | 1.037e-06 | 0.087164 | 0.087164 | 0.087164 | 0.97238 | -0.53196 | 0.97234 | -0.53263 | 5.9865
226 | 0.054269 | 0.013582 | -0.05426 | -0.013577 | 8.8884e-06 | 5.0066e-06 | 0.083043 | 0.083043 | 0.083043 | 0.97234 | -0.53263 | 0.97217 | -0.53607 | 5.7035
227 | 0.051688 | 0.012933 | -0.051683 | -0.01293 | 5.9086e-06 | 3.2821e-06 | 0.079107 | 0.079107 | 0.079107 | 0.97217 | -0.53607 | 0.97205 | -0.53848 | 5.4332
228 | -0.046148 | -0.011541 | 0.046148 | 0.011541 | 1.8079e-07 | 9.655e-08 | 0.070644 | 0.070644 | 0.070644 | 0.97191 | -0.54132 | 0.97191 | -0.54123 | 4.852
229 | 0.043766 | 0.010944 | -0.043762 | -0.010941 | 4.1511e-06 | 2.1678e-06 | 0.066998 | 0.066998 | 0.066998 | 0.97191 | -0.54132 | 0.97181 | -0.54331 | 4.6015
230 | -0.048917 | -0.012235 | 0.048924 | 0.012238 | 6.4177e-06 | 3.5021e-06 | 0.074884 | 0.074884 | 0.074884 | 0.97191 | -0.54123 | 0.97205 | -0.53848 | 5.1431
231 | 0.041024 | 0.010255 | -0.041019 | -0.010253 | 5.5982e-06 | 2.8327e-06 | 0.062807 | 0.062807 | 0.062807 | 0.97181 | -0.54331 | 0.97166 | -0.54618 | 4.3137
232 | 0.038715 | 0.0096751 | -0.038715 | -0.0096751 | 5.8639e-09 | 2.8633e-09 | 0.059279 | 0.059279 | 0.059279 | 0.97166 | -0.54618 | 0.97166 | -0.54618 | 4.0713
233 | 0.036024 | 0.0090006 | -0.036021 | -0.0089993 | 2.8753e-06 | 1.3408e-06 | 0.055157 | 0.055158 | 0.055158 | 0.97166 | -0.54618 | 0.97158 | -0.54786 | 3.7883
234 | 0.033361 | 0.0083327 | -0.03336 | -0.0083323 | 1.0051e-06 | 4.3978e-07 | 0.051084 | 0.051084 | 0.051084 | 0.97158 | -0.54786 | 0.97154 | -0.5485 | 3.5085
235 | 0.030714 | 0.0076691 | -0.030712 | -0.0076684 | 1.6464e-06 | 6.6044e-07 | 0.047031 | 0.047031 | 0.047031 | 0.97154 | -0.5485 | 0.97149 | -0.54963 | 3.2302
236 | -0.021497 | -0.0053906 | 0.021499 | 0.0053917 | 1.8403e-06 | 1.1218e-06 | 0.032941 | 0.032941 | 0.032941 | 0.97112 | -0.55687 | 0.97121 | -0.55508 | 9.0497
237 | -0.25387 | -0.064998 | 0.25392 | 0.065033 | 5.5051e-05 | 3.5024e-05 | 0.38135 | 0.38135 | 0.38135 | 0.99186 | -0.15391 | 0.9921 | -0.14943 | 26.1914
238 | -0.25557 | -0.065446 | 0.25592 | 0.065669 | 0.00035075 | 0.00022317 | 0.38382 | 0.38382 | 0.38382 | 0.9921 | -0.14943 | 0.99358 | -0.12114 | 26.3611
239 | -0.25654 | -0.065824 | 0.25659 | 0.065861 | 5.7792e-05 | 3.6771e-05 | 0.38474 | 0.38474 | 0.38474 | 0.99358 | -0.12114 | 0.99383 | -0.1165 | 26.4245
240 | -0.02446 | -0.0061011 | 0.024462 | 0.0061017 | 2.3805e-06 | 6.2764e-07 | 0.037462 | 0.037461 | 0.037462 | 0.97129 | -0.55349 | 0.9714 | -0.55144 | 2.5729
241 | -0.025328 | -0.0063187 | 0.025328 | 0.0063188 | 5.9748e-07 | 1.7261e-07 | 0.038787 | 0.038787 | 0.038787 | 0.9714 | -0.55144 | 0.97142 | -0.55095 | 2.664
242 | -0.028049 | -0.0070008 | 0.028051 | 0.0070014 | 1.7577e-06 | 6.2172e-07 | 0.042955 | 0.042955 | 0.042955 | 0.97142 | -0.55095 | 0.97149 | -0.54963 | 2.9502
243 | 0.0035841 | 0.00088978 | -0.0035836 | -0.00089813 | 4.9691e-07 | -8.3499e-06 | 0.005494 | 0.0054971 | 0.0054971 | 0.9702 | -0.57535 | 0.97005 | -0.57827 | 0.37755
244 | -0.0046872 | -0.0011742 | 0.0046876 | 0.0011742 | 3.9841e-07 | -1.9524e-08 | 0.0070499 | 0.0070498 | 0.0070499 | 0.98931 | -0.20311 | 0.9894 | -0.20132 | 1.9368
245 | 0.0030056 | 0.00075274 | -0.0030055 | -0.00075291 | 1.6595e-07 | -1.7183e-07 | 0.0045206 | 0.0045207 | 0.0045207 | 0.98931 | -0.20311 | 0.98925 | -0.20427 | 1.2419
246 | 0.0014453 | 0.0003619 | -0.0014453 | -0.00036222 | 4.89e-08 | -3.2291e-07 | 0.0021739 | 0.0021741 | 0.0021741 | 0.98925 | -0.20427 | 0.98921 | -0.20498 | 0.59727
247 | 0.010353 | 0.0025951 | -0.010351 | -0.0025939 | 2.2627e-06 | 1.1383e-06 | 0.015692 | 0.015692 | 0.015692 | 0.9818 | -0.34795 | 0.98157 | -0.35254 | 4.311
248 | -0.25791 | -0.066191 | 0.25822 | 0.066385 | 0.00030456 | 0.00019379 | 0.38672 | 0.38672 | 0.38672 | 0.99383 | -0.1165 | 0.99511 | -0.092198 | 26.5601
249 | -0.47673 | -0.12243 | 0.47762 | 0.123 | 0.00088964 | 0.0005684 | 0.71392 | 0.71392 | 0.71392 | 0.99511 | -0.092198 | 0.99714 | -0.05384 | 49.0328
250 | -0.4782 | -0.12314 | 0.47928 | 0.12384 | 0.0010875 | 0.00069479 | 0.71478 | 0.71478 | 0.71478 | 0.99714 | -0.05384 | 0.99962 | -0.0072185 | 49.0922
251 | -0.47984 | -0.12398 | 0.48001 | 0.12409 | 0.00016905 | 0.00010801 | 0.71561 | 0.71561 | 0.71561 | 0.99962 | -0.0072185 | 1 | 0 | 49.149
252 | -0.0020355 | -0.00051014 | 0.0020355 | 0.00050998 | 5.6631e-08 | -1.6422e-07 | 0.0030858 | 0.0030857 | 0.0030858 | 0.98154 | -0.35312 | 0.98157 | -0.35254 | 0.84775
253 | 0.0083157 | 0.002084 | -0.0083145 | -0.0020835 | 1.1549e-06 | 4.9423e-07 | 0.012606 | 0.012606 | 0.012606 | 0.98157 | -0.35254 | 0.98142 | -0.35546 | 3.4632
254 | -0.0020927 | -0.00052449 | 0.0020928 | 0.0005244 | 3.3743e-08 | -9.1242e-08 | 0.0031737 | 0.0031737 | 0.0031737 | 0.98119 | -0.3599 | 0.98121 | -0.35956 | 0.8719
255 | -0.0041854 | -0.0010489 | 0.004186 | 0.0010488 | 5.5978e-07 | -1.0983e-07 | 0.0063472 | 0.006347 | 0.0063472 | 0.98121 | -0.35956 | 0.98136 | -0.35675 | 1.7437
256 | 0.0062791 | 0.0015733 | -0.0062787 | -0.0015732 | 3.8809e-07 | 1.041e-07 | 0.0095201 | 0.0095202 | 0.0095202 | 0.98142 | -0.35546 | 0.98136 | -0.35675 | 2.6154
257 | 0.019048 | 0.0047767 | -0.019045 | -0.004775 | 2.9114e-06 | 1.7487e-06 | 0.02907 | 0.02907 | 0.02907 | 0.97507 | -0.4798 | 0.9749 | -0.483 | 7.9862
258 | 0.0093389 | 0.0023388 | -0.0093387 | -0.0023387 | 1.8565e-07 | 8.8477e-08 | 0.014259 | 0.014259 | 0.014259 | 0.97453 | -0.49046 | 0.97451 | -0.49088 | 3.9173
259 | 0.014413 | 0.003614 | -0.01441 | -0.0036124 | 2.7952e-06 | 1.597e-06 | 0.021999 | 0.022 | 0.022 | 0.9749 | -0.483 | 0.9747 | -0.48708 | 6.0438
260 | -0.011599 | -0.0029069 | 0.011602 | 0.0029086 | 3.1211e-06 | 1.667e-06 | 0.017712 | 0.017712 | 0.017712 | 0.97441 | -0.49272 | 0.9747 | -0.48708 | 4.866
261 | 0.0060194 | 0.0015086 | -0.0060194 | -0.0015086 | 9.4141e-09 | 2.3242e-09 | 0.0091922 | 0.0091922 | 0.0091922 | 0.97441 | -0.49272 | 0.97441 | -0.49276 | 2.5253
262 | 0.0029668 | 0.00074352 | -0.0029667 | -0.00074354 | 1.2675e-08 | -1.24e-08 | 0.0045305 | 0.0045305 | 0.0045305 | 0.97441 | -0.49276 | 0.97441 | -0.49284 | 1.2446

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48228 | 0.12424

## res_load
| p_mw | q_mvar
0 | 0.001346 | 0.00033733
1 | 0.0018035 | 0.00045199
2 | 0.0012315 | 0.00030864
3 | 0.0012769 | 0.00032001
4 | 0.0048811 | 0.0012233
5 | 0.0025549 | 0.00064032
6 | 0.0020131 | 0.00050454
7 | 0.0022583 | 0.00056598
8 | 0.00021777 | 5.4578e-05
9 | 0.0007559 | 0.00018945
10 | 0.0016859 | 0.00042253
11 | 0.00040851 | 0.00010238
12 | 0.0015096 | 0.00037834
13 | 0.0051415 | 0.0012886
14 | 0.0019201 | 0.00048123
15 | 0.00083162 | 0.00020842
16 | 0.0052572 | 0.0013176
17 | 0.0021267 | 0.00053299
18 | 0.0031739 | 0.00079546
19 | 0.003707 | 0.00092907
20 | 0.0002772 | 6.9473e-05
21 | 0.0023555 | 0.00059034
22 | 0.0017898 | 0.00044856
23 | 0.0014546 | 0.00036455
24 | 0.0048631 | 0.0012188
25 | 0.0037962 | 0.00095142
26 | 0.0025929 | 0.00064984
27 | 0.0024682 | 0.0006186
28 | 0.002655 | 0.0006654
29 | 0.0033855 | 0.00084849
30 | 0.0011252 | 0.000282
31 | 0.0046783 | 0.0011725
32 | 0.0024517 | 0.00061446
33 | 0.0027787 | 0.0006964
34 | 0.002478 | 0.00062104
35 | 0.0010888 | 0.00027288
36 | 0.0026476 | 0.00066356
37 | 0.0012778 | 0.00032024
38 | 0.001388 | 0.00034787
39 | 0.0016451 | 0.00041231
40 | 0.0019363 | 0.00048529
41 | 0.0025609 | 0.00064183
42 | 0.0034532 | 0.00086546
43 | 0.001453 | 0.00036416
44 | 0.0021676 | 0.00054324
45 | 0.003387 | 0.00084885
46 | 0.003597 | 0.00090149
47 | 0.0020111 | 0.00050402
48 | 0.0019211 | 0.00048148
49 | 0.00071121 | 0.00017825
50 | 0.0033869 | 0.00084883
51 | 0.0018533 | 0.00046447
52 | 0.0013709 | 0.00034357
53 | 0.00067413 | 0.00016895
54 | 0.0020352 | 0.00051008
55 | 0.0034516 | 0.00086505
56 | 0.002917 | 0.00073106
57 | 0.0029274 | 0.00073367
58 | 0.0022321 | 0.00055941
59 | 0.0015641 | 0.000392
60 | 0.0013591 | 0.00034062
61 | 0.0019335 | 0.00048458
62 | 0.0011222 | 0.00028124
63 | 0.0035831 | 0.00089802
64 | 0.0021974 | 0.00055072
65 | 0.0017556 | 0.00044001
66 | 0.0018427 | 0.00046183
67 | 0.0067908 | 0.0017019
68 | 0.0010797 | 0.0002706
69 | 0.0040282 | 0.0010096
70 | 0.0056616 | 0.0014189
71 | 0.002914 | 0.00073033
72 | 0.00071163 | 0.00017835
73 | 0.00064104 | 0.00016066
74 | 0.0005003 | 0.00012539
75 | 0.0017832 | 0.0004469
76 | 0.0030356 | 0.00076078
77 | 0.0016433 | 0.00041186
78 | 0.0020356 | 0.00051016
79 | 0.0020355 | 0.00051014
80 | 0.0013402 | 0.00033589
81 | 0.0010607 | 0.00026585
82 | 0.0036518 | 0.00091523
83 | 0.0021907 | 0.00054904
84 | 0.0013906 | 0.00034851
85 | 0.0019652 | 0.00049253
86 | 0.0025729 | 0.00064484
87 | 0.0012722 | 0.00031885
88 | 0.0011302 | 0.00028326
89 | 0.0016646 | 0.00041718
90 | 0.0021827 | 0.00054704
91 | 0.0010762 | 0.00026972
92 | 0.0026479 | 0.00066363
93 | 0.0017801 | 0.00044614
94 | 0.0016593 | 0.00041586
95 | 0.0016383 | 0.00041059
96 | 0.0014102 | 0.00035344
97 | 0.0014914 | 0.00037379
98 | 0.0060935 | 0.0015272
99 | 0.0022937 | 0.00057484
100 | 0.0020474 | 0.00051312
101 | 0.00089535 | 0.00022439
102 | 0.0025895 | 0.00064898
103 | 0.0011157 | 0.00027962
104 | 0.0011527 | 0.0002889
105 | 0.0020511 | 0.00051405
106 | 0.0013703 | 0.00034344
107 | 0.0036628 | 0.00091799
108 | 0.0013396 | 0.00033574
109 | 0.0017989 | 0.00045085
110 | 0.0015566 | 0.00039013
111 | 0.0016824 | 0.00042165
112 | 0.0032571 | 0.00081632
113 | 0.003516 | 0.0008812
114 | 0.0011801 | 0.00029576
115 | 0.0029805 | 0.00074697
116 | 0.0020154 | 0.00050511
117 | 0.0020693 | 0.00051861
118 | 0.0016321 | 0.00040904
119 | 0.0014331 | 0.00035916
120 | 0.0023644 | 0.00059257
121 | 0.003345 | 0.00083834
122 | 0.0018523 | 0.00046423
123 | 0.0013375 | 0.00033522
124 | 0.0045396 | 0.0011377
125 | 0.0012125 | 0.00030389
126 | 0.0024401 | 0.00061155
127 | 0.0010063 | 0.00025219
128 | 0.001119 | 0.00028046
129 | 0.0013938 | 0.00034931
130 | 0.0017946 | 0.00044977
131 | 0.0034702 | 0.00086971
132 | 0.0024494 | 0.00061387
133 | 0.00098728 | 0.00024744
134 | 0.0024715 | 0.00061941
135 | 0.0025889 | 0.00064883
136 | 0.0032758 | 0.00082098
137 | 0.0026739 | 0.00067013
138 | 0.0015042 | 0.000377
139 | 0.0015783 | 0.00039555
140 | 0.0018954 | 0.00047502
141 | 0.0034889 | 0.0008744
142 | 0.00086392 | 0.00021652
143 | 0.0020239 | 0.00050723
144 | 0.0016386 | 0.00041066
145 | 0.0036454 | 0.00091362
146 | 0.003003 | 0.00075261
147 | 0.0023005 | 0.00057657
148 | 0.0018785 | 0.00047079
149 | 0.0019753 | 0.00049507
150 | 0.0016043 | 0.00040209
151 | 0.0022049 | 0.00055261
152 | 0.00087041 | 0.00021815
153 | 0.0024422 | 0.00061208
154 | 0.002116 | 0.00053032
155 | 0.0014667 | 0.00036759
156 | 0.0026044 | 0.00065272
157 | 0.0024728 | 0.00061975
158 | 0.0015002 | 0.00037598
159 | 0.0020607 | 0.00051646
160 | 0.0033214 | 0.00083243
161 | 0.0018769 | 0.0004704
162 | 0.00087842 | 0.00022015
163 | 0.00087557 | 0.00021944
164 | 0.0017707 | 0.00044378
165 | 0.0021253 | 0.00053264
166 | 0.0036454 | 0.00091362
167 | 0.0021564 | 0.00054045
168 | 0.0020864 | 0.00052289
169 | 0.0021009 | 0.00052654
170 | 0.0036454 | 0.00091362
171 | 0.0018814 | 0.00047152
172 | 0.0023237 | 0.00058238
173 | 0.0026926 | 0.00067483
174 | 0.0025717 | 0.00064452
175 | 0.0023817 | 0.00059692
176 | 0.0027692 | 0.00069402
177 | 0.0027374 | 0.00068606
178 | 0.0027591 | 0.00069149
179 | 0.0023038 | 0.00057739
180 | 0.0026912 | 0.00067449
181 | 0.0026597 | 0.00066658
182 | 0.0026463 | 0.00066321
183 | 0.001409 | 0.00035313
184 | 0.001596 | 0.0004
185 | 0.0014968 | 0.00037514
186 | 0.0016471 | 0.0004128
187 | 0.00061749 | 0.00015476
188 | 0.0015804 | 0.0003961
189 | 0.0015021 | 0.00037645
190 | 0.00086558 | 0.00021694
191 | 0.002721 | 0.00068194
192 | 0.0026614 | 0.000667
193 | 0.00072505 | 0.00018172
194 | 0.0035836 | 0.00089813
195 | 0.0016816 | 0.00042145
196 | 0.0014892 | 0.00037324
197 | 0.0015601 | 0.00039101
198 | 0.0014453 | 0.00036222
199 | 0.00080297 | 0.00020124
200 | 0.0013185 | 0.00033045
201 | 0.0005798 | 0.00014531
202 | 0.00055598 | 0.00013934
203 | 0.00061646 | 0.0001545
204 | 0.0020355 | 0.00051014
205 | 0.0020927 | 0.00052449
206 | 0.0020927 | 0.00052447
207 | 0.0020354 | 0.00051012
208 | 0.0020927 | 0.00052448
209 | 0.0011836 | 0.00029663
210 | 0.0033467 | 0.00083877
211 | 0.0012938 | 0.00032426
212 | 0.0046323 | 0.001161
213 | 0.0055793 | 0.0013983
214 | 0.0028083 | 0.00070384
215 | 0.0030526 | 0.00076506
216 | 0.0029667 | 0.00074354
217 | 0.0011112 | 0.00027849

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1