## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_155-22_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_155-22_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_155-22_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_155-22_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_155-22_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_155-22_0_5_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_155-22_0_5_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_155-22_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_155-22_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_155-22_0_5_node_135 | 0.4 | n |  | TRUE
10 | bus_LV_155-22_0_5_node_139 | 0.4 | n |  | TRUE
11 | bus_LV_155-22_0_5_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_155-22_0_5_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_155-22_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_155-22_0_5_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_155-22_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_155-22_0_5_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_155-22_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_155-22_0_5_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_155-22_0_5_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_155-22_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_155-22_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_155-22_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_155-22_0_5_node_136 | 0.4 | n |  | TRUE
24 | bus_LV_155-22_0_5_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_155-22_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_155-22_0_5_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_155-22_0_5_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_155-22_0_5_node_102 | 0.4 | n |  | TRUE
29 | bus_LV_155-22_0_5_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_155-22_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_155-22_0_5_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_155-22_0_5_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_155-22_0_5_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_155-22_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_155-22_0_5_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_155-22_0_5_node_90 | 0.4 | n |  | TRUE
37 | bus_LV_155-22_0_5_node_105 | 0.4 | n |  | TRUE
38 | bus_LV_155-22_0_5_node_81 | 0.4 | n |  | TRUE
39 | bus_LV_155-22_0_5_node_87 | 0.4 | n |  | TRUE
40 | bus_LV_155-22_0_5_node_106 | 0.4 | n |  | TRUE
41 | bus_LV_155-22_0_5_node_80 | 0.4 | n |  | TRUE
42 | bus_LV_155-22_0_5_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_155-22_0_5_node_101 | 0.4 | n |  | TRUE
44 | bus_LV_155-22_0_5_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_155-22_0_5_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_155-22_0_5_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_155-22_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_155-22_0_5_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_155-22_0_5_node_59 | 0.4 | n |  | TRUE
50 | bus_LV_155-22_0_5_node_126 | 0.4 | n |  | TRUE
51 | bus_LV_155-22_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_155-22_0_5_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_155-22_0_5_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_155-22_0_5_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_155-22_0_5_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_155-22_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_155-22_0_5_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_155-22_0_5_node_129 | 0.4 | n |  | TRUE
59 | bus_LV_155-22_0_5_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_155-22_0_5_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_155-22_0_5_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_155-22_0_5_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_155-22_0_5_node_83 | 0.4 | n |  | TRUE
64 | bus_LV_155-22_0_5_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_155-22_0_5_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_155-22_0_5_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_155-22_0_5_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_155-22_0_5_node_119 | 0.4 | n |  | TRUE
69 | bus_LV_155-22_0_5_node_78 | 0.4 | n |  | TRUE
70 | bus_LV_155-22_0_5_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_155-22_0_5_node_118 | 0.4 | n |  | TRUE
72 | bus_LV_155-22_0_5_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_155-22_0_5_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_155-22_0_5_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_155-22_0_5_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_155-22_0_5_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_155-22_0_5_node_137 | 0.4 | n |  | TRUE
78 | bus_LV_155-22_0_5_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_155-22_0_5_node_128 | 0.4 | n |  | TRUE
80 | bus_LV_155-22_0_5_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_155-22_0_5_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_155-22_0_5_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_155-22_0_5_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_155-22_0_5_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_155-22_0_5_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_155-22_0_5_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_155-22_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_155-22_0_5_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_155-22_0_5_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_155-22_0_5_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_155-22_0_5_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_155-22_0_5_node_117 | 0.4 | n |  | TRUE
93 | bus_LV_155-22_0_5_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_155-22_0_5_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_155-22_0_5_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_155-22_0_5_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_155-22_0_5_node_74 | 0.4 | n |  | TRUE
98 | bus_LV_155-22_0_5_node_141 | 0.4 | n |  | TRUE
99 | bus_LV_155-22_0_5_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_155-22_0_5_node_140 | 0.4 | n |  | TRUE
101 | bus_LV_155-22_0_5_node_133 | 0.4 | n |  | TRUE
102 | bus_LV_155-22_0_5_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_155-22_0_5_node_134 | 0.4 | n |  | TRUE
104 | bus_LV_155-22_0_5_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_155-22_0_5_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_155-22_0_5_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_155-22_0_5_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_155-22_0_5_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_155-22_0_5_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_155-22_0_5_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_155-22_0_5_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_155-22_0_5_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_155-22_0_5_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_155-22_0_5_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_155-22_0_5_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_155-22_0_5_node_97 | 0.4 | n |  | TRUE
117 | bus_LV_155-22_0_5_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_155-22_0_5_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_155-22_0_5_node_131 | 0.4 | n |  | TRUE
120 | bus_LV_155-22_0_5_node_100 | 0.4 | n |  | TRUE
121 | bus_LV_155-22_0_5_node_138 | 0.4 | n |  | TRUE
122 | bus_LV_155-22_0_5_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_155-22_0_5_node_130 | 0.4 | n |  | TRUE
124 | bus_LV_155-22_0_5_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_155-22_0_5_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_155-22_0_5_node_104 | 0.4 | n |  | TRUE
127 | bus_LV_155-22_0_5_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_155-22_0_5_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_155-22_0_5_node_110 | 0.4 | n |  | TRUE
130 | bus_LV_155-22_0_5_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_155-22_0_5_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_155-22_0_5_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_155-22_0_5_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_155-22_0_5_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_155-22_0_5_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_155-22_0_5_node_122 | 0.4 | n |  | TRUE
137 | bus_MV_361_0_node_169 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_155-22_0_5_load_0 | 0 | 0.009187 | 0.0023025 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_155-22_0_5_load_1 | 1 | 0.0029534 | 0.00074019 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_155-22_0_5_load_3 | 3 | 0.0032567 | 0.0008162 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_155-22_0_5_load_4 | 4 | 0.0026829 | 0.0006724 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_155-22_0_5_load_36 | 5 | 0.0046517 | 0.0011658 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_155-22_0_5_load_29 | 6 | 0.0028322 | 0.00070983 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_155-22_0_5_load_135 | 9 | 0.0028641 | 0.00071781 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_155-22_0_5_load_139 | 10 | 0.0032567 | 0.00081622 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_155-22_0_5_load_30 | 12 | 0.0017857 | 0.00044753 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_155-22_0_5_load_17 | 14 | 0.0055253 | 0.0013848 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_155-22_0_5_load_13 | 15 | 0.0049536 | 0.0012415 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_155-22_0_5_load_28 | 16 | 0.0034723 | 0.00087023 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_155-22_0_5_load_11 | 17 | 0.0058892 | 0.001476 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_155-22_0_5_load_7 | 18 | 0.0069321 | 0.0017374 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_155-22_0_5_load_8 | 19 | 0.0062162 | 0.0015579 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_155-22_0_5_load_12 | 21 | 0.0071459 | 0.0017909 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_155-22_0_5_load_136 | 23 | 0.0069291 | 0.0017366 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_155-22_0_5_load_25 | 27 | 0.0055779 | 0.001398 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_155-22_0_5_load_108 | 29 | 0.0015378 | 0.00038542 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_155-22_0_5_load_22 | 30 | 0.0055922 | 0.0014015 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_155-22_0_5_load_19 | 31 | 0.0072831 | 0.0018253 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_155-22_0_5_load_20 | 32 | 0.0067046 | 0.0016803 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_155-22_0_5_load_24 | 34 | 0.000618 | 0.00015489 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_155-22_0_5_load_90 | 36 | 0.0010443 | 0.00026172 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_155-22_0_5_load_105 | 37 | 0.0038928 | 0.00097562 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_155-22_0_5_load_81 | 38 | 0.00044128 | 0.0001106 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_155-22_0_5_load_80 | 41 | 0.0012503 | 0.00031335 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_155-22_0_5_load_103 | 42 | 0.0027131 | 0.00067998 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_155-22_0_5_load_101 | 43 | 0.0017444 | 0.00043719 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_155-22_0_5_load_31 | 44 | 0.0020926 | 0.00052444 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_155-22_0_5_load_32 | 45 | 0.0016606 | 0.00041618 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_155-22_0_5_load_33 | 46 | 0.0013883 | 0.00034794 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_155-22_0_5_load_34 | 47 | 0.0019984 | 0.00050085 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_155-22_0_5_load_35 | 48 | 0.0019475 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_155-22_0_5_load_59 | 49 | 0.002143 | 0.00053709 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_155-22_0_5_load_126 | 50 | 0.0031699 | 0.00079445 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_155-22_0_5_load_46 | 52 | 0.009534 | 0.0023894 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_155-22_0_5_load_45 | 53 | 0.018285 | 0.0045826 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_155-22_0_5_load_41 | 55 | 0.010908 | 0.0027339 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_155-22_0_5_load_47 | 56 | 0.0060339 | 0.0015122 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_155-22_0_5_load_129 | 58 | 0.0015334 | 0.0003843 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_155-22_0_5_load_48 | 60 | 0.013115 | 0.0032869 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_155-22_0_5_load_43 | 62 | 0.0061892 | 0.0015512 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_155-22_0_5_load_58 | 65 | 0.003106 | 0.00077843 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_155-22_0_5_load_55 | 66 | 0.0034749 | 0.00087088 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_155-22_0_5_load_51 | 67 | 0.0012627 | 0.00031646 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_155-22_0_5_load_119 | 68 | 0.0016815 | 0.00042142 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_155-22_0_5_load_78 | 69 | 0.0028376 | 0.00071117 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_155-22_0_5_load_53 | 70 | 0.0034304 | 0.00085973 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_155-22_0_5_load_52 | 72 | 0.0062223 | 0.0015595 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_155-22_0_5_load_56 | 74 | 0.0051415 | 0.0012886 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_155-22_0_5_load_57 | 75 | 0.00043584 | 0.00010923 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_155-22_0_5_load_137 | 77 | 0.0063957 | 0.0016029 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_155-22_0_5_load_60 | 78 | 0.0074701 | 0.0018722 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_155-22_0_5_load_128 | 79 | 0.0014749 | 0.00036965 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_155-22_0_5_load_79 | 80 | 0.0053754 | 0.0013472 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_155-22_0_5_load_127 | 81 | 0.0018856 | 0.00047257 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_155-22_0_5_load_61 | 82 | 0.0031496 | 0.00078937 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_155-22_0_5_load_63 | 83 | 0.0025746 | 0.00064527 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_155-22_0_5_load_65 | 84 | 0.0047321 | 0.001186 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_155-22_0_5_load_64 | 85 | 0.0042155 | 0.0010565 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_155-22_0_5_load_69 | 86 | 0.0031053 | 0.00077825 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_155-22_0_5_load_67 | 89 | 0.004599 | 0.0011526 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_155-22_0_5_load_77 | 91 | 0.0082925 | 0.0020783 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_155-22_0_5_load_117 | 92 | 0.0031439 | 0.00078794 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_155-22_0_5_load_73 | 93 | 0.00050967 | 0.00012773 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_155-22_0_5_load_116 | 94 | 0.0038659 | 0.00096889 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_155-22_0_5_load_71 | 96 | 0.0034827 | 0.00087283 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_155-22_0_5_load_141 | 98 | 0.00061917 | 0.00015518 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_155-22_0_5_load_140 | 100 | 0.0018918 | 0.00047412 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_155-22_0_5_load_133 | 101 | 0.0011195 | 0.00028056 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_155-22_0_5_load_72 | 102 | 0.0022517 | 0.00056434 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_155-22_0_5_load_134 | 103 | 0.00030077 | 7.538e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_155-22_0_5_load_82 | 104 | 0.0011982 | 0.0003003 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_155-22_0_5_load_84 | 105 | 0.00081653 | 0.00020464 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_155-22_0_5_load_85 | 106 | 0.0008795 | 0.00022042 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_155-22_0_5_load_86 | 107 | 0.0014684 | 0.00036802 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_155-22_0_5_load_88 | 108 | 0.00095156 | 0.00023848 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_155-22_0_5_load_89 | 109 | 0.0024471 | 0.00061331 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_155-22_0_5_load_91 | 110 | 0.00031206 | 7.821e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_155-22_0_5_load_92 | 111 | 0.00068363 | 0.00017133 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_155-22_0_5_load_93 | 112 | 0.0015162 | 0.00038 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_155-22_0_5_load_95 | 114 | 0.00091224 | 0.00022863 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_155-22_0_5_load_96 | 115 | 0.00073036 | 0.00018305 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_155-22_0_5_load_99 | 117 | 0.0009529 | 0.00023882 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_155-22_0_5_load_100 | 120 | 0.00062814 | 0.00015743 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_155-22_0_5_load_138 | 121 | 0.045388 | 0.011375 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_155-22_0_5_load_130 | 123 | 0.0022037 | 0.00055231 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_155-22_0_5_load_114 | 124 | 0.0056334 | 0.0014119 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_155-22_0_5_load_112 | 125 | 0.0028543 | 0.00071535 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_155-22_0_5_load_104 | 126 | 0.0038462 | 0.00096395 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_155-22_0_5_load_107 | 127 | 0.0036241 | 0.00090829 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_155-22_0_5_load_109 | 128 | 0.0092845 | 0.0023269 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_155-22_0_5_load_110 | 129 | 0.00132 | 0.00033082 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_155-22_0_5_load_115 | 130 | 0.0019631 | 0.00049199 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_155-22_0_5_load_125 | 134 | 0.005053 | 0.0012664 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_155-22_0_5_load_121 | 135 | 0.00067397 | 0.00016891 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_155-22_0_5_load_122 | 136 | 0.0032356 | 0.00081092 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 107 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_155-22_0_5_line_0 |  | 0 | 1 | 0.016035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_155-22_0_5_line_1 |  | 0 | 2 | 0.015904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_155-22_0_5_line_2 |  | 1 | 3 | 0.027673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_155-22_0_5_line_3 |  | 2 | 4 | 0.0067777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_155-22_0_5_line_4 |  | 3 | 5 | 0.032449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_155-22_0_5_line_5 |  | 4 | 6 | 0.013631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_155-22_0_5_line_6 |  | 6 | 12 | 0.024078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_155-22_0_5_line_7 |  | 7 | 8 | 0.043484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_155-22_0_5_line_8 |  | 7 | 9 | 0.041137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_155-22_0_5_line_9 |  | 8 | 10 | 0.012224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_155-22_0_5_line_10 |  | 8 | 11 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_155-22_0_5_line_11 |  | 11 | 16 | 0.032467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_155-22_0_5_line_12 |  | 11 | 17 | 0.013363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_155-22_0_5_line_13 |  | 12 | 44 | 0.012819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_155-22_0_5_line_14 |  | 13 | 14 | 0.021272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_155-22_0_5_line_15 |  | 13 | 15 | 0.038192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_155-22_0_5_line_16 |  | 14 | 22 | 0.019412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_155-22_0_5_line_17 |  | 15 | 24 | 0.0073158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_155-22_0_5_line_18 |  | 16 | 22 | 0.016371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_155-22_0_5_line_19 |  | 17 | 20 | 0.014789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_155-22_0_5_line_20 |  | 18 | 19 | 0.020036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_155-22_0_5_line_21 |  | 18 | 20 | 0.018603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_155-22_0_5_line_22 |  | 20 | 21 | 0.016425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_155-22_0_5_line_23 |  | 21 | 23 | 0.019997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_155-22_0_5_line_24 |  | 24 | 25 | 0.050753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_155-22_0_5_line_25 |  | 25 | 26 | 0.003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_155-22_0_5_line_26 |  | 25 | 27 | 0.019775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_155-22_0_5_line_27 |  | 26 | 28 | 0.051331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_155-22_0_5_line_28 |  | 26 | 29 | 0.018553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_155-22_0_5_line_29 |  | 27 | 30 | 0.032959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_155-22_0_5_line_30 |  | 28 | 42 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_155-22_0_5_line_31 |  | 28 | 43 | 0.015938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_155-22_0_5_line_32 |  | 29 | 40 | 0.0092919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_155-22_0_5_line_33 |  | 30 | 32 | 0.03416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_155-22_0_5_line_34 |  | 31 | 32 | 0.031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_155-22_0_5_line_35 |  | 31 | 33 | 0.038538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_155-22_0_5_line_36 |  | 33 | 34 | 0.012792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_155-22_0_5_line_37 |  | 34 | 38 | 0.029661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_155-22_0_5_line_38 |  | 35 | 36 | 0.028783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_155-22_0_5_line_39 |  | 35 | 37 | 0.040084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_155-22_0_5_line_40 |  | 36 | 39 | 0.0060834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_155-22_0_5_line_41 |  | 37 | 40 | 0.028173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_155-22_0_5_line_42 |  | 38 | 41 | 0.00083394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_155-22_0_5_line_43 |  | 39 | 108 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_155-22_0_5_line_44 |  | 39 | 106 | 0.014703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_155-22_0_5_line_45 |  | 40 | 127 | 0.026414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_155-22_0_5_line_46 |  | 41 | 104 | 0.0077449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_155-22_0_5_line_47 |  | 42 | 126 | 0.0086821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_155-22_0_5_line_48 |  | 43 | 120 | 0.024063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_155-22_0_5_line_49 |  | 44 | 45 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_155-22_0_5_line_50 |  | 45 | 46 | 0.0008435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_155-22_0_5_line_51 |  | 46 | 47 | 0.00031431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_155-22_0_5_line_52 |  | 47 | 48 | 0.0060833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_155-22_0_5_line_53 |  | 48 | 49 | 0.0087966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_155-22_0_5_line_54 |  | 49 | 50 | 0.014554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_155-22_0_5_line_55 |  | 50 | 81 | 0.0062779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_155-22_0_5_line_56 |  | 51 | 52 | 0.050704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_155-22_0_5_line_57 |  | 51 | 53 | 0.04268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_155-22_0_5_line_58 |  | 52 | 56 | 0.023091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_155-22_0_5_line_59 |  | 53 | 54 | 0.013705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_155-22_0_5_line_60 |  | 54 | 55 | 0.026211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_155-22_0_5_line_61 |  | 56 | 62 | 0.029259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_155-22_0_5_line_62 |  | 57 | 58 | 0.005573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_155-22_0_5_line_63 |  | 57 | 59 | 0.012813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_155-22_0_5_line_64 |  | 58 | 63 | 0.014395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_155-22_0_5_line_65 |  | 59 | 62 | 0.021391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_155-22_0_5_line_66 |  | 60 | 61 | 0.017763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_155-22_0_5_line_67 |  | 61 | 64 | 0.027592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_155-22_0_5_line_68 |  | 63 | 79 | 0.010939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_155-22_0_5_line_69 |  | 63 | 81 | 0.017593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_155-22_0_5_line_70 |  | 63 | 104 | 0.015334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_155-22_0_5_line_71 |  | 64 | 65 | 0.02165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_155-22_0_5_line_72 |  | 64 | 66 | 0.0084616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_155-22_0_5_line_73 |  | 65 | 69 | 0.00028542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_155-22_0_5_line_74 |  | 66 | 70 | 0.008721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_155-22_0_5_line_75 |  | 67 | 68 | 0.0068534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_155-22_0_5_line_76 |  | 68 | 71 | 0.069527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_155-22_0_5_line_77 |  | 69 | 80 | 0.017245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_155-22_0_5_line_78 |  | 70 | 72 | 0.02321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_155-22_0_5_line_79 |  | 71 | 94 | 0.059495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_155-22_0_5_line_80 |  | 72 | 73 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_155-22_0_5_line_81 |  | 73 | 74 | 0.0092273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_155-22_0_5_line_82 |  | 73 | 75 | 0.017723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_155-22_0_5_line_83 |  | 74 | 76 | 0.012486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_155-22_0_5_line_84 |  | 75 | 77 | 0.010207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_155-22_0_5_line_85 |  | 76 | 78 | 0.0081765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_155-22_0_5_line_86 |  | 77 | 79 | 0.023858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_155-22_0_5_line_87 |  | 78 | 82 | 0.031806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_155-22_0_5_line_88 |  | 82 | 83 | 0.0098372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_155-22_0_5_line_89 |  | 83 | 84 | 0.030551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_155-22_0_5_line_90 |  | 84 | 87 | 0.014041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_155-22_0_5_line_91 |  | 85 | 86 | 0.020299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_155-22_0_5_line_92 |  | 86 | 88 | 0.010089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_155-22_0_5_line_93 |  | 87 | 89 | 0.025787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_155-22_0_5_line_94 |  | 87 | 90 | 0.009025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_155-22_0_5_line_95 |  | 88 | 95 | 0.05045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_155-22_0_5_line_96 |  | 88 | 96 | 0.019621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_155-22_0_5_line_97 |  | 90 | 91 | 0.021964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_155-22_0_5_line_98 |  | 90 | 92 | 0.015657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_155-22_0_5_line_99 |  | 91 | 93 | 0.025895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_155-22_0_5_line_100 |  | 92 | 94 | 0.025913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_155-22_0_5_line_101 |  | 93 | 102 | 0.00084289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_155-22_0_5_line_102 |  | 95 | 100 | 0.009399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_155-22_0_5_line_103 |  | 95 | 97 | 0.011213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_155-22_0_5_line_104 |  | 96 | 102 | 0.037327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_155-22_0_5_line_105 |  | 97 | 98 | 0.002923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_155-22_0_5_line_106 |  | 97 | 99 | 0.087309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_155-22_0_5_line_107 |  | 99 | 101 | 0.0065795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_155-22_0_5_line_108 |  | 101 | 103 | 0.014696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_155-22_0_5_line_109 |  | 103 | 131 | 0.059895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_155-22_0_5_line_110 |  | 105 | 106 | 0.0061063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_155-22_0_5_line_111 |  | 105 | 107 | 0.0094365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_155-22_0_5_line_112 |  | 108 | 109 | 0.0071628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_155-22_0_5_line_113 |  | 110 | 111 | 0.028219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_155-22_0_5_line_114 |  | 110 | 112 | 0.04898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_155-22_0_5_line_115 |  | 111 | 113 | 0.0274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_155-22_0_5_line_116 |  | 113 | 114 | 0.011171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_155-22_0_5_line_117 |  | 113 | 115 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_155-22_0_5_line_118 |  | 114 | 116 | 0.1324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_155-22_0_5_line_119 |  | 115 | 117 | 0.0034613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_155-22_0_5_line_120 |  | 116 | 118 | 0.025195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_155-22_0_5_line_121 |  | 116 | 119 | 0.25998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_155-22_0_5_line_122 |  | 117 | 120 | 0.053498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_155-22_0_5_line_123 |  | 118 | 121 | 0.046374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_155-22_0_5_line_124 |  | 118 | 122 | 0.13459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_155-22_0_5_line_125 |  | 119 | 123 | 0.038163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_155-22_0_5_line_126 |  | 122 | 124 | 0.0081752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_155-22_0_5_line_127 |  | 122 | 125 | 0.010457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_155-22_0_5_line_128 |  | 124 | 130 | 0.019379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_155-22_0_5_line_129 |  | 125 | 129 | 0.029006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_155-22_0_5_line_130 |  | 128 | 129 | 0.0066568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_155-22_0_5_line_131 |  | 131 | 132 | 0.16464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_155-22_0_5_line_132 |  | 132 | 136 | 0.017106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_155-22_0_5_line_133 |  | 133 | 134 | 0.003585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_155-22_0_5_line_134 |  | 133 | 135 | 0.010009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_155-22_0_5_line_135 |  | 135 | 136 | 0.044703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_155-22_0_5_trafo_86 | 0.63 MVA 20/0.4 kV | 137 | 107 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2695279.9675 | 1235098.4634 | 2695277.495 | 1235098.3163 | 2695268.7914 | 1235099.6332 | 2695264.2921 | 1235101.1715
1 | 2695295.0286 | 1235102.9119 | 2695285.171 | 1235098.773 | 2695279.9675 | 1235098.4634
2 | 2695238.8303 | 1235111.9679 | 2695259.2541 | 1235102.8938 | 2695264.2921 | 1235101.1715
3 | 2695295.0286 | 1235102.9119 | 2695291.8619 | 1235108.9043
4 | 2695238.8303 | 1235111.9679 | 2695216.3305 | 1235121.9644 | 2695209.1921 | 1235125.1782
5 | 2695285.4931 | 1235120.9562 | 2695291.8619 | 1235108.9043
6 | 2695278.8348 | 1235143.8407 | 2695280.1486 | 1235133.4401 | 2695283.8882 | 1235123.9932 | 2695285.4931 | 1235120.9562
7 | 2695325.7127 | 1235062.5967 | 2695325.5857 | 1235069.0883 | 2695332.0934 | 1235069.2372 | 2695332.8122 | 1235071.6172 | 2695337.7412 | 1235088.0528 | 2695340.2336 | 1235090.7614 | 2695346.8434 | 1235093.5028
8 | 2695325.7127 | 1235062.5967 | 2695325.9283 | 1235056.7069 | 2695326.9956 | 1235053.4105 | 2695332.702 | 1235046.4191 | 2695336.0028 | 1235039.3224 | 2695339.0215 | 1235024.7038
9 | 2695347.6814 | 1235081.3851 | 2695346.6812 | 1235086.1615 | 2695346.8434 | 1235093.5028
10 | 2695346.8434 | 1235093.5028 | 2695349.3521 | 1235098.0241 | 2695356.355 | 1235100.3271
11 | 2695356.355 | 1235100.3271 | 2695383.7439 | 1235082.8934
12 | 2695356.355 | 1235100.3271 | 2695355.4503 | 1235105.2829 | 2695359.4531 | 1235112.5822
13 | 2695279.8886 | 1235156.6095 | 2695278.7959 | 1235144.1485 | 2695278.8348 | 1235143.8407
14 | 2695433.9747 | 1235056.1073 | 2695414.6639 | 1235065.0299
15 | 2695433.9747 | 1235056.1073 | 2695444.4378 | 1235083.7957 | 2695447.5678 | 1235091.7977
16 | 2695397.5548 | 1235074.1024 | 2695403.8578 | 1235070.0228 | 2695414.6639 | 1235065.0299
17 | 2695450.2328 | 1235098.6108 | 2695447.5678 | 1235091.7977
18 | 2695397.5548 | 1235074.1024 | 2695383.7439 | 1235082.8934
19 | 2695366.8303 | 1235125.3914 | 2695364.2903 | 1235121.4032 | 2695359.4531 | 1235112.5822
20 | 2695383.676 | 1235118.7675 | 2695401.1372 | 1235108.9412
21 | 2695366.8303 | 1235125.3914 | 2695371.7645 | 1235125.4706 | 2695383.676 | 1235118.7675
22 | 2695366.8303 | 1235125.3914 | 2695363.0321 | 1235130.9345 | 2695354.9156 | 1235136.2566
23 | 2695338.1927 | 1235147.222 | 2695354.9156 | 1235136.2566
24 | 2695450.2328 | 1235098.6108 | 2695468.6236 | 1235145.9299
25 | 2695468.6236 | 1235145.9299 | 2695469.737 | 1235148.7165
26 | 2695468.6236 | 1235145.9299 | 2695457.0985 | 1235152.772 | 2695451.7741 | 1235156.2724
27 | 2695469.737 | 1235148.7165 | 2695482.033 | 1235174.4329 | 2695495.8807 | 1235192.6244
28 | 2695469.737 | 1235148.7165 | 2695453.8419 | 1235158.2849
29 | 2695423.6411 | 1235173.4289 | 2695443.8247 | 1235161.4985 | 2695451.7741 | 1235156.2724
30 | 2695495.8807 | 1235192.6244 | 2695482.2185 | 1235200.4301
31 | 2695495.8807 | 1235192.6244 | 2695507.2701 | 1235203.7737
32 | 2695445.881 | 1235163.0771 | 2695453.8419 | 1235158.2849
33 | 2695393.8063 | 1235190.0504 | 2695411.8494 | 1235180.3989 | 2695423.6411 | 1235173.4289
34 | 2695367.8319 | 1235207.5614 | 2695384.1409 | 1235195.2205 | 2695393.8063 | 1235190.0504
35 | 2695342.9726 | 1235233.6881 | 2695341.9149 | 1235230.2575 | 2695342.3968 | 1235228.0636 | 2695350.1106 | 1235220.9711 | 2695367.8319 | 1235207.5614
36 | 2695342.9726 | 1235233.6881 | 2695336.4852 | 1235242.1902 | 2695334.7384 | 1235243.3517
37 | 2695334.7384 | 1235243.3517 | 2695332.4682 | 1235244.8611 | 2695329.33 | 1235245.6113 | 2695321.8648 | 1235242.8784 | 2695317.4834 | 1235242.3188 | 2695312.3051 | 1235241.891 | 2695306.2587 | 1235240.7934
38 | 2695386.9384 | 1235197.3114 | 2695399.5958 | 1235223.1614
39 | 2695386.9384 | 1235197.3114 | 2695408.8129 | 1235186.588 | 2695422.0896 | 1235178.1671
40 | 2695402.271 | 1235228.625 | 2695399.5958 | 1235223.1614
41 | 2695445.881 | 1235163.0771 | 2695422.0896 | 1235178.1671
42 | 2695306.2587 | 1235240.7934 | 2695305.4382 | 1235240.6445
43 | 2695402.271 | 1235228.625 | 2695408.5382 | 1235241.0513
44 | 2695402.271 | 1235228.625 | 2695389.8864 | 1235236.5503
45 | 2695445.881 | 1235163.0771 | 2695445.2593 | 1235167.8484 | 2695445.4823 | 1235178.9379 | 2695445.7604 | 1235184.7133 | 2695448.2161 | 1235188.7557
46 | 2695305.4382 | 1235240.6445 | 2695305.3839 | 1235240.6346 | 2695299.0383 | 1235238.4201 | 2695298.1733 | 1235237.984
47 | 2695474.6801 | 1235204.737 | 2695482.2185 | 1235200.4301
48 | 2695525.7528 | 1235219.1491 | 2695510.8822 | 1235207.3096 | 2695507.2701 | 1235203.7737
49 | 2695279.8886 | 1235156.6095 | 2695281.7906 | 1235178.2997
50 | 2695281.7906 | 1235178.2997 | 2695281.8643 | 1235179.14
51 | 2695281.8643 | 1235179.14 | 2695281.8918 | 1235179.4531
52 | 2695282.4232 | 1235185.5132 | 2695281.8918 | 1235179.4531
53 | 2695282.4232 | 1235185.5132 | 2695282.8783 | 1235190.7037 | 2695283.0912 | 1235194.2835
54 | 2695283.0912 | 1235194.2835 | 2695283.9548 | 1235208.8115
55 | 2695284.3274 | 1235215.0783 | 2695283.9548 | 1235208.8115
56 | 2695161.4318 | 1235237.3919 | 2695162.7796 | 1235243.0399 | 2695162.6174 | 1235253.1558 | 2695164.7234 | 1235261.0842 | 2695168.7052 | 1235265.7959 | 2695178.4266 | 1235266.6078 | 2695184.3304 | 1235265.6905 | 2695187.6192 | 1235263.108 | 2695188.0014 | 1235262.7918
57 | 2695161.4318 | 1235237.3919 | 2695169.4104 | 1235236.9082 | 2695178.3305 | 1235234.8273 | 2695182.0181 | 1235232.8627 | 2695182.4678 | 1235229.8344 | 2695182.5717 | 1235223.3535 | 2695182.9661 | 1235211.5547
58 | 2695188.0014 | 1235262.7918 | 2695191.7463 | 1235259.6938 | 2695194.8161 | 1235257.5525 | 2695199.9799 | 1235252.7428 | 2695205.1021 | 1235249.5893 | 2695206.4849 | 1235249.2849
59 | 2695188.8308 | 1235200.7483 | 2695183.7086 | 1235203.9019 | 2695182.9789 | 1235211.1733 | 2695182.9661 | 1235211.5547
60 | 2695188.8308 | 1235200.7483 | 2695198.2163 | 1235197.4962 | 2695207.5971 | 1235195.0114 | 2695214.0479 | 1235193.7474
61 | 2695206.4849 | 1235249.2849 | 2695209.3865 | 1235248.6461 | 2695216.3336 | 1235245.9221 | 2695220.2065 | 1235244.2051 | 2695223.9234 | 1235240.4174 | 2695228.8479 | 1235236.8493 | 2695231.9727 | 1235236.1538
62 | 2695263.9816 | 1235232.8762 | 2695269.5539 | 1235232.7949
63 | 2695263.9816 | 1235232.8762 | 2695260.4178 | 1235230.8954 | 2695251.9217 | 1235228.7242
64 | 2695283.9473 | 1235232.585 | 2695269.5539 | 1235232.7949
65 | 2695251.9217 | 1235228.7242 | 2695248.0503 | 1235229.8741 | 2695241.3027 | 1235233.3686 | 2695235.7913 | 1235235.3039 | 2695231.9727 | 1235236.1538
66 | 2695193.5302 | 1235323.1245 | 2695184.4954 | 1235313.9508 | 2695181.6756 | 1235309.9586
67 | 2695218.6558 | 1235312.586 | 2695216.6313 | 1235313.7433 | 2695201.7759 | 1235322.0225 | 2695193.5302 | 1235323.1245
68 | 2695283.9473 | 1235232.585 | 2695282.0192 | 1235243.3528
69 | 2695283.9473 | 1235232.585 | 2695284.9408 | 1235225.3956 | 2695284.3274 | 1235215.0783
70 | 2695283.9473 | 1235232.585 | 2695290.1553 | 1235233.9411 | 2695298.1733 | 1235237.984
71 | 2695218.6558 | 1235312.586 | 2695226.142 | 1235327.6949 | 2695227.2234 | 1235332.3591
72 | 2695218.6558 | 1235312.586 | 2695225.7651 | 1235307.9972
73 | 2695227.2878 | 1235332.6371 | 2695227.2234 | 1235332.3591
74 | 2695225.7651 | 1235307.9972 | 2695233.0923 | 1235303.2677
75 | 2695220.043 | 1235439.1822 | 2695218.1861 | 1235432.5851
76 | 2695220.4951 | 1235508.0035 | 2695218.0657 | 1235501.8489 | 2695217.7348 | 1235492.7481 | 2695221.3741 | 1235456.0238 | 2695220.1113 | 1235439.4247 | 2695220.043 | 1235439.1822
77 | 2695231.1828 | 1235349.4361 | 2695227.2878 | 1235332.6371
78 | 2695252.5931 | 1235290.6805 | 2695233.0923 | 1235303.2677
79 | 2695220.4951 | 1235508.0035 | 2695226.8812 | 1235489.2699 | 2695236.1361 | 1235453.0805 | 2695236.8582 | 1235450.8452
80 | 2695267.7118 | 1235290.5339 | 2695265.3776 | 1235289.2955 | 2695262.7019 | 1235288.5743 | 2695258.9653 | 1235288.4032 | 2695255.4932 | 1235289.2037 | 2695252.5931 | 1235290.6805 | 2695252.5931 | 1235290.6805
81 | 2695267.7118 | 1235290.5339 | 2695269.7351 | 1235292.7568 | 2695271.4656 | 1235295.2976 | 2695272.3634 | 1235298.3142
82 | 2695267.7118 | 1235290.5339 | 2695279.0276 | 1235276.8942
83 | 2695272.2162 | 1235310.7876 | 2695272.565 | 1235301.7866 | 2695272.3634 | 1235298.3142
84 | 2695281.5559 | 1235267.1333 | 2695281.2415 | 1235271.4813 | 2695279.0276 | 1235276.8942
85 | 2695272.2162 | 1235310.7876 | 2695271.6066 | 1235318.9414
86 | 2695282.0192 | 1235243.3528 | 2695281.6026 | 1235245.6792 | 2695281.0229 | 1235255.3882 | 2695281.6599 | 1235265.6948 | 2695281.5559 | 1235267.1333
87 | 2695271.6066 | 1235318.9414 | 2695270.7416 | 1235330.5118 | 2695268.1821 | 1235346.616 | 2695267.3466 | 1235350.4221
88 | 2695267.3466 | 1235350.4221 | 2695265.2373 | 1235360.0305
89 | 2695257.0408 | 1235389.4426 | 2695260.0409 | 1235380.3658 | 2695264.5481 | 1235363.1699 | 2695265.2373 | 1235360.0305
90 | 2695252.6343 | 1235402.7746 | 2695257.0408 | 1235389.4426
91 | 2695318.7347 | 1235330.8262 | 2695323.5631 | 1235339.8436 | 2695327.9855 | 1235348.8904
92 | 2695332.4162 | 1235357.9545 | 2695327.9855 | 1235348.8904
93 | 2695227.5825 | 1235404.4855 | 2695245.382 | 1235400.4678 | 2695252.6343 | 1235402.7746
94 | 2695249.6365 | 1235411.2884 | 2695252.6343 | 1235402.7746
95 | 2695332.4162 | 1235357.9545 | 2695341.7468 | 1235364.2421 | 2695345.4097 | 1235362.3995 | 2695349.0405 | 1235367.2725 | 2695347.098 | 1235392.0818 | 2695343.5147 | 1235394.148
96 | 2695332.4162 | 1235357.9545 | 2695315.6032 | 1235368.0687
97 | 2695249.6365 | 1235411.2884 | 2695259.8929 | 1235414.5997 | 2695265.4197 | 1235414.9997 | 2695270.5516 | 1235412.6469
98 | 2695249.6365 | 1235411.2884 | 2695244.8236 | 1235426.1874
99 | 2695287.0551 | 1235392.8435 | 2695276.1574 | 1235407.6553 | 2695270.5516 | 1235412.6469 | 2695270.5516 | 1235412.6469
100 | 2695236.8582 | 1235450.8452 | 2695244.8236 | 1235426.1874
101 | 2695287.5546 | 1235392.1646 | 2695287.0551 | 1235392.8435
102 | 2695343.5147 | 1235394.148 | 2695334.7251 | 1235397.5428
103 | 2695343.1905 | 1235403.0271 | 2695345.9535 | 1235402.0708 | 2695343.5147 | 1235394.148
104 | 2695315.6032 | 1235368.0687 | 2695311.2444 | 1235370.6909 | 2695295.7684 | 1235382.2623 | 2695292.9105 | 1235384.885 | 2695287.5546 | 1235392.1646
105 | 2695340.4199 | 1235403.9834 | 2695343.1905 | 1235403.0271
106 | 2695326.2667 | 1235459.5193 | 2695334.0797 | 1235459.9005 | 2695341.0294 | 1235456.0648 | 2695342.7853 | 1235450.8891 | 2695346.9184 | 1235443.8058 | 2695343.7482 | 1235439.474 | 2695341.2873 | 1235432.9297 | 2695342.7891 | 1235427.0828 | 2695351.5288 | 1235424.9103 | 2695349.4069 | 1235419.4056 | 2695352.3067 | 1235418.418 | 2695346.9508 | 1235401.7198 | 2695345.9535 | 1235402.0708 | 2695343.1905 | 1235403.0271
107 | 2695326.2667 | 1235459.5193 | 2695325.8207 | 1235466.0837
108 | 2695327.6369 | 1235480.6672 | 2695325.8207 | 1235466.0837 | 2695325.8207 | 1235466.0837
109 | 2695332.7613 | 1235540.1272 | 2695333.7862 | 1235529.5693 | 2695332.3379 | 1235518.4156 | 2695327.6369 | 1235480.6672
110 | 2695384.7431 | 1235239.8416 | 2695389.8864 | 1235236.5503
111 | 2695376.7947 | 1235244.928 | 2695384.7431 | 1235239.8416
112 | 2695411.7637 | 1235247.4468 | 2695408.5382 | 1235241.0513
113 | 2695521.5104 | 1235307.2741 | 2695546.5489 | 1235294.2591
114 | 2695476.4723 | 1235320.184 | 2695486.3478 | 1235323.1782 | 2695502.8736 | 1235316.9615 | 2695521.5104 | 1235307.2741
115 | 2695570.3637 | 1235280.731 | 2695555.4523 | 1235289.6311 | 2695546.5489 | 1235294.2591
116 | 2695570.3637 | 1235280.731 | 2695577.5189 | 1235282.9589 | 2695581.1913 | 1235283.1428
117 | 2695570.3637 | 1235280.731 | 2695567.0588 | 1235277.7201 | 2695561.1861 | 1235262.0597
118 | 2695677.7648 | 1235359.395 | 2695675.0827 | 1235355.7936 | 2695638.237 | 1235304.8852 | 2695628.2363 | 1235292.7487 | 2695622.6434 | 1235288.4555 | 2695616.2989 | 1235285.24 | 2695605.655 | 1235284.3681 | 2695581.1913 | 1235283.1428
119 | 2695561.1861 | 1235262.0597 | 2695559.9707 | 1235258.8188
120 | 2695655.2582 | 1235370.3629 | 2695660.9613 | 1235365.9293 | 2695677.7648 | 1235359.395
121 | 2695677.7648 | 1235359.395 | 2695896.812 | 1235499.4181
122 | 2695525.7528 | 1235219.1491 | 2695539.1336 | 1235229.8025 | 2695547.215 | 1235236.5707 | 2695552.7443 | 1235243.4091 | 2695556.0204 | 1235249.1549 | 2695558.0225 | 1235253.6237 | 2695559.9707 | 1235258.8188
123 | 2695655.2582 | 1235370.3629 | 2695650.9798 | 1235368.1146 | 2695642.0136 | 1235367.8924 | 2695636.4319 | 1235368.0805 | 2695629.3045 | 1235365.5417 | 2695617.2957 | 1235361.0673 | 2695610.7751 | 1235359.3945
124 | 2695554.2691 | 1235389.4966 | 2695558.4916 | 1235389.0976 | 2695565.2105 | 1235389.2724 | 2695582.5326 | 1235388.128 | 2695590.9576 | 1235388.5861 | 2695597.4455 | 1235389.9359 | 2695602.9958 | 1235392.1712 | 2695609.7121 | 1235395.7931 | 2695632.4397 | 1235410.5697 | 2695637.8775 | 1235410.8574 | 2695647.3893 | 1235398.8239 | 2695650.3143 | 1235392.5108 | 2695652.3837 | 1235380.1127 | 2695655.2582 | 1235370.3629
125 | 2695896.812 | 1235499.4181 | 2695914.793 | 1235486.054 | 2695927.4251 | 1235476.6303
126 | 2695554.2691 | 1235389.4966 | 2695552.6644 | 1235394.1965 | 2695551.7395 | 1235395.6938 | 2695550.8058 | 1235396.8019
127 | 2695554.2691 | 1235389.4966 | 2695552.7354 | 1235389.7833 | 2695544.1214 | 1235392.0098
128 | 2695534.2144 | 1235404.7521 | 2695536.4191 | 1235401.8076 | 2695537.4193 | 1235400.8007 | 2695538.9728 | 1235399.7471 | 2695540.836 | 1235399.21 | 2695544.2798 | 1235398.7539 | 2695547.8196 | 1235398.4551 | 2695549.3508 | 1235397.8459 | 2695550.8058 | 1235396.8019
129 | 2695544.1214 | 1235392.0098 | 2695537.6702 | 1235393.6772 | 2695516.0235 | 1235399.2111 | 2695516.0235 | 1235399.2111
130 | 2695509.4478 | 1235400.2476 | 2695516.0235 | 1235399.2111
131 | 2695332.7613 | 1235540.1272 | 2695356.7362 | 1235547.4729 | 2695391.7599 | 1235552.1274 | 2695424.2559 | 1235553.4501 | 2695447.6999 | 1235557.5519 | 2695461.3591 | 1235562.9309 | 2695460.2878 | 1235572.5985 | 2695458.3698 | 1235579.8508 | 2695456.9677 | 1235585.1433 | 2695455.8226 | 1235591.3962 | 2695457.0605 | 1235595.3746
132 | 2695457.0605 | 1235595.3746 | 2695473.5994 | 1235599.7438
133 | 2695505.1776 | 1235568.0832 | 2695501.5823 | 1235568.081
134 | 2695501.5823 | 1235568.081 | 2695498.7537 | 1235577.6819
135 | 2695498.7537 | 1235577.6819 | 2695491.5825 | 1235602.023 | 2695489.5983 | 1235603.9704 | 2695473.5994 | 1235599.7438

## bus_geodata
| x | y | coords
0 | 2695279.9675 | 1235098.4634
1 | 2695264.2921 | 1235101.1715
2 | 2695295.0286 | 1235102.9119
3 | 2695238.8303 | 1235111.968
4 | 2695291.8619 | 1235108.9043
5 | 2695209.1921 | 1235125.1782
6 | 2695285.4931 | 1235120.9562
7 | 2695325.7127 | 1235062.5967
8 | 2695346.8434 | 1235093.5028
9 | 2695339.0215 | 1235024.7038
10 | 2695347.6814 | 1235081.3851
11 | 2695356.355 | 1235100.3271
12 | 2695278.8348 | 1235143.8407
13 | 2695433.9747 | 1235056.1073
14 | 2695414.6639 | 1235065.0299
15 | 2695447.5678 | 1235091.7977
16 | 2695383.7439 | 1235082.8934
17 | 2695359.4531 | 1235112.5822
18 | 2695383.676 | 1235118.7675
19 | 2695401.1372 | 1235108.9412
20 | 2695366.8303 | 1235125.3914
21 | 2695354.9156 | 1235136.2566
22 | 2695397.5548 | 1235074.1024
23 | 2695338.1927 | 1235147.222
24 | 2695450.2328 | 1235098.6108
25 | 2695468.6236 | 1235145.9299
26 | 2695469.737 | 1235148.7165
27 | 2695451.7741 | 1235156.2724
28 | 2695495.8807 | 1235192.6244
29 | 2695453.8419 | 1235158.2849
30 | 2695423.6411 | 1235173.4289
31 | 2695367.8319 | 1235207.5614
32 | 2695393.8063 | 1235190.0504
33 | 2695342.9726 | 1235233.6881
34 | 2695334.7383 | 1235243.3517
35 | 2695386.9384 | 1235197.3114
36 | 2695399.5958 | 1235223.1614
37 | 2695422.0896 | 1235178.1671
38 | 2695306.2587 | 1235240.7935
39 | 2695402.271 | 1235228.625
40 | 2695445.881 | 1235163.0771
41 | 2695305.4382 | 1235240.6445
42 | 2695482.2185 | 1235200.4301
43 | 2695507.2701 | 1235203.7737
44 | 2695279.8886 | 1235156.6095
45 | 2695281.7906 | 1235178.2997
46 | 2695281.8643 | 1235179.14
47 | 2695281.8918 | 1235179.4531
48 | 2695282.4232 | 1235185.5132
49 | 2695283.0912 | 1235194.2835
50 | 2695283.9548 | 1235208.8115
51 | 2695161.4318 | 1235237.3919
52 | 2695188.0014 | 1235262.7918
53 | 2695182.9661 | 1235211.5547
54 | 2695188.8308 | 1235200.7483
55 | 2695214.0479 | 1235193.7474
56 | 2695206.4849 | 1235249.2849
57 | 2695263.9816 | 1235232.8762
58 | 2695269.5539 | 1235232.7949
59 | 2695251.9217 | 1235228.7242
60 | 2695181.6756 | 1235309.9586
61 | 2695193.5302 | 1235323.1245
62 | 2695231.9727 | 1235236.1538
63 | 2695283.9473 | 1235232.585
64 | 2695218.6558 | 1235312.586
65 | 2695227.2234 | 1235332.3591
66 | 2695225.7651 | 1235307.9972
67 | 2695218.1861 | 1235432.5851
68 | 2695220.043 | 1235439.1822
69 | 2695227.2878 | 1235332.6371
70 | 2695233.0923 | 1235303.2677
71 | 2695220.4951 | 1235508.0035
72 | 2695252.5931 | 1235290.6805
73 | 2695267.7118 | 1235290.5339
74 | 2695272.3634 | 1235298.3142
75 | 2695279.0276 | 1235276.8942
76 | 2695272.2162 | 1235310.7876
77 | 2695281.5559 | 1235267.1333
78 | 2695271.6066 | 1235318.9414
79 | 2695282.0192 | 1235243.3528
80 | 2695231.1828 | 1235349.4361
81 | 2695284.3274 | 1235215.0783
82 | 2695267.3466 | 1235350.4221
83 | 2695265.2373 | 1235360.0305
84 | 2695257.0408 | 1235389.4426
85 | 2695318.7347 | 1235330.8262
86 | 2695327.9855 | 1235348.8904
87 | 2695252.6343 | 1235402.7746
88 | 2695332.4162 | 1235357.9545
89 | 2695227.5825 | 1235404.4855
90 | 2695249.6365 | 1235411.2884
91 | 2695270.5516 | 1235412.6469
92 | 2695244.8236 | 1235426.1874
93 | 2695287.0551 | 1235392.8435
94 | 2695236.8582 | 1235450.8452
95 | 2695343.5147 | 1235394.148
96 | 2695315.6032 | 1235368.0687
97 | 2695343.1905 | 1235403.0271
98 | 2695340.4199 | 1235403.9834
99 | 2695326.2667 | 1235459.5193
100 | 2695334.7251 | 1235397.5428
101 | 2695325.8207 | 1235466.0837
102 | 2695287.5546 | 1235392.1646
103 | 2695327.6369 | 1235480.6672
104 | 2695298.1733 | 1235237.984
105 | 2695384.7431 | 1235239.8416
106 | 2695389.8864 | 1235236.5503
107 | 2695376.7947 | 1235244.928
108 | 2695408.5382 | 1235241.0513
109 | 2695411.7637 | 1235247.4468
110 | 2695521.5104 | 1235307.2741
111 | 2695546.5489 | 1235294.2591
112 | 2695476.4723 | 1235320.184
113 | 2695570.3637 | 1235280.731
114 | 2695581.1913 | 1235283.1428
115 | 2695561.1861 | 1235262.0597
116 | 2695677.7648 | 1235359.395
117 | 2695559.9707 | 1235258.8188
118 | 2695655.2582 | 1235370.363
119 | 2695896.812 | 1235499.4181
120 | 2695525.7528 | 1235219.1491
121 | 2695610.7751 | 1235359.3945
122 | 2695554.2691 | 1235389.4966
123 | 2695927.4251 | 1235476.6303
124 | 2695550.8058 | 1235396.8019
125 | 2695544.1214 | 1235392.0098
126 | 2695474.6801 | 1235204.737
127 | 2695448.2161 | 1235188.7557
128 | 2695509.4478 | 1235400.2476
129 | 2695516.0235 | 1235399.2111
130 | 2695534.2144 | 1235404.7521
131 | 2695332.7613 | 1235540.1272
132 | 2695457.0605 | 1235595.3746
133 | 2695501.5823 | 1235568.081
134 | 2695505.1776 | 1235568.0832
135 | 2695498.7537 | 1235577.6819
136 | 2695473.5994 | 1235599.7438
137 | 2695402.271 | 1235228.625

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97466 | -0.48766 | 0.009187 | 0.0023025
1 | 0.97449 | -0.49086 | 0.0029534 | 0.00074019
2 | 0.97495 | -0.48181 | 0 | 0
3 | 0.97429 | -0.49488 | 0.0032567 | 0.0008162
4 | 0.97508 | -0.47932 | 0.0026829 | 0.0006724
5 | 0.97415 | -0.49765 | 0.0046517 | 0.0011658
6 | 0.97537 | -0.47364 | 0.0028322 | 0.00070983
7 | 0.97995 | -0.38451 | 0 | 0
8 | 0.98006 | -0.38225 | 0 | 0
9 | 0.97984 | -0.38665 | 0.0028641 | 0.00071781
10 | 0.98003 | -0.38297 | 0.0032567 | 0.00081622
11 | 0.98013 | -0.38085 | 0 | 0
12 | 0.97594 | -0.46237 | 0.0017857 | 0.00044753
13 | 0.98368 | -0.31164 | 0 | 0
14 | 0.98273 | -0.33014 | 0.0055253 | 0.0013848
15 | 0.98538 | -0.27851 | 0.0049536 | 0.0012415
16 | 0.98131 | -0.35776 | 0.0034723 | 0.00087023
17 | 0.97972 | -0.38888 | 0.0058892 | 0.001476
18 | 0.97912 | -0.40064 | 0.0069321 | 0.0017374
19 | 0.97901 | -0.40291 | 0.0062162 | 0.0015579
20 | 0.97935 | -0.3962 | 0 | 0
21 | 0.97914 | -0.4004 | 0.0071459 | 0.0017909
22 | 0.98196 | -0.34512 | 0 | 0
23 | 0.97901 | -0.40292 | 0.0069291 | 0.0017366
24 | 0.98574 | -0.27153 | 0 | 0
25 | 0.98824 | -0.22322 | 0 | 0
26 | 0.98841 | -0.22005 | 0 | 0
27 | 0.98735 | -0.2404 | 0.0055779 | 0.001398
28 | 0.98761 | -0.23521 | 0 | 0
29 | 0.98971 | -0.19498 | 0.0015378 | 0.00038542
30 | 0.98589 | -0.26844 | 0.0055922 | 0.0014015
31 | 0.9831 | -0.32239 | 0.0072831 | 0.0018253
32 | 0.98442 | -0.2969 | 0.0067046 | 0.0016803
33 | 0.98154 | -0.35274 | 0 | 0
34 | 0.98102 | -0.36283 | 0.000618 | 0.00015489
35 | 0.99527 | -0.089092 | 0 | 0
36 | 0.99735 | -0.049857 | 0.0010443 | 0.00026172
37 | 0.99238 | -0.14401 | 0.0038928 | 0.00097562
38 | 0.97982 | -0.38621 | 0.00044128 | 0.0001106
39 | 0.99779 | -0.041563 | 0 | 0
40 | 0.99037 | -0.1824 | 0 | 0
41 | 0.97979 | -0.38687 | 0.0012503 | 0.00031335
42 | 0.98752 | -0.23706 | 0.0027131 | 0.00067998
43 | 0.98739 | -0.23955 | 0.0017444 | 0.00043719
44 | 0.97627 | -0.45595 | 0.0020926 | 0.00052444
45 | 0.97686 | -0.44423 | 0.0016606 | 0.00041618
46 | 0.97689 | -0.44376 | 0.0013883 | 0.00034794
47 | 0.9769 | -0.44357 | 0.0019984 | 0.00050085
48 | 0.97709 | -0.43974 | 0.0019475 | 0.0004881
49 | 0.97739 | -0.43389 | 0.002143 | 0.00053709
50 | 0.97791 | -0.42365 | 0.0031699 | 0.00079445
51 | 0.97284 | -0.52326 | 0 | 0
52 | 0.97422 | -0.49603 | 0.009534 | 0.0023894
53 | 0.97168 | -0.54623 | 0.018285 | 0.0045826
54 | 0.97154 | -0.54899 | 0 | 0
55 | 0.97127 | -0.55427 | 0.010908 | 0.0027339
56 | 0.97505 | -0.47962 | 0.0060339 | 0.0015122
57 | 0.9779 | -0.42382 | 0 | 0
58 | 0.97816 | -0.41865 | 0.0015334 | 0.0003843
59 | 0.97729 | -0.43573 | 0 | 0
60 | 0.97533 | -0.47435 | 0.013115 | 0.0032869
61 | 0.97555 | -0.47008 | 0 | 0
62 | 0.97628 | -0.45564 | 0.0061892 | 0.0015512
63 | 0.97887 | -0.40489 | 0 | 0
64 | 0.97589 | -0.46345 | 0 | 0
65 | 0.97566 | -0.46794 | 0.003106 | 0.00077843
66 | 0.97608 | -0.45967 | 0.0034749 | 0.00087088
67 | 0.97552 | -0.47073 | 0.0012627 | 0.00031646
68 | 0.97553 | -0.47057 | 0.0016815 | 0.00042142
69 | 0.97566 | -0.46798 | 0.0028376 | 0.00071117
70 | 0.97631 | -0.45522 | 0.0034304 | 0.00085973
71 | 0.97572 | -0.46682 | 0 | 0
72 | 0.97698 | -0.44192 | 0.0062223 | 0.0015595
73 | 0.97754 | -0.43097 | 0 | 0
74 | 0.97742 | -0.43341 | 0.0051415 | 0.0012886
75 | 0.9779 | -0.42386 | 0.00043584 | 0.00010923
76 | 0.97726 | -0.43648 | 0 | 0
77 | 0.97811 | -0.41976 | 0.0063957 | 0.0016029
78 | 0.97716 | -0.43849 | 0.0074701 | 0.0018722
79 | 0.97863 | -0.4096 | 0.0014749 | 0.00036965
80 | 0.97557 | -0.46968 | 0.0053754 | 0.0013472
81 | 0.97815 | -0.41887 | 0.0018856 | 0.00047257
82 | 0.9768 | -0.44544 | 0.0031496 | 0.00078937
83 | 0.9767 | -0.44747 | 0.0025746 | 0.00064527
84 | 0.97639 | -0.45352 | 0.0047321 | 0.001186
85 | 0.97553 | -0.47053 | 0.0042155 | 0.0010565
86 | 0.97561 | -0.46897 | 0.0031053 | 0.00077825
87 | 0.97626 | -0.45605 | 0 | 0
88 | 0.97568 | -0.46761 | 0 | 0
89 | 0.97615 | -0.45822 | 0.004599 | 0.0011526
90 | 0.97619 | -0.45753 | 0 | 0
91 | 0.97605 | -0.46032 | 0.0082925 | 0.0020783
92 | 0.97604 | -0.46038 | 0.0031439 | 0.00078794
93 | 0.97592 | -0.46284 | 0.00050967 | 0.00012773
94 | 0.97588 | -0.46361 | 0.0038659 | 0.00096889
95 | 0.97556 | -0.47 | 0 | 0
96 | 0.97575 | -0.46616 | 0.0034827 | 0.00087283
97 | 0.97553 | -0.47045 | 0 | 0
98 | 0.97553 | -0.47049 | 0.00061917 | 0.00015518
99 | 0.97525 | -0.476 | 0 | 0
100 | 0.97554 | -0.47033 | 0.0018918 | 0.00047412
101 | 0.97519 | -0.47725 | 0.0011195 | 0.00028056
102 | 0.97592 | -0.46292 | 0.0022517 | 0.00056434
103 | 0.97506 | -0.47975 | 0.00030077 | 7.538e-05
104 | 0.97948 | -0.39294 | 0.0011982 | 0.0003003
105 | 0.99931 | -0.01298 | 0.00081653 | 0.00020464
106 | 0.99886 | -0.021371 | 0.0008795 | 0.00022042
107 | 1 | 0 | -0.40413 | -0.10405
108 | 0.99775 | -0.042391 | 0.00095156 | 0.00023848
109 | 0.99773 | -0.042698 | 0.0024471 | 0.00061331
110 | 0.98545 | -0.27686 | 0.00031206 | 7.821e-05
111 | 0.9855 | -0.27593 | 0.00068363 | 0.00017133
112 | 0.98538 | -0.27819 | 0.0015162 | 0.00038
113 | 0.98556 | -0.2747 | 0 | 0
114 | 0.98483 | -0.28865 | 0.00091224 | 0.00022863
115 | 0.98627 | -0.26099 | 0.00073036 | 0.00018305
116 | 0.97636 | -0.45345 | 0 | 0
117 | 0.98632 | -0.26009 | 0.0009529 | 0.00023882
118 | 0.97479 | -0.48411 | 0 | 0
119 | 0.97582 | -0.46396 | 0 | 0
120 | 0.98705 | -0.24596 | 0.00062814 | 0.00015743
121 | 0.97283 | -0.5228 | 0.045388 | 0.011375
122 | 0.97215 | -0.53624 | 0 | 0
123 | 0.97575 | -0.4655 | 0.0022037 | 0.00055231
124 | 0.97209 | -0.53739 | 0.0056334 | 0.0014119
125 | 0.97202 | -0.53884 | 0.0028543 | 0.00071535
126 | 0.98749 | -0.23765 | 0.0038462 | 0.00096395
127 | 0.99028 | -0.18411 | 0.0036241 | 0.00090829
128 | 0.97168 | -0.54565 | 0.0092845 | 0.0023269
129 | 0.97173 | -0.54451 | 0.00132 | 0.00033082
130 | 0.97206 | -0.53809 | 0.0019631 | 0.00049199
131 | 0.97456 | -0.4896 | 0 | 0
132 | 0.97319 | -0.51673 | 0 | 0
133 | 0.97276 | -0.5252 | 0 | 0
134 | 0.97274 | -0.52554 | 0.005053 | 0.0012664
135 | 0.97281 | -0.52427 | 0.00067397 | 0.00016891
136 | 0.97304 | -0.51956 | 0.0032356 | 0.00081092
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010866 | 0.0027237 | -0.010864 | -0.0027228 | 1.6547e-06 | 8.5919e-07 | 0.016589 | 0.016589 | 0.016589 | 0.97466 | -0.48766 | 0.97449 | -0.49086 | 4.5573
1 | -0.020053 | -0.0050262 | 0.020058 | 0.0050296 | 5.5897e-06 | 3.3792e-06 | 0.030615 | 0.030615 | 0.030615 | 0.97466 | -0.48766 | 0.97495 | -0.48181 | 8.4106
2 | 0.0079105 | 0.0019826 | -0.0079089 | -0.001982 | 1.5141e-06 | 6.2433e-07 | 0.012079 | 0.012079 | 0.012079 | 0.97449 | -0.49086 | 0.97429 | -0.49488 | 3.3184
3 | -0.020058 | -0.0050296 | 0.020061 | 0.005031 | 2.3821e-06 | 1.44e-06 | 0.030615 | 0.030615 | 0.030615 | 0.97495 | -0.48181 | 0.97508 | -0.47932 | 8.4106
4 | 0.0046523 | 0.0011658 | -0.0046517 | -0.0011658 | 6.1433e-07 | -1.0868e-08 | 0.0071053 | 0.0071054 | 0.0071054 | 0.97429 | -0.49488 | 0.97415 | -0.49765 | 1.952
5 | -0.022743 | -0.0057034 | 0.02275 | 0.0057072 | 6.158e-06 | 3.7711e-06 | 0.034709 | 0.034709 | 0.034709 | 0.97508 | -0.47932 | 0.97537 | -0.47364 | 9.5354
6 | -0.025582 | -0.006417 | 0.025596 | 0.0064255 | 1.3755e-05 | 8.5022e-06 | 0.03903 | 0.039029 | 0.03903 | 0.97537 | -0.47364 | 0.97594 | -0.46237 | 10.7224
7 | -0.0028644 | -0.00071748 | 0.0028647 | 0.00071713 | 3.0845e-07 | -3.5048e-07 | 0.0043493 | 0.0043491 | 0.0043493 | 0.97995 | -0.38451 | 0.98006 | -0.38225 | 1.1949
8 | 0.0028644 | 0.00071748 | -0.0028641 | -0.00071781 | 2.9183e-07 | -3.3143e-07 | 0.0043493 | 0.0043495 | 0.0043495 | 0.97995 | -0.38451 | 0.97984 | -0.38665 | 1.1949
9 | 0.0032569 | 0.00081613 | -0.0032567 | -0.00081622 | 1.1208e-07 | -8.2299e-08 | 0.0049448 | 0.0049449 | 0.0049449 | 0.98006 | -0.38225 | 0.98003 | -0.38297 | 1.3585
10 | -0.0061216 | -0.0015333 | 0.006122 | 0.0015334 | 4.0627e-07 | 1.0195e-07 | 0.0092939 | 0.0092939 | 0.0092939 | 0.98006 | -0.38225 | 0.98013 | -0.38085 | 2.5533
11 | -0.039264 | -0.0098496 | 0.039307 | 0.0098769 | 4.3266e-05 | 2.7281e-05 | 0.059613 | 0.059613 | 0.059613 | 0.98013 | -0.38085 | 0.98131 | -0.35776 | 16.3771
12 | 0.033142 | 0.0083162 | -0.033129 | -0.0083083 | 1.2688e-05 | 7.9518e-06 | 0.050319 | 0.050319 | 0.050319 | 0.98013 | -0.38085 | 0.97972 | -0.38888 | 13.8239
13 | -0.027381 | -0.006873 | 0.02739 | 0.0068782 | 8.38e-06 | 5.203e-06 | 0.041752 | 0.041752 | 0.041752 | 0.97594 | -0.46237 | 0.97627 | -0.45595 | 11.4703
14 | 0.048404 | 0.012195 | -0.048361 | -0.012168 | 4.2795e-05 | 2.7119e-05 | 0.073244 | 0.073244 | 0.073244 | 0.98368 | -0.31164 | 0.98273 | -0.33014 | 20.1219
15 | -0.048404 | -0.012195 | 0.048481 | 0.012243 | 7.6832e-05 | 4.8687e-05 | 0.073244 | 0.073244 | 0.073244 | 0.98368 | -0.31164 | 0.98538 | -0.27851 | 20.1219
16 | 0.042836 | 0.010783 | -0.042805 | -0.010763 | 3.064e-05 | 1.9364e-05 | 0.064878 | 0.064878 | 0.064878 | 0.98273 | -0.33014 | 0.98196 | -0.34512 | 17.8235
17 | -0.053434 | -0.013485 | 0.053452 | 0.013496 | 1.7877e-05 | 1.1348e-05 | 0.080724 | 0.080724 | 0.080724 | 0.98538 | -0.27851 | 0.98574 | -0.27153 | 22.1769
18 | -0.042779 | -0.010747 | 0.042805 | 0.010763 | 2.5841e-05 | 1.6331e-05 | 0.064878 | 0.064878 | 0.064878 | 0.98131 | -0.35776 | 0.98196 | -0.34512 | 17.8236
19 | 0.02724 | 0.0068323 | -0.02723 | -0.0068264 | 9.4933e-06 | 5.8896e-06 | 0.041374 | 0.041374 | 0.041374 | 0.97972 | -0.38888 | 0.97935 | -0.3962 | 11.3666
20 | 0.0062169 | 0.0015581 | -0.0062162 | -0.0015579 | 6.7072e-07 | 1.7729e-07 | 0.0094481 | 0.0094482 | 0.0094482 | 0.97912 | -0.40064 | 0.97901 | -0.40291 | 2.5957
21 | -0.013149 | -0.0032955 | 0.013152 | 0.003297 | 2.7857e-06 | 1.5488e-06 | 0.019983 | 0.019983 | 0.019983 | 0.97912 | -0.40064 | 0.97935 | -0.3962 | 5.4899
22 | 0.014079 | 0.0035294 | -0.014076 | -0.0035278 | 2.8185e-06 | 1.5972e-06 | 0.021391 | 0.021391 | 0.021391 | 0.97935 | -0.3962 | 0.97914 | -0.4004 | 5.8768
23 | 0.0069299 | 0.0017369 | -0.0069291 | -0.0017366 | 8.3175e-07 | 2.8084e-07 | 0.010532 | 0.010532 | 0.010532 | 0.97914 | -0.4004 | 0.97901 | -0.40292 | 2.8933
24 | -0.053452 | -0.013496 | 0.053576 | 0.013575 | 0.00012402 | 7.8725e-05 | 0.080724 | 0.080724 | 0.080724 | 0.98574 | -0.27153 | 0.98824 | -0.22322 | 22.1769
25 | -0.29932 | -0.076169 | 0.29937 | 0.076198 | 4.5787e-05 | 2.9111e-05 | 0.45111 | 0.45111 | 0.45111 | 0.98824 | -0.22322 | 0.98841 | -0.22005 | 24.7861
26 | 0.24574 | 0.062594 | -0.24554 | -0.062465 | 0.00020346 | 0.00012895 | 0.37038 | 0.37038 | 0.37038 | 0.98824 | -0.22322 | 0.98735 | -0.2404 | 20.3507
27 | 0.083727 | 0.021368 | -0.083665 | -0.021332 | 6.1301e-05 | 3.5945e-05 | 0.12619 | 0.12619 | 0.12619 | 0.98841 | -0.22005 | 0.98761 | -0.23521 | 6.9333
28 | -0.38309 | -0.097566 | 0.38356 | 0.097862 | 0.00046373 | 0.0002956 | 0.57729 | 0.57729 | 0.57729 | 0.98841 | -0.22005 | 0.98971 | -0.19498 | 31.7193
29 | 0.23996 | 0.061067 | -0.23964 | -0.060862 | 0.00032389 | 0.00020519 | 0.36198 | 0.36198 | 0.36198 | 0.98735 | -0.2404 | 0.98589 | -0.26844 | 19.8889
30 | 0.00656 | 0.001644 | -0.0065594 | -0.0016439 | 5.7643e-07 | 1.6758e-07 | 0.0098838 | 0.0098839 | 0.0098839 | 0.98761 | -0.23521 | 0.98752 | -0.23706 | 2.7153
31 | 0.077105 | 0.019688 | -0.077089 | -0.019679 | 1.6169e-05 | 9.3287e-06 | 0.1163 | 0.1163 | 0.1163 | 0.98761 | -0.23521 | 0.98739 | -0.23955 | 6.3903
32 | -0.38509 | -0.098247 | 0.38533 | 0.098397 | 0.00023411 | 0.00014924 | 0.5796 | 0.5796 | 0.5796 | 0.98971 | -0.19498 | 0.99037 | -0.1824 | 31.8463
33 | 0.23405 | 0.059461 | -0.23373 | -0.059258 | 0.00032022 | 0.00020277 | 0.35354 | 0.35354 | 0.35354 | 0.98589 | -0.26844 | 0.98442 | -0.2969 | 19.4252
34 | -0.22674 | -0.057402 | 0.22702 | 0.057577 | 0.00027783 | 0.00017582 | 0.3434 | 0.3434 | 0.3434 | 0.9831 | -0.32239 | 0.98442 | -0.2969 | 18.8684
35 | 0.21946 | 0.055576 | -0.21914 | -0.055374 | 0.00031932 | 0.00020192 | 0.33238 | 0.33238 | 0.33238 | 0.9831 | -0.32239 | 0.98154 | -0.35274 | 18.2627
36 | 0.21914 | 0.055374 | -0.21904 | -0.055307 | 0.00010599 | 6.7028e-05 | 0.33238 | 0.33238 | 0.33238 | 0.98154 | -0.35274 | 0.98102 | -0.36283 | 18.2627
37 | 0.21842 | 0.055152 | -0.21817 | -0.054998 | 0.00024438 | 0.00015453 | 0.33144 | 0.33145 | 0.33145 | 0.98102 | -0.36283 | 0.97982 | -0.38621 | 18.2113
38 | -0.39462 | -0.10141 | 0.39537 | 0.10189 | 0.00075369 | 0.00048049 | 0.59088 | 0.59088 | 0.59088 | 0.99527 | -0.089092 | 0.99735 | -0.049857 | 32.4662
39 | 0.39462 | 0.10141 | -0.39357 | -0.10074 | 0.0010496 | 0.00066916 | 0.59088 | 0.59088 | 0.59088 | 0.99527 | -0.089092 | 0.99238 | -0.14401 | 32.4662
40 | -0.39642 | -0.10215 | 0.39658 | 0.10225 | 0.00016014 | 0.00010209 | 0.59244 | 0.59244 | 0.59244 | 0.99735 | -0.049857 | 0.99779 | -0.041563 | 32.5517
41 | 0.38968 | 0.099766 | -0.38895 | -0.099305 | 0.00072324 | 0.00046106 | 0.58505 | 0.58505 | 0.58505 | 0.99238 | -0.14401 | 0.99037 | -0.1824 | 32.1455
42 | 0.21773 | 0.054887 | -0.21773 | -0.054883 | 6.8432e-06 | 4.3271e-06 | 0.33077 | 0.33078 | 0.33078 | 0.97982 | -0.38621 | 0.97979 | -0.38687 | 18.1745
43 | 0.0033989 | 0.00085163 | -0.0033987 | -0.00085172 | 1.3409e-07 | -9.5955e-08 | 0.0050687 | 0.0050688 | 0.0050688 | 0.99779 | -0.041563 | 0.99775 | -0.042391 | 1.3925
44 | -0.39998 | -0.10311 | 0.40037 | 0.10336 | 0.0003937 | 0.00025101 | 0.59751 | 0.59751 | 0.59751 | 0.99779 | -0.041563 | 0.99886 | -0.021371 | 32.8302
45 | 0.0036244 | 0.00090814 | -0.0036241 | -0.00090829 | 2.9374e-07 | -1.5187e-07 | 0.0054456 | 0.0054457 | 0.0054457 | 0.99037 | -0.1824 | 0.99028 | -0.18411 | 1.4961
46 | 0.21648 | 0.05457 | -0.21641 | -0.05453 | 6.2826e-05 | 3.9721e-05 | 0.32888 | 0.32888 | 0.32888 | 0.97979 | -0.38687 | 0.97948 | -0.39294 | 18.0701
47 | 0.0038463 | 0.0009639 | -0.0038462 | -0.00096395 | 1.0936e-07 | -4.1083e-08 | 0.0057957 | 0.0057957 | 0.0057957 | 0.98752 | -0.23706 | 0.98749 | -0.23765 | 1.5922
48 | 0.075345 | 0.019242 | -0.075321 | -0.019228 | 2.332e-05 | 1.3387e-05 | 0.11367 | 0.11368 | 0.11368 | 0.98739 | -0.23955 | 0.98705 | -0.24596 | 6.2459
49 | -0.029482 | -0.0074027 | 0.029499 | 0.007413 | 1.6491e-05 | 1.0282e-05 | 0.044941 | 0.044941 | 0.044941 | 0.97627 | -0.45595 | 0.97686 | -0.44423 | 12.3466
50 | -0.031159 | -0.0078291 | 0.03116 | 0.0078296 | 7.1281e-07 | 4.4564e-07 | 0.047471 | 0.047471 | 0.047471 | 0.97686 | -0.44423 | 0.97689 | -0.44376 | 13.0414
51 | -0.032548 | -0.0081775 | 0.032549 | 0.0081777 | 2.898e-07 | 1.8154e-07 | 0.049586 | 0.049586 | 0.049586 | 0.97689 | -0.44376 | 0.9769 | -0.44357 | 13.6224
52 | -0.034547 | -0.0086785 | 0.034553 | 0.0086825 | 6.3188e-06 | 3.9678e-06 | 0.05263 | 0.05263 | 0.05263 | 0.9769 | -0.44357 | 0.97709 | -0.43974 | 14.4587
53 | -0.036501 | -0.0091706 | 0.036511 | 0.009177 | 1.0196e-05 | 6.4151e-06 | 0.055595 | 0.055595 | 0.055595 | 0.97709 | -0.43974 | 0.97739 | -0.43389 | 15.2735
54 | -0.038654 | -0.0097141 | 0.038673 | 0.009726 | 1.8907e-05 | 1.1918e-05 | 0.058858 | 0.058858 | 0.058858 | 0.97739 | -0.43389 | 0.97791 | -0.42365 | 16.1698
55 | -0.041843 | -0.01052 | 0.041852 | 0.010527 | 9.547e-06 | 6.0313e-06 | 0.063681 | 0.063681 | 0.063681 | 0.97791 | -0.42365 | 0.97815 | -0.41887 | 17.4949
56 | -0.029229 | -0.0073386 | 0.029267 | 0.0073623 | 3.8013e-05 | 2.3698e-05 | 0.044713 | 0.044713 | 0.044713 | 0.97284 | -0.52326 | 0.97422 | -0.49603 | 12.2837
57 | 0.029229 | 0.0073386 | -0.029197 | -0.0073187 | 3.1998e-05 | 1.9949e-05 | 0.044713 | 0.044713 | 0.044713 | 0.97284 | -0.52326 | 0.97168 | -0.54623 | 12.2838
58 | -0.038801 | -0.0097518 | 0.038832 | 0.0097709 | 3.0423e-05 | 1.9183e-05 | 0.059275 | 0.059274 | 0.059275 | 0.97422 | -0.49603 | 0.97505 | -0.47962 | 16.2842
59 | 0.010913 | 0.0027361 | -0.010911 | -0.0027353 | 1.4353e-06 | 7.4889e-07 | 0.016712 | 0.016712 | 0.016712 | 0.97168 | -0.54623 | 0.97154 | -0.54899 | 4.5912
60 | 0.010911 | 0.0027353 | -0.010908 | -0.0027339 | 2.7452e-06 | 1.4324e-06 | 0.016712 | 0.016712 | 0.016712 | 0.97154 | -0.54899 | 0.97127 | -0.55427 | 4.5912
61 | -0.044866 | -0.011283 | 0.044917 | 0.011316 | 5.1458e-05 | 3.2568e-05 | 0.068483 | 0.068483 | 0.068483 | 0.97505 | -0.47962 | 0.97628 | -0.45564 | 18.8139
62 | -0.051184 | -0.012916 | 0.051197 | 0.012924 | 1.2687e-05 | 8.0499e-06 | 0.077916 | 0.077916 | 0.077916 | 0.9779 | -0.42382 | 0.97816 | -0.41865 | 21.4054
63 | 0.051184 | 0.012916 | -0.051155 | -0.012898 | 2.917e-05 | 1.8508e-05 | 0.077916 | 0.077916 | 0.077916 | 0.9779 | -0.42382 | 0.97729 | -0.43573 | 21.4055
64 | -0.05273 | -0.013309 | 0.052765 | 0.013331 | 3.4763e-05 | 2.2067e-05 | 0.080248 | 0.080248 | 0.080248 | 0.97816 | -0.41865 | 0.97887 | -0.40489 | 22.0463
65 | 0.051155 | 0.012898 | -0.051106 | -0.012867 | 4.8698e-05 | 3.0899e-05 | 0.077916 | 0.077916 | 0.077916 | 0.97729 | -0.43573 | 0.97628 | -0.45564 | 21.4055
66 | -0.013115 | -0.0032869 | 0.013118 | 0.0032884 | 2.6668e-06 | 1.485e-06 | 0.020009 | 0.020009 | 0.020009 | 0.97533 | -0.47435 | 0.97555 | -0.47008 | 5.4969
67 | -0.013118 | -0.0032884 | 0.013122 | 0.0032907 | 4.1424e-06 | 2.3065e-06 | 0.020009 | 0.020009 | 0.020009 | 0.97555 | -0.47008 | 0.97589 | -0.46345 | 5.4969
68 | 0.11856 | 0.029804 | -0.11853 | -0.029787 | 2.6658e-05 | 1.6374e-05 | 0.18026 | 0.18026 | 0.18026 | 0.97887 | -0.40489 | 0.97863 | -0.4096 | 9.9043
69 | 0.043767 | 0.011018 | -0.043738 | -0.010999 | 2.9219e-05 | 1.8479e-05 | 0.06655 | 0.06655 | 0.06655 | 0.97887 | -0.40489 | 0.97815 | -0.41887 | 18.2829
70 | -0.21509 | -0.054152 | 0.21521 | 0.05423 | 0.00012302 | 7.7766e-05 | 0.32706 | 0.32706 | 0.32706 | 0.97887 | -0.40489 | 0.97948 | -0.39294 | 17.9701
71 | 0.011322 | 0.0028381 | -0.011319 | -0.0028369 | 2.4196e-06 | 1.2781e-06 | 0.017264 | 0.017264 | 0.017264 | 0.97589 | -0.46345 | 0.97566 | -0.46794 | 4.7428
72 | -0.024444 | -0.0061289 | 0.024448 | 0.0061316 | 4.4081e-06 | 2.7155e-06 | 0.037272 | 0.037272 | 0.037272 | 0.97589 | -0.46345 | 0.97608 | -0.45967 | 10.2396
73 | 0.0082134 | 0.0020584 | -0.0082134 | -0.0020584 | 1.6795e-08 | 7.1846e-09 | 0.012527 | 0.012527 | 0.012527 | 0.97566 | -0.46794 | 0.97566 | -0.46798 | 3.4414
74 | -0.027923 | -0.0070025 | 0.027929 | 0.0070061 | 5.9264e-06 | 3.6839e-06 | 0.042569 | 0.042569 | 0.042569 | 0.97608 | -0.45967 | 0.97631 | -0.45522 | 11.6949
75 | -0.0012627 | -0.00031646 | 0.0012627 | 0.00031638 | 9.534e-09 | -7.9463e-08 | 0.0019261 | 0.001926 | 0.0019261 | 0.97552 | -0.47073 | 0.97553 | -0.47057 | 0.52914
76 | -0.0029442 | -0.0007378 | 0.0029447 | 0.00073727 | 5.2579e-07 | -5.3171e-07 | 0.0044909 | 0.0044906 | 0.0044909 | 0.97553 | -0.47057 | 0.97572 | -0.46682 | 1.2338
77 | 0.0053758 | 0.0013473 | -0.0053754 | -0.0013472 | 4.3471e-07 | 6.2875e-08 | 0.0081989 | 0.008199 | 0.008199 | 0.97566 | -0.46798 | 0.97557 | -0.46968 | 2.2525
78 | -0.031359 | -0.0078659 | 0.031379 | 0.0078783 | 1.9885e-05 | 1.2436e-05 | 0.047798 | 0.047798 | 0.047798 | 0.97631 | -0.45522 | 0.97698 | -0.44192 | 13.1313
79 | -0.0029447 | -0.00073727 | 0.0029452 | 0.00073682 | 4.4987e-07 | -4.553e-07 | 0.0044906 | 0.0044903 | 0.0044906 | 0.97572 | -0.46682 | 0.97588 | -0.46361 | 1.2337
80 | -0.037601 | -0.0094378 | 0.037621 | 0.0094501 | 1.9648e-05 | 1.2374e-05 | 0.057275 | 0.057275 | 0.057275 | 0.97698 | -0.44192 | 0.97754 | -0.43097 | 15.7348
81 | 0.072489 | 0.018184 | -0.072481 | -0.01818 | 8.4271e-06 | 4.815e-06 | 0.11035 | 0.11035 | 0.11035 | 0.97754 | -0.43097 | 0.97742 | -0.43341 | 6.0632
82 | -0.11011 | -0.027635 | 0.11015 | 0.027657 | 3.7347e-05 | 2.2791e-05 | 0.16762 | 0.16762 | 0.16762 | 0.97754 | -0.43097 | 0.9779 | -0.42386 | 9.2101
83 | 0.067339 | 0.016891 | -0.067329 | -0.016886 | 9.843e-06 | 5.5172e-06 | 0.10252 | 0.10252 | 0.10252 | 0.97742 | -0.43341 | 0.97726 | -0.43648 | 5.6331
84 | -0.11058 | -0.027767 | 0.11061 | 0.02778 | 2.1681e-05 | 1.3235e-05 | 0.16829 | 0.16829 | 0.16829 | 0.9779 | -0.42386 | 0.97811 | -0.41976 | 9.2465
85 | 0.067329 | 0.016886 | -0.067323 | -0.016882 | 6.4457e-06 | 3.6131e-06 | 0.10252 | 0.10252 | 0.10252 | 0.97726 | -0.43648 | 0.97716 | -0.43849 | 5.6331
86 | -0.117 | -0.029383 | 0.11706 | 0.029418 | 5.6705e-05 | 3.4793e-05 | 0.17802 | 0.17802 | 0.17802 | 0.97811 | -0.41976 | 0.97863 | -0.4096 | 9.7811
87 | 0.059853 | 0.01501 | -0.059833 | -0.014999 | 1.9818e-05 | 1.0692e-05 | 0.091147 | 0.091148 | 0.091148 | 0.97716 | -0.43849 | 0.9768 | -0.44544 | 5.0081
88 | 0.056683 | 0.01421 | -0.056678 | -0.014207 | 5.5012e-06 | 2.9052e-06 | 0.08635 | 0.08635 | 0.08635 | 0.9768 | -0.44544 | 0.9767 | -0.44747 | 4.7445
89 | 0.054103 | 0.013562 | -0.054088 | -0.013554 | 1.5568e-05 | 8.0524e-06 | 0.082428 | 0.082429 | 0.082429 | 0.9767 | -0.44747 | 0.97639 | -0.45352 | 4.529
90 | 0.049356 | 0.012368 | -0.04935 | -0.012365 | 5.9581e-06 | 2.9352e-06 | 0.075217 | 0.075217 | 0.075217 | 0.97639 | -0.45352 | 0.97626 | -0.45605 | 4.1328
91 | -0.0042155 | -0.0010565 | 0.0042159 | 0.0010565 | 3.1473e-07 | -5.2026e-08 | 0.0064301 | 0.0064301 | 0.0064301 | 0.97553 | -0.47053 | 0.97561 | -0.46897 | 1.7665
92 | -0.0073211 | -0.0018347 | 0.0073216 | 0.0018349 | 4.7173e-07 | 1.7592e-07 | 0.011166 | 0.011166 | 0.011166 | 0.97561 | -0.46897 | 0.97568 | -0.46761 | 3.0677
93 | 0.0045994 | 0.0011526 | -0.004599 | -0.0011526 | 4.7525e-07 | -1.8243e-08 | 0.0070104 | 0.0070105 | 0.0070105 | 0.97626 | -0.45605 | 0.97615 | -0.45822 | 1.926
94 | 0.04475 | 0.011212 | -0.044747 | -0.011211 | 3.1489e-06 | 1.4511e-06 | 0.068207 | 0.068207 | 0.068207 | 0.97626 | -0.45605 | 0.97619 | -0.45753 | 3.7476
95 | 0.012919 | 0.0032361 | -0.012917 | -0.0032383 | 1.4688e-06 | -2.2099e-06 | 0.019702 | 0.019703 | 0.019703 | 0.97568 | -0.46761 | 0.97556 | -0.47 | 1.0826
96 | -0.02024 | -0.005071 | 0.020242 | 0.0050707 | 1.4021e-06 | -3.2794e-07 | 0.030868 | 0.030867 | 0.030868 | 0.97568 | -0.46761 | 0.97575 | -0.46616 | 1.696
97 | 0.03479 | 0.0087159 | -0.034785 | -0.0087143 | 4.6325e-06 | 1.592e-06 | 0.053029 | 0.05303 | 0.05303 | 0.97619 | -0.45753 | 0.97605 | -0.46032 | 2.9137
98 | 0.0099574 | 0.0024947 | -0.0099561 | -0.002494 | 1.3526e-06 | 6.6994e-07 | 0.015178 | 0.015178 | 0.015178 | 0.97619 | -0.45753 | 0.97604 | -0.46038 | 4.1698
99 | 0.026493 | 0.006636 | -0.026489 | -0.0066356 | 3.1679e-06 | 4.0946e-07 | 0.040387 | 0.040388 | 0.040388 | 0.97605 | -0.46032 | 0.97592 | -0.46284 | 2.2191
100 | 0.0068121 | 0.0017061 | -0.0068111 | -0.0017057 | 1.048e-06 | 3.469e-07 | 0.010385 | 0.010385 | 0.010385 | 0.97604 | -0.46038 | 0.97588 | -0.46361 | 2.853
101 | 0.02598 | 0.0065079 | -0.02598 | -0.0065078 | 9.9188e-08 | 1.0821e-08 | 0.039611 | 0.039611 | 0.039611 | 0.97592 | -0.46284 | 0.97592 | -0.46292 | 2.1764
102 | 0.0018918 | 0.00047402 | -0.0018918 | -0.00047412 | 2.9347e-08 | -9.857e-08 | 0.0028855 | 0.0028855 | 0.0028855 | 0.97556 | -0.47 | 0.97554 | -0.47033 | 0.79273
103 | 0.011025 | 0.0027643 | -0.011025 | -0.0027648 | 2.3786e-07 | -5.478e-07 | 0.016817 | 0.016818 | 0.016818 | 0.97556 | -0.47 | 0.97553 | -0.47045 | 0.92404
104 | -0.023724 | -0.0059435 | 0.023728 | 0.0059435 | 3.6642e-06 | 1.3454e-08 | 0.036178 | 0.036178 | 0.036178 | 0.97575 | -0.46616 | 0.97592 | -0.46292 | 1.9878
105 | 0.00061918 | 0.00015514 | -0.00061917 | -0.00015518 | 9.7772e-10 | -3.5868e-08 | 0.00094444 | 0.00094445 | 0.00094445 | 0.97553 | -0.47045 | 0.97553 | -0.47049 | 0.25946
106 | 0.010406 | 0.0026097 | -0.010403 | -0.0026112 | 2.7499e-06 | -1.5093e-06 | 0.015873 | 0.015874 | 0.015874 | 0.97553 | -0.47045 | 0.97525 | -0.476 | 1.4537
107 | 0.010403 | 0.0026112 | -0.010403 | -0.0026109 | 6.2174e-07 | 3.1582e-07 | 0.015874 | 0.015874 | 0.015874 | 0.97525 | -0.476 | 0.97519 | -0.47725 | 4.3611
108 | 0.0092831 | 0.0023303 | -0.009282 | -0.0023298 | 1.106e-06 | 5.2449e-07 | 0.014166 | 0.014166 | 0.014166 | 0.97519 | -0.47725 | 0.97506 | -0.47975 | 3.8918
109 | 0.0089812 | 0.0022544 | -0.008977 | -0.0022525 | 4.2202e-06 | 1.9542e-06 | 0.013707 | 0.013707 | 0.013707 | 0.97506 | -0.47975 | 0.97456 | -0.4896 | 3.7658
110 | 0.40141 | 0.10368 | -0.40125 | -0.10358 | 0.00016422 | 0.0001047 | 0.59882 | 0.59882 | 0.59882 | 0.99931 | -0.01298 | 0.99886 | -0.021371 | 32.9022
111 | -0.40223 | -0.10389 | 0.40248 | 0.10405 | 0.00025481 | 0.00016246 | 0.60004 | 0.60004 | 0.60004 | 0.99931 | -0.01298 | 1 | 0 | 32.969
112 | 0.0024472 | 0.00061324 | -0.0024471 | -0.00061331 | 3.5778e-08 | -7.0648e-08 | 0.0036496 | 0.0036497 | 0.0036497 | 0.99775 | -0.042391 | 0.99773 | -0.042698 | 1.0027
113 | -0.0018284 | -0.00045765 | 0.0018285 | 0.00045734 | 8.0643e-08 | -3.0792e-07 | 0.0027606 | 0.0027605 | 0.0027606 | 0.98545 | -0.27686 | 0.9855 | -0.27593 | 0.75841
114 | 0.0015163 | 0.00037944 | -0.0015162 | -0.00038 | 9.6281e-08 | -5.6236e-07 | 0.0022894 | 0.0022896 | 0.0022896 | 0.98545 | -0.27686 | 0.98538 | -0.27819 | 0.62902
115 | -0.0025121 | -0.00062867 | 0.0025122 | 0.00062842 | 1.478e-07 | -2.5455e-07 | 0.0037927 | 0.0037926 | 0.0037927 | 0.9855 | -0.27593 | 0.98556 | -0.2747 | 1.042
116 | 0.070395 | 0.017959 | -0.070348 | -0.017929 | 4.7423e-05 | 3.0208e-05 | 0.1064 | 0.1064 | 0.1064 | 0.98556 | -0.2747 | 0.98483 | -0.28865 | 29.2301
117 | -0.072907 | -0.018588 | 0.072956 | 0.018618 | 4.8255e-05 | 3.0343e-05 | 0.11019 | 0.11019 | 0.11019 | 0.98556 | -0.2747 | 0.98627 | -0.26099 | 15.136
118 | 0.069436 | 0.0177 | -0.068888 | -0.017351 | 0.00054758 | 0.00034878 | 0.10502 | 0.10502 | 0.10502 | 0.98483 | -0.28865 | 0.97636 | -0.45345 | 28.8516
119 | -0.073686 | -0.018801 | 0.073689 | 0.018803 | 3.2153e-06 | 1.837e-06 | 0.11129 | 0.11129 | 0.11129 | 0.98627 | -0.26099 | 0.98632 | -0.26009 | 6.1149
120 | 0.066683 | 0.016802 | -0.066585 | -0.01674 | 9.7645e-05 | 6.2178e-05 | 0.10166 | 0.10166 | 0.10166 | 0.97636 | -0.45345 | 0.97479 | -0.48411 | 27.9288
121 | 0.002205 | 0.00054939 | -0.0022039 | -0.00055194 | 1.1006e-06 | -2.5452e-06 | 0.0033594 | 0.0033606 | 0.0033606 | 0.97636 | -0.45345 | 0.97582 | -0.46396 | 0.92323
122 | -0.074642 | -0.019042 | 0.074693 | 0.019071 | 5.0989e-05 | 2.9216e-05 | 0.11273 | 0.11273 | 0.11273 | 0.98632 | -0.26009 | 0.98705 | -0.24596 | 6.1939
123 | 0.045472 | 0.011428 | -0.045388 | -0.011375 | 8.3817e-05 | 5.3066e-05 | 0.069424 | 0.069425 | 0.069425 | 0.97479 | -0.48411 | 0.97283 | -0.5228 | 19.0727
124 | 0.021113 | 0.0053114 | -0.021061 | -0.0052796 | 5.2448e-05 | 3.1894e-05 | 0.032236 | 0.032237 | 0.032237 | 0.97479 | -0.48411 | 0.97215 | -0.53624 | 8.8563
125 | 0.0022039 | 0.00055194 | -0.0022037 | -0.00055231 | 1.6163e-07 | -3.7328e-07 | 0.0033606 | 0.0033607 | 0.0033607 | 0.97582 | -0.46396 | 0.97575 | -0.4655 | 0.92328
126 | 0.0075969 | 0.0019038 | -0.0075965 | -0.0019037 | 4.1453e-07 | 1.6394e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97215 | -0.53624 | 0.97209 | -0.53739 | 3.1946
127 | 0.013464 | 0.0033757 | -0.013462 | -0.0033748 | 1.6656e-06 | 9.3631e-07 | 0.020609 | 0.020609 | 0.020609 | 0.97215 | -0.53624 | 0.97202 | -0.53884 | 5.6618
128 | 0.0019631 | 0.00049179 | -0.0019631 | -0.00049199 | 6.5621e-08 | -1.9824e-07 | 0.0030049 | 0.003005 | 0.003005 | 0.97209 | -0.53739 | 0.97206 | -0.53809 | 0.82556
129 | 0.010608 | 0.0026594 | -0.010605 | -0.002658 | 2.8685e-06 | 1.4764e-06 | 0.016239 | 0.016239 | 0.016239 | 0.97202 | -0.53884 | 0.97173 | -0.54451 | 4.4614
130 | -0.0092845 | -0.0023269 | 0.009285 | 0.0023272 | 5.0465e-07 | 2.4051e-07 | 0.014218 | 0.014218 | 0.014218 | 0.97168 | -0.54565 | 0.97173 | -0.54451 | 3.9061
131 | 0.008977 | 0.0022525 | -0.0089654 | -0.0022471 | 1.1601e-05 | 5.3761e-06 | 0.013707 | 0.013708 | 0.013708 | 0.97456 | -0.4896 | 0.97319 | -0.51673 | 3.766
132 | 0.0089654 | 0.0022471 | -0.0089642 | -0.0022465 | 1.2055e-06 | 5.5897e-07 | 0.013708 | 0.013708 | 0.013708 | 0.97319 | -0.51673 | 0.97304 | -0.51956 | 3.766
133 | 0.0050531 | 0.0012664 | -0.005053 | -0.0012664 | 8.0322e-08 | 6.9021e-09 | 0.0077296 | 0.0077296 | 0.0077296 | 0.97276 | -0.5252 | 0.97274 | -0.52554 | 2.1235
134 | -0.0050531 | -0.0012664 | 0.0050533 | 0.0012664 | 2.2425e-07 | 1.9261e-08 | 0.0077296 | 0.0077296 | 0.0077296 | 0.97276 | -0.5252 | 0.97281 | -0.52427 | 2.1235
135 | -0.0057273 | -0.0014353 | 0.0057286 | 0.0014356 | 1.2865e-06 | 2.6823e-07 | 0.0087605 | 0.0087603 | 0.0087605 | 0.97281 | -0.52427 | 0.97304 | -0.51956 | 2.4067

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4056 | 0.10442

## res_load
| p_mw | q_mvar
0 | 0.009187 | 0.0023025
1 | 0.0029534 | 0.00074019
2 | 0.0032567 | 0.0008162
3 | 0.0026829 | 0.0006724
4 | 0.0046517 | 0.0011658
5 | 0.0028322 | 0.00070983
6 | 0.0028641 | 0.00071781
7 | 0.0032567 | 0.00081622
8 | 0.0017857 | 0.00044753
9 | 0.0055253 | 0.0013848
10 | 0.0049536 | 0.0012415
11 | 0.0034723 | 0.00087023
12 | 0.0058892 | 0.001476
13 | 0.0069321 | 0.0017374
14 | 0.0062162 | 0.0015579
15 | 0.0071459 | 0.0017909
16 | 0.0069291 | 0.0017366
17 | 0.0055779 | 0.001398
18 | 0.0015378 | 0.00038542
19 | 0.0055922 | 0.0014015
20 | 0.0072831 | 0.0018253
21 | 0.0067046 | 0.0016803
22 | 0.000618 | 0.00015489
23 | 0.0010443 | 0.00026172
24 | 0.0038928 | 0.00097562
25 | 0.00044128 | 0.0001106
26 | 0.0012503 | 0.00031335
27 | 0.0027131 | 0.00067998
28 | 0.0017444 | 0.00043719
29 | 0.0020926 | 0.00052444
30 | 0.0016606 | 0.00041618
31 | 0.0013883 | 0.00034794
32 | 0.0019984 | 0.00050085
33 | 0.0019475 | 0.0004881
34 | 0.002143 | 0.00053709
35 | 0.0031699 | 0.00079445
36 | 0.009534 | 0.0023894
37 | 0.018285 | 0.0045826
38 | 0.010908 | 0.0027339
39 | 0.0060339 | 0.0015122
40 | 0.0015334 | 0.0003843
41 | 0.013115 | 0.0032869
42 | 0.0061892 | 0.0015512
43 | 0.003106 | 0.00077843
44 | 0.0034749 | 0.00087088
45 | 0.0012627 | 0.00031646
46 | 0.0016815 | 0.00042142
47 | 0.0028376 | 0.00071117
48 | 0.0034304 | 0.00085973
49 | 0.0062223 | 0.0015595
50 | 0.0051415 | 0.0012886
51 | 0.00043584 | 0.00010923
52 | 0.0063957 | 0.0016029
53 | 0.0074701 | 0.0018722
54 | 0.0014749 | 0.00036965
55 | 0.0053754 | 0.0013472
56 | 0.0018856 | 0.00047257
57 | 0.0031496 | 0.00078937
58 | 0.0025746 | 0.00064527
59 | 0.0047321 | 0.001186
60 | 0.0042155 | 0.0010565
61 | 0.0031053 | 0.00077825
62 | 0.004599 | 0.0011526
63 | 0.0082925 | 0.0020783
64 | 0.0031439 | 0.00078794
65 | 0.00050967 | 0.00012773
66 | 0.0038659 | 0.00096889
67 | 0.0034827 | 0.00087283
68 | 0.00061917 | 0.00015518
69 | 0.0018918 | 0.00047412
70 | 0.0011195 | 0.00028056
71 | 0.0022517 | 0.00056434
72 | 0.00030077 | 7.538e-05
73 | 0.0011982 | 0.0003003
74 | 0.00081653 | 0.00020464
75 | 0.0008795 | 0.00022042
76 | 0.0014684 | 0.00036802
77 | 0.00095156 | 0.00023848
78 | 0.0024471 | 0.00061331
79 | 0.00031206 | 7.821e-05
80 | 0.00068363 | 0.00017133
81 | 0.0015162 | 0.00038
82 | 0.00091224 | 0.00022863
83 | 0.00073036 | 0.00018305
84 | 0.0009529 | 0.00023882
85 | 0.00062814 | 0.00015743
86 | 0.045388 | 0.011375
87 | 0.0022037 | 0.00055231
88 | 0.0056334 | 0.0014119
89 | 0.0028543 | 0.00071535
90 | 0.0038462 | 0.00096395
91 | 0.0036241 | 0.00090829
92 | 0.0092845 | 0.0023269
93 | 0.00132 | 0.00033082
94 | 0.0019631 | 0.00049199
95 | 0.005053 | 0.0012664
96 | 0.00067397 | 0.00016891
97 | 0.0032356 | 0.00081092

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1