## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_155-3_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_155-3_0_7_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_155-3_0_7_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_155-3_0_7_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_155-3_0_7_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_155-3_0_7_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_155-3_0_7_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_155-3_0_7_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_155-3_0_7_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_155-3_0_7_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_155-3_0_7_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_155-3_0_7_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_155-3_0_7_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_155-3_0_7_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_155-3_0_7_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_155-3_0_7_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_155-3_0_7_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_155-3_0_7_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_155-3_0_7_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_155-3_0_7_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_155-3_0_7_node_108 | 0.4 | n |  | TRUE
21 | bus_LV_155-3_0_7_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_155-3_0_7_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_155-3_0_7_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_155-3_0_7_node_112 | 0.4 | n |  | TRUE
25 | bus_LV_155-3_0_7_node_111 | 0.4 | n |  | TRUE
26 | bus_LV_155-3_0_7_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_155-3_0_7_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_155-3_0_7_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_155-3_0_7_node_132 | 0.4 | n |  | TRUE
30 | bus_LV_155-3_0_7_node_131 | 0.4 | n |  | TRUE
31 | bus_LV_155-3_0_7_node_74 | 0.4 | n |  | TRUE
32 | bus_LV_155-3_0_7_node_76 | 0.4 | n |  | TRUE
33 | bus_LV_155-3_0_7_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_155-3_0_7_node_130 | 0.4 | n |  | TRUE
35 | bus_LV_155-3_0_7_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_155-3_0_7_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_155-3_0_7_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_155-3_0_7_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_155-3_0_7_node_129 | 0.4 | n |  | TRUE
40 | bus_LV_155-3_0_7_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_155-3_0_7_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_155-3_0_7_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_155-3_0_7_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_155-3_0_7_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_155-3_0_7_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_155-3_0_7_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_155-3_0_7_node_149 | 0.4 | n |  | TRUE
48 | bus_LV_155-3_0_7_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_155-3_0_7_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_155-3_0_7_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_155-3_0_7_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_155-3_0_7_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_155-3_0_7_node_146 | 0.4 | n |  | TRUE
54 | bus_LV_155-3_0_7_node_86 | 0.4 | n |  | TRUE
55 | bus_LV_155-3_0_7_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_155-3_0_7_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_155-3_0_7_node_152 | 0.4 | n |  | TRUE
58 | bus_LV_155-3_0_7_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_155-3_0_7_node_67 | 0.4 | n |  | TRUE
60 | bus_LV_155-3_0_7_node_78 | 0.4 | n |  | TRUE
61 | bus_LV_155-3_0_7_node_141 | 0.4 | n |  | TRUE
62 | bus_LV_155-3_0_7_node_94 | 0.4 | n |  | TRUE
63 | bus_LV_155-3_0_7_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_155-3_0_7_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_155-3_0_7_node_106 | 0.4 | n |  | TRUE
66 | bus_LV_155-3_0_7_node_103 | 0.4 | n |  | TRUE
67 | bus_LV_155-3_0_7_node_85 | 0.4 | n |  | TRUE
68 | bus_LV_155-3_0_7_node_84 | 0.4 | n |  | TRUE
69 | bus_LV_155-3_0_7_node_143 | 0.4 | n |  | TRUE
70 | bus_LV_155-3_0_7_node_148 | 0.4 | n |  | TRUE
71 | bus_LV_155-3_0_7_node_142 | 0.4 | n |  | TRUE
72 | bus_LV_155-3_0_7_node_135 | 0.4 | n |  | TRUE
73 | bus_LV_155-3_0_7_node_137 | 0.4 | n |  | TRUE
74 | bus_LV_155-3_0_7_node_99 | 0.4 | n |  | TRUE
75 | bus_LV_155-3_0_7_node_145 | 0.4 | n |  | TRUE
76 | bus_LV_155-3_0_7_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_155-3_0_7_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_155-3_0_7_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_155-3_0_7_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_155-3_0_7_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_155-3_0_7_node_56 | 0.4 | n |  | TRUE
82 | bus_LV_155-3_0_7_node_57 | 0.4 | n |  | TRUE
83 | bus_LV_155-3_0_7_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_155-3_0_7_node_121 | 0.4 | n |  | TRUE
85 | bus_LV_155-3_0_7_node_134 | 0.4 | n |  | TRUE
86 | bus_LV_155-3_0_7_node_156 | 0.4 | n |  | TRUE
87 | bus_LV_155-3_0_7_node_133 | 0.4 | n |  | TRUE
88 | bus_LV_155-3_0_7_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_155-3_0_7_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_155-3_0_7_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_155-3_0_7_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_155-3_0_7_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_155-3_0_7_node_91 | 0.4 | n |  | TRUE
94 | bus_LV_155-3_0_7_node_92 | 0.4 | n |  | TRUE
95 | bus_LV_155-3_0_7_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_155-3_0_7_node_102 | 0.4 | n |  | TRUE
97 | bus_LV_155-3_0_7_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_155-3_0_7_node_140 | 0.4 | n |  | TRUE
99 | bus_LV_155-3_0_7_node_72 | 0.4 | n |  | TRUE
100 | bus_LV_155-3_0_7_node_105 | 0.4 | n |  | TRUE
101 | bus_LV_155-3_0_7_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_155-3_0_7_node_155 | 0.4 | n |  | TRUE
103 | bus_LV_155-3_0_7_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_155-3_0_7_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_155-3_0_7_node_120 | 0.4 | n |  | TRUE
106 | bus_LV_155-3_0_7_node_119 | 0.4 | n |  | TRUE
107 | bus_LV_155-3_0_7_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_155-3_0_7_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_155-3_0_7_node_147 | 0.4 | n |  | TRUE
110 | bus_LV_155-3_0_7_node_144 | 0.4 | n |  | TRUE
111 | bus_LV_155-3_0_7_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_155-3_0_7_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_155-3_0_7_node_150 | 0.4 | n |  | TRUE
114 | bus_LV_155-3_0_7_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_155-3_0_7_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_155-3_0_7_node_88 | 0.4 | n |  | TRUE
117 | bus_LV_155-3_0_7_node_89 | 0.4 | n |  | TRUE
118 | bus_LV_155-3_0_7_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_155-3_0_7_node_96 | 0.4 | n |  | TRUE
120 | bus_LV_155-3_0_7_node_97 | 0.4 | n |  | TRUE
121 | bus_LV_155-3_0_7_node_128 | 0.4 | n |  | TRUE
122 | bus_LV_155-3_0_7_node_153 | 0.4 | n |  | TRUE
123 | bus_LV_155-3_0_7_node_125 | 0.4 | n |  | TRUE
124 | bus_LV_155-3_0_7_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_155-3_0_7_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_155-3_0_7_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_155-3_0_7_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_155-3_0_7_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_155-3_0_7_node_118 | 0.4 | n |  | TRUE
130 | bus_LV_155-3_0_7_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_155-3_0_7_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_155-3_0_7_node_122 | 0.4 | n |  | TRUE
133 | bus_LV_155-3_0_7_node_151 | 0.4 | n |  | TRUE
134 | bus_LV_155-3_0_7_node_127 | 0.4 | n |  | TRUE
135 | bus_LV_155-3_0_7_node_123 | 0.4 | n |  | TRUE
136 | bus_LV_155-3_0_7_node_136 | 0.4 | n |  | TRUE
137 | bus_LV_155-3_0_7_node_138 | 0.4 | n |  | TRUE
138 | bus_LV_155-3_0_7_node_139 | 0.4 | n |  | TRUE
139 | bus_MV_361_0_node_167 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_155-3_0_7_load_0 | 0 | 0.0056034 | 0.0014043 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_155-3_0_7_load_5 | 2 | 0.0079032 | 0.0019807 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_155-3_0_7_load_18 | 5 | 0.0023218 | 0.0005819 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_155-3_0_7_load_21 | 6 | 0.001179 | 0.00029548 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_155-3_0_7_load_8 | 8 | 0.0029615 | 0.00074223 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_155-3_0_7_load_44 | 10 | 0.0007977 | 0.00019992 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_155-3_0_7_load_24 | 13 | 0.00040127 | 0.00010057 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_155-3_0_7_load_25 | 14 | 0.00088092 | 0.00022078 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_155-3_0_7_load_23 | 15 | 0.00081719 | 0.00020481 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_155-3_0_7_load_15 | 16 | 0.0041385 | 0.0010372 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_155-3_0_7_load_13 | 17 | 0.0021806 | 0.00054652 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_155-3_0_7_load_22 | 18 | 0.0014999 | 0.00037591 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_155-3_0_7_load_9 | 19 | 0.0047455 | 0.0011893 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_155-3_0_7_load_108 | 20 | 0.00048604 | 0.00012181 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_155-3_0_7_load_107 | 21 | 0.0014124 | 0.00035398 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_155-3_0_7_load_10 | 22 | 0.0012711 | 0.00031858 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_155-3_0_7_load_12 | 23 | 0.0013737 | 0.00034428 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_155-3_0_7_load_112 | 24 | 0.0022163 | 0.00055545 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_155-3_0_7_load_19 | 26 | 0.0059999 | 0.0015037 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_155-3_0_7_load_20 | 27 | 0.0041612 | 0.0010429 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_155-3_0_7_load_42 | 28 | 0.0016945 | 0.00042467 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_155-3_0_7_load_132 | 29 | 0.00043818 | 0.00010982 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_155-3_0_7_load_76 | 32 | 0.0029801 | 0.0007469 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_155-3_0_7_load_26 | 35 | 0.0084102 | 0.0021078 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_155-3_0_7_load_29 | 37 | 0.0027173 | 0.00068101 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_155-3_0_7_load_129 | 39 | 0.0021841 | 0.00054739 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_155-3_0_7_load_35 | 41 | 0.0031469 | 0.00078868 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_155-3_0_7_load_32 | 42 | 0.0024932 | 0.00062484 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_155-3_0_7_load_36 | 43 | 0.0018818 | 0.00047162 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_155-3_0_7_load_37 | 44 | 0.0024558 | 0.00061548 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_155-3_0_7_load_39 | 45 | 0.0013104 | 0.00032842 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_155-3_0_7_load_149 | 47 | 0.00087498 | 0.00021929 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_155-3_0_7_load_41 | 48 | 0.001972 | 0.00049424 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_155-3_0_7_load_50 | 51 | 0.0012208 | 0.00030597 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_155-3_0_7_load_47 | 52 | 0.0025223 | 0.00063216 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_155-3_0_7_load_146 | 53 | 0.0073674 | 0.0018464 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_155-3_0_7_load_86 | 54 | 0.0014991 | 0.0003757 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_155-3_0_7_load_48 | 55 | 0.0021129 | 0.00052954 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_155-3_0_7_load_152 | 57 | 0.0023745 | 0.0005951 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_155-3_0_7_load_141 | 61 | 0.0031184 | 0.00078154 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_155-3_0_7_load_93 | 64 | 0.0057669 | 0.0014453 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_155-3_0_7_load_106 | 65 | 0.015694 | 0.0039334 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_155-3_0_7_load_103 | 66 | 0.0051015 | 0.0012786 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_155-3_0_7_load_85 | 67 | 0.0020357 | 0.0005102 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_155-3_0_7_load_84 | 68 | 0.0012264 | 0.00030737 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_155-3_0_7_load_148 | 70 | 0.0027834 | 0.00069759 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_155-3_0_7_load_137 | 73 | 0.0063145 | 0.0015826 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_155-3_0_7_load_51 | 76 | 0.004638 | 0.0011624 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_155-3_0_7_load_52 | 78 | 0.0047716 | 0.0011959 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_155-3_0_7_load_57 | 82 | 0.012139 | 0.0030424 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_155-3_0_7_load_58 | 83 | 0.011847 | 0.0029691 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_155-3_0_7_load_134 | 85 | 0.0084338 | 0.0021137 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_155-3_0_7_load_156 | 86 | 0.010622 | 0.002662 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_155-3_0_7_load_133 | 87 | 0.0051152 | 0.001282 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_155-3_0_7_load_73 | 89 | 0.0049479 | 0.0012401 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_155-3_0_7_load_70 | 90 | 0.007994 | 0.0020035 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_155-3_0_7_load_71 | 91 | 0.027935 | 0.0070011 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_155-3_0_7_load_91 | 93 | 0.0060955 | 0.0015277 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_155-3_0_7_load_92 | 94 | 0.0034332 | 0.00086045 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_155-3_0_7_load_90 | 95 | 0.0031945 | 0.00080062 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_155-3_0_7_load_77 | 97 | 0.0014821 | 0.00037144 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_155-3_0_7_load_140 | 98 | 0.0024691 | 0.0006188 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_155-3_0_7_load_105 | 100 | 0.0019218 | 0.00048165 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_155-3_0_7_load_101 | 101 | 0.0047404 | 0.001188 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_155-3_0_7_load_155 | 102 | 0.005871 | 0.0014714 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_155-3_0_7_load_100 | 103 | 0.0087352 | 0.0021892 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_155-3_0_7_load_81 | 104 | 0.0037955 | 0.00095123 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_155-3_0_7_load_120 | 105 | 0.002027 | 0.00050802 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_155-3_0_7_load_80 | 107 | 0.0018471 | 0.00046294 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_155-3_0_7_load_147 | 109 | 0.0031694 | 0.00079433 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_155-3_0_7_load_144 | 110 | 0.0059327 | 0.0014869 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_155-3_0_7_load_82 | 111 | 0.0035256 | 0.0008836 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_155-3_0_7_load_83 | 112 | 0.00070989 | 0.00017791 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_155-3_0_7_load_150 | 113 | 0.0010367 | 0.00025983 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_155-3_0_7_load_113 | 114 | 0.001609 | 0.00040326 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_155-3_0_7_load_87 | 115 | 0.0016385 | 0.00041064 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_155-3_0_7_load_88 | 116 | 0.0063335 | 0.0015873 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_155-3_0_7_load_98 | 118 | 0.0063836 | 0.0015999 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_155-3_0_7_load_96 | 119 | 0.0078375 | 0.0019643 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_155-3_0_7_load_97 | 120 | 0.0039778 | 0.00099693 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_155-3_0_7_load_153 | 122 | 0.0031036 | 0.00077783 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_155-3_0_7_load_114 | 126 | 0.0021035 | 0.00052719 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_155-3_0_7_load_115 | 127 | 0.0012224 | 0.00030636 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_155-3_0_7_load_116 | 128 | 0.0012648 | 0.000317 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_155-3_0_7_load_118 | 129 | 0.0025754 | 0.00064546 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_155-3_0_7_load_126 | 130 | 0.0013081 | 0.00032784 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_155-3_0_7_load_124 | 131 | 0.0011498 | 0.00028818 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_155-3_0_7_load_122 | 132 | 0.00087058 | 0.00021819 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_155-3_0_7_load_151 | 133 | 0.0010862 | 0.00027223 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_155-3_0_7_load_127 | 134 | 0.0012191 | 0.00030552 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_155-3_0_7_load_123 | 135 | 0.0027835 | 0.00069761 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_155-3_0_7_load_136 | 136 | 0.0063747 | 0.0015976 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_155-3_0_7_load_138 | 137 | 0.0028261 | 0.00070829 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_155-3_0_7_load_139 | 138 | 0.0031249 | 0.00078317 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 71 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_155-3_0_7_line_0 |  | 0 | 1 | 0.15339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_155-3_0_7_line_1 |  | 1 | 2 | 0.09333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_155-3_0_7_line_2 |  | 1 | 3 | 0.01128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_155-3_0_7_line_3 |  | 3 | 7 | 0.010959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_155-3_0_7_line_4 |  | 3 | 8 | 0.020285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_155-3_0_7_line_5 |  | 4 | 5 | 0.033368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_155-3_0_7_line_6 |  | 4 | 6 | 0.057938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_155-3_0_7_line_7 |  | 5 | 7 | 0.011153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_155-3_0_7_line_8 |  | 6 | 18 | 0.018816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_155-3_0_7_line_9 |  | 7 | 17 | 0.014195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_155-3_0_7_line_10 |  | 8 | 19 | 0.011208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_155-3_0_7_line_11 |  | 9 | 10 | 0.0072352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_155-3_0_7_line_12 |  | 9 | 11 | 0.14461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_155-3_0_7_line_13 |  | 10 | 28 | 0.099907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_155-3_0_7_line_14 |  | 11 | 16 | 0.038039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_155-3_0_7_line_15 |  | 11 | 17 | 0.096084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_155-3_0_7_line_16 |  | 12 | 13 | 0.099279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_155-3_0_7_line_17 |  | 12 | 14 | 0.19136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_155-3_0_7_line_18 |  | 12 | 15 | 0.12471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_155-3_0_7_line_19 |  | 13 | 29 | 0.0055143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_155-3_0_7_line_20 |  | 14 | 30 | 0.016561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_155-3_0_7_line_21 |  | 15 | 18 | 0.01859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_155-3_0_7_line_22 |  | 16 | 26 | 0.082625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_155-3_0_7_line_23 |  | 20 | 21 | 0.015639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_155-3_0_7_line_24 |  | 21 | 124 | 0.022692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_155-3_0_7_line_25 |  | 22 | 23 | 0.013636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_155-3_0_7_line_26 |  | 23 | 24 | 0.0087791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_155-3_0_7_line_27 |  | 24 | 25 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_155-3_0_7_line_28 |  | 25 | 114 | 0.01242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_155-3_0_7_line_29 |  | 25 | 124 | 0.018657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_155-3_0_7_line_30 |  | 26 | 27 | 0.060303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_155-3_0_7_line_31 |  | 27 | 31 | 0.024664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_155-3_0_7_line_32 |  | 28 | 48 | 0.0051162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_155-3_0_7_line_33 |  | 30 | 34 | 0.1194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_155-3_0_7_line_34 |  | 31 | 32 | 0.02554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_155-3_0_7_line_35 |  | 31 | 33 | 0.050695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_155-3_0_7_line_36 |  | 32 | 104 | 0.035278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_155-3_0_7_line_37 |  | 33 | 97 | 0.011153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_155-3_0_7_line_38 |  | 34 | 39 | 0.031314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_155-3_0_7_line_39 |  | 35 | 36 | 0.044083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_155-3_0_7_line_40 |  | 36 | 37 | 0.005656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_155-3_0_7_line_41 |  | 36 | 38 | 0.051849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_155-3_0_7_line_42 |  | 37 | 39 | 0.03404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_155-3_0_7_line_43 |  | 38 | 40 | 0.026073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_155-3_0_7_line_44 |  | 38 | 41 | 0.0086184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_155-3_0_7_line_45 |  | 40 | 42 | 0.011909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_155-3_0_7_line_46 |  | 41 | 43 | 0.069947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_155-3_0_7_line_47 |  | 43 | 44 | 0.020723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_155-3_0_7_line_48 |  | 44 | 45 | 0.10892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_155-3_0_7_line_49 |  | 45 | 46 | 0.011455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_155-3_0_7_line_50 |  | 46 | 47 | 0.084495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_155-3_0_7_line_51 |  | 49 | 50 | 0.082428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_155-3_0_7_line_52 |  | 49 | 51 | 0.052069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_155-3_0_7_line_53 |  | 49 | 52 | 0.028435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_155-3_0_7_line_54 |  | 50 | 53 | 0.025627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_155-3_0_7_line_55 |  | 51 | 54 | 0.02205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_155-3_0_7_line_56 |  | 52 | 55 | 0.0073688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_155-3_0_7_line_57 |  | 53 | 75 | 0.019254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_155-3_0_7_line_58 |  | 54 | 68 | 0.048159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_155-3_0_7_line_59 |  | 56 | 57 | 0.0095393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_155-3_0_7_line_60 |  | 56 | 58 | 0.069418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_155-3_0_7_line_61 |  | 58 | 62 | 0.028701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_155-3_0_7_line_62 |  | 58 | 63 | 0.0348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_155-3_0_7_line_63 |  | 58 | 64 | 0.021864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_155-3_0_7_line_64 |  | 59 | 60 | 0.022901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_155-3_0_7_line_65 |  | 59 | 61 | 0.020758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_155-3_0_7_line_66 |  | 60 | 97 | 0.036372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_155-3_0_7_line_67 |  | 61 | 98 | 0.003387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_155-3_0_7_line_68 |  | 62 | 92 | 0.055356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_155-3_0_7_line_69 |  | 62 | 93 | 0.020756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_155-3_0_7_line_70 |  | 63 | 65 | 0.019679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_155-3_0_7_line_71 |  | 63 | 66 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_155-3_0_7_line_72 |  | 66 | 96 | 0.021147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_155-3_0_7_line_73 |  | 67 | 68 | 0.024838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_155-3_0_7_line_74 |  | 69 | 70 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_155-3_0_7_line_75 |  | 69 | 71 | 0.013532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_155-3_0_7_line_76 |  | 70 | 109 | 0.0045356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_155-3_0_7_line_77 |  | 71 | 98 | 0.025282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_155-3_0_7_line_78 |  | 71 | 138 | 0.01693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_155-3_0_7_line_79 |  | 72 | 73 | 0.013233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_155-3_0_7_line_80 |  | 72 | 74 | 0.002367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_155-3_0_7_line_81 |  | 73 | 136 | 0.0028569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_155-3_0_7_line_82 |  | 74 | 120 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_155-3_0_7_line_83 |  | 75 | 110 | 0.047732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_155-3_0_7_line_84 |  | 75 | 108 | 0.000999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_155-3_0_7_line_85 |  | 76 | 77 | 0.017095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_155-3_0_7_line_86 |  | 77 | 80 | 0.021106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_155-3_0_7_line_87 |  | 77 | 81 | 0.029502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_155-3_0_7_line_88 |  | 78 | 79 | 0.019528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_155-3_0_7_line_89 |  | 79 | 80 | 0.025813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_155-3_0_7_line_90 |  | 79 | 82 | 0.025903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_155-3_0_7_line_91 |  | 80 | 83 | 0.011219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_155-3_0_7_line_92 |  | 81 | 84 | 0.020976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_155-3_0_7_line_93 |  | 81 | 85 | 0.0033794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_155-3_0_7_line_94 |  | 84 | 86 | 0.029121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_155-3_0_7_line_95 |  | 85 | 87 | 0.028638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_155-3_0_7_line_96 |  | 87 | 89 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_155-3_0_7_line_97 |  | 88 | 89 | 0.012469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_155-3_0_7_line_98 |  | 88 | 90 | 0.0181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_155-3_0_7_line_99 |  | 90 | 91 | 0.0089713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_155-3_0_7_line_100 |  | 91 | 99 | 0.024259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_155-3_0_7_line_101 |  | 92 | 118 | 0.018351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_155-3_0_7_line_102 |  | 93 | 117 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_155-3_0_7_line_103 |  | 94 | 95 | 0.019748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_155-3_0_7_line_104 |  | 95 | 117 | 0.023501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_155-3_0_7_line_105 |  | 96 | 103 | 0.020353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_155-3_0_7_line_106 |  | 99 | 100 | 0.013802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_155-3_0_7_line_107 |  | 99 | 101 | 0.030079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_155-3_0_7_line_108 |  | 100 | 102 | 0.015559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_155-3_0_7_line_109 |  | 101 | 103 | 0.032672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_155-3_0_7_line_110 |  | 104 | 107 | 0.00030862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_155-3_0_7_line_111 |  | 105 | 106 | 0.04593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_155-3_0_7_line_112 |  | 106 | 132 | 0.010981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_155-3_0_7_line_113 |  | 106 | 129 | 0.015148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_155-3_0_7_line_114 |  | 107 | 111 | 0.029433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_155-3_0_7_line_115 |  | 108 | 109 | 0.015971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_155-3_0_7_line_116 |  | 111 | 112 | 0.009576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_155-3_0_7_line_117 |  | 112 | 113 | 0.0020766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_155-3_0_7_line_118 |  | 113 | 114 | 0.017333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_155-3_0_7_line_119 |  | 115 | 116 | 0.010077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_155-3_0_7_line_120 |  | 115 | 117 | 0.0021537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_155-3_0_7_line_121 |  | 118 | 119 | 0.010641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_155-3_0_7_line_122 |  | 119 | 120 | 0.01553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_155-3_0_7_line_123 |  | 121 | 122 | 0.020967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_155-3_0_7_line_124 |  | 121 | 123 | 0.071283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_155-3_0_7_line_125 |  | 123 | 134 | 0.02304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_155-3_0_7_line_126 |  | 123 | 135 | 0.011032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_155-3_0_7_line_127 |  | 124 | 125 | 0.026464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_155-3_0_7_line_128 |  | 125 | 126 | 0.023902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_155-3_0_7_line_129 |  | 126 | 127 | 0.022009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_155-3_0_7_line_130 |  | 127 | 128 | 0.012346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_155-3_0_7_line_131 |  | 128 | 129 | 0.0089985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_155-3_0_7_line_132 |  | 130 | 131 | 0.029665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_155-3_0_7_line_133 |  | 131 | 135 | 0.014958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_155-3_0_7_line_134 |  | 132 | 133 | 0.0038728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_155-3_0_7_line_135 |  | 133 | 134 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_155-3_0_7_line_136 |  | 136 | 137 | 0.040642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_155-3_0_7_line_137 |  | 137 | 138 | 0.0019899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_155-3_0_7_trafo_142 | 0.63 MVA 20/0.4 kV | 139 | 71 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2696255.657 | 1234652.8077 | 2696264.7307 | 1234657.2023 | 2696269.3572 | 1234658.5449 | 2696273.2452 | 1234659.2084 | 2696276.2812 | 1234658.2569 | 2696279.7637 | 1234656.3786 | 2696289.1277 | 1234649.8811 | 2696298.7164 | 1234643.0648 | 2696322.1981 | 1234624.9653 | 2696348.6992 | 1234599.0203 | 2696366.2936 | 1234582.649 | 2696374.0004 | 1234578.4487 | 2696378.6011 | 1234577.4971
1 | 2696255.657 | 1234652.8077 | 2696273.0924 | 1234633.6093 | 2696292.3506 | 1234609.8594 | 2696309.1283 | 1234577.0849
2 | 2696255.657 | 1234652.8077 | 2696247.8334 | 1234660.9536
3 | 2696240.7256 | 1234669.3113 | 2696247.8334 | 1234660.9536
4 | 2696247.8334 | 1234660.9536 | 2696235.399 | 1234651.8455 | 2696232.2121 | 1234648.1614
5 | 2696266.0456 | 1234705.915 | 2696253.8264 | 1234687.2812 | 2696247.2927 | 1234678.326
6 | 2696266.0456 | 1234705.915 | 2696275.8012 | 1234720.5505 | 2696274.0516 | 1234739.7474 | 2696273.4811 | 1234745.9872 | 2696282.2031 | 1234757.9522
7 | 2696240.7256 | 1234669.3113 | 2696241.6513 | 1234670.5828 | 2696242.4806 | 1234671.7304 | 2696247.2927 | 1234678.326
8 | 2696282.2031 | 1234757.9522 | 2696285.9817 | 1234763.1357 | 2696275.7854 | 1234770.1942
9 | 2696240.7256 | 1234669.3113 | 2696235.3159 | 1234676.1287 | 2696230.5169 | 1234678.799
10 | 2696232.2121 | 1234648.1614 | 2696225.6047 | 1234640.5231 | 2696224.88 | 1234639.6841
11 | 2696051.4159 | 1234831.1009 | 2696045.659 | 1234835.4834
12 | 2696051.4159 | 1234831.1009 | 2696072.335 | 1234810.346 | 2696118.9153 | 1234760.2401 | 2696151.3126 | 1234726.317
13 | 2695966.2659 | 1234896.13 | 2695979.1324 | 1234886.129 | 2696030.5915 | 1234846.9538 | 2696045.659 | 1234835.4834
14 | 2696151.3126 | 1234726.317 | 2696127.7374 | 1234704.4195 | 2696122.7052 | 1234701.4112
15 | 2696151.3126 | 1234726.317 | 2696177.7584 | 1234697.635 | 2696183.595 | 1234692.5035 | 2696191.2825 | 1234688.0691 | 2696213.3821 | 1234682.3559 | 2696228.8302 | 1234679.7375 | 2696230.5169 | 1234678.799
16 | 2696209.9623 | 1234894.3677 | 2696206.6066 | 1234901.0405 | 2696198.2394 | 1234924.0776 | 2696177.5188 | 1234980.7172 | 2696175.017 | 1234987.2433
17 | 2696209.9623 | 1234894.3677 | 2696270.8041 | 1234934.4603 | 2696277.9548 | 1234940.7141 | 2696282.4474 | 1234947.4919 | 2696307.2489 | 1234992.6381 | 2696308.8653 | 1234997.5235 | 2696309.3709 | 1235005.5598 | 2696308.6735 | 1235009.3513 | 2696302.959 | 1235041.1438
18 | 2696209.9623 | 1234894.3677 | 2696242.6605 | 1234808.7008 | 2696250.1752 | 1234793.9116 | 2696261.7019 | 1234782.2033
19 | 2696173.1073 | 1234992.4138 | 2696173.3376 | 1234991.6242 | 2696175.017 | 1234987.2433
20 | 2696300.8143 | 1235057.5261 | 2696300.9852 | 1235052.1249 | 2696302.959 | 1235041.1438
21 | 2696275.7854 | 1234770.1942 | 2696268.6864 | 1234775.1087 | 2696261.7019 | 1234782.2033
22 | 2696122.7052 | 1234701.4112 | 2696111.2198 | 1234694.5451 | 2696080.9219 | 1234671.2381 | 2696071.3659 | 1234663.8893 | 2696056.7824 | 1234651.7672
23 | 2696090.9427 | 1234468.0246 | 2696103.5446 | 1234458.7641
24 | 2696072.6591 | 1234481.465 | 2696084.0828 | 1234473.0658 | 2696090.9427 | 1234468.0246
25 | 2696082.6491 | 1234524.7395 | 2696081.3638 | 1234523.2031 | 2696074.8135 | 1234513.5895
26 | 2696069.8702 | 1234506.3344 | 2696074.8135 | 1234513.5895
27 | 2696063.6676 | 1234497.2313 | 2696069.8702 | 1234506.3344
28 | 2696063.6676 | 1234497.2313 | 2696061.3623 | 1234504.9552 | 2696059.1679 | 1234508.7215
29 | 2696063.6676 | 1234497.2313 | 2696064.0875 | 1234493.2685 | 2696067.286 | 1234487.427 | 2696072.6591 | 1234481.465
30 | 2696007.2868 | 1234620.6609 | 2696031.8106 | 1234641.4223 | 2696046.4985 | 1234643.2166 | 2696048.0372 | 1234644.498 | 2696056.7824 | 1234651.7672
31 | 2695988.3495 | 1234604.86 | 2696005.6197 | 1234619.2496 | 2696007.2868 | 1234620.6609
32 | 2695962.2265 | 1234899.2698 | 2695966.2659 | 1234896.13
33 | 2696351.0543 | 1235165.8425 | 2696341.2354 | 1235144.9012 | 2696336.3675 | 1235135.1373 | 2696325.5342 | 1235110.9328 | 2696310.398 | 1235078.9861 | 2696303.6902 | 1235065.5008 | 2696300.8143 | 1235057.5261
34 | 2695988.3495 | 1234604.86 | 2695990.1076 | 1234602.4088 | 2696003.8123 | 1234584.5343
35 | 2695957.7254 | 1234645.2507 | 2695972.8623 | 1234627.2263 | 2695988.3495 | 1234604.86
36 | 2696003.8123 | 1234584.5343 | 2696014.3599 | 1234570.7774 | 2696024.6463 | 1234556.0762
37 | 2695957.7254 | 1234645.2507 | 2695949.8361 | 1234653.1342
38 | 2696351.0543 | 1235165.8425 | 2696340.9441 | 1235168.9253 | 2696333.4297 | 1235174.3742 | 2696324.8481 | 1235181.9725
39 | 2696295.2039 | 1235208.3686 | 2696292.6012 | 1235222.2922 | 2696286.0658 | 1235230.8704 | 2696285.9178 | 1235238.1289 | 2696295.3588 | 1235245.3309
40 | 2696295.2039 | 1235208.3686 | 2696299.3218 | 1235204.4913
41 | 2696257.26 | 1235243.6798 | 2696263.1292 | 1235238.838 | 2696295.2039 | 1235208.3686
42 | 2696324.8481 | 1235181.9725 | 2696314.2527 | 1235191.3536 | 2696300.3004 | 1235203.5698 | 2696299.3218 | 1235204.4913
43 | 2696246.9125 | 1235230.1245 | 2696253.7616 | 1235233.0153 | 2696263.1292 | 1235238.838 | 2696257.26 | 1235243.6798
44 | 2696257.26 | 1235243.6798 | 2696251.3511 | 1235249.9538
45 | 2696246.9125 | 1235230.1245 | 2696246.2405 | 1235218.2349
46 | 2696251.3511 | 1235249.9538 | 2696250.8132 | 1235250.5249 | 2696233.1353 | 1235268.4518 | 2696216.8237 | 1235284.7441 | 2696201.4499 | 1235298.9479
47 | 2696201.4499 | 1235298.9479 | 2696186.2291 | 1235313.0103
48 | 2696186.2291 | 1235313.0103 | 2696179.223 | 1235319.4832 | 2696141.2296 | 1235349.0568 | 2696117.0154 | 1235367.7233 | 2696100.4337 | 1235380.0525
49 | 2696091.2415 | 1235386.8873 | 2696100.4337 | 1235380.0525
50 | 2696091.2415 | 1235386.8873 | 2696086.2099 | 1235380.6791 | 2696083.063 | 1235377.2813 | 2696080.4574 | 1235374.5816 | 2696076.7025 | 1235370.8626 | 2696074.5524 | 1235369.0153 | 2696072.5336 | 1235367.4704 | 2696070.056 | 1235365.7513 | 2696067.1832 | 1235364.1259 | 2696063.9312 | 1235362.5388 | 2696056.8213 | 1235359.3994 | 2696040.87 | 1235352.0584 | 2696031.8919 | 1235346.9539 | 2696021.6744 | 1235340.9228
51 | 2695938.7825 | 1234819.206 | 2695981.1084 | 1234748.4152
52 | 2695938.7825 | 1234819.206 | 2695905.9135 | 1234829.9501 | 2695889.1766 | 1234835.021
53 | 2695938.7825 | 1234819.206 | 2695951.1845 | 1234816.2708 | 2695958.128 | 1234814.7596 | 2695966.6571 | 1234813.7905
54 | 2695981.1084 | 1234748.4152 | 2695987.2985 | 1234738.7303 | 2695988.0339 | 1234727.8898 | 2695985.8887 | 1234725.4254
55 | 2695869.457 | 1234844.8728 | 2695869.457 | 1234844.8728 | 2695888.736 | 1234835.1545 | 2695889.1766 | 1234835.021
56 | 2695973.9788 | 1234812.9586 | 2695966.6571 | 1234813.7905
57 | 2695972.8217 | 1234711.71 | 2695977.2338 | 1234718.3528 | 2695983.0171 | 1234722.1267 | 2695985.8887 | 1234725.4254
58 | 2695829.9476 | 1234872.4103 | 2695869.457 | 1234844.8728
59 | 2695804.2044 | 1234749.0278 | 2695804.5269 | 1234744.0516 | 2695802.6104 | 1234739.922
60 | 2695763.0672 | 1234791.3069 | 2695761.1146 | 1234787.0501 | 2695759.082 | 1234782.5919 | 2695763.0061 | 1234780.5425 | 2695777.7449 | 1234772.1183 | 2695796.9638 | 1234761.4424 | 2695803.3758 | 1234757.2205 | 2695802.2537 | 1234754.9785 | 2695804.2044 | 1234749.0278
61 | 2695763.0672 | 1234791.3069 | 2695769.2972 | 1234788.5053 | 2695773.3566 | 1234787.4588 | 2695777.3653 | 1234786.267 | 2695789.2941 | 1234779.8101
62 | 2695742.1901 | 1234770.5553 | 2695741.8642 | 1234775.2758 | 2695748.0903 | 1234781.6363 | 2695751.0295 | 1234783.3961 | 2695756.4961 | 1234783.3397 | 2695759.082 | 1234782.5919 | 2695761.1146 | 1234787.0501 | 2695763.0672 | 1234791.3069
63 | 2695763.0672 | 1234791.3069 | 2695756.9994 | 1234794.8451 | 2695756.3705 | 1234800.5169 | 2695755.913 | 1234809.6385
64 | 2695924.1078 | 1234678.8438 | 2695906.0882 | 1234693.0411
65 | 2695906.0882 | 1234693.0411 | 2695916.5329 | 1234702.5612 | 2695920.1635 | 1234706.0334 | 2695921.3884 | 1234707.0651 | 2695921.3884 | 1234707.0651
66 | 2695924.1078 | 1234678.8438 | 2695949.8361 | 1234653.1342
67 | 2695919.1519 | 1234709.6086 | 2695921.3884 | 1234707.0651
68 | 2695789.2941 | 1234779.8101 | 2695794.7507 | 1234776.6179 | 2695801.8582 | 1234771.0506 | 2695810.9633 | 1234764.5927 | 2695820.3976 | 1234758.8517 | 2695835.8876 | 1234749.8615
69 | 2695789.2941 | 1234779.8101 | 2695790.8023 | 1234783.4593 | 2695790.9439 | 1234790.1665 | 2695796.0452 | 1234798.8819
70 | 2695742.1901 | 1234770.5553 | 2695759.9153 | 1234761.9012
71 | 2695742.1901 | 1234770.5553 | 2695730.6599 | 1234760.2731 | 2695728.3789 | 1234758.5378
72 | 2695713.8725 | 1234744.0908 | 2695714.0776 | 1234746.3958 | 2695717.4603 | 1234750.2309 | 2695728.3789 | 1234758.5378
73 | 2695829.9476 | 1234872.4103 | 2695825.0814 | 1234875.802 | 2695809.0521 | 1234885.8283
74 | 2695946.7027 | 1234734.7607 | 2695957.2827 | 1234724.8769
75 | 2695946.7027 | 1234734.7607 | 2695945.519 | 1234735.8646 | 2695936.9551 | 1234727.5536
76 | 2695960.597 | 1234721.7807 | 2695957.2827 | 1234724.8769
77 | 2695936.9551 | 1234727.5536 | 2695928.1822 | 1234719.0502 | 2695927.6016 | 1234718.4404 | 2695921.6012 | 1234712.1722 | 2695920.8866 | 1234711.4157 | 2695919.1519 | 1234709.6086
78 | 2695936.9551 | 1234727.5536 | 2695923.9862 | 1234738.4359
79 | 2695878.5055 | 1234758.9334 | 2695889.3775 | 1234751.3898
80 | 2695878.5055 | 1234758.9334 | 2695876.4942 | 1234760.1907
81 | 2695891.7247 | 1234749.7612 | 2695889.3775 | 1234751.3898
82 | 2695876.4942 | 1234760.1907 | 2695864.1589 | 1234768.1678
83 | 2695972.8217 | 1234711.71 | 2695973.3774 | 1234711.0518 | 2696004.6726 | 1234676.1598
84 | 2695972.8217 | 1234711.71 | 2695972.2674 | 1234710.8782
85 | 2695898.2754 | 1234644.7685 | 2695913.4267 | 1234636.8522
86 | 2695883.9223 | 1234658.3469 | 2695886.3711 | 1234651.0922 | 2695898.2754 | 1234644.7685
87 | 2695898.2754 | 1234644.7685 | 2695889.2855 | 1234640.7872 | 2695879.9145 | 1234640.2467 | 2695871.6422 | 1234634.0198
88 | 2695895.5718 | 1234681.3962 | 2695912.1582 | 1234671.0901
89 | 2695895.5718 | 1234681.3962 | 2695883.9223 | 1234658.3469
90 | 2695895.5718 | 1234681.3962 | 2695889.5212 | 1234692.7625 | 2695878.3427 | 1234699.4503
91 | 2695883.9223 | 1234658.3469 | 2695876.351 | 1234666.6263
92 | 2695888.2921 | 1234621.2012 | 2695871.6422 | 1234634.0198
93 | 2695871.6422 | 1234634.0198 | 2695868.964 | 1234636.0808
94 | 2695888.2921 | 1234621.2012 | 2695882.4239 | 1234613.7677 | 2695874.5822 | 1234603.845 | 2695875.5375 | 1234600.0021 | 2695877.9825 | 1234598.1401
95 | 2695868.964 | 1234636.0808 | 2695846.2688 | 1234653.5464
96 | 2695835.5304 | 1234661.8104 | 2695846.2688 | 1234653.5464
97 | 2695825.6487 | 1234669.4151 | 2695835.5304 | 1234661.8104
98 | 2695825.6487 | 1234669.4151 | 2695810.7423 | 1234679.6825
99 | 2695810.7423 | 1234679.6825 | 2695803.3541 | 1234684.7715
100 | 2695783.3755 | 1234698.5328 | 2695803.3541 | 1234684.7715
101 | 2695835.8876 | 1234749.8615 | 2695845.8533 | 1234765.2712
102 | 2695805.0288 | 1234816.6463 | 2695800.0571 | 1234805.736 | 2695796.0452 | 1234798.8819
103 | 2695785.0385 | 1234829.0001 | 2695777.634 | 1234833.4393 | 2695767.579 | 1234838.175
104 | 2695805.0288 | 1234816.6463 | 2695793.419 | 1234823.9757 | 2695785.0385 | 1234829.0001
105 | 2695713.8725 | 1234744.0908 | 2695730.8946 | 1234732.9332
106 | 2695783.3755 | 1234698.5328 | 2695774.8636 | 1234691.2013 | 2695772.8672 | 1234689.5858
107 | 2695783.3755 | 1234698.5328 | 2695758.2195 | 1234715.0221
108 | 2695760.5225 | 1234680.1176 | 2695770.6714 | 1234687.809 | 2695772.8672 | 1234689.5858
109 | 2695730.8946 | 1234732.9332 | 2695758.2195 | 1234715.0221
110 | 2696024.8232 | 1234555.8233 | 2696024.6463 | 1234556.0762
111 | 2695982.5747 | 1234510.6197 | 2695992.4316 | 1234519.0518 | 2695975.9087 | 1234545.5266 | 2695974.8739 | 1234546.9391
112 | 2695982.5747 | 1234510.6197 | 2695974.2534 | 1234503.4541
113 | 2695982.5747 | 1234510.6197 | 2695995.2162 | 1234502.2733
114 | 2696024.8232 | 1234555.8233 | 2696041.6969 | 1234531.7075
115 | 2695972.2674 | 1234710.8782 | 2695960.597 | 1234721.7807
116 | 2696047.1868 | 1234523.8614 | 2696041.6969 | 1234531.7075
117 | 2696048.3773 | 1234522.1599 | 2696047.1868 | 1234523.8614
118 | 2696059.1679 | 1234508.7215 | 2696057.7104 | 1234511.223 | 2696052.3021 | 1234516.5506 | 2696048.3773 | 1234522.1599
119 | 2695812.1704 | 1234807.0767 | 2695807.7822 | 1234814.9006 | 2695806.8476 | 1234815.4931
120 | 2695805.0288 | 1234816.6463 | 2695806.8476 | 1234815.4931
121 | 2695851.6317 | 1234774.2062 | 2695845.8533 | 1234765.2712
122 | 2695851.6317 | 1234774.2062 | 2695852.5724 | 1234775.6607 | 2695864.1589 | 1234768.1678
123 | 2695871.6117 | 1234466.1516 | 2695868.8907 | 1234468.2203 | 2695860.9969 | 1234476.9883 | 2695856.1026 | 1234480.0077
124 | 2695939.4425 | 1234476.1091 | 2695934.0165 | 1234468.9495 | 2695875.2362 | 1234466.7327 | 2695871.6117 | 1234466.1516
125 | 2695939.4425 | 1234476.1091 | 2695945.4245 | 1234484.0003 | 2695956.8984 | 1234490.4004
126 | 2695939.4425 | 1234476.1091 | 2695949.7689 | 1234472.2277
127 | 2696051.3331 | 1234466.4648 | 2696057.8483 | 1234468.9942 | 2696063.4898 | 1234472.1878 | 2696072.6591 | 1234481.465
128 | 2696051.3331 | 1234466.4648 | 2696042.4475 | 1234476.6176 | 2696033.23 | 1234481.4555
129 | 2696033.23 | 1234481.4555 | 2696013.7424 | 1234491.6836
130 | 2696002.9619 | 1234497.6932 | 2696008.2486 | 1234494.5671 | 2696013.7424 | 1234491.6836
131 | 2696002.9619 | 1234497.6932 | 2695995.2162 | 1234502.2733
132 | 2695990.5716 | 1234454.3384 | 2695971.4561 | 1234464.0838 | 2695963.7716 | 1234466.9689
133 | 2695949.7689 | 1234472.2277 | 2695953.5109 | 1234470.8212 | 2695963.7716 | 1234466.9689
134 | 2695971.3187 | 1234500.927 | 2695974.2534 | 1234503.4541
135 | 2695971.3187 | 1234500.927 | 2695971.2179 | 1234500.8403 | 2695963.1615 | 1234493.8939 | 2695956.8984 | 1234490.4004
136 | 2695891.7247 | 1234749.7612 | 2695901.5272 | 1234742.9598 | 2695902.6472 | 1234742.0438 | 2695903.4901 | 1234741.4125 | 2695910.732 | 1234749.5576 | 2695922.4619 | 1234739.715
137 | 2695923.9862 | 1234738.4359 | 2695922.4619 | 1234739.715

## bus_geodata
| x | y | coords
0 | 2696378.6011 | 1234577.4971
1 | 2696255.657 | 1234652.8077
2 | 2696309.1283 | 1234577.0849
3 | 2696247.8334 | 1234660.9536
4 | 2696266.0456 | 1234705.915
5 | 2696247.2927 | 1234678.326
6 | 2696282.2031 | 1234757.9522
7 | 2696240.7256 | 1234669.3113
8 | 2696232.2121 | 1234648.1614
9 | 2696051.4159 | 1234831.1009
10 | 2696045.659 | 1234835.4834
11 | 2696151.3126 | 1234726.317
12 | 2696209.9623 | 1234894.3677
13 | 2696175.017 | 1234987.2433
14 | 2696302.959 | 1235041.1438
15 | 2696261.7019 | 1234782.2033
16 | 2696122.7052 | 1234701.4112
17 | 2696230.5169 | 1234678.799
18 | 2696275.7854 | 1234770.1942
19 | 2696224.88 | 1234639.6841
20 | 2696103.5446 | 1234458.7641
21 | 2696090.9427 | 1234468.0246
22 | 2696082.6491 | 1234524.7395
23 | 2696074.8135 | 1234513.5895
24 | 2696069.8702 | 1234506.3344
25 | 2696063.6676 | 1234497.2313
26 | 2696056.7824 | 1234651.7672
27 | 2696007.2868 | 1234620.6609
28 | 2695966.2659 | 1234896.13
29 | 2696173.1073 | 1234992.4138
30 | 2696300.8143 | 1235057.5261
31 | 2695988.3495 | 1234604.86
32 | 2696003.8123 | 1234584.5343
33 | 2695957.7254 | 1234645.2507
34 | 2696351.0543 | 1235165.8425
35 | 2696295.3588 | 1235245.3309
36 | 2696295.2039 | 1235208.3686
37 | 2696299.3218 | 1235204.4913
38 | 2696257.26 | 1235243.6798
39 | 2696324.8481 | 1235181.9725
40 | 2696246.9125 | 1235230.1245
41 | 2696251.3511 | 1235249.9538
42 | 2696246.2405 | 1235218.2349
43 | 2696201.4499 | 1235298.9479
44 | 2696186.2291 | 1235313.0103
45 | 2696100.4337 | 1235380.0525
46 | 2696091.2415 | 1235386.8873
47 | 2696021.6744 | 1235340.9228
48 | 2695962.2265 | 1234899.2698
49 | 2695938.7825 | 1234819.206
50 | 2695981.1084 | 1234748.4152
51 | 2695889.1766 | 1234835.021
52 | 2695966.6571 | 1234813.7905
53 | 2695985.8887 | 1234725.4254
54 | 2695869.457 | 1234844.8728
55 | 2695973.9788 | 1234812.9586
56 | 2695804.2044 | 1234749.0278
57 | 2695802.6104 | 1234739.922
58 | 2695763.0672 | 1234791.3069
59 | 2695906.0882 | 1234693.0411
60 | 2695924.1078 | 1234678.8438
61 | 2695921.3884 | 1234707.0651
62 | 2695789.2941 | 1234779.8101
63 | 2695742.1901 | 1234770.5553
64 | 2695755.913 | 1234809.6385
65 | 2695759.9153 | 1234761.9012
66 | 2695728.3789 | 1234758.5378
67 | 2695809.0521 | 1234885.8283
68 | 2695829.9476 | 1234872.4103
69 | 2695946.7027 | 1234734.7607
70 | 2695957.2827 | 1234724.8769
71 | 2695936.9551 | 1234727.5536
72 | 2695878.5055 | 1234758.9334
73 | 2695889.3775 | 1234751.3898
74 | 2695876.4942 | 1234760.1907
75 | 2695972.8217 | 1234711.71
76 | 2695913.4267 | 1234636.8522
77 | 2695898.2754 | 1234644.7685
78 | 2695912.1582 | 1234671.0901
79 | 2695895.5718 | 1234681.3962
80 | 2695883.9223 | 1234658.3469
81 | 2695871.6422 | 1234634.0198
82 | 2695878.3427 | 1234699.4503
83 | 2695876.351 | 1234666.6263
84 | 2695888.2921 | 1234621.2012
85 | 2695868.964 | 1234636.0808
86 | 2695877.9825 | 1234598.1401
87 | 2695846.2688 | 1234653.5464
88 | 2695825.6487 | 1234669.4151
89 | 2695835.5304 | 1234661.8104
90 | 2695810.7423 | 1234679.6825
91 | 2695803.3541 | 1234684.7715
92 | 2695835.8876 | 1234749.8615
93 | 2695796.0452 | 1234798.8819
94 | 2695767.579 | 1234838.175
95 | 2695785.0385 | 1234829.0001
96 | 2695713.8725 | 1234744.0908
97 | 2695949.8361 | 1234653.1342
98 | 2695919.1519 | 1234709.6086
99 | 2695783.3755 | 1234698.5328
100 | 2695772.8672 | 1234689.5858
101 | 2695758.2195 | 1234715.0221
102 | 2695760.5225 | 1234680.1176
103 | 2695730.8946 | 1234732.9332
104 | 2696024.6463 | 1234556.0762
105 | 2695974.8739 | 1234546.9391
106 | 2695982.5747 | 1234510.6197
107 | 2696024.8232 | 1234555.8233
108 | 2695972.2674 | 1234710.8782
109 | 2695960.597 | 1234721.7807
110 | 2696004.6726 | 1234676.1598
111 | 2696041.6969 | 1234531.7075
112 | 2696047.1868 | 1234523.8614
113 | 2696048.3773 | 1234522.1599
114 | 2696059.1679 | 1234508.7215
115 | 2695806.8476 | 1234815.4931
116 | 2695812.1704 | 1234807.0767
117 | 2695805.0288 | 1234816.6463
118 | 2695845.8533 | 1234765.2712
119 | 2695851.6317 | 1234774.2062
120 | 2695864.1589 | 1234768.1678
121 | 2695871.6117 | 1234466.1516
122 | 2695856.1026 | 1234480.0077
123 | 2695939.4425 | 1234476.109
124 | 2696072.6591 | 1234481.465
125 | 2696051.3331 | 1234466.4648
126 | 2696033.23 | 1234481.4555
127 | 2696013.7424 | 1234491.6836
128 | 2696002.9619 | 1234497.6932
129 | 2695995.2162 | 1234502.2733
130 | 2695990.5716 | 1234454.3384
131 | 2695963.7716 | 1234466.9689
132 | 2695974.2534 | 1234503.4541
133 | 2695971.3187 | 1234500.927
134 | 2695956.8984 | 1234490.4004
135 | 2695949.7689 | 1234472.2277
136 | 2695891.7247 | 1234749.7612
137 | 2695922.4619 | 1234739.715
138 | 2695923.9862 | 1234738.4359
139 | 2695946.7027 | 1234734.7607

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9864 | -0.26065 | 0.0056034 | 0.0014043
1 | 0.98719 | -0.24526 | 0 | 0
2 | 0.98651 | -0.25846 | 0.0079032 | 0.0019807
3 | 0.98733 | -0.24253 | 0 | 0
4 | 0.98695 | -0.24974 | 0 | 0
5 | 0.98743 | -0.24057 | 0.0023218 | 0.0005819
6 | 0.98612 | -0.26568 | 0.001179 | 0.00029548
7 | 0.98754 | -0.23837 | 0 | 0
8 | 0.98719 | -0.24533 | 0.0029615 | 0.00074223
9 | 0.98886 | -0.21305 | 0 | 0
10 | 0.98883 | -0.21363 | 0.0007977 | 0.00019992
11 | 0.98946 | -0.20153 | 0 | 0
12 | 0.98196 | -0.34619 | 0 | 0
13 | 0.98188 | -0.3477 | 0.00040127 | 0.00010057
14 | 0.97725 | -0.43788 | 0.00088092 | 0.00022078
15 | 0.98512 | -0.28501 | 0.00081719 | 0.00020481
16 | 0.99017 | -0.18779 | 0.0041385 | 0.0010372
17 | 0.98778 | -0.23379 | 0.0021806 | 0.00054652
18 | 0.98561 | -0.27565 | 0.0014999 | 0.00037591
19 | 0.98714 | -0.24628 | 0.0047455 | 0.0011893
20 | 0.98894 | -0.21215 | 0.00048604 | 0.00012181
21 | 0.98894 | -0.21201 | 0.0014124 | 0.00035398
22 | 0.98929 | -0.2054 | 0.0012711 | 0.00031858
23 | 0.9893 | -0.20509 | 0.0013737 | 0.00034428
24 | 0.98932 | -0.20468 | 0.0022163 | 0.00055545
25 | 0.98937 | -0.20372 | 0 | 0
26 | 0.99183 | -0.15597 | 0.0059999 | 0.0015037
27 | 0.99314 | -0.13068 | 0.0041612 | 0.0010429
28 | 0.9885 | -0.22016 | 0.0016945 | 0.00042467
29 | 0.98188 | -0.34775 | 0.00043818 | 0.00010982
30 | 0.97686 | -0.44559 | 0 | 0
31 | 0.99372 | -0.11976 | 0 | 0
32 | 0.99271 | -0.13916 | 0.0029801 | 0.0007469
33 | 0.99555 | -0.084549 | 0 | 0
34 | 0.97402 | -0.50134 | 0 | 0
35 | 0.97208 | -0.53961 | 0.0084102 | 0.0021078
36 | 0.97243 | -0.53277 | 0 | 0
37 | 0.97253 | -0.53062 | 0.0027173 | 0.00068101
38 | 0.97184 | -0.54441 | 0 | 0
39 | 0.97327 | -0.51602 | 0.0021841 | 0.00054739
40 | 0.97178 | -0.54561 | 0 | 0
41 | 0.97176 | -0.54595 | 0.0031469 | 0.00078868
42 | 0.97175 | -0.54616 | 0.0024932 | 0.00062484
43 | 0.97133 | -0.55439 | 0.0018818 | 0.00047162
44 | 0.97124 | -0.55617 | 0.0024558 | 0.00061548
45 | 0.97102 | -0.56058 | 0.0013104 | 0.00032842
46 | 0.97101 | -0.56076 | 0 | 0
47 | 0.97094 | -0.56213 | 0.00087498 | 0.00021929
48 | 0.98849 | -0.22034 | 0.001972 | 0.00049424
49 | 0.9974 | -0.049988 | 0 | 0
50 | 0.9982 | -0.034657 | 0 | 0
51 | 0.99712 | -0.055451 | 0.0012208 | 0.00030597
52 | 0.99728 | -0.052298 | 0.0025223 | 0.00063216
53 | 0.99845 | -0.029894 | 0.0073674 | 0.0018464
54 | 0.99702 | -0.057293 | 0.0014991 | 0.0003757
55 | 0.99727 | -0.052571 | 0.0021129 | 0.00052954
56 | 0.98759 | -0.23672 | 0 | 0
57 | 0.98757 | -0.23713 | 0.0023745 | 0.0005951
58 | 0.98774 | -0.23378 | 0 | 0
59 | 0.99814 | -0.035337 | 0 | 0
60 | 0.9973 | -0.051343 | 0 | 0
61 | 0.9989 | -0.020852 | 0.0031184 | 0.00078154
62 | 0.98906 | -0.2084 | 0 | 0
63 | 0.98623 | -0.26294 | 0 | 0
64 | 0.98763 | -0.23603 | 0.0057669 | 0.0014453
65 | 0.98595 | -0.26848 | 0.015694 | 0.0039334
66 | 0.98553 | -0.27661 | 0.0051015 | 0.0012786
67 | 0.99683 | -0.060936 | 0.0020357 | 0.0005102
68 | 0.99688 | -0.060049 | 0.0012264 | 0.00030737
69 | 0.99963 | -0.0070508 | 0 | 0
70 | 0.99924 | -0.0146 | 0.0027834 | 0.00069759
71 | 1 | 0 | -0.36793 | -0.093673
72 | 0.99536 | -0.087974 | 0 | 0
73 | 0.99612 | -0.073428 | 0.0063145 | 0.0015826
74 | 0.99522 | -0.090578 | 0 | 0
75 | 0.99876 | -0.023839 | 0 | 0
76 | 0.97404 | -0.501 | 0.004638 | 0.0011624
77 | 0.97411 | -0.49954 | 0 | 0
78 | 0.97305 | -0.52045 | 0.0047716 | 0.0011959
79 | 0.97314 | -0.51873 | 0 | 0
80 | 0.97354 | -0.5107 | 0 | 0
81 | 0.97503 | -0.48146 | 0 | 0
82 | 0.97284 | -0.52452 | 0.012139 | 0.0030424
83 | 0.97342 | -0.51314 | 0.011847 | 0.0029691
84 | 0.97482 | -0.48555 | 0 | 0
85 | 0.97517 | -0.47873 | 0.0084338 | 0.0021137
86 | 0.97453 | -0.49122 | 0.010622 | 0.002662
87 | 0.97656 | -0.45124 | 0.0051152 | 0.001282
88 | 0.97802 | -0.42278 | 0 | 0
89 | 0.97729 | -0.43699 | 0.0049479 | 0.0012401
90 | 0.97907 | -0.40218 | 0.007994 | 0.0020035
91 | 0.97966 | -0.39068 | 0.027935 | 0.0070011
92 | 0.99196 | -0.15288 | 0 | 0
93 | 0.98867 | -0.21606 | 0.0060955 | 0.0015277
94 | 0.9882 | -0.22524 | 0.0034332 | 0.00086045
95 | 0.98826 | -0.22403 | 0.0031945 | 0.00080062
96 | 0.98474 | -0.29177 | 0 | 0
97 | 0.99596 | -0.07682 | 0.0014821 | 0.00037144
98 | 0.99903 | -0.018429 | 0.0024691 | 0.0006188
99 | 0.98188 | -0.3474 | 0 | 0
100 | 0.98178 | -0.34935 | 0.0019218 | 0.00048165
101 | 0.98287 | -0.32816 | 0.0047404 | 0.001188
102 | 0.98169 | -0.351 | 0.005871 | 0.0014714
103 | 0.98399 | -0.30638 | 0.0087352 | 0.0021892
104 | 0.99141 | -0.16416 | 0.0037955 | 0.00095123
105 | 0.98704 | -0.24895 | 0.002027 | 0.00050802
106 | 0.98713 | -0.24729 | 0 | 0
107 | 0.9914 | -0.16436 | 0.0018471 | 0.00046294
108 | 0.99878 | -0.023421 | 0 | 0
109 | 0.99913 | -0.016746 | 0.0031694 | 0.00079433
110 | 0.9985 | -0.028789 | 0.0059327 | 0.0014869
111 | 0.99048 | -0.18231 | 0.0035256 | 0.0008836
112 | 0.9902 | -0.18756 | 0.00070989 | 0.00017791
113 | 0.99015 | -0.18867 | 0.0010367 | 0.00025983
114 | 0.98968 | -0.19765 | 0.001609 | 0.00040326
115 | 0.98839 | -0.22156 | 0.0016385 | 0.00041064
116 | 0.98833 | -0.22269 | 0.0063335 | 0.0015873
117 | 0.9884 | -0.22125 | 0 | 0
118 | 0.99291 | -0.13454 | 0.0063836 | 0.0015999
119 | 0.99349 | -0.12353 | 0.0078375 | 0.0019643
120 | 0.99437 | -0.10676 | 0.0039778 | 0.00099693
121 | 0.98644 | -0.26077 | 0 | 0
122 | 0.98638 | -0.26194 | 0.0031036 | 0.00077783
123 | 0.98664 | -0.25681 | 0 | 0
124 | 0.98898 | -0.21124 | 0 | 0
125 | 0.98848 | -0.22102 | 0 | 0
126 | 0.98803 | -0.22986 | 0.0021035 | 0.00052719
127 | 0.98765 | -0.23718 | 0.0012224 | 0.00030636
128 | 0.98745 | -0.24102 | 0.0012648 | 0.000317
129 | 0.98732 | -0.24361 | 0.0025754 | 0.00064546
130 | 0.98652 | -0.2592 | 0.0013081 | 0.00032784
131 | 0.98656 | -0.2585 | 0.0011498 | 0.00028818
132 | 0.98701 | -0.24955 | 0.00087058 | 0.00021819
133 | 0.98698 | -0.25029 | 0.0010862 | 0.00027223
134 | 0.98682 | -0.25336 | 0.0012191 | 0.00030552
135 | 0.98659 | -0.25784 | 0.0027835 | 0.00069761
136 | 0.99629 | -0.070185 | 0.0063747 | 0.0015976
137 | 0.9988 | -0.02266 | 0.0028261 | 0.00070829
138 | 0.99892 | -0.020307 | 0.0031249 | 0.00078317
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0056034 | -0.0014043 | 0.0056075 | 0.001405 | 4.1096e-06 | 6.706e-07 | 0.0084529 | 0.0084522 | 0.0084529 | 0.9864 | -0.26065 | 0.98719 | -0.24526 | 2.3222
1 | 0.0079082 | 0.0019827 | -0.0079032 | -0.0019807 | 4.9734e-06 | 1.9905e-06 | 0.01192 | 0.011921 | 0.011921 | 0.98719 | -0.24526 | 0.98651 | -0.25846 | 3.275
2 | -0.013516 | -0.0033877 | 0.013517 | 0.0033887 | 1.7556e-06 | 9.7937e-07 | 0.020373 | 0.020373 | 0.020373 | 0.98719 | -0.24526 | 0.98733 | -0.24253 | 5.5969
3 | -0.021226 | -0.0053207 | 0.02123 | 0.0053232 | 4.2056e-06 | 2.5514e-06 | 0.03199 | 0.03199 | 0.03199 | 0.98733 | -0.24253 | 0.98754 | -0.23837 | 8.7885
4 | 0.0077083 | 0.001932 | -0.0077073 | -0.0019316 | 1.0266e-06 | 3.9766e-07 | 0.011617 | 0.011617 | 0.011617 | 0.98733 | -0.24253 | 0.98719 | -0.24533 | 3.1916
5 | -0.031068 | -0.0079176 | 0.031081 | 0.0079255 | 1.3754e-05 | 7.9495e-06 | 0.046887 | 0.046887 | 0.046887 | 0.98695 | -0.24974 | 0.98743 | -0.24057 | 6.4405
6 | 0.031068 | 0.0079176 | -0.031044 | -0.0079038 | 2.3882e-05 | 1.3805e-05 | 0.046887 | 0.046888 | 0.046888 | 0.98695 | -0.24974 | 0.98612 | -0.26568 | 6.4406
7 | -0.033403 | -0.0085074 | 0.033407 | 0.0085093 | 3.5393e-06 | 1.8371e-06 | 0.050386 | 0.050386 | 0.050386 | 0.98743 | -0.24057 | 0.98754 | -0.23837 | 4.6141
8 | 0.029865 | 0.0076083 | -0.02985 | -0.0075994 | 1.4357e-05 | 8.9487e-06 | 0.045109 | 0.045109 | 0.045109 | 0.98612 | -0.26568 | 0.98561 | -0.27565 | 12.3925
9 | -0.054637 | -0.013833 | 0.054649 | 0.01384 | 1.204e-05 | 7.1608e-06 | 0.082375 | 0.082375 | 0.082375 | 0.98754 | -0.23837 | 0.98778 | -0.23379 | 7.5435
10 | 0.0047458 | 0.0011893 | -0.0047455 | -0.0011893 | 2.1508e-07 | -5.6427e-09 | 0.0071534 | 0.0071535 | 0.0071535 | 0.98719 | -0.24533 | 0.98714 | -0.24628 | 1.9652
11 | 0.0044655 | 0.0011182 | -0.0044653 | -0.0011182 | 1.2249e-07 | -1.4419e-08 | 0.0067192 | 0.0067192 | 0.0067192 | 0.98886 | -0.21305 | 0.98883 | -0.21363 | 1.8459
12 | -0.0044655 | -0.0011182 | 0.0044679 | 0.0011179 | 2.448e-06 | -2.8951e-07 | 0.0067192 | 0.0067185 | 0.0067192 | 0.98886 | -0.21305 | 0.98946 | -0.20153 | 1.8459
13 | 0.0036676 | 0.0009183 | -0.0036665 | -0.00091885 | 1.1412e-06 | -5.5081e-07 | 0.0055188 | 0.0055193 | 0.0055193 | 0.98883 | -0.21363 | 0.9885 | -0.22016 | 1.5163
14 | -0.061385 | -0.015557 | 0.061426 | 0.015581 | 4.0576e-05 | 2.4502e-05 | 0.092377 | 0.092377 | 0.092377 | 0.98946 | -0.20153 | 0.99017 | -0.18779 | 8.4594
15 | 0.056917 | 0.014439 | -0.056829 | -0.014386 | 8.8128e-05 | 5.2706e-05 | 0.085659 | 0.08566 | 0.08566 | 0.98946 | -0.20153 | 0.98778 | -0.23379 | 7.8443
16 | 0.00083951 | 0.0002091 | -0.00083945 | -0.00021032 | 6.023e-08 | -1.2172e-06 | 0.0012717 | 0.0012722 | 0.0012722 | 0.98196 | -0.34619 | 0.98188 | -0.3477 | 0.34949
17 | 0.0266 | 0.0067513 | -0.026483 | -0.006679 | 0.00011677 | 7.2325e-05 | 0.040339 | 0.04034 | 0.04034 | 0.98196 | -0.34619 | 0.97725 | -0.43788 | 11.0824
18 | -0.027439 | -0.0069604 | 0.02752 | 0.0070107 | 8.0975e-05 | 5.0241e-05 | 0.041611 | 0.04161 | 0.041611 | 0.98196 | -0.34619 | 0.98512 | -0.28501 | 11.4315
19 | 0.00043818 | 0.00010975 | -0.00043818 | -0.00010982 | 9.1181e-10 | -6.9161e-08 | 0.00066403 | 0.00066406 | 0.00066406 | 0.98188 | -0.3477 | 0.98188 | -0.34775 | 0.18243
20 | 0.025602 | 0.0064582 | -0.025593 | -0.0064524 | 9.4452e-06 | 5.8375e-06 | 0.038998 | 0.038999 | 0.038999 | 0.97725 | -0.43788 | 0.97686 | -0.44559 | 10.7139
21 | -0.028338 | -0.0072155 | 0.02835 | 0.0072234 | 1.2797e-05 | 7.953e-06 | 0.042844 | 0.042844 | 0.042844 | 0.98512 | -0.28501 | 0.98561 | -0.27565 | 11.7704
22 | -0.065564 | -0.016619 | 0.065665 | 0.01668 | 0.0001004 | 6.1063e-05 | 0.098596 | 0.098595 | 0.098596 | 0.99017 | -0.18779 | 0.99183 | -0.15597 | 9.0289
23 | -0.00048604 | -0.00012181 | 0.00048604 | 0.00012161 | 3.1362e-09 | -1.9865e-07 | 0.00073133 | 0.00073126 | 0.00073133 | 0.98894 | -0.21215 | 0.98894 | -0.21201 | 0.20091
24 | -0.0018984 | -0.00047559 | 0.0018985 | 0.00047535 | 6.9428e-08 | -2.4674e-07 | 0.0028564 | 0.0028563 | 0.0028564 | 0.98894 | -0.21201 | 0.98898 | -0.21124 | 0.78473
25 | -0.0012711 | -0.00031858 | 0.0012712 | 0.00031842 | 1.8693e-08 | -1.6312e-07 | 0.001912 | 0.0019119 | 0.001912 | 0.98929 | -0.2054 | 0.9893 | -0.20509 | 0.52527
26 | -0.0026448 | -0.00066269 | 0.0026449 | 0.00066261 | 5.2098e-08 | -7.9384e-08 | 0.0039781 | 0.003978 | 0.0039781 | 0.9893 | -0.20509 | 0.98932 | -0.20468 | 1.0929
27 | -0.0048612 | -0.0012181 | 0.0048614 | 0.0012181 | 2.2082e-07 | -1.2679e-10 | 0.0073115 | 0.0073114 | 0.0073115 | 0.98932 | -0.20468 | 0.98937 | -0.20372 | 2.0086
28 | -0.02752 | -0.0069096 | 0.027528 | 0.0069146 | 7.9805e-06 | 4.948e-06 | 0.041395 | 0.041395 | 0.041395 | 0.98937 | -0.20372 | 0.98968 | -0.19765 | 11.3722
29 | 0.022659 | 0.0056916 | -0.022651 | -0.0056866 | 8.1276e-06 | 4.9621e-06 | 0.034083 | 0.034084 | 0.034084 | 0.98937 | -0.20372 | 0.98898 | -0.21124 | 9.3636
30 | -0.071665 | -0.018183 | 0.071752 | 0.018237 | 8.7265e-05 | 5.3512e-05 | 0.1076 | 0.1076 | 0.1076 | 0.99183 | -0.15597 | 0.99314 | -0.13068 | 9.8531
31 | -0.075913 | -0.01928 | 0.075953 | 0.019304 | 3.9947e-05 | 2.4608e-05 | 0.11383 | 0.11383 | 0.11383 | 0.99314 | -0.13068 | 0.99372 | -0.11976 | 10.424
32 | 0.001972 | 0.00049418 | -0.001972 | -0.00049424 | 1.6907e-08 | -5.4764e-08 | 0.0029686 | 0.0029686 | 0.0029686 | 0.9885 | -0.22016 | 0.98849 | -0.22034 | 0.81555
33 | 0.025593 | 0.0064524 | -0.025525 | -0.0064103 | 6.8096e-05 | 4.2091e-05 | 0.038999 | 0.038999 | 0.038999 | 0.97686 | -0.44559 | 0.97402 | -0.50134 | 10.714
34 | 0.043172 | 0.010888 | -0.043132 | -0.010863 | 4.0057e-05 | 2.5306e-05 | 0.064671 | 0.064671 | 0.064671 | 0.99372 | -0.11976 | 0.99271 | -0.13916 | 17.7668
35 | -0.11913 | -0.030192 | 0.11933 | 0.03032 | 0.00020191 | 0.00012725 | 0.1785 | 0.1785 | 0.1785 | 0.99372 | -0.11976 | 0.99555 | -0.084549 | 16.3462
36 | 0.040152 | 0.010116 | -0.040104 | -0.010086 | 4.7949e-05 | 3.0232e-05 | 0.060204 | 0.060204 | 0.060204 | 0.99271 | -0.13916 | 0.99141 | -0.16416 | 16.5396
37 | -0.11933 | -0.03032 | 0.11937 | 0.030348 | 4.442e-05 | 2.7994e-05 | 0.1785 | 0.1785 | 0.1785 | 0.99555 | -0.084549 | 0.99596 | -0.07682 | 16.3462
38 | 0.025525 | 0.0064103 | -0.025507 | -0.0063993 | 1.786e-05 | 1.1041e-05 | 0.038999 | 0.038999 | 0.038999 | 0.97402 | -0.50134 | 0.97327 | -0.51602 | 10.7141
39 | -0.0084102 | -0.0021078 | 0.0084129 | 0.002109 | 2.7398e-06 | 1.2068e-06 | 0.012874 | 0.012874 | 0.012874 | 0.97208 | -0.53961 | 0.97243 | -0.53277 | 3.5368
40 | -0.020587 | -0.0051596 | 0.020589 | 0.0051609 | 2.1049e-06 | 1.277e-06 | 0.031503 | 0.031503 | 0.031503 | 0.97243 | -0.53277 | 0.97253 | -0.53062 | 8.6546
41 | 0.012174 | 0.0030506 | -0.012167 | -0.0030469 | 6.7476e-06 | 3.6756e-06 | 0.018629 | 0.018629 | 0.018629 | 0.97243 | -0.53277 | 0.97184 | -0.54441 | 5.1179
42 | -0.023306 | -0.0058419 | 0.023323 | 0.0058519 | 1.6233e-05 | 9.9662e-06 | 0.03566 | 0.03566 | 0.03566 | 0.97253 | -0.53062 | 0.97327 | -0.51602 | 9.7967
43 | 0.0024934 | 0.00062451 | -0.0024932 | -0.00062474 | 1.4249e-07 | -2.3184e-07 | 0.0038175 | 0.0038177 | 0.0038177 | 0.97184 | -0.54441 | 0.97178 | -0.54561 | 1.0488
44 | 0.0096741 | 0.0024224 | -0.0096734 | -0.0024221 | 7.0902e-07 | 3.47e-07 | 0.014812 | 0.014812 | 0.014812 | 0.97184 | -0.54441 | 0.97176 | -0.54595 | 4.0691
45 | 0.0024932 | 0.00062474 | -0.0024932 | -0.00062484 | 6.5086e-08 | -1.0588e-07 | 0.0038177 | 0.0038177 | 0.0038177 | 0.97178 | -0.54561 | 0.97175 | -0.54616 | 1.0488
46 | 0.0065265 | 0.0016334 | -0.0065239 | -0.0016326 | 2.6194e-06 | 8.1023e-07 | 0.0099929 | 0.0099933 | 0.0099933 | 0.97176 | -0.54595 | 0.97133 | -0.55439 | 2.7454
47 | 0.0046421 | 0.001161 | -0.0046417 | -0.001161 | 3.929e-07 | -5.0236e-09 | 0.0071105 | 0.0071106 | 0.0071106 | 0.97133 | -0.55439 | 0.97124 | -0.55617 | 1.9535
48 | 0.0021859 | 0.00054551 | -0.0021855 | -0.00054657 | 4.5795e-07 | -1.0546e-06 | 0.0033481 | 0.0033486 | 0.0033486 | 0.97124 | -0.55617 | 0.97102 | -0.56058 | 0.91995
49 | 0.00087504 | 0.00021814 | -0.00087503 | -0.00021828 | 7.7192e-09 | -1.3675e-07 | 0.0013405 | 0.0013406 | 0.0013406 | 0.97102 | -0.56058 | 0.97101 | -0.56076 | 0.36829
50 | 0.00087503 | 0.00021828 | -0.00087498 | -0.00021929 | 5.6959e-08 | -1.0087e-06 | 0.0013406 | 0.0013409 | 0.0013409 | 0.97101 | -0.56076 | 0.97094 | -0.56213 | 0.36839
51 | -0.01062 | -0.0026605 | 0.010628 | 0.0026644 | 7.7592e-06 | 3.8893e-06 | 0.015844 | 0.015844 | 0.015844 | 0.9974 | -0.049988 | 0.9982 | -0.034657 | 4.3527
52 | 0.0059845 | 0.0014989 | -0.005983 | -0.0014986 | 1.5564e-06 | 3.1673e-07 | 0.0089279 | 0.0089282 | 0.0089282 | 0.9974 | -0.049988 | 0.99712 | -0.055451 | 2.4528
53 | 0.0046358 | 0.0011616 | -0.0046352 | -0.0011616 | 5.1002e-07 | -4.4646e-08 | 0.006916 | 0.0069161 | 0.0069161 | 0.9974 | -0.049988 | 0.99728 | -0.052298 | 1.9
54 | -0.010628 | -0.0026644 | 0.01063 | 0.0026656 | 2.4123e-06 | 1.2088e-06 | 0.015844 | 0.015843 | 0.015844 | 0.9982 | -0.034657 | 0.99845 | -0.029894 | 4.3526
55 | 0.0047621 | 0.0011926 | -0.0047617 | -0.0011926 | 4.1758e-07 | -2.0342e-08 | 0.0071063 | 0.0071064 | 0.0071064 | 0.99712 | -0.055451 | 0.99702 | -0.057293 | 1.9523
56 | 0.0021129 | 0.00052946 | -0.0021129 | -0.00052954 | 2.7464e-08 | -7.8571e-08 | 0.0031526 | 0.0031526 | 0.0031526 | 0.99728 | -0.052298 | 0.99727 | -0.052571 | 0.8661
57 | -0.017998 | -0.004512 | 0.018003 | 0.0045151 | 5.1948e-06 | 3.0728e-06 | 0.026823 | 0.026823 | 0.026823 | 0.99845 | -0.029894 | 0.99876 | -0.023839 | 7.369
58 | 0.0032626 | 0.00081694 | -0.0032622 | -0.0008173 | 4.2818e-07 | -3.5393e-07 | 0.0048691 | 0.0048693 | 0.0048693 | 0.99702 | -0.057293 | 0.99688 | -0.060049 | 1.3377
59 | 0.0023745 | 0.00059501 | -0.0023745 | -0.0005951 | 4.5789e-08 | -9.2756e-08 | 0.0035777 | 0.0035777 | 0.0035777 | 0.98759 | -0.23672 | 0.98757 | -0.23713 | 0.98289
60 | -0.0023745 | -0.00059501 | 0.0023749 | 0.00059433 | 3.3317e-07 | -6.7516e-07 | 0.0035777 | 0.0035774 | 0.0035777 | 0.98759 | -0.23672 | 0.98774 | -0.23378 | 0.98288
61 | -0.14985 | -0.03801 | 0.15003 | 0.038126 | 0.00018309 | 0.00011607 | 0.2259 | 0.2259 | 0.2259 | 0.98774 | -0.23378 | 0.98906 | -0.2084 | 20.6872
62 | 0.1417 | 0.03597 | -0.14151 | -0.035844 | 0.00019854 | 0.00012573 | 0.21364 | 0.21364 | 0.21364 | 0.98774 | -0.23378 | 0.98623 | -0.26294 | 19.5639
63 | 0.0057675 | 0.0014454 | -0.0057669 | -0.0014453 | 6.1896e-07 | 1.1632e-07 | 0.0086886 | 0.0086887 | 0.0086887 | 0.98774 | -0.23378 | 0.98763 | -0.23603 | 2.387
64 | 0.1211 | 0.030872 | -0.121 | -0.030813 | 9.3486e-05 | 5.8934e-05 | 0.18071 | 0.18071 | 0.18071 | 0.99814 | -0.035337 | 0.9973 | -0.051343 | 16.5489
65 | -0.1211 | -0.030872 | 0.12118 | 0.030925 | 8.4735e-05 | 5.3416e-05 | 0.18071 | 0.18071 | 0.18071 | 0.99814 | -0.035337 | 0.9989 | -0.020852 | 16.5488
66 | 0.121 | 0.030813 | -0.12085 | -0.030719 | 0.00014848 | 9.3604e-05 | 0.18071 | 0.18071 | 0.18071 | 0.9973 | -0.051343 | 0.99596 | -0.07682 | 16.5489
67 | -0.1243 | -0.031707 | 0.12431 | 0.031716 | 1.4546e-05 | 9.1764e-06 | 0.18536 | 0.18536 | 0.18536 | 0.9989 | -0.020852 | 0.99903 | -0.018429 | 16.9742
68 | -0.17074 | -0.04332 | 0.1712 | 0.04361 | 0.00045723 | 0.00029049 | 0.25706 | 0.25706 | 0.25706 | 0.98906 | -0.2084 | 0.99196 | -0.15288 | 23.5402
69 | 0.020708 | 0.0051936 | -0.0207 | -0.005189 | 7.5553e-06 | 4.5691e-06 | 0.031156 | 0.031156 | 0.031156 | 0.98906 | -0.2084 | 0.98867 | -0.21606 | 8.5593
70 | 0.015698 | 0.0039358 | -0.015694 | -0.0039334 | 4.1402e-06 | 2.3987e-06 | 0.023686 | 0.023686 | 0.023686 | 0.98623 | -0.26294 | 0.98595 | -0.26848 | 6.5072
71 | 0.12581 | 0.031909 | -0.12572 | -0.031857 | 8.2605e-05 | 5.2167e-05 | 0.18995 | 0.18995 | 0.18995 | 0.98623 | -0.26294 | 0.98553 | -0.27661 | 17.3949
72 | 0.12062 | 0.030578 | -0.12054 | -0.030523 | 8.78e-05 | 5.5385e-05 | 0.18225 | 0.18225 | 0.18225 | 0.98553 | -0.27661 | 0.98474 | -0.29177 | 16.6896
73 | -0.0020357 | -0.0005102 | 0.0020358 | 0.00050993 | 8.6009e-08 | -2.6877e-07 | 0.0030388 | 0.0030387 | 0.0030388 | 0.99683 | -0.060936 | 0.99688 | -0.060049 | 0.83484
74 | 0.029912 | 0.0075075 | -0.029901 | -0.0075008 | 1.0766e-05 | 6.7003e-06 | 0.044529 | 0.044529 | 0.044529 | 0.99963 | -0.0070508 | 0.99924 | -0.0146 | 12.2333
75 | -0.029912 | -0.0075075 | 0.029922 | 0.0075138 | 1.0062e-05 | 6.2622e-06 | 0.044529 | 0.044529 | 0.044529 | 0.99963 | -0.0070508 | 1 | 0 | 12.2333
76 | 0.027117 | 0.0068032 | -0.027115 | -0.0068015 | 2.7739e-06 | 1.7159e-06 | 0.040384 | 0.040384 | 0.040384 | 0.99924 | -0.0146 | 0.99913 | -0.016746 | 11.0946
77 | 0.1269 | 0.032406 | -0.12678 | -0.032335 | 0.00011293 | 7.1282e-05 | 0.18904 | 0.18904 | 0.18904 | 1 | 0 | 0.99903 | -0.018429 | 17.311
78 | 0.20946 | 0.053753 | -0.20926 | -0.053622 | 0.00020618 | 0.00013129 | 0.31213 | 0.31213 | 0.31213 | 1 | 0 | 0.99892 | -0.020307 | 28.5836
79 | -0.18996 | -0.048533 | 0.1901 | 0.048618 | 0.00013371 | 8.5057e-05 | 0.28431 | 0.28431 | 0.28431 | 0.99536 | -0.087974 | 0.99612 | -0.073428 | 26.0362
80 | 0.18996 | 0.048533 | -0.18994 | -0.048518 | 2.3917e-05 | 1.5215e-05 | 0.28431 | 0.28432 | 0.28432 | 0.99536 | -0.087974 | 0.99522 | -0.090578 | 26.0362
81 | -0.19641 | -0.050201 | 0.19644 | 0.05022 | 3.0815e-05 | 1.961e-05 | 0.29375 | 0.29375 | 0.29375 | 0.99612 | -0.073428 | 0.99629 | -0.070185 | 26.8999
82 | 0.18994 | 0.048518 | -0.18979 | -0.048423 | 0.00014843 | 9.4424e-05 | 0.28432 | 0.28432 | 0.28432 | 0.99522 | -0.090578 | 0.99437 | -0.10676 | 26.0362
83 | 0.0059341 | 0.0014871 | -0.0059327 | -0.0014869 | 1.3991e-06 | 2.7093e-07 | 0.0088409 | 0.0088412 | 0.0088412 | 0.99876 | -0.023839 | 0.9985 | -0.028789 | 2.4289
84 | -0.023937 | -0.0060022 | 0.023938 | 0.0060025 | 4.765e-07 | 2.9188e-07 | 0.035664 | 0.035664 | 0.035664 | 0.99876 | -0.023839 | 0.99878 | -0.023421 | 9.7978
85 | -0.004638 | -0.0011624 | 0.0046384 | 0.0011624 | 3.2183e-07 | -6.822e-09 | 0.0070855 | 0.0070854 | 0.0070855 | 0.97404 | -0.501 | 0.97411 | -0.49954 | 1.9466
86 | 0.028785 | 0.0072233 | -0.028769 | -0.0072138 | 1.5305e-05 | 9.5324e-06 | 0.043974 | 0.043974 | 0.043974 | 0.97411 | -0.49954 | 0.97354 | -0.5107 | 12.0807
87 | -0.033423 | -0.0083857 | 0.033452 | 0.0084038 | 2.8842e-05 | 1.8091e-05 | 0.051059 | 0.051059 | 0.051059 | 0.97411 | -0.49954 | 0.97503 | -0.48146 | 14.0272
88 | -0.0047716 | -0.0011959 | 0.004772 | 0.0011959 | 3.899e-07 | 6.9456e-09 | 0.0072969 | 0.0072968 | 0.0072969 | 0.97305 | -0.52045 | 0.97314 | -0.51873 | 2.0046
89 | -0.016915 | -0.0042401 | 0.016921 | 0.0042439 | 6.4754e-06 | 3.8235e-06 | 0.025864 | 0.025864 | 0.025864 | 0.97314 | -0.51873 | 0.97354 | -0.5107 | 7.1056
90 | 0.012143 | 0.0030442 | -0.012139 | -0.0030424 | 3.3488e-06 | 1.8215e-06 | 0.018568 | 0.018568 | 0.018568 | 0.97314 | -0.51873 | 0.97284 | -0.52452 | 5.101
91 | 0.011848 | 0.0029698 | -0.011847 | -0.0029691 | 1.3798e-06 | 7.4359e-07 | 0.01811 | 0.01811 | 0.01811 | 0.97354 | -0.5107 | 0.97342 | -0.51314 | 4.9752
92 | 0.010627 | 0.0026646 | -0.010625 | -0.0026635 | 2.069e-06 | 1.0626e-06 | 0.016218 | 0.016218 | 0.016218 | 0.97503 | -0.48146 | 0.97482 | -0.48555 | 4.4555
93 | -0.044078 | -0.011068 | 0.044084 | 0.011072 | 5.736e-06 | 3.6289e-06 | 0.067277 | 0.067277 | 0.067277 | 0.97503 | -0.48146 | 0.97517 | -0.47873 | 18.4827
94 | 0.010625 | 0.0026635 | -0.010622 | -0.002662 | 2.8724e-06 | 1.4754e-06 | 0.016218 | 0.016218 | 0.016218 | 0.97482 | -0.48555 | 0.97453 | -0.49122 | 4.4556
95 | -0.052518 | -0.013186 | 0.052587 | 0.013229 | 6.8982e-05 | 4.3791e-05 | 0.080146 | 0.080146 | 0.080146 | 0.97517 | -0.47873 | 0.97656 | -0.45124 | 22.0182
96 | -0.057702 | -0.014511 | 0.057741 | 0.014536 | 3.9296e-05 | 2.498e-05 | 0.08794 | 0.08794 | 0.08794 | 0.97656 | -0.45124 | 0.97729 | -0.43699 | 24.1594
97 | 0.062732 | 0.015804 | -0.062689 | -0.015777 | 4.2622e-05 | 2.7122e-05 | 0.095474 | 0.095474 | 0.095474 | 0.97802 | -0.42278 | 0.97729 | -0.43699 | 26.229
98 | -0.062732 | -0.015804 | 0.062794 | 0.015843 | 6.187e-05 | 3.937e-05 | 0.095474 | 0.095474 | 0.095474 | 0.97802 | -0.42278 | 0.97907 | -0.40218 | 26.229
99 | -0.070788 | -0.017846 | 0.070827 | 0.017871 | 3.8967e-05 | 2.4826e-05 | 0.10762 | 0.10762 | 0.10762 | 0.97907 | -0.40218 | 0.97966 | -0.39068 | 29.5668
100 | -0.098762 | -0.024872 | 0.098966 | 0.025003 | 0.00020483 | 0.00013079 | 0.15005 | 0.15005 | 0.15005 | 0.97966 | -0.39068 | 0.98188 | -0.3474 | 41.2235
101 | -0.1712 | -0.04361 | 0.17135 | 0.043706 | 0.00015158 | 9.63e-05 | 0.25706 | 0.25706 | 0.25706 | 0.99196 | -0.15288 | 0.99291 | -0.13454 | 23.5401
102 | 0.014605 | 0.0036614 | -0.014601 | -0.0036593 | 3.6116e-06 | 2.0559e-06 | 0.021982 | 0.021982 | 0.021982 | 0.98867 | -0.21606 | 0.9884 | -0.22125 | 6.039
103 | -0.0034332 | -0.00086045 | 0.0034334 | 0.00086032 | 1.9791e-07 | -1.2635e-07 | 0.0051697 | 0.0051696 | 0.0051697 | 0.9882 | -0.22524 | 0.98826 | -0.22403 | 1.4203
104 | -0.0066279 | -0.0016609 | 0.0066288 | 0.0016612 | 8.7769e-07 | 2.6056e-07 | 0.0099796 | 0.0099795 | 0.0099796 | 0.98826 | -0.22403 | 0.9884 | -0.22125 | 2.7416
105 | 0.12054 | 0.030523 | -0.12045 | -0.030469 | 8.4503e-05 | 5.3306e-05 | 0.18225 | 0.18225 | 0.18225 | 0.98474 | -0.29177 | 0.98399 | -0.30638 | 16.6896
106 | 0.0077939 | 0.0019534 | -0.0077932 | -0.0019531 | 7.221e-07 | 2.8759e-07 | 0.011812 | 0.011812 | 0.011812 | 0.98188 | -0.3474 | 0.98178 | -0.34935 | 3.245
107 | -0.10676 | -0.026957 | 0.10686 | 0.027019 | 9.8509e-05 | 6.1903e-05 | 0.16187 | 0.16186 | 0.16187 | 0.98188 | -0.3474 | 0.98287 | -0.32816 | 14.8228
108 | 0.0058714 | 0.0014715 | -0.005871 | -0.0014714 | 4.6204e-07 | 9.8977e-08 | 0.0088989 | 0.008899 | 0.008899 | 0.98178 | -0.34935 | 0.98169 | -0.351 | 2.4448
109 | -0.1116 | -0.028207 | 0.11172 | 0.02828 | 0.0001167 | 7.3444e-05 | 0.16904 | 0.16904 | 0.16904 | 0.98287 | -0.32816 | 0.98399 | -0.30638 | 15.48
110 | 0.036308 | 0.0091345 | -0.036308 | -0.0091343 | 3.4384e-07 | 2.1608e-07 | 0.054508 | 0.054508 | 0.054508 | 0.99141 | -0.16416 | 0.9914 | -0.16436 | 14.9746
111 | -0.002027 | -0.00050802 | 0.0020272 | 0.00050754 | 1.6083e-07 | -4.8418e-07 | 0.0030559 | 0.0030556 | 0.0030559 | 0.98704 | -0.24895 | 0.98713 | -0.24729 | 0.83952
112 | 0.011526 | 0.0028883 | -0.011525 | -0.0028877 | 1.2432e-06 | 6.5527e-07 | 0.017375 | 0.017375 | 0.017375 | 0.98713 | -0.24729 | 0.98701 | -0.24955 | 4.7733
113 | -0.013554 | -0.0033959 | 0.013556 | 0.0033972 | 2.3711e-06 | 1.3238e-06 | 0.020431 | 0.02043 | 0.020431 | 0.98713 | -0.24729 | 0.98732 | -0.24361 | 5.6128
114 | 0.034461 | 0.0086713 | -0.034431 | -0.0086528 | 2.9542e-05 | 1.8528e-05 | 0.051735 | 0.051735 | 0.051735 | 0.9914 | -0.16436 | 0.99048 | -0.18231 | 14.213
115 | -0.023938 | -0.0060025 | 0.023945 | 0.0060072 | 7.6176e-06 | 4.6662e-06 | 0.035664 | 0.035664 | 0.035664 | 0.99878 | -0.023421 | 0.99913 | -0.016746 | 9.7978
116 | 0.030906 | 0.0077692 | -0.030898 | -0.0077644 | 7.7442e-06 | 4.833e-06 | 0.046439 | 0.046439 | 0.046439 | 0.99048 | -0.18231 | 0.9902 | -0.18756 | 12.7579
117 | 0.030188 | 0.0075864 | -0.030186 | -0.0075854 | 1.6031e-06 | 9.9928e-07 | 0.045372 | 0.045372 | 0.045372 | 0.9902 | -0.18756 | 0.99015 | -0.18867 | 12.4648
118 | 0.02915 | 0.0073256 | -0.029137 | -0.0073178 | 1.2477e-05 | 7.7628e-06 | 0.043814 | 0.043814 | 0.043814 | 0.99015 | -0.18867 | 0.98968 | -0.19765 | 12.0368
119 | 0.0063339 | 0.0015874 | -0.0063335 | -0.0015873 | 3.4361e-07 | 9.0769e-08 | 0.0095357 | 0.0095357 | 0.0095357 | 0.98839 | -0.22156 | 0.98833 | -0.22269 | 2.6197
120 | -0.0079723 | -0.0019981 | 0.0079725 | 0.0019981 | 1.1634e-07 | 4.6857e-08 | 0.012002 | 0.012002 | 0.012002 | 0.98839 | -0.22156 | 0.9884 | -0.22125 | 3.2974
121 | -0.17773 | -0.045306 | 0.17782 | 0.045366 | 9.4554e-05 | 6.0102e-05 | 0.26662 | 0.26662 | 0.26662 | 0.99291 | -0.13454 | 0.99349 | -0.12353 | 24.4162
122 | -0.18566 | -0.047331 | 0.18581 | 0.047426 | 0.00015042 | 9.5667e-05 | 0.27836 | 0.27836 | 0.27836 | 0.99349 | -0.12353 | 0.99437 | -0.10676 | 25.4911
123 | 0.0031037 | 0.00077767 | -0.0031036 | -0.00077783 | 1.7235e-07 | -1.5734e-07 | 0.0046818 | 0.0046819 | 0.0046819 | 0.98644 | -0.26077 | 0.98638 | -0.26194 | 1.2862
124 | -0.0031037 | -0.00077767 | 0.0031043 | 0.00077713 | 5.8589e-07 | -5.3521e-07 | 0.0046818 | 0.0046815 | 0.0046818 | 0.98644 | -0.26077 | 0.98664 | -0.25681 | 1.2862
125 | -0.0083462 | -0.0020903 | 0.0083475 | 0.0020909 | 1.3688e-06 | 5.8175e-07 | 0.012587 | 0.012587 | 0.012587 | 0.98664 | -0.25681 | 0.98682 | -0.25336 | 3.4579
126 | 0.0052418 | 0.0013132 | -0.0052416 | -0.0013131 | 2.5853e-07 | 2.4582e-08 | 0.0079053 | 0.0079054 | 0.0079054 | 0.98664 | -0.25681 | 0.98659 | -0.25784 | 2.1718
127 | 0.020752 | 0.0052113 | -0.020743 | -0.0052054 | 9.6773e-06 | 5.8541e-06 | 0.031227 | 0.031227 | 0.031227 | 0.98898 | -0.21124 | 0.98848 | -0.22102 | 8.5789
128 | 0.020743 | 0.0052054 | -0.020734 | -0.0052001 | 8.7405e-06 | 5.2876e-06 | 0.031227 | 0.031227 | 0.031227 | 0.98848 | -0.22102 | 0.98803 | -0.22986 | 8.579
129 | 0.01863 | 0.0046729 | -0.018624 | -0.004669 | 6.4981e-06 | 3.877e-06 | 0.028059 | 0.02806 | 0.02806 | 0.98803 | -0.22986 | 0.98765 | -0.23718 | 7.7087
130 | 0.017401 | 0.0043627 | -0.017398 | -0.0043608 | 3.1825e-06 | 1.8788e-06 | 0.026218 | 0.026218 | 0.026218 | 0.98765 | -0.23718 | 0.98745 | -0.24102 | 7.2027
131 | 0.016133 | 0.0040438 | -0.016131 | -0.0040427 | 1.9945e-06 | 1.1614e-06 | 0.024312 | 0.024312 | 0.024312 | 0.98745 | -0.24102 | 0.98732 | -0.24361 | 6.6791
132 | -0.0013081 | -0.00032784 | 0.0013081 | 0.00032749 | 4.3304e-08 | -3.5106e-07 | 0.0019731 | 0.0019729 | 0.0019731 | 0.98652 | -0.2592 | 0.98656 | -0.2585 | 0.54205
133 | -0.002458 | -0.00061567 | 0.0024581 | 0.00061553 | 7.7088e-08 | -1.4166e-07 | 0.0037072 | 0.0037072 | 0.0037072 | 0.98656 | -0.2585 | 0.98659 | -0.25784 | 1.0185
134 | 0.010655 | 0.0026695 | -0.010654 | -0.0026693 | 3.747e-07 | 1.9031e-07 | 0.016062 | 0.016062 | 0.016062 | 0.98701 | -0.24955 | 0.98698 | -0.25029 | 4.4128
135 | 0.009568 | 0.0023971 | -0.0095666 | -0.0023964 | 1.4e-06 | 6.6674e-07 | 0.014425 | 0.014425 | 0.014425 | 0.98698 | -0.25029 | 0.98682 | -0.25336 | 3.9629
136 | -0.20282 | -0.051818 | 0.20328 | 0.052115 | 0.00046724 | 0.00029744 | 0.30327 | 0.30327 | 0.30327 | 0.99629 | -0.070185 | 0.9988 | -0.02266 | 27.7718
137 | -0.20611 | -0.052824 | 0.20613 | 0.052839 | 2.3516e-05 | 1.4972e-05 | 0.30748 | 0.30748 | 0.30748 | 0.9988 | -0.02266 | 0.99892 | -0.020307 | 28.1573

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36793 | 0.093673

## res_load
| p_mw | q_mvar
0 | 0.0056034 | 0.0014043
1 | 0.0079032 | 0.0019807
2 | 0.0023218 | 0.0005819
3 | 0.001179 | 0.00029548
4 | 0.0029615 | 0.00074223
5 | 0.0007977 | 0.00019992
6 | 0.00040127 | 0.00010057
7 | 0.00088092 | 0.00022078
8 | 0.00081719 | 0.00020481
9 | 0.0041385 | 0.0010372
10 | 0.0021806 | 0.00054652
11 | 0.0014999 | 0.00037591
12 | 0.0047455 | 0.0011893
13 | 0.00048604 | 0.00012181
14 | 0.0014124 | 0.00035398
15 | 0.0012711 | 0.00031858
16 | 0.0013737 | 0.00034428
17 | 0.0022163 | 0.00055545
18 | 0.0059999 | 0.0015037
19 | 0.0041612 | 0.0010429
20 | 0.0016945 | 0.00042467
21 | 0.00043818 | 0.00010982
22 | 0.0029801 | 0.0007469
23 | 0.0084102 | 0.0021078
24 | 0.0027173 | 0.00068101
25 | 0.0021841 | 0.00054739
26 | 0.0031469 | 0.00078868
27 | 0.0024932 | 0.00062484
28 | 0.0018818 | 0.00047162
29 | 0.0024558 | 0.00061548
30 | 0.0013104 | 0.00032842
31 | 0.00087498 | 0.00021929
32 | 0.001972 | 0.00049424
33 | 0.0012208 | 0.00030597
34 | 0.0025223 | 0.00063216
35 | 0.0073674 | 0.0018464
36 | 0.0014991 | 0.0003757
37 | 0.0021129 | 0.00052954
38 | 0.0023745 | 0.0005951
39 | 0.0031184 | 0.00078154
40 | 0.0057669 | 0.0014453
41 | 0.015694 | 0.0039334
42 | 0.0051015 | 0.0012786
43 | 0.0020357 | 0.0005102
44 | 0.0012264 | 0.00030737
45 | 0.0027834 | 0.00069759
46 | 0.0063145 | 0.0015826
47 | 0.004638 | 0.0011624
48 | 0.0047716 | 0.0011959
49 | 0.012139 | 0.0030424
50 | 0.011847 | 0.0029691
51 | 0.0084338 | 0.0021137
52 | 0.010622 | 0.002662
53 | 0.0051152 | 0.001282
54 | 0.0049479 | 0.0012401
55 | 0.007994 | 0.0020035
56 | 0.027935 | 0.0070011
57 | 0.0060955 | 0.0015277
58 | 0.0034332 | 0.00086045
59 | 0.0031945 | 0.00080062
60 | 0.0014821 | 0.00037144
61 | 0.0024691 | 0.0006188
62 | 0.0019218 | 0.00048165
63 | 0.0047404 | 0.001188
64 | 0.005871 | 0.0014714
65 | 0.0087352 | 0.0021892
66 | 0.0037955 | 0.00095123
67 | 0.002027 | 0.00050802
68 | 0.0018471 | 0.00046294
69 | 0.0031694 | 0.00079433
70 | 0.0059327 | 0.0014869
71 | 0.0035256 | 0.0008836
72 | 0.00070989 | 0.00017791
73 | 0.0010367 | 0.00025983
74 | 0.001609 | 0.00040326
75 | 0.0016385 | 0.00041064
76 | 0.0063335 | 0.0015873
77 | 0.0063836 | 0.0015999
78 | 0.0078375 | 0.0019643
79 | 0.0039778 | 0.00099693
80 | 0.0031036 | 0.00077783
81 | 0.0021035 | 0.00052719
82 | 0.0012224 | 0.00030636
83 | 0.0012648 | 0.000317
84 | 0.0025754 | 0.00064546
85 | 0.0013081 | 0.00032784
86 | 0.0011498 | 0.00028818
87 | 0.00087058 | 0.00021819
88 | 0.0010862 | 0.00027223
89 | 0.0012191 | 0.00030552
90 | 0.0027835 | 0.00069761
91 | 0.0063747 | 0.0015976
92 | 0.0028261 | 0.00070829
93 | 0.0031249 | 0.00078317

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1