## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_155-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_155-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_155-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_155-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_155-9_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_155-9_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_155-9_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_155-9_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_155-9_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_155-9_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_155-9_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_155-9_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_155-9_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_155-9_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_155-9_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_155-9_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_155-9_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_155-9_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_155-9_0_4_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_155-9_0_4_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_155-9_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_155-9_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_155-9_0_4_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_155-9_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_155-9_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_155-9_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_155-9_0_4_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_155-9_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_155-9_0_4_node_75 | 0.4 | n |  | TRUE
29 | bus_LV_155-9_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_155-9_0_4_node_79 | 0.4 | n |  | TRUE
31 | bus_LV_155-9_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_155-9_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_155-9_0_4_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_155-9_0_4_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_155-9_0_4_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_155-9_0_4_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_155-9_0_4_node_78 | 0.4 | n |  | TRUE
38 | bus_LV_155-9_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_155-9_0_4_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_155-9_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_155-9_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_155-9_0_4_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_155-9_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_155-9_0_4_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_155-9_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_155-9_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_155-9_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_155-9_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_155-9_0_4_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_155-9_0_4_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_155-9_0_4_node_85 | 0.4 | n |  | TRUE
52 | bus_LV_155-9_0_4_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_155-9_0_4_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_155-9_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_155-9_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_155-9_0_4_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_155-9_0_4_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_155-9_0_4_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_155-9_0_4_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_155-9_0_4_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_155-9_0_4_node_83 | 0.4 | n |  | TRUE
62 | bus_LV_155-9_0_4_node_81 | 0.4 | n |  | TRUE
63 | bus_LV_155-9_0_4_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_155-9_0_4_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_155-9_0_4_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_155-9_0_4_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_155-9_0_4_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_155-9_0_4_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_155-9_0_4_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_155-9_0_4_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_155-9_0_4_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_155-9_0_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_155-9_0_4_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_155-9_0_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_155-9_0_4_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_155-9_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_MV_361_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_155-9_0_4_load_0 | 0 | 0.0036686 | 0.00091944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_155-9_0_4_load_6 | 4 | 0.0049091 | 0.0012303 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_155-9_0_4_load_14 | 5 | 0.0024012 | 0.00060179 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_155-9_0_4_load_12 | 6 | 0.012157 | 0.0030468 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_155-9_0_4_load_7 | 9 | 0.039063 | 0.0097902 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_155-9_0_4_load_16 | 10 | 0.0082665 | 0.0020718 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_155-9_0_4_load_8 | 12 | 0.035394 | 0.0088705 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_155-9_0_4_load_10 | 13 | 0.018782 | 0.0047072 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_155-9_0_4_load_23 | 14 | 0.0034648 | 0.00086835 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_155-9_0_4_load_19 | 15 | 0.021846 | 0.005475 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_155-9_0_4_load_13 | 16 | 0.0024379 | 0.00061101 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_155-9_0_4_load_24 | 17 | 0.01362 | 0.0034134 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_155-9_0_4_load_52 | 18 | 0.0015189 | 0.00038066 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_155-9_0_4_load_53 | 19 | 0.0014883 | 0.000373 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_155-9_0_4_load_27 | 22 | 0.0047263 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_155-9_0_4_load_20 | 23 | 0.01653 | 0.0041429 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_155-9_0_4_load_22 | 25 | 0.0077656 | 0.0019462 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_155-9_0_4_load_74 | 26 | 0.0087068 | 0.0021821 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_155-9_0_4_load_75 | 28 | 0.016327 | 0.004092 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_155-9_0_4_load_40 | 33 | 0.0017075 | 0.00042795 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_155-9_0_4_load_37 | 34 | 0.026247 | 0.0065782 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_155-9_0_4_load_78 | 37 | 0.0084187 | 0.0021099 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_155-9_0_4_load_31 | 38 | 0.0018042 | 0.00045219 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_155-9_0_4_load_32 | 39 | 0.0038451 | 0.00096368 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_155-9_0_4_load_35 | 41 | 0.0048597 | 0.001218 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_155-9_0_4_load_77 | 42 | 0.0013857 | 0.00034729 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_155-9_0_4_load_39 | 43 | 0.002709 | 0.00067895 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_155-9_0_4_load_47 | 45 | 0.0014541 | 0.00036443 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_155-9_0_4_load_41 | 46 | 0.0012088 | 0.00030295 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_155-9_0_4_load_45 | 49 | 0.00039053 | 9.7875e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_155-9_0_4_load_85 | 51 | 0.0019685 | 0.00049334 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_155-9_0_4_load_51 | 52 | 0.00051406 | 0.00012884 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_155-9_0_4_load_55 | 54 | 0.00066185 | 0.00016588 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_155-9_0_4_load_57 | 56 | 0.0023999 | 0.00060148 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_155-9_0_4_load_84 | 57 | 0.0018916 | 0.00047408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_155-9_0_4_load_54 | 58 | 0.00087375 | 0.00021898 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_155-9_0_4_load_82 | 60 | 0.0041973 | 0.001052 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_155-9_0_4_load_81 | 62 | 0.0096201 | 0.002411 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_155-9_0_4_load_71 | 64 | 0.0082796 | 0.0020751 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_155-9_0_4_load_68 | 65 | 0.0073241 | 0.0018356 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_155-9_0_4_load_61 | 66 | 0.0052908 | 0.001326 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_155-9_0_4_load_60 | 67 | 0.0023385 | 0.00058607 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_155-9_0_4_load_62 | 70 | 0.011755 | 0.0029461 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_155-9_0_4_load_72 | 73 | 0.001412 | 0.00035388 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_155-9_0_4_load_80 | 75 | 0.016722 | 0.0041909 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_155-9_0_4_load_70 | 76 | 0.001991 | 0.00049899 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_155-9_0_4_line_0 |  | 0 | 1 | 0.052931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_155-9_0_4_line_1 |  | 0 | 2 | 0.011522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_155-9_0_4_line_2 |  | 1 | 3 | 0.04671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_155-9_0_4_line_3 |  | 2 | 4 | 0.024619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_155-9_0_4_line_4 |  | 3 | 5 | 0.066232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_155-9_0_4_line_5 |  | 5 | 6 | 0.018208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_155-9_0_4_line_6 |  | 6 | 16 | 0.019333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_155-9_0_4_line_7 |  | 6 | 13 | 0.067285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_155-9_0_4_line_8 |  | 7 | 8 | 0.036933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_155-9_0_4_line_9 |  | 7 | 9 | 0.03049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_155-9_0_4_line_10 |  | 8 | 14 | 0.0091168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_155-9_0_4_line_11 |  | 8 | 15 | 0.022512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_155-9_0_4_line_12 |  | 9 | 12 | 0.004068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_155-9_0_4_line_13 |  | 10 | 11 | 0.013618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_155-9_0_4_line_14 |  | 11 | 24 | 0.011154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_155-9_0_4_line_15 |  | 11 | 15 | 0.035017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_155-9_0_4_line_16 |  | 12 | 13 | 0.032001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_155-9_0_4_line_17 |  | 14 | 17 | 0.007013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_155-9_0_4_line_18 |  | 17 | 31 | 0.018543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_155-9_0_4_line_19 |  | 18 | 19 | 0.046902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_155-9_0_4_line_20 |  | 19 | 58 | 0.025628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_155-9_0_4_line_21 |  | 20 | 21 | 0.039907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_155-9_0_4_line_22 |  | 20 | 22 | 0.0088237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_155-9_0_4_line_23 |  | 21 | 26 | 0.020222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_155-9_0_4_line_24 |  | 21 | 30 | 0.042636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_155-9_0_4_line_25 |  | 22 | 29 | 0.0072107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_155-9_0_4_line_26 |  | 23 | 24 | 0.036546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_155-9_0_4_line_27 |  | 24 | 25 | 0.039468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_155-9_0_4_line_28 |  | 25 | 26 | 0.0069382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_155-9_0_4_line_29 |  | 27 | 28 | 0.027839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_155-9_0_4_line_30 |  | 27 | 29 | 0.028713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_155-9_0_4_line_31 |  | 30 | 37 | 0.0065481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_155-9_0_4_line_32 |  | 31 | 32 | 0.004811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_155-9_0_4_line_33 |  | 32 | 33 | 0.074778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_155-9_0_4_line_34 |  | 32 | 34 | 0.042726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_155-9_0_4_line_35 |  | 33 | 35 | 0.032094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_155-9_0_4_line_36 |  | 34 | 36 | 0.022733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_155-9_0_4_line_37 |  | 35 | 44 | 0.022422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_155-9_0_4_line_38 |  | 35 | 45 | 0.033204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_155-9_0_4_line_39 |  | 36 | 43 | 0.001882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_155-9_0_4_line_40 |  | 37 | 42 | 0.02672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_155-9_0_4_line_41 |  | 38 | 39 | 0.031075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_155-9_0_4_line_42 |  | 38 | 40 | 0.0045736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_155-9_0_4_line_43 |  | 40 | 41 | 0.0088091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_155-9_0_4_line_44 |  | 41 | 42 | 0.01585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_155-9_0_4_line_45 |  | 44 | 62 | 0.018133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_155-9_0_4_line_46 |  | 46 | 47 | 0.02704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_155-9_0_4_line_47 |  | 47 | 48 | 0.006034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_155-9_0_4_line_48 |  | 47 | 49 | 0.0084938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_155-9_0_4_line_49 |  | 47 | 50 | 0.018015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_155-9_0_4_line_50 |  | 48 | 51 | 0.018956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_155-9_0_4_line_51 |  | 49 | 52 | 0.0070724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_155-9_0_4_line_52 |  | 50 | 53 | 0.041845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_155-9_0_4_line_53 |  | 50 | 54 | 0.020009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_155-9_0_4_line_54 |  | 51 | 57 | 0.027894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_155-9_0_4_line_55 |  | 53 | 55 | 0.014045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_155-9_0_4_line_56 |  | 53 | 56 | 0.026745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_155-9_0_4_line_57 |  | 54 | 58 | 0.0026331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_155-9_0_4_line_58 |  | 55 | 66 | 0.045807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_155-9_0_4_line_59 |  | 55 | 67 | 0.021859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_155-9_0_4_line_60 |  | 57 | 61 | 0.017474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_155-9_0_4_line_61 |  | 59 | 60 | 0.017042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_155-9_0_4_line_62 |  | 59 | 61 | 0.042514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_155-9_0_4_line_63 |  | 59 | 62 | 0.017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_155-9_0_4_line_64 |  | 63 | 64 | 0.027054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_155-9_0_4_line_65 |  | 63 | 65 | 0.041117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_155-9_0_4_line_66 |  | 64 | 72 | 0.025989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_155-9_0_4_line_67 |  | 65 | 76 | 0.007797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_155-9_0_4_line_68 |  | 66 | 68 | 0.033795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_155-9_0_4_line_69 |  | 68 | 69 | 0.064771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_155-9_0_4_line_70 |  | 68 | 70 | 0.052398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_155-9_0_4_line_71 |  | 69 | 73 | 0.012088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_155-9_0_4_line_72 |  | 70 | 71 | 0.03173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_155-9_0_4_line_73 |  | 71 | 72 | 0.051478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_155-9_0_4_line_74 |  | 72 | 74 | 0.039295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_155-9_0_4_line_75 |  | 74 | 75 | 0.032117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_155-9_0_4_trafo_37 | 0.63 MVA 20/0.4 kV | 77 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2695680.0756 | 1233831.711 | 2695671.8346 | 1233835.2032 | 2695631.6018 | 1233852.9687
1 | 2695636.1864 | 1233863.5391 | 2695631.6018 | 1233852.9687
2 | 2695680.0756 | 1233831.711 | 2695661.1629 | 1233804.3977 | 2695655.0044 | 1233792.3565
3 | 2695636.1864 | 1233863.5391 | 2695642.4984 | 1233878.2737 | 2695650.2212 | 1233882.034
4 | 2695655.0044 | 1233792.3565 | 2695617.8834 | 1233807.7593 | 2695593.8144 | 1233817.7018
5 | 2695576.9833 | 1233824.6472 | 2695589.6435 | 1233819.4247 | 2695593.8144 | 1233817.7018
6 | 2695576.9833 | 1233824.6472 | 2695559.113 | 1233832.025
7 | 2695576.9833 | 1233824.6472 | 2695587.4486 | 1233855.1267 | 2695585.9355 | 1233872.4595 | 2695569.1917 | 1233878.0734
8 | 2695581.3735 | 1233978.0968 | 2695569.2304 | 1233943.2093
9 | 2695569.2304 | 1233943.2093 | 2695570.3266 | 1233922.1337 | 2695569.6942 | 1233912.7695
10 | 2695581.3735 | 1233978.0968 | 2695579.8266 | 1233978.7168 | 2695572.9085 | 1233981.4821
11 | 2695581.3735 | 1233978.0968 | 2695595.57 | 1233972.4209 | 2695602.2455 | 1233969.6618
12 | 2695569.6942 | 1233912.7695 | 2695569.4201 | 1233908.7107
13 | 2695634.6532 | 1233956.4046 | 2695631.5938 | 1233950.3287 | 2695626.4928 | 1233945.8087
14 | 2695634.6532 | 1233956.4046 | 2695644.9302 | 1233952.0001
15 | 2695634.6532 | 1233956.4046 | 2695631.3672 | 1233957.8195 | 2695625.4252 | 1233960.0811 | 2695602.2455 | 1233969.6618
16 | 2695569.1917 | 1233878.0734 | 2695567.3917 | 1233878.6769 | 2695569.4201 | 1233908.7107
17 | 2695572.9085 | 1233981.4821 | 2695566.3965 | 1233984.0851
18 | 2695549.178 | 1233990.9663 | 2695565.2795 | 1233984.5316 | 2695566.3965 | 1233984.0851
19 | 2695487.2774 | 1233861.6825 | 2695468.911 | 1233869.2652 | 2695443.9249 | 1233879.5811
20 | 2695443.9249 | 1233879.5811 | 2695420.2367 | 1233889.3611
21 | 2695667.7105 | 1234014.6126 | 2695688.7796 | 1234007.6578 | 2695694.5327 | 1233996.4422 | 2695699.1458 | 1233998.6514
22 | 2695699.1458 | 1233998.6514 | 2695701.7981 | 1233999.9173 | 2695707.6672 | 1233999.4872
23 | 2695667.7105 | 1234014.6126 | 2695660.7967 | 1233995.6097
24 | 2695667.7105 | 1234014.6126 | 2695628.0024 | 1234030.4296
25 | 2695714.8587 | 1233998.9602 | 2695707.6672 | 1233999.4872
26 | 2695644.9302 | 1233952.0001 | 2695678.6519 | 1233937.9123
27 | 2695644.9302 | 1233952.0001 | 2695658.4245 | 1233989.0896
28 | 2695658.4245 | 1233989.0896 | 2695660.7967 | 1233995.6097
29 | 2695736.0418 | 1233986.3477 | 2695731.0265 | 1233971.0446 | 2695732.4249 | 1233967.8981 | 2695732.3957 | 1233967.831 | 2695730.7025 | 1233965.78 | 2695725.4925 | 1233967.7197
30 | 2695714.8587 | 1233998.9602 | 2695721.8348 | 1233996.8933 | 2695737.274 | 1233991.16 | 2695736.0418 | 1233986.3477
31 | 2695628.0024 | 1234030.4296 | 2695621.7524 | 1234032.3828
32 | 2695549.178 | 1233990.9663 | 2695544.6974 | 1233992.7511
33 | 2695544.6974 | 1233992.7511 | 2695483.2713 | 1234017.3042 | 2695475.2613 | 1234020.5062
34 | 2695544.6974 | 1233992.7511 | 2695540.9171 | 1233982.0714 | 2695528.2448 | 1233987.127 | 2695522.2141 | 1233970.429
35 | 2695445.4602 | 1234032.4191 | 2695475.2613 | 1234020.5062
36 | 2695501.1717 | 1233979.0305 | 2695522.2141 | 1233970.429
37 | 2695424.7441 | 1234040.9927 | 2695438.222 | 1234035.2605 | 2695445.4602 | 1234032.4191
38 | 2695445.4602 | 1234032.4191 | 2695435.4664 | 1234003.6709 | 2695434.522 | 1234001.0682
39 | 2695501.1717 | 1233979.0305 | 2695502.7682 | 1233980.0346
40 | 2695596.2493 | 1234040.3529 | 2695621.7524 | 1234032.3828
41 | 2695568.3469 | 1234049.0726 | 2695538.6866 | 1234058.3408
42 | 2695572.7124 | 1234047.7085 | 2695568.3469 | 1234049.0726
43 | 2695572.7124 | 1234047.7085 | 2695581.1204 | 1234045.0808
44 | 2695581.1204 | 1234045.0808 | 2695596.2493 | 1234040.3529
45 | 2695424.7441 | 1234040.9927 | 2695420.359 | 1234028.3575 | 2695419.5213 | 1234025.8311 | 2695418.8052 | 1234023.86
46 | 2695405.1973 | 1233915.0312 | 2695413.972 | 1233940.6075
47 | 2695399.4795 | 1233917.0075 | 2695405.1973 | 1233915.0312
48 | 2695405.1973 | 1233915.0312 | 2695413.2234 | 1233912.2514
49 | 2695399.3078 | 1233898.002 | 2695405.1973 | 1233915.0312
50 | 2695399.4795 | 1233917.0075 | 2695405.7631 | 1233934.8916
51 | 2695413.2234 | 1233912.2514 | 2695419.9062 | 1233909.9369
52 | 2695399.3078 | 1233898.002 | 2695393.3334 | 1233900.3967 | 2695360.5833 | 1233913.8588
53 | 2695399.3078 | 1233898.002 | 2695417.8028 | 1233890.366
54 | 2695415.0095 | 1233961.2081 | 2695405.7631 | 1233934.8916
55 | 2695347.6165 | 1233919.3437 | 2695360.5833 | 1233913.8588
56 | 2695360.5833 | 1233913.8588 | 2695351.6365 | 1233888.6549
57 | 2695417.8028 | 1233890.366 | 2695420.2367 | 1233889.3611
58 | 2695347.6165 | 1233919.3437 | 2695305.4468 | 1233937.231
59 | 2695347.6165 | 1233919.3437 | 2695355.5552 | 1233939.7104
60 | 2695420.802 | 1233977.6942 | 2695415.0095 | 1233961.2081
61 | 2695412.5575 | 1234007.3502 | 2695396.5871 | 1234013.2985
62 | 2695412.5575 | 1234007.3502 | 2695410.7642 | 1234002.0953 | 2695409.846 | 1233999.4009 | 2695407.1417 | 1233991.4739 | 2695406.3318 | 1233989.1036 | 2695404.4448 | 1233983.5581 | 2695420.802 | 1233977.6942
63 | 2695412.5575 | 1234007.3502 | 2695413.1068 | 1234008.9713 | 2695413.6564 | 1234010.5813 | 2695416.1134 | 1234016.4584 | 2695417.0344 | 1234018.9861 | 2695418.8052 | 1234023.86
64 | 2695369.1387 | 1234061.4485 | 2695343.6174 | 1234070.424
65 | 2695369.1387 | 1234061.4485 | 2695355.9283 | 1234023.6533 | 2695356.9342 | 1234023.2625
66 | 2695319.8122 | 1234080.838 | 2695341.926 | 1234071.0189 | 2695343.6174 | 1234070.424
67 | 2695364.2022 | 1234020.4393 | 2695356.9342 | 1234023.2625
68 | 2695275.5005 | 1233952.8228 | 2695297.9592 | 1233940.4071 | 2695305.4468 | 1233937.231
69 | 2695224.5777 | 1233975.401 | 2695245.4025 | 1233957.6884 | 2695253.1744 | 1233953.1986 | 2695262.9384 | 1233946.7726 | 2695265.7706 | 1233945.795 | 2695269.1126 | 1233946.5492 | 2695271.2955 | 1233945.9281 | 2695275.5005 | 1233952.8228
70 | 2695275.5005 | 1233952.8228 | 2695277.4235 | 1233956.6008 | 2695281.5549 | 1233964.7842 | 2695293.5408 | 1234001.888
71 | 2695224.5777 | 1233975.401 | 2695217.7638 | 1233969.721 | 2695215.0698 | 1233967.9622
72 | 2695303.2946 | 1234032.0819 | 2695293.5408 | 1234001.888
73 | 2695303.2946 | 1234032.0819 | 2695313.668 | 1234062.6929 | 2695319.8122 | 1234080.838
74 | 2695319.8122 | 1234080.838 | 2695313.668 | 1234062.6929 | 2695295.8172 | 1234072.0135
75 | 2695295.8172 | 1234072.0135 | 2695283.4571 | 1234059.9954 | 2695270.8093 | 1234067.8284

## bus_geodata
| x | y | coords
0 | 2695631.6018 | 1233852.9687
1 | 2695680.0756 | 1233831.711
2 | 2695636.1864 | 1233863.5391
3 | 2695655.0044 | 1233792.3565
4 | 2695650.2212 | 1233882.034
5 | 2695593.8144 | 1233817.7018
6 | 2695576.9833 | 1233824.6472
7 | 2695569.2304 | 1233943.2093
8 | 2695581.3735 | 1233978.0968
9 | 2695569.6942 | 1233912.7695
10 | 2695626.4928 | 1233945.8087
11 | 2695634.6532 | 1233956.4046
12 | 2695569.4201 | 1233908.7107
13 | 2695569.1917 | 1233878.0734
14 | 2695572.9085 | 1233981.4821
15 | 2695602.2455 | 1233969.6618
16 | 2695559.113 | 1233832.025
17 | 2695566.3965 | 1233984.0851
18 | 2695487.2774 | 1233861.6825
19 | 2695443.9249 | 1233879.5811
20 | 2695699.1458 | 1233998.6514
21 | 2695667.7105 | 1234014.6126
22 | 2695707.6672 | 1233999.4872
23 | 2695678.6519 | 1233937.9123
24 | 2695644.9302 | 1233952.0001
25 | 2695658.4245 | 1233989.0896
26 | 2695660.7967 | 1233995.6097
27 | 2695736.0418 | 1233986.3477
28 | 2695725.4925 | 1233967.7197
29 | 2695714.8587 | 1233998.9602
30 | 2695628.0024 | 1234030.4296
31 | 2695549.178 | 1233990.9663
32 | 2695544.6975 | 1233992.7511
33 | 2695475.2613 | 1234020.5062
34 | 2695522.2141 | 1233970.429
35 | 2695445.4602 | 1234032.4191
36 | 2695501.1717 | 1233979.0305
37 | 2695621.7524 | 1234032.3828
38 | 2695568.3469 | 1234049.0726
39 | 2695538.6866 | 1234058.3408
40 | 2695572.7124 | 1234047.7085
41 | 2695581.1204 | 1234045.0808
42 | 2695596.2493 | 1234040.3529
43 | 2695502.7682 | 1233980.0346
44 | 2695424.7441 | 1234040.9927
45 | 2695434.522 | 1234001.0682
46 | 2695413.972 | 1233940.6075
47 | 2695405.1973 | 1233915.0312
48 | 2695399.4795 | 1233917.0075
49 | 2695413.2234 | 1233912.2514
50 | 2695399.3078 | 1233898.002
51 | 2695405.7631 | 1233934.8916
52 | 2695419.9062 | 1233909.9369
53 | 2695360.5833 | 1233913.8588
54 | 2695417.8028 | 1233890.366
55 | 2695347.6165 | 1233919.3437
56 | 2695351.6365 | 1233888.6549
57 | 2695415.0095 | 1233961.2081
58 | 2695420.2367 | 1233889.3611
59 | 2695412.5575 | 1234007.3502
60 | 2695396.5871 | 1234013.2985
61 | 2695420.802 | 1233977.6942
62 | 2695418.8052 | 1234023.86
63 | 2695369.1387 | 1234061.4485
64 | 2695343.6174 | 1234070.424
65 | 2695356.9342 | 1234023.2625
66 | 2695305.4468 | 1233937.231
67 | 2695355.5552 | 1233939.7104
68 | 2695275.5005 | 1233952.8228
69 | 2695224.5777 | 1233975.401
70 | 2695293.5408 | 1234001.888
71 | 2695303.2946 | 1234032.0819
72 | 2695319.8122 | 1234080.838
73 | 2695215.0698 | 1233967.9622
74 | 2695295.8172 | 1234072.0135
75 | 2695270.8093 | 1234067.8284
76 | 2695364.2022 | 1234020.4393
77 | 2695501.1717 | 1233979.0305

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98049 | -0.37606 | 0.0036686 | 0.00091944
1 | 0.98091 | -0.36783 | 0 | 0
2 | 0.98044 | -0.37709 | 0 | 0
3 | 0.98128 | -0.36057 | 0 | 0
4 | 0.98033 | -0.37928 | 0.0049091 | 0.0012303
5 | 0.98181 | -0.35029 | 0.0024012 | 0.00060179
6 | 0.98199 | -0.34667 | 0.012157 | 0.0030468
7 | 0.98853 | -0.2194 | 0 | 0
8 | 0.99257 | -0.14144 | 0 | 0
9 | 0.98519 | -0.28424 | 0.039063 | 0.0097902
10 | 0.98764 | -0.23673 | 0.0082665 | 0.0020718
11 | 0.98774 | -0.23472 | 0 | 0
12 | 0.98489 | -0.29007 | 0.035394 | 0.0088705
13 | 0.98358 | -0.31561 | 0.018782 | 0.0047072
14 | 0.99351 | -0.12345 | 0.0034648 | 0.00086835
15 | 0.99041 | -0.18315 | 0.021846 | 0.005475
16 | 0.98195 | -0.34753 | 0.0024379 | 0.00061101
17 | 0.994 | -0.11409 | 0.01362 | 0.0034134
18 | 0.98458 | -0.29443 | 0.0015189 | 0.00038066
19 | 0.98465 | -0.29314 | 0.0014883 | 0.000373
20 | 0.983 | -0.32693 | 0 | 0
21 | 0.98378 | -0.31179 | 0 | 0
22 | 0.98283 | -0.33029 | 0.0047263 | 0.0011845
23 | 0.98642 | -0.26036 | 0.01653 | 0.0041429
24 | 0.98698 | -0.24955 | 0 | 0
25 | 0.98487 | -0.29049 | 0.0077656 | 0.0019462
26 | 0.98455 | -0.29673 | 0.0087068 | 0.0021821
27 | 0.98229 | -0.34088 | 0 | 0
28 | 0.98187 | -0.34909 | 0.016327 | 0.004092
29 | 0.98272 | -0.33241 | 0 | 0
30 | 0.98298 | -0.3274 | 0 | 0
31 | 0.99537 | -0.087918 | 0 | 0
32 | 0.99572 | -0.081138 | 0 | 0
33 | 0.99376 | -0.11848 | 0.0017075 | 0.00042795
34 | 1 | 0 | -0.33465 | -0.085333
35 | 0.99293 | -0.13423 | 0 | 0
36 | 0.99994 | -0.0010736 | 0 | 0
37 | 0.98286 | -0.3298 | 0.0084187 | 0.0021099
38 | 0.98234 | -0.33991 | 0.0018042 | 0.00045219
39 | 0.98223 | -0.34207 | 0.0038451 | 0.00096368
40 | 0.98236 | -0.33945 | 0 | 0
41 | 0.98241 | -0.33855 | 0.0048597 | 0.001218
42 | 0.98256 | -0.33554 | 0.0013857 | 0.00034729
43 | 0.99994 | -0.0011625 | 0.002709 | 0.00067895
44 | 0.99237 | -0.14505 | 0 | 0
45 | 0.99289 | -0.13508 | 0.0014541 | 0.00036443
46 | 0.98582 | -0.27045 | 0.0012088 | 0.00030295
47 | 0.98585 | -0.26986 | 0 | 0
48 | 0.98621 | -0.26292 | 0 | 0
49 | 0.98585 | -0.27 | 0.00039053 | 9.7875e-05
50 | 0.98481 | -0.28994 | 0 | 0
51 | 0.98735 | -0.24114 | 0.0019685 | 0.00049334
52 | 0.98584 | -0.27007 | 0.00051406 | 0.00012884
53 | 0.98257 | -0.3333 | 0 | 0
54 | 0.98473 | -0.29157 | 0.00066185 | 0.00016588
55 | 0.98185 | -0.34729 | 0 | 0
56 | 0.98251 | -0.33446 | 0.0023999 | 0.00060148
57 | 0.98906 | -0.2082 | 0.0018916 | 0.00047408
58 | 0.98472 | -0.29176 | 0.00087375 | 0.00021898
59 | 0.99151 | -0.16135 | 0 | 0
60 | 0.99145 | -0.16262 | 0.0041973 | 0.001052
61 | 0.99017 | -0.18704 | 0 | 0
62 | 0.99191 | -0.15382 | 0.0096201 | 0.002411
63 | 0.97253 | -0.52988 | 0 | 0
64 | 0.97277 | -0.52523 | 0.0082796 | 0.0020751
65 | 0.97217 | -0.53694 | 0.0073241 | 0.0018356
66 | 0.9796 | -0.39111 | 0.0052908 | 0.001326
67 | 0.98181 | -0.34821 | 0.0023385 | 0.00058607
68 | 0.97811 | -0.42031 | 0 | 0
69 | 0.97802 | -0.42197 | 0 | 0
70 | 0.97586 | -0.4644 | 0.011755 | 0.0029461
71 | 0.97484 | -0.48435 | 0 | 0
72 | 0.97319 | -0.51681 | 0 | 0
73 | 0.978 | -0.42229 | 0.001412 | 0.00035388
74 | 0.97258 | -0.52891 | 0 | 0
75 | 0.97208 | -0.53881 | 0.016722 | 0.0041909
76 | 0.97216 | -0.53722 | 0.001991 | 0.00049899
77 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0085785 | -0.0021498 | 0.0085819 | 0.0021513 | 3.3642e-06 | 1.4852e-06 | 0.013019 | 0.013019 | 0.013019 | 0.98049 | -0.37606 | 0.98091 | -0.36783 | 3.5766
1 | 0.0049099 | 0.0012304 | -0.0049097 | -0.0012304 | 2.399e-07 | 8.2232e-09 | 0.0074513 | 0.0074514 | 0.0074514 | 0.98049 | -0.37606 | 0.98044 | -0.37709 | 2.0471
2 | -0.0085819 | -0.0021513 | 0.0085849 | 0.0021526 | 2.9687e-06 | 1.3101e-06 | 0.013019 | 0.013018 | 0.013019 | 0.98091 | -0.36783 | 0.98128 | -0.36057 | 3.5766
3 | 0.0049097 | 0.0012304 | -0.0049091 | -0.0012303 | 5.1261e-07 | 1.763e-08 | 0.0074514 | 0.0074515 | 0.0074515 | 0.98044 | -0.37709 | 0.98033 | -0.37928 | 2.0471
4 | -0.0085849 | -0.0021526 | 0.0085891 | 0.0021545 | 4.2093e-06 | 1.8568e-06 | 0.013018 | 0.013018 | 0.013018 | 0.98128 | -0.36057 | 0.98181 | -0.35029 | 3.5765
5 | -0.01099 | -0.0027563 | 0.010992 | 0.0027572 | 1.8945e-06 | 9.8218e-07 | 0.016657 | 0.016657 | 0.016657 | 0.98181 | -0.35029 | 0.98199 | -0.34667 | 4.5762
6 | 0.002438 | 0.00061082 | -0.0024379 | -0.00061101 | 9.895e-08 | -1.8125e-07 | 0.0036943 | 0.0036944 | 0.0036944 | 0.98199 | -0.34667 | 0.98195 | -0.34753 | 1.0149
7 | -0.025587 | -0.0064148 | 0.025625 | 0.0064382 | 3.7931e-05 | 2.3423e-05 | 0.038773 | 0.038772 | 0.038773 | 0.98199 | -0.34667 | 0.98358 | -0.31561 | 10.6518
8 | -0.11931 | -0.03009 | 0.11976 | 0.030376 | 0.00044705 | 0.00028564 | 0.17966 | 0.17966 | 0.17966 | 0.98853 | -0.2194 | 0.99257 | -0.14144 | 49.3576
9 | 0.11931 | 0.03009 | -0.11894 | -0.029855 | 0.00036906 | 0.00023581 | 0.17966 | 0.17966 | 0.17966 | 0.98853 | -0.2194 | 0.98519 | -0.28424 | 49.3577
10 | -0.22493 | -0.056999 | 0.22512 | 0.057123 | 0.00019463 | 0.00012433 | 0.33743 | 0.33743 | 0.33743 | 0.99257 | -0.14144 | 0.99351 | -0.12345 | 46.3498
11 | 0.10517 | 0.026623 | -0.10496 | -0.026489 | 0.00021012 | 0.00013419 | 0.15776 | 0.15776 | 0.15776 | 0.99257 | -0.14144 | 0.99041 | -0.18315 | 43.342
12 | 0.079877 | 0.020064 | -0.079855 | -0.02005 | 2.221e-05 | 1.4163e-05 | 0.12066 | 0.12066 | 0.12066 | 0.98519 | -0.28424 | 0.98489 | -0.29007 | 33.1487
13 | -0.0082665 | -0.0020718 | 0.0082673 | 0.0020721 | 7.9215e-07 | 3.3269e-07 | 0.012455 | 0.012455 | 0.012455 | 0.98764 | -0.23673 | 0.98774 | -0.23472 | 3.4216
14 | 0.074646 | 0.018811 | -0.074593 | -0.018777 | 5.2928e-05 | 3.3731e-05 | 0.11249 | 0.11249 | 0.11249 | 0.98774 | -0.23472 | 0.98698 | -0.24955 | 30.9036
15 | -0.082913 | -0.020883 | 0.083118 | 0.021014 | 0.00020499 | 0.00013075 | 0.12494 | 0.12494 | 0.12494 | 0.98774 | -0.23472 | 0.99041 | -0.18315 | 34.3252
16 | 0.044461 | 0.01118 | -0.044407 | -0.011145 | 5.417e-05 | 3.4262e-05 | 0.067187 | 0.067187 | 0.067187 | 0.98489 | -0.29007 | 0.98358 | -0.31561 | 18.458
17 | -0.22859 | -0.057992 | 0.22869 | 0.058057 | 0.0001029 | 6.5585e-05 | 0.34262 | 0.34262 | 0.34262 | 0.99351 | -0.12345 | 0.994 | -0.11409 | 31.375
18 | -0.24231 | -0.06147 | 0.24262 | 0.061665 | 0.00030542 | 0.00019475 | 0.363 | 0.363 | 0.363 | 0.994 | -0.11409 | 0.99537 | -0.087918 | 33.2421
19 | -0.0015189 | -0.00038066 | 0.0015189 | 0.00038012 | 9.2667e-08 | -5.3723e-07 | 0.0022955 | 0.0022953 | 0.0022955 | 0.98458 | -0.29443 | 0.98465 | -0.29314 | 0.63062
20 | -0.0030072 | -0.00075312 | 0.0030074 | 0.00075292 | 1.9846e-07 | -1.9898e-07 | 0.0045444 | 0.0045443 | 0.0045444 | 0.98465 | -0.29314 | 0.98472 | -0.29176 | 1.2485
21 | -0.021071 | -0.0052871 | 0.021087 | 0.0052963 | 1.5228e-05 | 9.2394e-06 | 0.031899 | 0.031899 | 0.031899 | 0.983 | -0.32693 | 0.98378 | -0.31179 | 8.7634
22 | 0.021071 | 0.0052871 | -0.021068 | -0.005285 | 3.3669e-06 | 2.043e-06 | 0.031899 | 0.031899 | 0.031899 | 0.983 | -0.32693 | 0.98283 | -0.33029 | 8.7635
23 | -0.041423 | -0.0104 | 0.041453 | 0.010419 | 2.9775e-05 | 1.8799e-05 | 0.062661 | 0.062661 | 0.062661 | 0.98378 | -0.31179 | 0.98455 | -0.29673 | 17.2147
24 | 0.020337 | 0.005104 | -0.020321 | -0.0050949 | 1.5131e-05 | 9.1427e-06 | 0.030763 | 0.030763 | 0.030763 | 0.98378 | -0.31179 | 0.98298 | -0.3274 | 8.4513
25 | 0.016342 | 0.0041005 | -0.01634 | -0.0040996 | 1.6555e-06 | 9.6815e-07 | 0.024743 | 0.024743 | 0.024743 | 0.98283 | -0.33029 | 0.98272 | -0.33241 | 6.7976
26 | -0.01653 | -0.0041429 | 0.016539 | 0.0041479 | 8.5217e-06 | 4.9871e-06 | 0.024936 | 0.024936 | 0.024936 | 0.98642 | -0.26036 | 0.98698 | -0.24955 | 6.8506
27 | 0.058054 | 0.014629 | -0.05794 | -0.014557 | 0.00011345 | 7.2108e-05 | 0.087553 | 0.087553 | 0.087553 | 0.98698 | -0.24955 | 0.98487 | -0.29049 | 24.0531
28 | 0.050175 | 0.012611 | -0.05016 | -0.012601 | 1.4957e-05 | 9.4844e-06 | 0.075821 | 0.075821 | 0.075821 | 0.98487 | -0.29049 | 0.98455 | -0.29673 | 20.8298
29 | 0.016334 | 0.0040957 | -0.016327 | -0.004092 | 6.3917e-06 | 3.7384e-06 | 0.024744 | 0.024744 | 0.024744 | 0.98229 | -0.34088 | 0.98187 | -0.34909 | 6.7977
30 | -0.016334 | -0.0040957 | 0.01634 | 0.0040996 | 6.5922e-06 | 3.8554e-06 | 0.024744 | 0.024743 | 0.024744 | 0.98229 | -0.34088 | 0.98272 | -0.33241 | 6.7977
31 | 0.020321 | 0.0050949 | -0.020319 | -0.0050935 | 2.3238e-06 | 1.4042e-06 | 0.030763 | 0.030763 | 0.030763 | 0.98298 | -0.3274 | 0.98286 | -0.3298 | 8.4513
32 | -0.24262 | -0.061665 | 0.2427 | 0.061716 | 7.9244e-05 | 5.0528e-05 | 0.363 | 0.363 | 0.363 | 0.99537 | -0.087918 | 0.99572 | -0.081138 | 33.2421
33 | 0.086298 | 0.022112 | -0.086142 | -0.022015 | 0.00015588 | 9.6849e-05 | 0.12914 | 0.12914 | 0.12914 | 0.99572 | -0.081138 | 0.99376 | -0.11848 | 11.8258
34 | -0.32899 | -0.083828 | 0.33029 | 0.084654 | 0.0012935 | 0.00082619 | 0.49214 | 0.49214 | 0.49214 | 0.99572 | -0.081138 | 1 | 0 | 45.0677
35 | 0.084434 | 0.021587 | -0.08437 | -0.021547 | 6.4279e-05 | 3.9892e-05 | 0.12658 | 0.12658 | 0.12658 | 0.99376 | -0.11848 | 0.99293 | -0.13423 | 11.5917
36 | 0.0027092 | 0.00067872 | -0.002709 | -0.00067893 | 1.3854e-07 | -2.0956e-07 | 0.0040312 | 0.0040313 | 0.0040313 | 1 | 0 | 0.99994 | -0.0010736 | 1.1075
37 | 0.082916 | 0.021183 | -0.082872 | -0.021157 | 4.3375e-05 | 2.6891e-05 | 0.1244 | 0.1244 | 0.1244 | 0.99293 | -0.13423 | 0.99237 | -0.14505 | 11.3921
38 | 0.0014542 | 0.00036404 | -0.0014541 | -0.00036443 | 5.9129e-08 | -3.9162e-07 | 0.0021791 | 0.0021792 | 0.0021792 | 0.99293 | -0.13423 | 0.99289 | -0.13508 | 0.59869
39 | 0.002709 | 0.00067893 | -0.002709 | -0.00067895 | 1.147e-08 | -1.7347e-08 | 0.0040313 | 0.0040313 | 0.0040313 | 0.99994 | -0.0010736 | 0.99994 | -0.0011625 | 1.1075
40 | 0.0119 | 0.0029836 | -0.011897 | -0.0029818 | 3.2526e-06 | 1.7432e-06 | 0.018017 | 0.018017 | 0.018017 | 0.98286 | -0.3298 | 0.98256 | -0.33554 | 4.9498
41 | 0.0038455 | 0.00096354 | -0.0038451 | -0.00096368 | 3.9541e-07 | -1.403e-07 | 0.005825 | 0.0058252 | 0.0058252 | 0.98234 | -0.33991 | 0.98223 | -0.34207 | 1.6003
42 | -0.0056498 | -0.0014157 | 0.0056499 | 0.0014158 | 1.2561e-07 | 2.249e-08 | 0.008558 | 0.008558 | 0.008558 | 0.98234 | -0.33991 | 0.98236 | -0.33945 | 2.3511
43 | -0.0056499 | -0.0014158 | 0.0056502 | 0.0014158 | 2.4194e-07 | 4.3308e-08 | 0.008558 | 0.008558 | 0.008558 | 0.98236 | -0.33945 | 0.98241 | -0.33855 | 2.3511
44 | -0.01051 | -0.0026338 | 0.010511 | 0.0026345 | 1.5062e-06 | 7.6326e-07 | 0.015919 | 0.015919 | 0.015919 | 0.98241 | -0.33855 | 0.98256 | -0.33554 | 4.3733
45 | 0.082872 | 0.021157 | -0.082837 | -0.021135 | 3.5079e-05 | 2.1748e-05 | 0.1244 | 0.1244 | 0.1244 | 0.99237 | -0.14505 | 0.99191 | -0.15382 | 11.3922
46 | -0.0012088 | -0.00030295 | 0.0012088 | 0.00030263 | 3.3753e-08 | -3.2316e-07 | 0.0018245 | 0.0018244 | 0.0018245 | 0.98582 | -0.27045 | 0.98585 | -0.26986 | 0.50125
47 | -0.064781 | -0.016465 | 0.064802 | 0.016478 | 2.1669e-05 | 1.3791e-05 | 0.09786 | 0.09786 | 0.09786 | 0.98585 | -0.26986 | 0.98621 | -0.26292 | 26.8846
48 | 0.00090459 | 0.00022652 | -0.00090459 | -0.00022662 | 5.9374e-09 | -1.045e-07 | 0.0013653 | 0.0013653 | 0.0013653 | 0.98585 | -0.26986 | 0.98585 | -0.27 | 0.37509
49 | 0.062667 | 0.015936 | -0.062607 | -0.015897 | 6.0547e-05 | 3.8521e-05 | 0.09467 | 0.09467 | 0.09467 | 0.98585 | -0.26986 | 0.98481 | -0.28994 | 26.0083
50 | -0.064802 | -0.016478 | 0.06487 | 0.016522 | 6.8075e-05 | 4.3326e-05 | 0.09786 | 0.09786 | 0.09786 | 0.98621 | -0.26292 | 0.98735 | -0.24114 | 26.8846
51 | 0.00051406 | 0.00012875 | -0.00051406 | -0.00012884 | 1.5966e-09 | -8.9154e-08 | 0.00077588 | 0.00077591 | 0.00077591 | 0.98585 | -0.27 | 0.98584 | -0.27007 | 0.21316
52 | 0.058063 | 0.014759 | -0.057942 | -0.014682 | 0.00012098 | 7.6898e-05 | 0.087806 | 0.087806 | 0.087806 | 0.98481 | -0.28994 | 0.98257 | -0.3333 | 24.1225
53 | 0.0045434 | 0.0011377 | -0.0045431 | -0.0011378 | 3.5359e-07 | -2.8276e-08 | 0.0068646 | 0.0068647 | 0.0068647 | 0.98481 | -0.28994 | 0.98473 | -0.29157 | 1.8859
54 | -0.066839 | -0.017015 | 0.066945 | 0.017083 | 0.00010634 | 6.7698e-05 | 0.10083 | 0.10083 | 0.10083 | 0.98735 | -0.24114 | 0.98906 | -0.2082 | 27.6996
55 | 0.055542 | 0.014081 | -0.055505 | -0.014057 | 3.7315e-05 | 2.3704e-05 | 0.084171 | 0.084171 | 0.084171 | 0.98257 | -0.3333 | 0.98185 | -0.34729 | 23.124
56 | 0.0024001 | 0.00060123 | -0.0023999 | -0.00060148 | 1.3249e-07 | -2.5393e-07 | 0.0036346 | 0.0036347 | 0.0036347 | 0.98257 | -0.3333 | 0.98251 | -0.33446 | 0.99854
57 | 0.0038812 | 0.0009719 | -0.0038812 | -0.00097191 | 3.3961e-08 | -1.1763e-08 | 0.0058646 | 0.0058646 | 0.0058646 | 0.98473 | -0.29157 | 0.98472 | -0.29176 | 1.6112
58 | 0.053166 | 0.013472 | -0.053055 | -0.013401 | 0.00011167 | 7.0889e-05 | 0.080627 | 0.080628 | 0.080628 | 0.98185 | -0.34729 | 0.9796 | -0.39111 | 22.1504
59 | 0.0023386 | 0.00058586 | -0.0023385 | -0.00058607 | 1.0296e-07 | -2.1055e-07 | 0.003544 | 0.0035441 | 0.0035441 | 0.98185 | -0.34729 | 0.98181 | -0.34821 | 0.97366
60 | -0.068837 | -0.017557 | 0.068907 | 0.017602 | 7.0429e-05 | 4.485e-05 | 0.10367 | 0.10367 | 0.10367 | 0.98906 | -0.2082 | 0.99017 | -0.18704 | 28.4814
61 | 0.0041976 | 0.0010519 | -0.0041973 | -0.001052 | 2.5361e-07 | -5.7473e-08 | 0.0062995 | 0.0062996 | 0.0062996 | 0.99151 | -0.16135 | 0.99145 | -0.16262 | 1.7307
62 | 0.068993 | 0.017655 | -0.068907 | -0.017602 | 8.5675e-05 | 5.3737e-05 | 0.10367 | 0.10367 | 0.10367 | 0.99151 | -0.16135 | 0.99017 | -0.18704 | 14.2407
63 | -0.07319 | -0.018707 | 0.073217 | 0.018724 | 2.6695e-05 | 1.6401e-05 | 0.10997 | 0.10997 | 0.10997 | 0.99151 | -0.16135 | 0.99191 | -0.15382 | 10.0706
64 | -0.0093182 | -0.002336 | 0.0093203 | 0.002337 | 2.0622e-06 | 9.8406e-07 | 0.014257 | 0.014257 | 0.014257 | 0.97253 | -0.52988 | 0.97277 | -0.52523 | 3.9169
65 | 0.0093182 | 0.002336 | -0.0093151 | -0.0023345 | 3.1343e-06 | 1.4959e-06 | 0.014257 | 0.014258 | 0.014258 | 0.97253 | -0.52988 | 0.97217 | -0.53694 | 3.9169
66 | -0.0176 | -0.004412 | 0.017607 | 0.0044162 | 7.0639e-06 | 4.1981e-06 | 0.026922 | 0.026922 | 0.026922 | 0.97277 | -0.52523 | 0.97319 | -0.51681 | 7.3963
67 | 0.001991 | 0.00049891 | -0.001991 | -0.00049899 | 2.7154e-08 | -7.9298e-08 | 0.0030474 | 0.0030475 | 0.0030475 | 0.97217 | -0.53694 | 0.97216 | -0.53722 | 0.83721
68 | 0.047764 | 0.012075 | -0.047697 | -0.012032 | 6.6781e-05 | 4.2315e-05 | 0.072591 | 0.072591 | 0.072591 | 0.9796 | -0.39111 | 0.97811 | -0.42031 | 19.9426
69 | 0.0014121 | 0.000353 | -0.001412 | -0.00035374 | 1.1208e-07 | -7.4114e-07 | 0.002148 | 0.0021482 | 0.0021482 | 0.97811 | -0.42031 | 0.97802 | -0.42197 | 0.59018
70 | 0.046285 | 0.011679 | -0.046188 | -0.011618 | 9.7505e-05 | 6.1747e-05 | 0.070443 | 0.070443 | 0.070443 | 0.97811 | -0.42031 | 0.97586 | -0.4644 | 19.3526
71 | 0.001412 | 0.00035374 | -0.001412 | -0.00035388 | 2.092e-08 | -1.383e-07 | 0.0021482 | 0.0021483 | 0.0021483 | 0.97802 | -0.42197 | 0.978 | -0.42229 | 0.59019
72 | 0.034432 | 0.0086715 | -0.0344 | -0.0086509 | 3.282e-05 | 2.0609e-05 | 0.052519 | 0.052519 | 0.052519 | 0.97586 | -0.4644 | 0.97484 | -0.48435 | 14.4283
73 | 0.0344 | 0.0086509 | -0.034346 | -0.0086175 | 5.3246e-05 | 3.3437e-05 | 0.052519 | 0.052519 | 0.052519 | 0.97484 | -0.48435 | 0.97319 | -0.51681 | 14.4284
74 | 0.016739 | 0.0042013 | -0.01673 | -0.0041956 | 9.6548e-06 | 5.6912e-06 | 0.025597 | 0.025597 | 0.025597 | 0.97319 | -0.51681 | 0.97258 | -0.52891 | 7.0322
75 | 0.01673 | 0.0041956 | -0.016722 | -0.0041909 | 7.8912e-06 | 4.652e-06 | 0.025597 | 0.025597 | 0.025597 | 0.97258 | -0.52891 | 0.97208 | -0.53881 | 7.0322

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36089 | 0.091911

## res_load
| p_mw | q_mvar
0 | 0.0036686 | 0.00091944
1 | 0.0049091 | 0.0012303
2 | 0.0024012 | 0.00060179
3 | 0.012157 | 0.0030468
4 | 0.039063 | 0.0097902
5 | 0.0082665 | 0.0020718
6 | 0.035394 | 0.0088705
7 | 0.018782 | 0.0047072
8 | 0.0034648 | 0.00086835
9 | 0.021846 | 0.005475
10 | 0.0024379 | 0.00061101
11 | 0.01362 | 0.0034134
12 | 0.0015189 | 0.00038066
13 | 0.0014883 | 0.000373
14 | 0.0047263 | 0.0011845
15 | 0.01653 | 0.0041429
16 | 0.0077656 | 0.0019462
17 | 0.0087068 | 0.0021821
18 | 0.016327 | 0.004092
19 | 0.0017075 | 0.00042795
20 | 0.026247 | 0.0065782
21 | 0.0084187 | 0.0021099
22 | 0.0018042 | 0.00045219
23 | 0.0038451 | 0.00096368
24 | 0.0048597 | 0.001218
25 | 0.0013857 | 0.00034729
26 | 0.002709 | 0.00067895
27 | 0.0014541 | 0.00036443
28 | 0.0012088 | 0.00030295
29 | 0.00039053 | 9.7875e-05
30 | 0.0019685 | 0.00049334
31 | 0.00051406 | 0.00012884
32 | 0.00066185 | 0.00016588
33 | 0.0023999 | 0.00060148
34 | 0.0018916 | 0.00047408
35 | 0.00087375 | 0.00021898
36 | 0.0041973 | 0.001052
37 | 0.0096201 | 0.002411
38 | 0.0082796 | 0.0020751
39 | 0.0073241 | 0.0018356
40 | 0.0052908 | 0.001326
41 | 0.0023385 | 0.00058607
42 | 0.011755 | 0.0029461
43 | 0.001412 | 0.00035388
44 | 0.016722 | 0.0041909
45 | 0.001991 | 0.00049899

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1