## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_156-20_1_3_node_2 | 0.4 | n |  | TRUE
1 | bus_LV_156-20_1_3_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_156-20_1_3_node_35 | 0.4 | n |  | TRUE
3 | bus_LV_156-20_1_3_node_105 | 0.4 | n |  | TRUE
4 | bus_LV_156-20_1_3_node_40 | 0.4 | n |  | TRUE
5 | bus_LV_156-20_1_3_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_156-20_1_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_156-20_1_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_156-20_1_3_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_156-20_1_3_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_156-20_1_3_node_56 | 0.4 | n |  | TRUE
11 | bus_LV_156-20_1_3_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_156-20_1_3_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_156-20_1_3_node_50 | 0.4 | n |  | TRUE
14 | bus_LV_156-20_1_3_node_109 | 0.4 | n |  | TRUE
15 | bus_LV_156-20_1_3_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_156-20_1_3_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_156-20_1_3_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_156-20_1_3_node_96 | 0.4 | n |  | TRUE
19 | bus_LV_156-20_1_3_node_112 | 0.4 | n |  | TRUE
20 | bus_LV_156-20_1_3_node_92 | 0.4 | n |  | TRUE
21 | bus_LV_156-20_1_3_node_47 | 0.4 | n |  | TRUE
22 | bus_LV_156-20_1_3_node_100 | 0.4 | n |  | TRUE
23 | bus_LV_156-20_1_3_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_156-20_1_3_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_156-20_1_3_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_156-20_1_3_node_53 | 0.4 | n |  | TRUE
27 | bus_LV_156-20_1_3_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_156-20_1_3_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_156-20_1_3_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_156-20_1_3_node_90 | 0.4 | n |  | TRUE
31 | bus_LV_156-20_1_3_node_132 | 0.4 | n |  | TRUE
32 | bus_LV_156-20_1_3_node_106 | 0.4 | n |  | TRUE
33 | bus_LV_156-20_1_3_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_156-20_1_3_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_156-20_1_3_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_156-20_1_3_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_156-20_1_3_node_94 | 0.4 | n |  | TRUE
38 | bus_LV_156-20_1_3_node_111 | 0.4 | n |  | TRUE
39 | bus_LV_156-20_1_3_node_101 | 0.4 | n |  | TRUE
40 | bus_LV_156-20_1_3_node_79 | 0.4 | n |  | TRUE
41 | bus_LV_156-20_1_3_node_67 | 0.4 | n |  | TRUE
42 | bus_LV_156-20_1_3_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_156-20_1_3_node_74 | 0.4 | n |  | TRUE
44 | bus_LV_156-20_1_3_node_84 | 0.4 | n |  | TRUE
45 | bus_LV_156-20_1_3_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_156-20_1_3_node_107 | 0.4 | n |  | TRUE
47 | bus_LV_156-20_1_3_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_156-20_1_3_node_69 | 0.4 | n |  | TRUE
49 | bus_LV_156-20_1_3_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_156-20_1_3_node_76 | 0.4 | n |  | TRUE
51 | bus_LV_156-20_1_3_node_73 | 0.4 | n |  | TRUE
52 | bus_LV_156-20_1_3_node_129 | 0.4 | n |  | TRUE
53 | bus_LV_156-20_1_3_node_80 | 0.4 | n |  | TRUE
54 | bus_LV_156-20_1_3_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_156-20_1_3_node_81 | 0.4 | n |  | TRUE
56 | bus_LV_156-20_1_3_node_82 | 0.4 | n |  | TRUE
57 | bus_LV_156-20_1_3_node_85 | 0.4 | n |  | TRUE
58 | bus_LV_156-20_1_3_node_86 | 0.4 | n |  | TRUE
59 | bus_LV_156-20_1_3_node_87 | 0.4 | n |  | TRUE
60 | bus_LV_156-20_1_3_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_156-20_1_3_node_89 | 0.4 | n |  | TRUE
62 | bus_LV_156-20_1_3_node_110 | 0.4 | n |  | TRUE
63 | bus_LV_156-20_1_3_node_93 | 0.4 | n |  | TRUE
64 | bus_LV_156-20_1_3_node_95 | 0.4 | n |  | TRUE
65 | bus_LV_156-20_1_3_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_156-20_1_3_node_108 | 0.4 | n |  | TRUE
67 | bus_MV_495_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_156-20_1_3_load_2 | 0 | 0.0122 | 0.0030576 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_156-20_1_3_load_10 | 1 | 0.0061264 | 0.0015354 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_156-20_1_3_load_105 | 3 | 0.002739 | 0.00068645 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_156-20_1_3_load_36 | 5 | 0.0034765 | 0.00087129 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_156-20_1_3_load_37 | 6 | 0.0017812 | 0.00044642 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_156-20_1_3_load_56 | 10 | 0.00068716 | 0.00017222 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_156-20_1_3_load_64 | 11 | 0.00062574 | 0.00015683 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_156-20_1_3_load_109 | 14 | 0.0022393 | 0.00056122 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_156-20_1_3_load_112 | 19 | 0.0060825 | 0.0015244 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_156-20_1_3_load_92 | 20 | 0.0010525 | 0.00026377 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_156-20_1_3_load_100 | 22 | 0.0083323 | 0.0020883 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_156-20_1_3_load_78 | 24 | 0.0014181 | 0.00035541 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_156-20_1_3_load_68 | 25 | 0.014879 | 0.0037291 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_156-20_1_3_load_83 | 27 | 0.079869 | 0.020017 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_156-20_1_3_load_77 | 29 | 0.0065273 | 0.0016359 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_156-20_1_3_load_90 | 30 | 0.0046383 | 0.0011625 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_156-20_1_3_load_132 | 31 | 0.017816 | 0.0044651 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_156-20_1_3_load_106 | 32 | 0.0016051 | 0.00040227 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_156-20_1_3_load_57 | 33 | 0.00046021 | 0.00011534 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_156-20_1_3_load_58 | 34 | 0.0020356 | 0.00051017 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_156-20_1_3_load_59 | 35 | 0.0022075 | 0.00055326 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_156-20_1_3_load_71 | 36 | 0.0051229 | 0.0012839 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_156-20_1_3_load_94 | 37 | 0.0057447 | 0.0014398 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_156-20_1_3_load_111 | 38 | 0.0082476 | 0.0020671 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_156-20_1_3_load_101 | 39 | 0.0011356 | 0.00028461 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_156-20_1_3_load_79 | 40 | 0.0018453 | 0.00046248 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_156-20_1_3_load_67 | 41 | 0.0078322 | 0.0019629 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_156-20_1_3_load_75 | 42 | 0.0052603 | 0.0013184 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_156-20_1_3_load_91 | 45 | 0.0018978 | 0.00047565 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_156-20_1_3_load_107 | 46 | 0.0019156 | 0.0004801 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_156-20_1_3_load_60 | 47 | 0.0022383 | 0.00056097 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_156-20_1_3_load_73 | 51 | 0.0056539 | 0.001417 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_156-20_1_3_load_129 | 52 | 0.0073109 | 0.0018323 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_156-20_1_3_load_72 | 54 | 0.028888 | 0.0072399 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_156-20_1_3_load_81 | 55 | 0.0036033 | 0.00090308 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_156-20_1_3_load_82 | 56 | 0.018079 | 0.004531 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_156-20_1_3_load_85 | 57 | 0.0051346 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_156-20_1_3_load_86 | 58 | 0.0016127 | 0.00040418 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_156-20_1_3_load_88 | 60 | 0.0014019 | 0.00035136 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_156-20_1_3_load_110 | 62 | 0.0037843 | 0.00094844 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_156-20_1_3_load_93 | 63 | 0.0057501 | 0.0014411 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_156-20_1_3_load_95 | 64 | 0.052331 | 0.013115 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_156-20_1_3_load_102 | 65 | 0.0063548 | 0.0015927 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_156-20_1_3_load_108 | 66 | 0.00062723 | 0.0001572 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_156-20_1_3_line_0 |  | 0 | 1 | 0.063085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_156-20_1_3_line_1 |  | 1 | 2 | 0.018924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_156-20_1_3_line_2 |  | 2 | 3 | 0.06126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_156-20_1_3_line_3 |  | 3 | 4 | 0.067067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_156-20_1_3_line_4 |  | 4 | 7 | 0.028551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_156-20_1_3_line_5 |  | 5 | 6 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_156-20_1_3_line_6 |  | 5 | 7 | 0.028154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_156-20_1_3_line_7 |  | 6 | 8 | 0.066121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_156-20_1_3_line_8 |  | 7 | 9 | 0.084005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_156-20_1_3_line_9 |  | 8 | 10 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_156-20_1_3_line_10 |  | 8 | 11 | 0.029297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_156-20_1_3_line_11 |  | 9 | 25 | 0.016689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_156-20_1_3_line_12 |  | 10 | 33 | 0.022636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_156-20_1_3_line_13 |  | 11 | 47 | 0.0096122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_156-20_1_3_line_14 |  | 12 | 13 | 0.009945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_156-20_1_3_line_15 |  | 12 | 14 | 0.017954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_156-20_1_3_line_16 |  | 13 | 28 | 0.041942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_156-20_1_3_line_17 |  | 13 | 29 | 0.017453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_156-20_1_3_line_18 |  | 14 | 36 | 0.028767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_156-20_1_3_line_19 |  | 15 | 16 | 0.058497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_156-20_1_3_line_20 |  | 15 | 17 | 0.037354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_156-20_1_3_line_21 |  | 15 | 18 | 0.011345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_156-20_1_3_line_22 |  | 15 | 19 | 0.035019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_156-20_1_3_line_23 |  | 16 | 20 | 0.012399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_156-20_1_3_line_24 |  | 16 | 21 | 0.052061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_156-20_1_3_line_25 |  | 16 | 22 | 0.010216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_156-20_1_3_line_26 |  | 17 | 26 | 0.28505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_156-20_1_3_line_27 |  | 17 | 27 | 0.018628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_156-20_1_3_line_28 |  | 18 | 37 | 0.021301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_156-20_1_3_line_29 |  | 19 | 38 | 0.020289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_156-20_1_3_line_30 |  | 21 | 23 | 0.033922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_156-20_1_3_line_31 |  | 21 | 24 | 0.021932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_156-20_1_3_line_32 |  | 22 | 39 | 0.0096504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_156-20_1_3_line_33 |  | 23 | 30 | 0.017766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_156-20_1_3_line_34 |  | 24 | 40 | 0.002328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_156-20_1_3_line_35 |  | 25 | 41 | 0.02424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_156-20_1_3_line_36 |  | 26 | 31 | 0.019967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_156-20_1_3_line_37 |  | 27 | 44 | 0.035012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_156-20_1_3_line_38 |  | 28 | 32 | 0.032047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_156-20_1_3_line_39 |  | 30 | 45 | 0.0013864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_156-20_1_3_line_40 |  | 32 | 46 | 0.05316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_156-20_1_3_line_41 |  | 34 | 35 | 0.0030218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_156-20_1_3_line_42 |  | 35 | 47 | 0.019964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_156-20_1_3_line_43 |  | 36 | 48 | 0.010608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_156-20_1_3_line_44 |  | 37 | 63 | 0.00087494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_156-20_1_3_line_45 |  | 39 | 65 | 0.030473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_156-20_1_3_line_46 |  | 40 | 53 | 0.014419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_156-20_1_3_line_47 |  | 41 | 48 | 0.0059315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_156-20_1_3_line_48 |  | 42 | 43 | 0.025781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_156-20_1_3_line_49 |  | 43 | 54 | 0.019563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_156-20_1_3_line_50 |  | 44 | 57 | 0.019907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_156-20_1_3_line_51 |  | 45 | 61 | 0.024506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_156-20_1_3_line_52 |  | 46 | 66 | 0.015219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_156-20_1_3_line_53 |  | 48 | 49 | 0.021047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_156-20_1_3_line_54 |  | 49 | 50 | 0.017849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_156-20_1_3_line_55 |  | 49 | 51 | 0.016104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_156-20_1_3_line_56 |  | 50 | 52 | 0.051643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_156-20_1_3_line_57 |  | 50 | 53 | 0.045487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_156-20_1_3_line_58 |  | 51 | 54 | 0.0096872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_156-20_1_3_line_59 |  | 53 | 55 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_156-20_1_3_line_60 |  | 55 | 56 | 0.011731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_156-20_1_3_line_61 |  | 58 | 59 | 0.0012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_156-20_1_3_line_62 |  | 58 | 60 | 0.019042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_156-20_1_3_line_63 |  | 59 | 61 | 0.045622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_156-20_1_3_line_64 |  | 61 | 62 | 0.020371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_156-20_1_3_line_65 |  | 63 | 64 | 0.0049387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_156-20_1_3_trafo_82 | 0.63 MVA 20/0.4 kV | 67 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28
0 | 2692895.5502 | 1235477.0699 | 2692914.3644 | 1235537.2837
1 | 2692877.1514 | 1235472.6437 | 2692895.5502 | 1235477.0699
2 | 2692877.1514 | 1235472.6437 | 2692872.1444 | 1235473.3659 | 2692867.7426 | 1235475.0762 | 2692863.3121 | 1235478.1425 | 2692851.1667 | 1235489.0718 | 2692835.9619 | 1235504.4565 | 2692830.6044 | 1235510.5601
3 | 2692791.0318 | 1235564.4874 | 2692800.0702 | 1235548.9283 | 2692817.7363 | 1235525.2203 | 2692830.6044 | 1235510.5601
4 | 2692782.1528 | 1235587.7657 | 2692778.8039 | 1235586.0455 | 2692783.6344 | 1235577.2367 | 2692791.0318 | 1235564.4874
5 | 2692794.7398 | 1235607.5012 | 2692798.0466 | 1235609.1517 | 2692810.5213 | 1235614.9063 | 2692814.3148 | 1235616.1143
6 | 2692782.1528 | 1235587.7657 | 2692780.3696 | 1235590.9624 | 2692779.7394 | 1235593.51 | 2692779.8379 | 1235595.9244 | 2692780.7968 | 1235598.4968 | 2692783.0013 | 1235600.7995 | 2692793.24 | 1235606.7526 | 2692794.7398 | 1235607.5012
7 | 2692878.599 | 1235631.2375 | 2692874.912 | 1235629.8455 | 2692867.1257 | 1235627.7667 | 2692855.097 | 1235625.4437 | 2692841.75 | 1235622.722 | 2692829.9022 | 1235620.4464 | 2692819.6646 | 1235617.8179 | 2692814.3148 | 1235616.1143
8 | 2692747.8051 | 1235529.5759 | 2692746.2325 | 1235532.8538 | 2692749.5198 | 1235537.0637 | 2692750.411 | 1235539.6128 | 2692752.0696 | 1235555.0611 | 2692754.8782 | 1235574.8971 | 2692753.428 | 1235578.5772 | 2692755.6423 | 1235579.2789 | 2692760.3121 | 1235581.7203 | 2692766.6031 | 1235586.0105 | 2692768.7765 | 1235586.9118 | 2692771.1093 | 1235586.8148 | 2692772.725 | 1235586.1062 | 2692774.8992 | 1235584.0497 | 2692778.8039 | 1235586.0455 | 2692782.1528 | 1235587.7657
9 | 2692878.599 | 1235631.2375 | 2692877.6171 | 1235628.6869 | 2692861.5559 | 1235623.8323 | 2692859.2184 | 1235623.2621 | 2692856.8274 | 1235621.7569 | 2692856.5116 | 1235621.61
10 | 2692878.599 | 1235631.2375 | 2692905.192 | 1235618.9442
11 | 2692747.8051 | 1235529.5759 | 2692747.9322 | 1235522.406 | 2692748.0258 | 1235512.8887
12 | 2692838.9512 | 1235609.0572 | 2692841.671 | 1235614.7039 | 2692856.5116 | 1235621.61
13 | 2692905.192 | 1235618.9442 | 2692914.7322 | 1235617.7703
14 | 2692706.9201 | 1235445.9659 | 2692698.3012 | 1235440.9612
15 | 2692706.9201 | 1235445.9659 | 2692714.5631 | 1235451.9117 | 2692720.5646 | 1235457.6022
16 | 2692665.0908 | 1235415.5246 | 2692669.7748 | 1235419.4895 | 2692674.1014 | 1235423.0818 | 2692689.5172 | 1235435.8649 | 2692698.3012 | 1235440.9612
17 | 2692698.3012 | 1235440.9612 | 2692713.9884 | 1235433.3111
18 | 2692720.5646 | 1235457.6022 | 2692721.2163 | 1235458.2201 | 2692744.0516 | 1235474.1965
19 | 2692775.3709 | 1235366.3763 | 2692777.2763 | 1235371.3541 | 2692794.3526 | 1235364.5825 | 2692812.5481 | 1235357.3948 | 2692820.5299 | 1235354.2505 | 2692826.7438 | 1235351.868
20 | 2692823.1902 | 1235376.7862 | 2692814.9841 | 1235361.836 | 2692812.5481 | 1235357.3948 | 2692820.5299 | 1235354.2505 | 2692826.7438 | 1235351.868
21 | 2692821.8246 | 1235341.6393 | 2692826.7438 | 1235351.868
22 | 2692826.7438 | 1235351.868 | 2692848.4578 | 1235344.2795 | 2692860.0364 | 1235341.0617
23 | 2692775.3709 | 1235366.3763 | 2692763.8684 | 1235371.0042
24 | 2692741.7456 | 1235391.7254 | 2692739.0247 | 1235387.1018 | 2692754.2681 | 1235380.8796 | 2692777.2763 | 1235371.3541 | 2692775.3709 | 1235366.3763
25 | 2692775.3709 | 1235366.3763 | 2692771.7202 | 1235356.8346
26 | 2692823.1902 | 1235376.7862 | 2692814.9841 | 1235361.836 | 2692821.9226 | 1235359.098 | 2692835.3353 | 1235354.2707 | 2692845.0779 | 1235351.3096 | 2692869.7397 | 1235344.9682 | 2692905.1689 | 1235334.5144 | 2692908.434 | 1235334.3431 | 2692910.7859 | 1235334.9692 | 2692912.8881 | 1235336.0695 | 2692914.5937 | 1235337.8419 | 2692915.6238 | 1235339.7372 | 2692916.2957 | 1235342.2718 | 2692914.4112 | 1235342.2534 | 2692909.6387 | 1235339.1098 | 2692904.969 | 1235338.1027 | 2692847.3874 | 1235354.1589 | 2692844.4103 | 1235356.2472 | 2692843.5524 | 1235359.3138 | 2692850.2612 | 1235376.1087 | 2692859.306 | 1235393.0846 | 2692875.6836 | 1235385.9798 | 2692883.6598 | 1235386.0935 | 2692883.285 | 1235388.7673 | 2692883.7807 | 1235391.4326 | 2692885.0988 | 1235393.7882 | 2692887.0987 | 1235395.6208 | 2692889.587 | 1235396.7161 | 2692892.2854 | 1235396.9584
27 | 2692823.1902 | 1235376.7862 | 2692832.1509 | 1235393.1173
28 | 2692821.8246 | 1235341.6393 | 2692832.8744 | 1235337.3755 | 2692829.5298 | 1235328.5297
29 | 2692879.585 | 1235335.6288 | 2692860.0364 | 1235341.0617
30 | 2692715.5528 | 1235390.9494 | 2692717.5719 | 1235395.9179 | 2692739.0247 | 1235387.1018 | 2692741.7456 | 1235391.7254
31 | 2692741.7456 | 1235391.7254 | 2692752.8628 | 1235410.6311
32 | 2692771.7202 | 1235356.8346 | 2692771.7202 | 1235356.8346 | 2692767.0974 | 1235358.6415 | 2692762.733 | 1235360.3505
33 | 2692715.5528 | 1235390.9494 | 2692708.8701 | 1235374.488
34 | 2692752.8628 | 1235410.6311 | 2692754.0428 | 1235412.6378
35 | 2692749.6383 | 1235488.7123 | 2692748.0738 | 1235508.0089 | 2692748.0258 | 1235512.8887
36 | 2692892.2854 | 1235396.9584 | 2692877.6081 | 1235410.5389
37 | 2692848.993 | 1235423.8125 | 2692832.1509 | 1235393.1173
38 | 2692665.0908 | 1235415.5246 | 2692640.6414 | 1235394.806
39 | 2692708.8701 | 1235374.488 | 2692708.3486 | 1235373.2034
40 | 2692640.6414 | 1235394.806 | 2692625.3625 | 1235381.8585 | 2692617.193 | 1235371.8128 | 2692618.192 | 1235368.4259 | 2692633.467 | 1235361.7911
41 | 2692931.0311 | 1235632.8973 | 2692928.6366 | 1235631.054
42 | 2692928.6366 | 1235631.054 | 2692923.6072 | 1235627.1826 | 2692919.2331 | 1235619.8756 | 2692917.1992 | 1235618.287 | 2692914.7322 | 1235617.7703
43 | 2692750.1177 | 1235482.8002 | 2692747.8883 | 1235478.6957 | 2692744.592 | 1235474.5746 | 2692744.0516 | 1235474.1965
44 | 2692829.2204 | 1235327.7113 | 2692829.5298 | 1235328.5297
45 | 2692747.687 | 1235344.7506 | 2692747.6659 | 1235349.9763 | 2692753.3354 | 1235364.0306 | 2692762.733 | 1235360.3505
46 | 2692761.3515 | 1235425.0668 | 2692754.0428 | 1235412.6378
47 | 2692750.1177 | 1235482.8002 | 2692749.6383 | 1235488.7123
48 | 2692793.4185 | 1235510.085 | 2692792.8789 | 1235512.6451 | 2692784.1552 | 1235522.5939 | 2692775.7102 | 1235527.8223
49 | 2692793.4185 | 1235510.085 | 2692785.4657 | 1235497.3404 | 2692783.4983 | 1235496.3312 | 2692781.4882 | 1235495.1545
50 | 2692848.993 | 1235423.8125 | 2692858.57 | 1235441.2646
51 | 2692699.1307 | 1235350.4971 | 2692708.3486 | 1235373.2034
52 | 2692647.426 | 1235355.7279 | 2692633.467 | 1235361.7911
53 | 2692750.1177 | 1235482.8002 | 2692768.6751 | 1235472.7715
54 | 2692784.4303 | 1235464.3002 | 2692768.6751 | 1235472.7715
55 | 2692768.6751 | 1235472.7715 | 2692776.6755 | 1235486.7473
56 | 2692784.4303 | 1235464.3002 | 2692791.5381 | 1235461.8538 | 2692810.797 | 1235451.9919 | 2692816.4056 | 1235449.0996 | 2692818.268 | 1235448.595 | 2692820.122 | 1235448.624 | 2692821.9704 | 1235449.0087 | 2692823.6283 | 1235450.4467 | 2692825.1721 | 1235453.373 | 2692826.2061 | 1235455.5018 | 2692825.9817 | 1235458.2336
57 | 2692784.4303 | 1235464.3002 | 2692761.3515 | 1235425.0668
58 | 2692781.4882 | 1235495.1545 | 2692781.4882 | 1235495.1545 | 2692776.6755 | 1235486.7473
59 | 2692761.3515 | 1235425.0668 | 2692781.2582 | 1235415.8932
60 | 2692792.123 | 1235419.5877 | 2692788.0091 | 1235416.9216 | 2692781.2582 | 1235415.8932
61 | 2692683.6504 | 1235317.098 | 2692682.5392 | 1235317.5699
62 | 2692665.0121 | 1235325.0131 | 2692682.5392 | 1235317.5699
63 | 2692699.1307 | 1235350.4971 | 2692690.7672 | 1235330.5744 | 2692692.8813 | 1235328.9729 | 2692694.3238 | 1235326.7604 | 2692694.9242 | 1235324.179 | 2692694.5942 | 1235321.5609 | 2692693.8631 | 1235319.9038 | 2692692.1307 | 1235317.8975 | 2692689.8195 | 1235316.605 | 2692687.1997 | 1235316.1749 | 2692683.6504 | 1235317.098
64 | 2692699.1307 | 1235350.4971 | 2692712.093 | 1235334.7546
65 | 2692827.4737 | 1235323.0918 | 2692829.2204 | 1235327.7113

## bus_geodata
| x | y | coords
0 | 2692914.3644 | 1235537.2837
1 | 2692895.5502 | 1235477.0699
2 | 2692877.1514 | 1235472.6437
3 | 2692830.6044 | 1235510.5601
4 | 2692791.0318 | 1235564.4874
5 | 2692794.7398 | 1235607.5012
6 | 2692814.3148 | 1235616.1143
7 | 2692782.1528 | 1235587.7657
8 | 2692878.599 | 1235631.2375
9 | 2692747.8051 | 1235529.5759
10 | 2692856.5116 | 1235621.61
11 | 2692905.192 | 1235618.9442
12 | 2692706.9201 | 1235445.9659
13 | 2692698.3012 | 1235440.9612
14 | 2692720.5646 | 1235457.6022
15 | 2692826.7438 | 1235351.868
16 | 2692775.3709 | 1235366.3763
17 | 2692823.1902 | 1235376.7862
18 | 2692821.8246 | 1235341.6393
19 | 2692860.0364 | 1235341.0617
20 | 2692763.8684 | 1235371.0042
21 | 2692741.7456 | 1235391.7254
22 | 2692771.7202 | 1235356.8346
23 | 2692715.5528 | 1235390.9494
24 | 2692752.8628 | 1235410.6311
25 | 2692748.0258 | 1235512.8887
26 | 2692892.2854 | 1235396.9584
27 | 2692832.1509 | 1235393.1173
28 | 2692665.0908 | 1235415.5246
29 | 2692713.9884 | 1235433.3111
30 | 2692708.8701 | 1235374.488
31 | 2692877.6081 | 1235410.5389
32 | 2692640.6414 | 1235394.806
33 | 2692838.9512 | 1235609.0572
34 | 2692931.0311 | 1235632.8973
35 | 2692928.6366 | 1235631.054
36 | 2692744.0516 | 1235474.1965
37 | 2692829.5298 | 1235328.5297
38 | 2692879.585 | 1235335.6288
39 | 2692762.733 | 1235360.3505
40 | 2692754.0428 | 1235412.6378
41 | 2692749.6383 | 1235488.7123
42 | 2692775.7102 | 1235527.8223
43 | 2692793.4185 | 1235510.085
44 | 2692848.993 | 1235423.8125
45 | 2692708.3486 | 1235373.2034
46 | 2692633.467 | 1235361.7911
47 | 2692914.7322 | 1235617.7703
48 | 2692750.1177 | 1235482.8002
49 | 2692768.6751 | 1235472.7715
50 | 2692784.4303 | 1235464.3002
51 | 2692776.6755 | 1235486.7473
52 | 2692825.9817 | 1235458.2336
53 | 2692761.3515 | 1235425.0668
54 | 2692781.4882 | 1235495.1545
55 | 2692781.2582 | 1235415.8932
56 | 2692792.123 | 1235419.5877
57 | 2692858.57 | 1235441.2646
58 | 2692682.5392 | 1235317.5699
59 | 2692683.6504 | 1235317.098
60 | 2692665.0121 | 1235325.0131
61 | 2692699.1307 | 1235350.4971
62 | 2692712.093 | 1235334.7546
63 | 2692829.2204 | 1235327.7113
64 | 2692827.4737 | 1235323.0918
65 | 2692747.687 | 1235344.7506
66 | 2692647.426 | 1235355.7279
67 | 2692761.3515 | 1235425.0668

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97945 | -0.39652 | 0.0122 | 0.0030576
1 | 0.98016 | -0.38254 | 0.0061264 | 0.0015354
2 | 0.98048 | -0.37625 | 0 | 0
3 | 0.98152 | -0.35592 | 0.002739 | 0.00068645
4 | 0.98283 | -0.33038 | 0 | 0
5 | 0.98304 | -0.3264 | 0.0034765 | 0.00087129
6 | 0.98284 | -0.33028 | 0.0017812 | 0.00044642
7 | 0.98339 | -0.31953 | 0 | 0
8 | 0.98233 | -0.34014 | 0 | 0
9 | 0.98607 | -0.2673 | 0 | 0
10 | 0.98231 | -0.34066 | 0.00068716 | 0.00017222
11 | 0.98214 | -0.3439 | 0.00062574 | 0.00015683
12 | 0.98733 | -0.24292 | 0 | 0
13 | 0.98724 | -0.24482 | 0 | 0
14 | 0.98751 | -0.23949 | 0.0022393 | 0.00056122
15 | 0.98591 | -0.2698 | 0 | 0
16 | 0.9908 | -0.17534 | 0 | 0
17 | 0.98236 | -0.33892 | 0 | 0
18 | 0.98524 | -0.28279 | 0 | 0
19 | 0.98545 | -0.2788 | 0.0060825 | 0.0015244
20 | 0.99079 | -0.17557 | 0.0010525 | 0.00026377
21 | 0.99397 | -0.11457 | 0 | 0
22 | 0.99065 | -0.17821 | 0.0083323 | 0.0020883
23 | 0.99356 | -0.12255 | 0 | 0
24 | 0.9954 | -0.087366 | 0.0014181 | 0.00035541
25 | 0.98661 | -0.25696 | 0.014879 | 0.0037291
26 | 0.97765 | -0.43111 | 0 | 0
27 | 0.98089 | -0.36756 | 0.079869 | 0.020017
28 | 0.98708 | -0.24794 | 0 | 0
29 | 0.98713 | -0.24686 | 0.0065273 | 0.0016359
30 | 0.99334 | -0.12674 | 0.0046383 | 0.0011625
31 | 0.97732 | -0.4376 | 0.017816 | 0.0044651
32 | 0.98695 | -0.25032 | 0.0016051 | 0.00040227
33 | 0.9823 | -0.34084 | 0.00046021 | 0.00011534
34 | 0.982 | -0.34667 | 0.0020356 | 0.00051017
35 | 0.98201 | -0.34655 | 0.0022075 | 0.00055326
36 | 0.98785 | -0.23285 | 0.0051229 | 0.0012839
37 | 0.98399 | -0.30723 | 0.0057447 | 0.0014398
38 | 0.9853 | -0.2818 | 0.0082476 | 0.0020671
39 | 0.99059 | -0.1795 | 0.0011356 | 0.00028461
40 | 0.99555 | -0.084464 | 0.0018453 | 0.00046248
41 | 0.98771 | -0.23551 | 0.0078322 | 0.0019629
42 | 0.98838 | -0.22273 | 0.0052603 | 0.0013184
43 | 0.9885 | -0.22031 | 0 | 0
44 | 0.98073 | -0.37082 | 0 | 0
45 | 0.99333 | -0.12695 | 0.0018978 | 0.00047565
46 | 0.98683 | -0.25274 | 0.0019156 | 0.0004801
47 | 0.98208 | -0.34502 | 0.0022383 | 0.00056097
48 | 0.98803 | -0.22943 | 0 | 0
49 | 0.98949 | -0.20116 | 0 | 0
50 | 0.99138 | -0.16464 | 0 | 0
51 | 0.9889 | -0.21258 | 0.0056539 | 0.001417
52 | 0.99103 | -0.17134 | 0.0073109 | 0.0018323
53 | 0.9965 | -0.066353 | 0 | 0
54 | 0.9886 | -0.21848 | 0.028888 | 0.0072399
55 | 0.99877 | -0.02324 | 0.0036033 | 0.00090308
56 | 1 | 0 | -0.34703 | -0.088433
57 | 0.98063 | -0.37268 | 0.0051346 | 0.0012869
58 | 0.99305 | -0.13239 | 0.0016127 | 0.00040418
59 | 0.99306 | -0.13233 | 0 | 0
60 | 0.99303 | -0.13287 | 0.0014019 | 0.00035136
61 | 0.99318 | -0.1299 | 0 | 0
62 | 0.99311 | -0.13126 | 0.0037843 | 0.00094844
63 | 0.98394 | -0.30815 | 0.0057501 | 0.0014411
64 | 0.98371 | -0.3128 | 0.052331 | 0.013115
65 | 0.99041 | -0.18294 | 0.0063548 | 0.0015927
66 | 0.98682 | -0.25291 | 0.00062723 | 0.0001572
67 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0122 | -0.0030576 | 0.012208 | 0.003062 | 8.1267e-06 | 4.4066e-06 | 0.018535 | 0.018534 | 0.018535 | 0.97945 | -0.39652 | 0.98016 | -0.38254 | 5.0919
1 | -0.018335 | -0.0045974 | 0.01834 | 0.0046007 | 5.4982e-06 | 3.2803e-06 | 0.027835 | 0.027835 | 0.027835 | 0.98016 | -0.38254 | 0.98048 | -0.37625 | 7.647
2 | -0.01834 | -0.0046007 | 0.018358 | 0.0046113 | 1.7799e-05 | 1.0618e-05 | 0.027835 | 0.027835 | 0.027835 | 0.98048 | -0.37625 | 0.98152 | -0.35592 | 7.647
3 | -0.021097 | -0.0052978 | 0.021123 | 0.0053134 | 2.5733e-05 | 1.562e-05 | 0.031987 | 0.031987 | 0.031987 | 0.98152 | -0.35592 | 0.98283 | -0.33038 | 8.7877
4 | -0.021123 | -0.0053134 | 0.021133 | 0.0053201 | 1.0955e-05 | 6.6489e-06 | 0.031987 | 0.031987 | 0.031987 | 0.98283 | -0.33038 | 0.98339 | -0.31953 | 8.7876
5 | 0.010043 | 0.0025176 | -0.010042 | -0.0025167 | 1.8561e-06 | 9.1648e-07 | 0.015203 | 0.015203 | 0.015203 | 0.98304 | -0.3264 | 0.98284 | -0.33028 | 4.1767
6 | -0.01352 | -0.0033889 | 0.013524 | 0.0033914 | 4.4219e-06 | 2.473e-06 | 0.020465 | 0.020465 | 0.020465 | 0.98304 | -0.3264 | 0.98339 | -0.31953 | 5.6223
7 | 0.0082604 | 0.0020703 | -0.0082565 | -0.0020687 | 3.8783e-06 | 1.6446e-06 | 0.012506 | 0.012507 | 0.012507 | 0.98284 | -0.33028 | 0.98233 | -0.34014 | 3.4359
8 | -0.034658 | -0.0087115 | 0.034745 | 0.0087659 | 8.6667e-05 | 5.4398e-05 | 0.052452 | 0.052451 | 0.052452 | 0.98339 | -0.31953 | 0.98607 | -0.2673 | 14.4098
9 | 0.0011474 | 0.00028697 | -0.0011474 | -0.00028727 | 2.8419e-08 | -2.9946e-07 | 0.0017378 | 0.001738 | 0.001738 | 0.98233 | -0.34014 | 0.98231 | -0.34066 | 0.47746
10 | 0.0071091 | 0.0017817 | -0.0071079 | -0.0017812 | 1.2741e-06 | 4.4457e-07 | 0.010769 | 0.010769 | 0.010769 | 0.98233 | -0.34014 | 0.98214 | -0.3439 | 2.9585
11 | -0.034745 | -0.0087659 | 0.034762 | 0.0087767 | 1.7218e-05 | 1.0806e-05 | 0.052451 | 0.052451 | 0.052451 | 0.98607 | -0.2673 | 0.98661 | -0.25696 | 14.4097
12 | 0.00046021 | 0.00011505 | -0.00046021 | -0.00011534 | 4.1248e-09 | -2.8391e-07 | 0.00069703 | 0.00069713 | 0.00069713 | 0.98231 | -0.34066 | 0.9823 | -0.34084 | 0.19152
13 | 0.0064821 | 0.0016244 | -0.0064818 | -0.0016243 | 3.4766e-07 | 1.0087e-07 | 0.0098208 | 0.0098209 | 0.0098209 | 0.98214 | -0.3439 | 0.98208 | -0.34502 | 2.698
14 | 0.010678 | 0.0026752 | -0.010677 | -0.0026747 | 9.6584e-07 | 4.9096e-07 | 0.016093 | 0.016093 | 0.016093 | 0.98733 | -0.24292 | 0.98724 | -0.24482 | 4.4211
15 | -0.010678 | -0.0026752 | 0.01068 | 0.0026761 | 1.7436e-06 | 8.8626e-07 | 0.016093 | 0.016093 | 0.016093 | 0.98733 | -0.24292 | 0.98751 | -0.23949 | 4.4211
16 | 0.0041493 | 0.0010386 | -0.0041487 | -0.0010388 | 6.1511e-07 | -1.4254e-07 | 0.0062536 | 0.0062538 | 0.0062538 | 0.98724 | -0.24482 | 0.98708 | -0.24794 | 1.7181
17 | 0.006528 | 0.0016361 | -0.0065273 | -0.0016359 | 6.3364e-07 | 1.8239e-07 | 0.0098393 | 0.0098394 | 0.0098394 | 0.98724 | -0.24482 | 0.98713 | -0.24686 | 2.7031
18 | -0.012919 | -0.0032373 | 0.012923 | 0.0032396 | 4.0882e-06 | 2.2483e-06 | 0.019467 | 0.019467 | 0.019467 | 0.98751 | -0.23949 | 0.98785 | -0.23285 | 5.3481
19 | -0.18165 | -0.045785 | 0.18248 | 0.046311 | 0.00082501 | 0.00052651 | 0.27426 | 0.27426 | 0.27426 | 0.98591 | -0.2698 | 0.9908 | -0.17534 | 37.673
20 | 0.10336 | 0.026111 | -0.10302 | -0.025893 | 0.00034123 | 0.00021791 | 0.15608 | 0.15608 | 0.15608 | 0.98591 | -0.2698 | 0.98236 | -0.33892 | 42.8784
21 | 0.063954 | 0.016078 | -0.063914 | -0.016053 | 3.9652e-05 | 2.5233e-05 | 0.096542 | 0.096542 | 0.096542 | 0.98591 | -0.2698 | 0.98524 | -0.28279 | 26.5225
22 | 0.014337 | 0.0035955 | -0.014331 | -0.003592 | 6.1497e-06 | 3.4895e-06 | 0.02164 | 0.02164 | 0.02164 | 0.98591 | -0.2698 | 0.98545 | -0.2788 | 5.9451
23 | 0.0010525 | 0.00026362 | -0.0010525 | -0.00026377 | 1.1616e-08 | -1.5225e-07 | 0.0015806 | 0.0015806 | 0.0015806 | 0.9908 | -0.17534 | 0.99079 | -0.17557 | 0.43424
24 | -0.19936 | -0.050542 | 0.19994 | 0.050914 | 0.00058416 | 0.00037184 | 0.29961 | 0.29961 | 0.29961 | 0.9908 | -0.17534 | 0.99397 | -0.11457 | 27.4366
25 | 0.015826 | 0.0039672 | -0.015824 | -0.003966 | 2.1644e-06 | 1.2537e-06 | 0.023769 | 0.023769 | 0.023769 | 0.9908 | -0.17534 | 0.99065 | -0.17821 | 6.5299
26 | 0.0179 | 0.0045152 | -0.017822 | -0.0044684 | 7.8649e-05 | 4.6744e-05 | 0.027125 | 0.027126 | 0.027126 | 0.98236 | -0.33892 | 0.97765 | -0.43111 | 7.4522
27 | 0.085122 | 0.021378 | -0.085005 | -0.021304 | 0.00011616 | 7.4107e-05 | 0.12895 | 0.12895 | 0.12895 | 0.98236 | -0.33892 | 0.98089 | -0.36756 | 35.4266
28 | 0.063914 | 0.016053 | -0.06384 | -0.016005 | 7.445e-05 | 4.7377e-05 | 0.096542 | 0.096542 | 0.096542 | 0.98524 | -0.28279 | 0.98399 | -0.30723 | 26.5226
29 | 0.0082488 | 0.0020675 | -0.0082476 | -0.0020671 | 1.1804e-06 | 4.9702e-07 | 0.012456 | 0.012456 | 0.012456 | 0.98545 | -0.2788 | 0.9853 | -0.2818 | 3.4219
30 | 0.013345 | 0.003346 | -0.013339 | -0.0033432 | 5.077e-06 | 2.8098e-06 | 0.019978 | 0.019978 | 0.019978 | 0.99397 | -0.11457 | 0.99356 | -0.12255 | 5.4885
31 | -0.21329 | -0.05426 | 0.21357 | 0.054438 | 0.00028 | 0.00017835 | 0.31959 | 0.31958 | 0.31959 | 0.99397 | -0.11457 | 0.9954 | -0.087366 | 29.266
32 | 0.0074919 | 0.0018777 | -0.0074914 | -0.0018775 | 4.5829e-07 | 1.6906e-07 | 0.011253 | 0.011253 | 0.011253 | 0.99065 | -0.17821 | 0.99059 | -0.1795 | 3.0916
33 | 0.013339 | 0.0033432 | -0.013337 | -0.0033417 | 2.6591e-06 | 1.4718e-06 | 0.019978 | 0.019978 | 0.019978 | 0.99356 | -0.12255 | 0.99334 | -0.12674 | 5.4885
34 | -0.21499 | -0.054794 | 0.21502 | 0.054813 | 3.0116e-05 | 1.9184e-05 | 0.3217 | 0.3217 | 0.3217 | 0.9954 | -0.087366 | 0.99555 | -0.084464 | 29.4601
35 | -0.049641 | -0.012506 | 0.049692 | 0.012538 | 5.0985e-05 | 3.232e-05 | 0.074893 | 0.074893 | 0.074893 | 0.98661 | -0.25696 | 0.98771 | -0.23551 | 20.5749
36 | 0.017822 | 0.0044684 | -0.017816 | -0.0044651 | 5.5095e-06 | 3.2758e-06 | 0.027126 | 0.027126 | 0.027126 | 0.97765 | -0.43111 | 0.97732 | -0.4376 | 7.4522
37 | 0.0051359 | 0.001287 | -0.0051351 | -0.0012869 | 7.9699e-07 | 6.8199e-08 | 0.0077911 | 0.0077912 | 0.0077912 | 0.98089 | -0.36756 | 0.98073 | -0.37082 | 2.1404
38 | 0.0041487 | 0.0010388 | -0.0041482 | -0.0010389 | 4.7002e-07 | -1.0878e-07 | 0.0062538 | 0.0062539 | 0.0062539 | 0.98708 | -0.24794 | 0.98695 | -0.25032 | 1.7181
39 | 0.0086985 | 0.0021792 | -0.0086984 | -0.0021792 | 8.8266e-08 | 3.8543e-08 | 0.01303 | 0.01303 | 0.01303 | 0.99334 | -0.12674 | 0.99333 | -0.12695 | 3.5796
40 | 0.0025431 | 0.00063661 | -0.0025428 | -0.0006371 | 2.9305e-07 | -4.9171e-07 | 0.003834 | 0.0038342 | 0.0038342 | 0.98695 | -0.25032 | 0.98683 | -0.25274 | 1.0534
41 | -0.0020356 | -0.00051017 | 0.0020356 | 0.00051014 | 1.0781e-08 | -3.133e-08 | 0.0030845 | 0.0030845 | 0.0030845 | 0.982 | -0.34667 | 0.98201 | -0.34655 | 0.8474
42 | -0.0042431 | -0.0010634 | 0.0042435 | 0.0010633 | 3.0949e-07 | -5.4525e-08 | 0.0064296 | 0.0064295 | 0.0064296 | 0.98201 | -0.34655 | 0.98208 | -0.34502 | 1.7664
43 | -0.018046 | -0.0045235 | 0.018049 | 0.0045252 | 2.9394e-06 | 1.7454e-06 | 0.027184 | 0.027184 | 0.027184 | 0.98785 | -0.23285 | 0.98803 | -0.22943 | 7.468
44 | 0.058095 | 0.014565 | -0.058093 | -0.014564 | 2.5325e-06 | 1.6097e-06 | 0.087855 | 0.087855 | 0.087855 | 0.98399 | -0.30723 | 0.98394 | -0.30815 | 24.136
45 | 0.0063558 | 0.0015929 | -0.0063548 | -0.0015927 | 1.0417e-06 | 2.7444e-07 | 0.0095475 | 0.0095476 | 0.0095476 | 0.99059 | -0.1795 | 0.99041 | -0.18294 | 2.623
46 | -0.21686 | -0.055275 | 0.21705 | 0.055396 | 0.00018974 | 0.00012087 | 0.32446 | 0.32446 | 0.32446 | 0.99555 | -0.084464 | 0.9965 | -0.066353 | 29.7127
47 | -0.057524 | -0.014501 | 0.057541 | 0.014512 | 1.6717e-05 | 1.0623e-05 | 0.086692 | 0.086692 | 0.086692 | 0.98771 | -0.23551 | 0.98803 | -0.22943 | 23.8165
48 | -0.0052603 | -0.0013184 | 0.005261 | 0.0013184 | 6.0634e-07 | 5.7611e-08 | 0.0079195 | 0.0079194 | 0.0079195 | 0.98838 | -0.22273 | 0.9885 | -0.22031 | 2.1757
49 | -0.005261 | -0.0013184 | 0.0052614 | 0.0013185 | 4.6009e-07 | 4.3653e-08 | 0.0079194 | 0.0079193 | 0.0079194 | 0.9885 | -0.22031 | 0.9886 | -0.21848 | 2.1757
50 | 0.0051351 | 0.0012869 | -0.0051346 | -0.0012869 | 4.5317e-07 | 3.8852e-08 | 0.0077912 | 0.0077913 | 0.0077913 | 0.98073 | -0.37082 | 0.98063 | -0.37268 | 2.1405
51 | 0.0068005 | 0.0017036 | -0.0067996 | -0.0017033 | 9.5367e-07 | 2.9317e-07 | 0.010187 | 0.010187 | 0.010187 | 0.99333 | -0.12695 | 0.99318 | -0.1299 | 2.7986
52 | 0.00062723 | 0.00015701 | -0.00062723 | -0.0001572 | 5.1047e-09 | -1.9117e-07 | 0.00094572 | 0.00094579 | 0.00094579 | 0.98683 | -0.25274 | 0.98682 | -0.25291 | 0.25983
53 | -0.07559 | -0.019037 | 0.075693 | 0.019102 | 0.00010235 | 6.5233e-05 | 0.11388 | 0.11388 | 0.11388 | 0.98803 | -0.22943 | 0.98949 | -0.20116 | 31.2845
54 | -0.11553 | -0.029097 | 0.11573 | 0.029226 | 0.00020214 | 0.00012914 | 0.17378 | 0.17378 | 0.17378 | 0.98949 | -0.20116 | 0.99138 | -0.16464 | 47.7427
55 | 0.039834 | 0.0099951 | -0.039813 | -0.0099814 | 2.1674e-05 | 1.3664e-05 | 0.059908 | 0.059908 | 0.059908 | 0.98949 | -0.20116 | 0.9889 | -0.21258 | 16.4583
56 | 0.0073133 | 0.0018331 | -0.0073109 | -0.0018323 | 2.3336e-06 | 8.2783e-07 | 0.010977 | 0.010977 | 0.010977 | 0.99138 | -0.16464 | 0.99103 | -0.17134 | 3.0157
57 | -0.12304 | -0.031059 | 0.12362 | 0.031432 | 0.00058228 | 0.00037207 | 0.18476 | 0.18476 | 0.18476 | 0.99138 | -0.16464 | 0.9965 | -0.066353 | 50.7583
58 | 0.034159 | 0.0085644 | -0.034149 | -0.0085584 | 9.5977e-06 | 6.0183e-06 | 0.051401 | 0.051401 | 0.051401 | 0.9889 | -0.21258 | 0.9886 | -0.21848 | 14.121
59 | -0.34067 | -0.086828 | 0.34139 | 0.087281 | 0.00071046 | 0.00045384 | 0.50922 | 0.50922 | 0.50922 | 0.9965 | -0.066353 | 0.99877 | -0.02324 | 46.6321
60 | -0.34499 | -0.088185 | 0.34538 | 0.088433 | 0.0003883 | 0.00024805 | 0.51459 | 0.51459 | 0.51459 | 0.99877 | -0.02324 | 1 | 0 | 47.1237
61 | -0.0030147 | -0.00075531 | 0.0030147 | 0.0007553 | 9.2371e-09 | -9.7062e-09 | 0.0045172 | 0.0045172 | 0.0045172 | 0.99305 | -0.13239 | 0.99306 | -0.13233 | 1.241
62 | 0.001402 | 0.00035113 | -0.0014019 | -0.00035136 | 3.1513e-08 | -2.2619e-07 | 0.0021007 | 0.0021008 | 0.0021008 | 0.99305 | -0.13239 | 0.99303 | -0.13287 | 0.57713
63 | -0.0030147 | -0.0007553 | 0.003015 | 0.00075494 | 3.4908e-07 | -3.6691e-07 | 0.0045172 | 0.004517 | 0.0045172 | 0.99306 | -0.13233 | 0.99318 | -0.1299 | 1.241
64 | 0.0037845 | 0.00094833 | -0.0037843 | -0.00094844 | 2.456e-07 | -1.0642e-07 | 0.0056701 | 0.0056702 | 0.0056702 | 0.99318 | -0.1299 | 0.99311 | -0.13126 | 1.5577
65 | 0.052342 | 0.013123 | -0.052331 | -0.013115 | 1.1605e-05 | 7.3645e-06 | 0.079159 | 0.079159 | 0.079159 | 0.98394 | -0.30815 | 0.98371 | -0.3128 | 21.747

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36511 | 0.092964

## res_load
| p_mw | q_mvar
0 | 0.0122 | 0.0030576
1 | 0.0061264 | 0.0015354
2 | 0.002739 | 0.00068645
3 | 0.0034765 | 0.00087129
4 | 0.0017812 | 0.00044642
5 | 0.00068716 | 0.00017222
6 | 0.00062574 | 0.00015683
7 | 0.0022393 | 0.00056122
8 | 0.0060825 | 0.0015244
9 | 0.0010525 | 0.00026377
10 | 0.0083323 | 0.0020883
11 | 0.0014181 | 0.00035541
12 | 0.014879 | 0.0037291
13 | 0.079869 | 0.020017
14 | 0.0065273 | 0.0016359
15 | 0.0046383 | 0.0011625
16 | 0.017816 | 0.0044651
17 | 0.0016051 | 0.00040227
18 | 0.00046021 | 0.00011534
19 | 0.0020356 | 0.00051017
20 | 0.0022075 | 0.00055326
21 | 0.0051229 | 0.0012839
22 | 0.0057447 | 0.0014398
23 | 0.0082476 | 0.0020671
24 | 0.0011356 | 0.00028461
25 | 0.0018453 | 0.00046248
26 | 0.0078322 | 0.0019629
27 | 0.0052603 | 0.0013184
28 | 0.0018978 | 0.00047565
29 | 0.0019156 | 0.0004801
30 | 0.0022383 | 0.00056097
31 | 0.0056539 | 0.001417
32 | 0.0073109 | 0.0018323
33 | 0.028888 | 0.0072399
34 | 0.0036033 | 0.00090308
35 | 0.018079 | 0.004531
36 | 0.0051346 | 0.0012869
37 | 0.0016127 | 0.00040418
38 | 0.0014019 | 0.00035136
39 | 0.0037843 | 0.00094844
40 | 0.0057501 | 0.0014411
41 | 0.052331 | 0.013115
42 | 0.0063548 | 0.0015927
43 | 0.00062723 | 0.0001572

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1