## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_156-29_1_2_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_156-29_1_2_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_156-29_1_2_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_156-29_1_2_node_37 | 0.4 | n |  | TRUE
4 | bus_LV_156-29_1_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_156-29_1_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_156-29_1_2_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_156-29_1_2_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_156-29_1_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_156-29_1_2_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_156-29_1_2_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_156-29_1_2_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_156-29_1_2_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_156-29_1_2_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_156-29_1_2_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_156-29_1_2_node_43 | 0.4 | n |  | TRUE
16 | bus_LV_156-29_1_2_node_88 | 0.4 | n |  | TRUE
17 | bus_LV_156-29_1_2_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_156-29_1_2_node_91 | 0.4 | n |  | TRUE
19 | bus_LV_156-29_1_2_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_156-29_1_2_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_156-29_1_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_156-29_1_2_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_156-29_1_2_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_156-29_1_2_node_89 | 0.4 | n |  | TRUE
25 | bus_LV_156-29_1_2_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_156-29_1_2_node_71 | 0.4 | n |  | TRUE
27 | bus_MV_496_0_node_76 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_156-29_1_2_load_5 | 0 | 0.044002 | 0.011028 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_156-29_1_2_load_6 | 1 | 0.033444 | 0.0083818 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_156-29_1_2_load_11 | 4 | 0.0062891 | 0.0015762 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_156-29_1_2_load_80 | 7 | 0.0073281 | 0.0018366 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_156-29_1_2_load_30 | 9 | 0.0043458 | 0.0010892 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_156-29_1_2_load_31 | 10 | 0.0046538 | 0.0011663 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_156-29_1_2_load_43 | 15 | 0.0065551 | 0.0016429 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_156-29_1_2_load_88 | 16 | 0.010967 | 0.0027486 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_156-29_1_2_load_91 | 18 | 0.0066716 | 0.0016721 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_156-29_1_2_load_36 | 19 | 0.024307 | 0.0060919 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_156-29_1_2_load_39 | 20 | 0.0061467 | 0.0015405 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_156-29_1_2_load_41 | 22 | 0.0060033 | 0.0015046 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_156-29_1_2_load_89 | 24 | 0.0053129 | 0.0013315 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_156-29_1_2_load_44 | 25 | 0.036154 | 0.009061 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_156-29_1_2_load_71 | 26 | 0.010693 | 0.00268 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_156-29_1_2_line_0 |  | 0 | 1 | 0.016968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_156-29_1_2_line_1 |  | 1 | 2 | 0.036322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_156-29_1_2_line_2 |  | 2 | 3 | 0.057552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_156-29_1_2_line_3 |  | 3 | 14 | 0.004401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_156-29_1_2_line_4 |  | 3 | 19 | 0.023269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_156-29_1_2_line_5 |  | 4 | 5 | 0.017426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_156-29_1_2_line_6 |  | 5 | 6 | 0.029196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_156-29_1_2_line_7 |  | 5 | 7 | 0.030207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_156-29_1_2_line_8 |  | 6 | 8 | 0.029614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_156-29_1_2_line_9 |  | 7 | 26 | 0.0079236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_156-29_1_2_line_10 |  | 8 | 14 | 0.032132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_156-29_1_2_line_11 |  | 8 | 15 | 0.01914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_156-29_1_2_line_12 |  | 9 | 10 | 0.0085621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_156-29_1_2_line_13 |  | 10 | 11 | 0.02875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_156-29_1_2_line_14 |  | 11 | 12 | 0.067049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_156-29_1_2_line_15 |  | 11 | 13 | 0.047094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_156-29_1_2_line_16 |  | 12 | 16 | 0.018217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_156-29_1_2_line_17 |  | 13 | 17 | 0.049181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_156-29_1_2_line_18 |  | 13 | 18 | 0.021981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_156-29_1_2_line_19 |  | 14 | 20 | 0.028445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_156-29_1_2_line_20 |  | 17 | 23 | 0.03842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_156-29_1_2_line_21 |  | 17 | 25 | 0.042452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_156-29_1_2_line_22 |  | 20 | 21 | 0.021838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_156-29_1_2_line_23 |  | 21 | 22 | 0.016298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_156-29_1_2_line_24 |  | 21 | 23 | 0.006746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_156-29_1_2_line_25 |  | 23 | 24 | 0.014207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_156-29_1_2_trafo_41 | 0.63 MVA 20/0.4 kV | 27 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2689569.2183 | 1236936.3733 | 2689583.433 | 1236927.1083
1 | 2689548.564 | 1236906.4959 | 2689569.2183 | 1236936.3733
2 | 2689502.1491 | 1236940.4544 | 2689529.7256 | 1236922.7904 | 2689548.564 | 1236906.4959
3 | 2689498.4356 | 1236942.8335 | 2689502.1491 | 1236940.4544
4 | 2689502.1491 | 1236940.4544 | 2689509.6981 | 1236955.2121 | 2689516.1141 | 1236953.3076
5 | 2689414.1733 | 1236977.1005 | 2689419.6813 | 1236993.6327
6 | 2689441.9623 | 1236967.9011 | 2689414.1733 | 1236977.1005
7 | 2689414.1733 | 1236977.1005 | 2689408.2023 | 1236947.4893
8 | 2689441.9623 | 1236967.9011 | 2689457.7126 | 1236962.6789 | 2689469.4828 | 1236956.9409
9 | 2689408.2023 | 1236947.4893 | 2689415.4495 | 1236944.2859
10 | 2689498.4356 | 1236942.8335 | 2689469.4828 | 1236956.9409
11 | 2689469.4828 | 1236956.9409 | 2689475.2557 | 1236975.1893
12 | 2689457.9257 | 1237016.8172 | 2689460.5631 | 1237024.963
13 | 2689446.9821 | 1237044.5544 | 2689447.2945 | 1237038.3879 | 2689452.9641 | 1237038.2621 | 2689457.2673 | 1237031.9001 | 2689460.6711 | 1237029.9833 | 2689461.4905 | 1237027.8274 | 2689460.5631 | 1237024.963
14 | 2689446.9821 | 1237044.5544 | 2689453.9335 | 1237044.7369 | 2689470.2626 | 1237046.284 | 2689476.1325 | 1237046.9284 | 2689492.9613 | 1237045.9479 | 2689511.149 | 1237048.6905 | 2689513.6851 | 1237048.6176
15 | 2689487.137 | 1237034.752 | 2689481.1397 | 1237036.0293 | 2689471.1099 | 1237039.2694 | 2689470.2626 | 1237046.284 | 2689453.9335 | 1237044.7369 | 2689446.9821 | 1237044.5544
16 | 2689513.6851 | 1237048.6176 | 2689512.1246 | 1237059.7688 | 2689513.6644 | 1237066.5525
17 | 2689487.137 | 1237034.752 | 2689493.3787 | 1237034.8239 | 2689502.7129 | 1237034.5643 | 2689510.6477 | 1237033.2607 | 2689520.2454 | 1237029.5693 | 2689526.1175 | 1237025.5549 | 2689532.8611 | 1237020.9532
18 | 2689485.437 | 1237056.6645 | 2689486.787 | 1237039.3945 | 2689487.137 | 1237034.752
19 | 2689498.4356 | 1236942.8335 | 2689506.8614 | 1236970.0015
20 | 2689515.2531 | 1236997.3263 | 2689522.1054 | 1237014.1195 | 2689526.1175 | 1237025.5549 | 2689532.8611 | 1237020.9532
21 | 2689532.8611 | 1237020.9532 | 2689546.4738 | 1237012.9637 | 2689560.2617 | 1237007.4008 | 2689571.6921 | 1237004.4687
22 | 2689513.3301 | 1236990.8593 | 2689506.8614 | 1236970.0015
23 | 2689513.3301 | 1236990.8593 | 2689529.4856 | 1236988.3787
24 | 2689513.3301 | 1236990.8593 | 2689515.2531 | 1236997.3263
25 | 2689515.2531 | 1236997.3263 | 2689501.6517 | 1237001.5577

## bus_geodata
| x | y | coords
0 | 2689583.433 | 1236927.1083
1 | 2689569.2183 | 1236936.3733
2 | 2689548.564 | 1236906.4959
3 | 2689502.1491 | 1236940.4544
4 | 2689419.6813 | 1236993.6327
5 | 2689414.1733 | 1236977.1005
6 | 2689441.9623 | 1236967.9011
7 | 2689408.2023 | 1236947.4893
8 | 2689469.4828 | 1236956.9409
9 | 2689457.9257 | 1237016.8172
10 | 2689460.5631 | 1237024.963
11 | 2689446.9821 | 1237044.5544
12 | 2689513.6851 | 1237048.6176
13 | 2689487.137 | 1237034.752
14 | 2689498.4356 | 1236942.8335
15 | 2689475.2557 | 1236975.1893
16 | 2689513.6644 | 1237066.5525
17 | 2689532.8611 | 1237020.9532
18 | 2689485.437 | 1237056.6645
19 | 2689516.1141 | 1236953.3076
20 | 2689506.8614 | 1236970.0015
21 | 2689513.3301 | 1236990.8593
22 | 2689529.4856 | 1236988.3787
23 | 2689515.2531 | 1236997.3263
24 | 2689501.6517 | 1237001.5577
25 | 2689571.6921 | 1237004.4687
26 | 2689415.4495 | 1236944.2859
27 | 2689529.0973 | 1236986.0267

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98441 | -0.30017 | 0.044002 | 0.011028
1 | 0.98509 | -0.28675 | 0.033444 | 0.0083818
2 | 0.98768 | -0.23636 | 0 | 0
3 | 0.99179 | -0.15705 | 0 | 0
4 | 0.98988 | -0.19404 | 0.0062891 | 0.0015762
5 | 0.98998 | -0.19209 | 0 | 0
6 | 0.99063 | -0.17948 | 0 | 0
7 | 0.98949 | -0.20178 | 0.0073281 | 0.0018366
8 | 0.99129 | -0.1667 | 0 | 0
9 | 0.99351 | -0.12465 | 0.0043458 | 0.0010892
10 | 0.99354 | -0.12399 | 0.0046538 | 0.0011663
11 | 0.99378 | -0.11943 | 0 | 0
12 | 0.99311 | -0.13241 | 0 | 0
13 | 0.99464 | -0.10284 | 0 | 0
14 | 0.9922 | -0.14912 | 0 | 0
15 | 0.99118 | -0.16893 | 0.0065551 | 0.0016429
16 | 0.99293 | -0.13594 | 0.010967 | 0.0027486
17 | 0.99583 | -0.079782 | 0 | 0
18 | 0.99451 | -0.10543 | 0.0066716 | 0.0016721
19 | 0.99127 | -0.16708 | 0.024307 | 0.0060919
20 | 0.99567 | -0.082564 | 0.0061467 | 0.0015405
21 | 0.99845 | -0.029431 | 0 | 0
22 | 1 | 0 | -0.21048 | -0.053094
23 | 0.99804 | -0.037468 | 0 | 0
24 | 0.99797 | -0.038789 | 0.0053129 | 0.0013315
25 | 0.99444 | -0.1068 | 0.036154 | 0.009061
26 | 0.98941 | -0.20329 | 0.010693 | 0.00268
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.044002 | -0.011028 | 0.04403 | 0.011046 | 2.8148e-05 | 1.7799e-05 | 0.066512 | 0.066512 | 0.066512 | 0.98441 | -0.30017 | 0.98509 | -0.28675 | 18.2726
1 | -0.077473 | -0.019427 | 0.07766 | 0.019546 | 0.00018655 | 0.00011893 | 0.11703 | 0.11703 | 0.11703 | 0.98509 | -0.28675 | 0.98768 | -0.23636 | 32.1511
2 | -0.07766 | -0.019546 | 0.077956 | 0.019735 | 0.00029559 | 0.00018844 | 0.11703 | 0.11703 | 0.11703 | 0.98768 | -0.23636 | 0.99179 | -0.15705 | 32.151
3 | -0.10227 | -0.025834 | 0.10231 | 0.025859 | 3.8895e-05 | 2.4836e-05 | 0.15352 | 0.15352 | 0.15352 | 0.99179 | -0.15705 | 0.9922 | -0.14912 | 42.1749
4 | 0.024318 | 0.006099 | -0.024307 | -0.0060919 | 1.1617e-05 | 7.1348e-06 | 0.036487 | 0.036487 | 0.036487 | 0.99179 | -0.15705 | 0.99127 | -0.16708 | 10.024
5 | -0.0062891 | -0.0015762 | 0.0062897 | 0.0015764 | 5.8404e-07 | 1.4976e-07 | 0.009454 | 0.0094539 | 0.009454 | 0.98988 | -0.19404 | 0.98998 | -0.19209 | 2.5972
6 | -0.02432 | -0.0060983 | 0.024335 | 0.0061072 | 1.4631e-05 | 8.9881e-06 | 0.036556 | 0.036556 | 0.036556 | 0.98998 | -0.19209 | 0.99063 | -0.17948 | 10.0429
7 | 0.01803 | 0.0045219 | -0.018022 | -0.004517 | 8.3205e-06 | 4.9369e-06 | 0.027102 | 0.027102 | 0.027102 | 0.98998 | -0.19209 | 0.98949 | -0.20178 | 7.4457
8 | -0.024335 | -0.0061072 | 0.02435 | 0.0061164 | 1.484e-05 | 9.1162e-06 | 0.036556 | 0.036556 | 0.036556 | 0.99063 | -0.17948 | 0.99129 | -0.1667 | 10.0428
9 | 0.010694 | 0.0026804 | -0.010693 | -0.00268 | 7.6849e-07 | 3.9007e-07 | 0.016082 | 0.016082 | 0.016082 | 0.98949 | -0.20178 | 0.98941 | -0.20329 | 4.4182
10 | -0.030905 | -0.0077594 | 0.030931 | 0.0077756 | 2.5938e-05 | 1.6186e-05 | 0.046397 | 0.046396 | 0.046397 | 0.99129 | -0.1667 | 0.9922 | -0.14912 | 12.7463
11 | 0.0065558 | 0.0016431 | -0.0065551 | -0.0016429 | 6.9508e-07 | 1.9813e-07 | 0.0098408 | 0.0098409 | 0.0098409 | 0.99129 | -0.1667 | 0.99118 | -0.16893 | 2.7036
12 | -0.0043458 | -0.0010892 | 0.004346 | 0.0010891 | 1.3603e-07 | -2.3822e-08 | 0.0065089 | 0.0065089 | 0.0065089 | 0.99351 | -0.12465 | 0.99354 | -0.12399 | 1.7882
13 | -0.0089997 | -0.0022555 | 0.0090017 | 0.0022564 | 1.9587e-06 | 8.8113e-07 | 0.013479 | 0.013479 | 0.013479 | 0.99354 | -0.12399 | 0.99378 | -0.11943 | 3.703
14 | 0.010976 | 0.002753 | -0.010969 | -0.0027495 | 6.7914e-06 | 3.4784e-06 | 0.016435 | 0.016435 | 0.016435 | 0.99378 | -0.11943 | 0.99311 | -0.13241 | 4.5151
15 | -0.019977 | -0.0050094 | 0.019993 | 0.0050189 | 1.5802e-05 | 9.5028e-06 | 0.029913 | 0.029913 | 0.029913 | 0.99378 | -0.11943 | 0.99464 | -0.10284 | 8.218
16 | 0.010969 | 0.0027495 | -0.010967 | -0.0027486 | 1.8452e-06 | 9.4529e-07 | 0.016435 | 0.016435 | 0.016435 | 0.99311 | -0.13241 | 0.99293 | -0.13594 | 4.5152
17 | -0.026665 | -0.0066912 | 0.026695 | 0.0067093 | 2.9355e-05 | 1.8148e-05 | 0.039895 | 0.039895 | 0.039895 | 0.99464 | -0.10284 | 0.99583 | -0.079782 | 10.9603
18 | 0.0066724 | 0.0016723 | -0.0066716 | -0.0016721 | 8.2136e-07 | 2.4042e-07 | 0.0099822 | 0.0099823 | 0.0099823 | 0.99464 | -0.10284 | 0.99451 | -0.10543 | 2.7424
19 | -0.13324 | -0.033634 | 0.13367 | 0.033907 | 0.0004263 | 0.00027246 | 0.19991 | 0.19991 | 0.19991 | 0.9922 | -0.14912 | 0.99567 | -0.082564 | 54.9212
20 | -0.062895 | -0.0158 | 0.063022 | 0.015881 | 0.00012729 | 8.0963e-05 | 0.093993 | 0.093993 | 0.093993 | 0.99583 | -0.079782 | 0.99804 | -0.037468 | 25.8223
21 | 0.0362 | 0.0090902 | -0.036154 | -0.009061 | 4.6591e-05 | 2.9267e-05 | 0.054098 | 0.054098 | 0.054098 | 0.99583 | -0.079782 | 0.99444 | -0.1068 | 14.8622
22 | -0.13982 | -0.035447 | 0.14018 | 0.035676 | 0.00035805 | 0.00022887 | 0.2091 | 0.2091 | 0.2091 | 0.99567 | -0.082564 | 0.99845 | -0.029431 | 57.4448
23 | -0.20854 | -0.052905 | 0.20883 | 0.053094 | 0.00029559 | 0.00018875 | 0.31101 | 0.31101 | 0.31101 | 0.99845 | -0.029431 | 1 | 0 | 42.7216
24 | 0.068362 | 0.017229 | -0.068336 | -0.017212 | 2.6276e-05 | 1.6728e-05 | 0.10191 | 0.10191 | 0.10191 | 0.99845 | -0.029431 | 0.99804 | -0.037468 | 27.9986
25 | 0.0053132 | 0.0013316 | -0.0053129 | -0.0013315 | 3.3433e-07 | 2.8331e-08 | 0.0079217 | 0.0079218 | 0.0079218 | 0.99804 | -0.037468 | 0.99797 | -0.038789 | 2.1763

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.21649 | 0.054598

## res_load
| p_mw | q_mvar
0 | 0.044002 | 0.011028
1 | 0.033444 | 0.0083818
2 | 0.0062891 | 0.0015762
3 | 0.0073281 | 0.0018366
4 | 0.0043458 | 0.0010892
5 | 0.0046538 | 0.0011663
6 | 0.0065551 | 0.0016429
7 | 0.010967 | 0.0027486
8 | 0.0066716 | 0.0016721
9 | 0.024307 | 0.0060919
10 | 0.0061467 | 0.0015405
11 | 0.0060033 | 0.0015046
12 | 0.0053129 | 0.0013315
13 | 0.036154 | 0.009061
14 | 0.010693 | 0.00268

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1