## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_156-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_156-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_156-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_156-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_156-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_156-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_156-3_0_4_node_108 | 0.4 | n |  | TRUE
7 | bus_LV_156-3_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_156-3_0_4_node_109 | 0.4 | n |  | TRUE
9 | bus_LV_156-3_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_156-3_0_4_node_129 | 0.4 | n |  | TRUE
11 | bus_LV_156-3_0_4_node_140 | 0.4 | n |  | TRUE
12 | bus_LV_156-3_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_156-3_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_156-3_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_156-3_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_156-3_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_156-3_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_156-3_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_156-3_0_4_node_137 | 0.4 | n |  | TRUE
20 | bus_LV_156-3_0_4_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_156-3_0_4_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_156-3_0_4_node_138 | 0.4 | n |  | TRUE
23 | bus_LV_156-3_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_156-3_0_4_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_156-3_0_4_node_128 | 0.4 | n |  | TRUE
26 | bus_LV_156-3_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_156-3_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_156-3_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_156-3_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_156-3_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_156-3_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_156-3_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_156-3_0_4_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_156-3_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_156-3_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_156-3_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_156-3_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_156-3_0_4_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_156-3_0_4_node_77 | 0.4 | n |  | TRUE
40 | bus_LV_156-3_0_4_node_141 | 0.4 | n |  | TRUE
41 | bus_LV_156-3_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_156-3_0_4_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_156-3_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_156-3_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_156-3_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_156-3_0_4_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_156-3_0_4_node_135 | 0.4 | n |  | TRUE
48 | bus_LV_156-3_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_156-3_0_4_node_136 | 0.4 | n |  | TRUE
50 | bus_LV_156-3_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_156-3_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_156-3_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_156-3_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_156-3_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_156-3_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_156-3_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_156-3_0_4_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_156-3_0_4_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_156-3_0_4_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_156-3_0_4_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_156-3_0_4_node_65 | 0.4 | n |  | TRUE
62 | bus_LV_156-3_0_4_node_64 | 0.4 | n |  | TRUE
63 | bus_LV_156-3_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_156-3_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_156-3_0_4_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_156-3_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_156-3_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_156-3_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_156-3_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_156-3_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_156-3_0_4_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_156-3_0_4_node_119 | 0.4 | n |  | TRUE
73 | bus_LV_156-3_0_4_node_120 | 0.4 | n |  | TRUE
74 | bus_LV_156-3_0_4_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_156-3_0_4_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_156-3_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_156-3_0_4_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_156-3_0_4_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_156-3_0_4_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_156-3_0_4_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_156-3_0_4_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_156-3_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_156-3_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_156-3_0_4_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_156-3_0_4_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_156-3_0_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_156-3_0_4_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_156-3_0_4_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_156-3_0_4_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_156-3_0_4_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_156-3_0_4_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_156-3_0_4_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_156-3_0_4_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_156-3_0_4_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_156-3_0_4_node_132 | 0.4 | n |  | TRUE
96 | bus_LV_156-3_0_4_node_133 | 0.4 | n |  | TRUE
97 | bus_LV_156-3_0_4_node_130 | 0.4 | n |  | TRUE
98 | bus_LV_156-3_0_4_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_156-3_0_4_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_156-3_0_4_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_156-3_0_4_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_156-3_0_4_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_156-3_0_4_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_156-3_0_4_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_156-3_0_4_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_156-3_0_4_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_156-3_0_4_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_156-3_0_4_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_156-3_0_4_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_156-3_0_4_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_156-3_0_4_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_156-3_0_4_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_156-3_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_156-3_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_156-3_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_156-3_0_4_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_156-3_0_4_node_139 | 0.4 | n |  | TRUE
118 | bus_LV_156-3_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_156-3_0_4_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_156-3_0_4_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_156-3_0_4_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_156-3_0_4_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_156-3_0_4_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_156-3_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_156-3_0_4_node_115 | 0.4 | n |  | TRUE
126 | bus_LV_156-3_0_4_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_156-3_0_4_node_127 | 0.4 | n |  | TRUE
128 | bus_LV_156-3_0_4_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_156-3_0_4_node_121 | 0.4 | n |  | TRUE
130 | bus_LV_156-3_0_4_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_156-3_0_4_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_156-3_0_4_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_156-3_0_4_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_156-3_0_4_node_134 | 0.4 | n |  | TRUE
135 | bus_LV_156-3_0_4_node_131 | 0.4 | n |  | TRUE
136 | bus_MV_496_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_156-3_0_4_load_0 | 0 | 0.0017706 | 0.00044375 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_156-3_0_4_load_1 | 1 | 0.0018491 | 0.00046344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_156-3_0_4_load_3 | 3 | 0.0018338 | 0.00045958 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_156-3_0_4_load_108 | 6 | 0.0020327 | 0.00050946 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_156-3_0_4_load_109 | 8 | 0.0021006 | 0.00052646 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_156-3_0_4_load_129 | 10 | 0.0023198 | 0.00058139 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_156-3_0_4_load_140 | 11 | 0.0027043 | 0.00067776 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_156-3_0_4_load_10 | 13 | 0.0083778 | 0.0020997 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_156-3_0_4_load_6 | 14 | 0.018577 | 0.0046557 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_156-3_0_4_load_9 | 17 | 0.0037044 | 0.00092842 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_156-3_0_4_load_137 | 19 | 0.0098999 | 0.0024811 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_156-3_0_4_load_107 | 21 | 0.0049962 | 0.0012522 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_156-3_0_4_load_138 | 22 | 0.0095461 | 0.0023925 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_156-3_0_4_load_37 | 24 | 0.0063201 | 0.001584 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_156-3_0_4_load_128 | 25 | 0.0023056 | 0.00057784 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_156-3_0_4_load_15 | 26 | 0.0022113 | 0.0005542 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_156-3_0_4_load_30 | 30 | 0.0076085 | 0.0019069 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_156-3_0_4_load_27 | 31 | 0.0019153 | 0.00048001 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_156-3_0_4_load_36 | 33 | 0.0058834 | 0.0014745 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_156-3_0_4_load_41 | 34 | 0.0088581 | 0.0022201 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_156-3_0_4_load_28 | 35 | 0.0019711 | 0.00049401 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_156-3_0_4_load_19 | 37 | 0.0012535 | 0.00031416 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_156-3_0_4_load_77 | 39 | 0.0054854 | 0.0013748 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_156-3_0_4_load_141 | 40 | 0.0015389 | 0.00038567 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_156-3_0_4_load_78 | 42 | 0.0051569 | 0.0012924 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_156-3_0_4_load_22 | 43 | 0.0028611 | 0.00071706 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_156-3_0_4_load_24 | 45 | 0.0051597 | 0.0012931 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_156-3_0_4_load_135 | 47 | 0.0024743 | 0.00062012 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_156-3_0_4_load_29 | 48 | 0.0020896 | 0.0005237 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_156-3_0_4_load_136 | 49 | 0.0033915 | 0.00084998 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_156-3_0_4_load_31 | 50 | 0.001746 | 0.00043758 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_156-3_0_4_load_32 | 51 | 0.0023844 | 0.00059759 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_156-3_0_4_load_34 | 52 | 0.0020454 | 0.00051263 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_156-3_0_4_load_38 | 53 | 0.0065067 | 0.0016307 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_156-3_0_4_load_40 | 54 | 0.0088493 | 0.0022178 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_156-3_0_4_load_42 | 55 | 0.0022256 | 0.00055779 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_156-3_0_4_load_46 | 57 | 0.0018109 | 0.00045385 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_156-3_0_4_load_47 | 58 | 0.0016365 | 0.00041014 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_156-3_0_4_load_85 | 60 | 0.0012605 | 0.00031591 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_156-3_0_4_load_65 | 61 | 0.0010022 | 0.00025117 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_156-3_0_4_load_48 | 63 | 0.0019096 | 0.00047858 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_156-3_0_4_load_49 | 64 | 0.0014223 | 0.00035645 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_156-3_0_4_load_51 | 66 | 0.0028566 | 0.00071594 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_156-3_0_4_load_52 | 67 | 0.0022216 | 0.00055677 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_156-3_0_4_load_53 | 68 | 0.0010186 | 0.00025528 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_156-3_0_4_load_54 | 69 | 0.0024568 | 0.00061574 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_156-3_0_4_load_56 | 71 | 0.0029326 | 0.00073498 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_156-3_0_4_load_119 | 72 | 0.0027903 | 0.00069932 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_156-3_0_4_load_120 | 73 | 0.0028263 | 0.00070834 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_156-3_0_4_load_57 | 74 | 0.008037 | 0.0020143 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_156-3_0_4_load_58 | 75 | 0.0035499 | 0.00088968 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_156-3_0_4_load_62 | 79 | 0.0055277 | 0.0013854 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_156-3_0_4_load_67 | 80 | 0.0057133 | 0.0014319 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_156-3_0_4_load_66 | 81 | 0.0040108 | 0.0010052 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_156-3_0_4_load_84 | 82 | 0.0019397 | 0.00048614 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_156-3_0_4_load_81 | 83 | 0.0022361 | 0.00056041 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_156-3_0_4_load_79 | 84 | 0.0045986 | 0.0011525 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_156-3_0_4_load_68 | 85 | 0.0036234 | 0.00090811 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_156-3_0_4_load_80 | 87 | 0.0022624 | 0.00056701 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_156-3_0_4_load_83 | 88 | 0.0013869 | 0.00034759 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_156-3_0_4_load_69 | 89 | 0.0063444 | 0.00159 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_156-3_0_4_load_70 | 90 | 0.0018036 | 0.00045202 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_156-3_0_4_load_71 | 91 | 0.001426 | 0.0003574 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_156-3_0_4_load_73 | 92 | 0.0029613 | 0.00074218 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_156-3_0_4_load_74 | 93 | 0.0036625 | 0.0009179 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_156-3_0_4_load_76 | 94 | 0.0019333 | 0.00048453 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_156-3_0_4_load_133 | 96 | 0.004481 | 0.001123 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_156-3_0_4_load_130 | 97 | 0.0023229 | 0.00058218 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_156-3_0_4_load_95 | 99 | 0.0024566 | 0.00061569 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_156-3_0_4_load_93 | 100 | 0.0019508 | 0.00048891 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_156-3_0_4_load_86 | 101 | 0.0022933 | 0.00057476 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_156-3_0_4_load_87 | 102 | 0.0015804 | 0.00039609 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_156-3_0_4_load_88 | 103 | 0.0026207 | 0.0006568 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_156-3_0_4_load_89 | 104 | 0.0016503 | 0.00041359 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_156-3_0_4_load_90 | 105 | 0.0021319 | 0.00053429 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_156-3_0_4_load_91 | 106 | 0.0022904 | 0.00057402 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_156-3_0_4_load_92 | 107 | 0.0020232 | 0.00050707 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_156-3_0_4_load_96 | 111 | 0.0027433 | 0.00068755 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_156-3_0_4_load_97 | 112 | 0.0068465 | 0.0017159 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_156-3_0_4_load_104 | 114 | 0.0020742 | 0.00051985 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_156-3_0_4_load_101 | 115 | 0.0031273 | 0.00078377 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_156-3_0_4_load_102 | 116 | 0.0040754 | 0.0010214 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_156-3_0_4_load_139 | 117 | 0.0065702 | 0.0016466 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_156-3_0_4_load_110 | 118 | 0.0019065 | 0.00047781 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_156-3_0_4_load_111 | 119 | 0.0019681 | 0.00049325 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_156-3_0_4_load_113 | 121 | 0.0025424 | 0.00063717 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_156-3_0_4_load_118 | 122 | 0.0024629 | 0.00061726 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_156-3_0_4_load_117 | 123 | 0.0024565 | 0.00061567 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_156-3_0_4_load_114 | 124 | 0.0020678 | 0.00051824 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_156-3_0_4_load_115 | 125 | 0.0023561 | 0.0005905 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_156-3_0_4_load_116 | 126 | 0.0025454 | 0.00063795 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_156-3_0_4_load_127 | 127 | 0.0027438 | 0.00068767 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_156-3_0_4_load_121 | 129 | 0.0096398 | 0.002416 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_156-3_0_4_load_122 | 130 | 0.005262 | 0.0013188 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_156-3_0_4_load_124 | 132 | 0.0051628 | 0.0012939 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_156-3_0_4_load_126 | 133 | 0.0032919 | 0.00082504 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_156-3_0_4_load_134 | 134 | 0.0027916 | 0.00069963 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_156-3_0_4_load_131 | 135 | 0.0028447 | 0.00071294 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 66 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_156-3_0_4_line_0 |  | 0 | 1 | 0.0058286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_156-3_0_4_line_1 |  | 0 | 2 | 0.016306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_156-3_0_4_line_2 |  | 1 | 3 | 0.011311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_156-3_0_4_line_3 |  | 2 | 4 | 0.050073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_156-3_0_4_line_4 |  | 2 | 5 | 0.034048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_156-3_0_4_line_5 |  | 4 | 6 | 0.031332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_156-3_0_4_line_6 |  | 5 | 7 | 0.023022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_156-3_0_4_line_7 |  | 6 | 8 | 0.0064805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_156-3_0_4_line_8 |  | 7 | 11 | 0.015245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_156-3_0_4_line_9 |  | 7 | 12 | 0.022999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_156-3_0_4_line_10 |  | 7 | 9 | 0.031995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_156-3_0_4_line_11 |  | 8 | 118 | 0.0062869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_156-3_0_4_line_12 |  | 9 | 10 | 0.022004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_156-3_0_4_line_13 |  | 10 | 25 | 0.0063705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_156-3_0_4_line_14 |  | 12 | 13 | 0.020657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_156-3_0_4_line_15 |  | 12 | 18 | 0.024035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_156-3_0_4_line_16 |  | 14 | 15 | 0.038184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_156-3_0_4_line_17 |  | 15 | 16 | 0.009278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_156-3_0_4_line_18 |  | 15 | 17 | 0.0068413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_156-3_0_4_line_19 |  | 16 | 18 | 0.001989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_156-3_0_4_line_20 |  | 16 | 19 | 0.025366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_156-3_0_4_line_21 |  | 17 | 20 | 0.021755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_156-3_0_4_line_22 |  | 18 | 21 | 0.012884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_156-3_0_4_line_23 |  | 19 | 22 | 0.018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_156-3_0_4_line_24 |  | 20 | 23 | 0.014389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_156-3_0_4_line_25 |  | 20 | 24 | 0.01551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_156-3_0_4_line_26 |  | 23 | 46 | 0.053711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_156-3_0_4_line_27 |  | 23 | 34 | 0.040045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_156-3_0_4_line_28 |  | 23 | 44 | 0.050977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_156-3_0_4_line_29 |  | 24 | 53 | 0.0034058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_156-3_0_4_line_30 |  | 25 | 67 | 0.0041758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_156-3_0_4_line_31 |  | 26 | 27 | 0.025732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_156-3_0_4_line_32 |  | 27 | 28 | 0.027445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_156-3_0_4_line_33 |  | 27 | 29 | 0.005178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_156-3_0_4_line_34 |  | 28 | 30 | 0.0031731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_156-3_0_4_line_35 |  | 28 | 31 | 0.025452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_156-3_0_4_line_36 |  | 29 | 32 | 0.012283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_156-3_0_4_line_37 |  | 29 | 33 | 0.011774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_156-3_0_4_line_38 |  | 30 | 34 | 0.026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_156-3_0_4_line_39 |  | 31 | 35 | 0.0095168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_156-3_0_4_line_40 |  | 32 | 36 | 0.015222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_156-3_0_4_line_41 |  | 32 | 37 | 0.020926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_156-3_0_4_line_42 |  | 35 | 48 | 0.0099561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_156-3_0_4_line_43 |  | 36 | 38 | 0.017025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_156-3_0_4_line_44 |  | 36 | 39 | 0.016495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_156-3_0_4_line_45 |  | 38 | 40 | 0.014042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_156-3_0_4_line_46 |  | 38 | 41 | 0.047341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_156-3_0_4_line_47 |  | 39 | 42 | 0.010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_156-3_0_4_line_48 |  | 41 | 50 | 0.008092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_156-3_0_4_line_49 |  | 43 | 44 | 0.0086149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_156-3_0_4_line_50 |  | 44 | 45 | 0.00567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_156-3_0_4_line_51 |  | 46 | 47 | 0.007499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_156-3_0_4_line_52 |  | 48 | 49 | 0.081894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_156-3_0_4_line_53 |  | 50 | 51 | 0.018076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_156-3_0_4_line_54 |  | 51 | 52 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_156-3_0_4_line_55 |  | 53 | 54 | 0.0034299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_156-3_0_4_line_56 |  | 55 | 56 | 0.021927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_156-3_0_4_line_57 |  | 56 | 57 | 0.011839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_156-3_0_4_line_58 |  | 56 | 58 | 0.031054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_156-3_0_4_line_59 |  | 57 | 59 | 0.021031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_156-3_0_4_line_60 |  | 58 | 60 | 0.024226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_156-3_0_4_line_61 |  | 59 | 61 | 0.01841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_156-3_0_4_line_62 |  | 60 | 62 | 0.0171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_156-3_0_4_line_63 |  | 61 | 68 | 0.0052465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_156-3_0_4_line_64 |  | 62 | 86 | 0.00615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_156-3_0_4_line_65 |  | 63 | 64 | 0.023735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_156-3_0_4_line_66 |  | 63 | 65 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_156-3_0_4_line_67 |  | 64 | 66 | 0.041535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_156-3_0_4_line_68 |  | 65 | 67 | 0.010232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_156-3_0_4_line_69 |  | 65 | 68 | 0.010794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_156-3_0_4_line_70 |  | 66 | 69 | 0.0076686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_156-3_0_4_line_71 |  | 69 | 70 | 0.0031354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_156-3_0_4_line_72 |  | 70 | 71 | 0.012364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_156-3_0_4_line_73 |  | 71 | 72 | 0.0028807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_156-3_0_4_line_74 |  | 72 | 73 | 0.0060418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_156-3_0_4_line_75 |  | 73 | 127 | 0.0027299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_156-3_0_4_line_76 |  | 74 | 75 | 0.011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_156-3_0_4_line_77 |  | 74 | 76 | 0.0049819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_156-3_0_4_line_78 |  | 75 | 77 | 0.01446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_156-3_0_4_line_79 |  | 76 | 78 | 0.031888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_156-3_0_4_line_80 |  | 76 | 79 | 0.027392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_156-3_0_4_line_81 |  | 77 | 80 | 0.016228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_156-3_0_4_line_82 |  | 77 | 81 | 0.018267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_156-3_0_4_line_83 |  | 78 | 82 | 0.010886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_156-3_0_4_line_84 |  | 78 | 83 | 0.012382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_156-3_0_4_line_85 |  | 79 | 84 | 0.019248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_156-3_0_4_line_86 |  | 80 | 85 | 0.013744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_156-3_0_4_line_87 |  | 83 | 86 | 0.0073103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_156-3_0_4_line_88 |  | 84 | 87 | 0.014648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_156-3_0_4_line_89 |  | 85 | 89 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_156-3_0_4_line_90 |  | 86 | 88 | 0.012762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_156-3_0_4_line_91 |  | 87 | 98 | 0.037273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_156-3_0_4_line_92 |  | 89 | 90 | 0.0095113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_156-3_0_4_line_93 |  | 90 | 91 | 0.022897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_156-3_0_4_line_94 |  | 92 | 93 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_156-3_0_4_line_95 |  | 93 | 94 | 0.014516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_156-3_0_4_line_96 |  | 94 | 95 | 0.0066385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_156-3_0_4_line_97 |  | 95 | 96 | 0.024965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_156-3_0_4_line_98 |  | 95 | 97 | 0.0039482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_156-3_0_4_line_99 |  | 97 | 135 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_156-3_0_4_line_100 |  | 98 | 99 | 0.013314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_156-3_0_4_line_101 |  | 98 | 100 | 0.031638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_156-3_0_4_line_102 |  | 99 | 108 | 0.0096902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_156-3_0_4_line_103 |  | 100 | 107 | 0.0057909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_156-3_0_4_line_104 |  | 101 | 102 | 0.0065016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_156-3_0_4_line_105 |  | 102 | 103 | 0.018674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_156-3_0_4_line_106 |  | 103 | 104 | 0.0051489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_156-3_0_4_line_107 |  | 104 | 105 | 0.021195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_156-3_0_4_line_108 |  | 105 | 106 | 0.00081024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_156-3_0_4_line_109 |  | 106 | 107 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_156-3_0_4_line_110 |  | 108 | 109 | 0.040774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_156-3_0_4_line_111 |  | 108 | 110 | 0.017064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_156-3_0_4_line_112 |  | 109 | 113 | 0.03672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_156-3_0_4_line_113 |  | 109 | 114 | 0.027552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_156-3_0_4_line_114 |  | 110 | 111 | 0.047886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_156-3_0_4_line_115 |  | 111 | 112 | 0.01926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_156-3_0_4_line_116 |  | 113 | 117 | 0.083259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_156-3_0_4_line_117 |  | 114 | 116 | 0.030221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_156-3_0_4_line_118 |  | 115 | 116 | 0.027285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_156-3_0_4_line_119 |  | 118 | 119 | 0.0060791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_156-3_0_4_line_120 |  | 119 | 120 | 0.0054406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_156-3_0_4_line_121 |  | 120 | 121 | 0.011219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_156-3_0_4_line_122 |  | 121 | 122 | 0.0079628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_156-3_0_4_line_123 |  | 122 | 123 | 0.00783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_156-3_0_4_line_124 |  | 123 | 126 | 0.0079629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_156-3_0_4_line_125 |  | 124 | 125 | 0.0070445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_156-3_0_4_line_126 |  | 125 | 126 | 0.0078036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_156-3_0_4_line_127 |  | 127 | 128 | 0.013423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_156-3_0_4_line_128 |  | 128 | 134 | 0.011005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_156-3_0_4_line_129 |  | 128 | 131 | 0.003403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_156-3_0_4_line_130 |  | 129 | 130 | 0.0099521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_156-3_0_4_line_131 |  | 129 | 131 | 0.030741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_156-3_0_4_line_132 |  | 130 | 132 | 0.016921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_156-3_0_4_line_133 |  | 131 | 133 | 0.0035363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_156-3_0_4_line_134 |  | 133 | 135 | 0.010816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_156-3_0_4_trafo_51 | 0.63 MVA 20/0.4 kV | 136 | 66 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2691914.5207 | 1236304.6715 | 2691918.0147 | 1236309.3367
1 | 2691904.7459 | 1236291.6198 | 2691914.5207 | 1236304.6715
2 | 2691924.7951 | 1236318.3901 | 2691918.0147 | 1236309.3367
3 | 2691904.7459 | 1236291.6198 | 2691891.8035 | 1236315.1479 | 2691891.2138 | 1236321.9548 | 2691898.1201 | 1236336.8392
4 | 2691904.7459 | 1236291.6198 | 2691918.2598 | 1236263.931 | 2691921.4611 | 1236263.4468
5 | 2691898.1201 | 1236336.8392 | 2691912.3538 | 1236364.7519
6 | 2691921.4611 | 1236263.4468 | 2691924.6743 | 1236260.2386 | 2691930.9825 | 1236254.1207 | 2691938.5785 | 1236260.1426
7 | 2691912.3538 | 1236364.7519 | 2691915.2978 | 1236370.5251
8 | 2691949.8515 | 1236250.1097 | 2691946.9817 | 1236254.1127 | 2691938.5785 | 1236260.1426
9 | 2691957.2056 | 1236273.7074 | 2691938.5785 | 1236260.1426
10 | 2691914.1195 | 1236239.5269 | 2691922.851 | 1236247.0008 | 2691930.9825 | 1236254.1207 | 2691938.5785 | 1236260.1426
11 | 2691918.1538 | 1236376.1259 | 2691915.2978 | 1236370.5251
12 | 2691914.1195 | 1236239.5269 | 2691922.8044 | 1236228.9869 | 2691929.1412 | 1236223.5536
13 | 2691933.9774 | 1236219.4069 | 2691929.1412 | 1236223.5536
14 | 2691957.2056 | 1236273.7074 | 2691948.4037 | 1236280.0647 | 2691946.1256 | 1236279.0954 | 2691939.392 | 1236276.2162
15 | 2691957.2056 | 1236273.7074 | 2691960.6774 | 1236276.2741 | 2691969.3346 | 1236281.701 | 2691974.3438 | 1236283.7133 | 2691978.3651 | 1236284.5206
16 | 2691989.5575 | 1236286.0394 | 2691985.1508 | 1236300.8264 | 2691980.433 | 1236316.6427 | 2691979.0458 | 1236322.7364
17 | 2691989.5575 | 1236286.0394 | 2691983.8723 | 1236285.1619 | 2691980.3356 | 1236284.8291
18 | 2691989.5575 | 1236286.0394 | 2691996.1898 | 1236287.7176
19 | 2691980.3356 | 1236284.8291 | 2691978.3651 | 1236284.5206
20 | 2691980.3356 | 1236284.8291 | 2691975.1546 | 1236298.7924 | 2691970.8599 | 1236308.3435
21 | 2692016.6751 | 1236294.7657 | 2692007.6727 | 1236290.6233 | 2691996.1898 | 1236287.7176
22 | 2691978.3651 | 1236284.5206 | 2691982.1297 | 1236272.199
23 | 2691963.1936 | 1236325.3933 | 2691970.8599 | 1236308.3435
24 | 2692016.6751 | 1236294.7657 | 2692029.6632 | 1236301.0381
25 | 2692016.6751 | 1236294.7657 | 2692021.8918 | 1236280.1598
26 | 2692019.6858 | 1236353.4551 | 2692018.949 | 1236346.7944 | 2692027.8767 | 1236310.8287 | 2692029.6632 | 1236301.0381
27 | 2692029.6632 | 1236301.0381 | 2692045.87 | 1236307.6495 | 2692059.2989 | 1236308.9141 | 2692068.2645 | 1236307.6577
28 | 2692029.6632 | 1236301.0381 | 2692027.8767 | 1236310.8287 | 2692047.9827 | 1236316.8445 | 2692054.5475 | 1236318.1027 | 2692054.5447 | 1236331.4568
29 | 2692021.8918 | 1236280.1598 | 2692023.0374 | 1236276.9524
30 | 2691933.9774 | 1236219.4069 | 2691937.1474 | 1236216.6888
31 | 2692124.8845 | 1236304.016 | 2692124.4055 | 1236316.3509 | 2692123.3293 | 1236329.695
32 | 2692097.4494 | 1236303.5681 | 2692106.946 | 1236302.6813 | 2692124.8845 | 1236304.016
33 | 2692130.0626 | 1236304.4077 | 2692124.8845 | 1236304.016
34 | 2692097.4494 | 1236303.5681 | 2692094.307 | 1236304.0084
35 | 2692097.4494 | 1236303.5681 | 2692096.8537 | 1236312.6988 | 2692100.0979 | 1236312.8604 | 2692098.7465 | 1236325.8443
36 | 2692130.0626 | 1236304.4077 | 2692133.8347 | 1236304.6886 | 2692142.1283 | 1236306.7076
37 | 2692130.0626 | 1236304.4077 | 2692135.7098 | 1236294.0766
38 | 2692094.307 | 1236304.0084 | 2692068.2645 | 1236307.6577
39 | 2692098.7465 | 1236325.8443 | 2692097.7613 | 1236335.3099
40 | 2692156.6068 | 1236311.5356 | 2692142.1283 | 1236306.7076
41 | 2692142.1283 | 1236306.7076 | 2692140.0683 | 1236318.9957 | 2692138.5613 | 1236327.3272
42 | 2692096.7306 | 1236345.2126 | 2692097.7613 | 1236335.3099
43 | 2692156.6068 | 1236311.5356 | 2692173.0892 | 1236315.9835
44 | 2692156.6068 | 1236311.5356 | 2692153.9375 | 1236295.2577
45 | 2692164.6667 | 1236325.6821 | 2692171.0014 | 1236322.7449 | 2692173.0892 | 1236315.9835
46 | 2692173.0892 | 1236315.9835 | 2692188.4143 | 1236317.956 | 2692197.6608 | 1236319.0447 | 2692194.3246 | 1236341.3759
47 | 2692152.2927 | 1236285.2273 | 2692153.9375 | 1236295.2577
48 | 2692194.3246 | 1236341.3759 | 2692189.6717 | 1236347.9965
49 | 2692054.5447 | 1236331.4568 | 2692054.0514 | 1236336.9198 | 2692054.0028 | 1236340.0492
50 | 2692048.8592 | 1236331.5799 | 2692054.5447 | 1236331.4568
51 | 2692019.6858 | 1236353.4551 | 2692022.3383 | 1236360.4693
52 | 2692096.7306 | 1236345.2126 | 2692088.6902 | 1236426.711
53 | 2692192.9206 | 1236364.3555 | 2692189.1415 | 1236356.4175 | 2692187.6071 | 1236350.9342 | 2692189.6717 | 1236347.9965
54 | 2692192.9206 | 1236364.3555 | 2692195.2905 | 1236369.3335 | 2692200.8173 | 1236380.9584
55 | 2692024.191 | 1236273.7223 | 2692023.0374 | 1236276.9524
56 | 2691922.5424 | 1236178.4572 | 2691907.3726 | 1236194.2896
57 | 2691922.5424 | 1236178.4572 | 2691934.3706 | 1236178.9648
58 | 2691922.3117 | 1236147.4088 | 2691922.5424 | 1236178.4572
59 | 2691955.382 | 1236179.8664 | 2691934.3706 | 1236178.9648
60 | 2691922.3117 | 1236147.4088 | 2691946.5367 | 1236147.6731
61 | 2691955.382 | 1236179.8664 | 2691950.7824 | 1236197.6926
62 | 2691963.6352 | 1236147.8597 | 2691946.5367 | 1236147.6731
63 | 2691949.4716 | 1236202.7727 | 2691950.7824 | 1236197.6926
64 | 2691969.8007 | 1236148.0331 | 2691963.6352 | 1236147.8597
65 | 2691965.6384 | 1236213.6175 | 2691989.3679 | 1236214.1123
66 | 2691946.7749 | 1236213.2241 | 2691965.6384 | 1236213.6175
67 | 2691989.3679 | 1236214.1123 | 2692004.8423 | 1236214.435 | 2692030.8935 | 1236214.9803
68 | 2691946.7749 | 1236213.2241 | 2691937.1474 | 1236216.6888 | 2691937.1474 | 1236216.6888
69 | 2691946.7749 | 1236213.2241 | 2691949.4716 | 1236202.7727
70 | 2692038.5604 | 1236215.1408 | 2692030.8935 | 1236214.9803
71 | 2692041.6952 | 1236215.2064 | 2692038.5604 | 1236215.1408
72 | 2692041.6952 | 1236215.2064 | 2692044.8199 | 1236215.266 | 2692054.0288 | 1236216.0075
73 | 2692054.0288 | 1236216.0075 | 2692056.9001 | 1236216.2387
74 | 2692062.9224 | 1236216.7237 | 2692056.9001 | 1236216.2387
75 | 2692062.9224 | 1236216.7237 | 2692065.6435 | 1236216.9428
76 | 2692026.4343 | 1236149.6426 | 2692037.737 | 1236149.965
77 | 2692021.4544 | 1236149.5006 | 2692026.4343 | 1236149.6426
78 | 2692052.1908 | 1236150.3773 | 2692037.737 | 1236149.965
79 | 2692021.4544 | 1236149.5006 | 2691989.4848 | 1236148.5937
80 | 2692021.4544 | 1236149.5006 | 2692020.4614 | 1236122.1262
81 | 2692052.1908 | 1236150.3773 | 2692054.8689 | 1236150.4522 | 2692068.3398 | 1236151.9079
82 | 2692052.1908 | 1236150.3773 | 2692050.1452 | 1236168.5293
83 | 2691989.8157 | 1236159.4735 | 2691989.4848 | 1236148.5937
84 | 2691989.4848 | 1236148.5937 | 2691977.108 | 1236148.2412
85 | 2692020.4614 | 1236122.1262 | 2692020.3143 | 1236118.0711 | 2692020.9907 | 1236107.1515 | 2692024.9072 | 1236105.5033
86 | 2692082.0041 | 1236153.3844 | 2692068.3398 | 1236151.9079
87 | 2691969.8007 | 1236148.0331 | 2691977.108 | 1236148.2412
88 | 2692024.9072 | 1236105.5033 | 2692036.7143 | 1236100.5346 | 2692036.5713 | 1236098.7026
89 | 2692082.0041 | 1236153.3844 | 2692096.0139 | 1236154.8983
90 | 2691970.307 | 1236160.7835 | 2691969.8007 | 1236148.0331
91 | 2692024.0899 | 1236066.3809 | 2692029.205 | 1236073.2874 | 2692034.8515 | 1236076.6773 | 2692036.5713 | 1236098.7026
92 | 2692105.4702 | 1236155.9202 | 2692096.0139 | 1236154.8983
93 | 2692105.4702 | 1236155.9202 | 2692128.2351 | 1236158.3801
94 | 2692163.5109 | 1236223.6565 | 2692163.5109 | 1236223.6565 | 2692151.6681 | 1236223.0724 | 2692143.3101 | 1236222.5302
95 | 2692128.8242 | 1236221.5907 | 2692143.3101 | 1236222.5302
96 | 2692122.1958 | 1236221.2251 | 2692128.457 | 1236221.5669 | 2692128.8242 | 1236221.5907
97 | 2692119.8123 | 1236246.0729 | 2692122.1958 | 1236221.2251
98 | 2692122.1958 | 1236221.2251 | 2692120.371 | 1236221.2857 | 2692118.2545 | 1236221.1282
99 | 2692118.2545 | 1236221.1282 | 2692109.2358 | 1236220.4569 | 2692098.9247 | 1236219.6854 | 2692096.7263 | 1236219.5002
100 | 2692024.0899 | 1236066.3809 | 2692021.5105 | 1236053.3187
101 | 2692024.0899 | 1236066.3809 | 2692005.1013 | 1236071.2237 | 2691993.3264 | 1236073.7424
102 | 2692023.3283 | 1236044.7089 | 2692020.5109 | 1236048.2567 | 2692021.5105 | 1236053.3187
103 | 2691993.3264 | 1236073.7424 | 2691987.6636 | 1236074.9537
104 | 2691924.0323 | 1236081.0596 | 2691930.5276 | 1236080.7748
105 | 2691949.184 | 1236079.9567 | 2691930.5276 | 1236080.7748
106 | 2691949.184 | 1236079.9567 | 2691954.328 | 1236079.7311
107 | 2691954.328 | 1236079.7311 | 2691968.1662 | 1236079.1243 | 2691975.3474 | 1236077.5882
108 | 2691976.1397 | 1236077.4187 | 2691975.3474 | 1236077.5882
109 | 2691976.1397 | 1236077.4187 | 2691987.6636 | 1236074.9537
110 | 2692023.1225 | 1236004.2763 | 2692022.3863 | 1236009.78 | 2692020.9767 | 1236019.1761 | 2692020.7693 | 1236026.7006 | 2692022.1413 | 1236037.3073 | 2692022.3029 | 1236038.5997 | 2692023.3283 | 1236044.7089
111 | 2692023.3283 | 1236044.7089 | 2692024.0068 | 1236048.2998 | 2692025.5923 | 1236057.342 | 2692026.4135 | 1236061.4911
112 | 2692030.0842 | 1235968.2245 | 2692023.1225 | 1236004.2763
113 | 2692023.1225 | 1236004.2763 | 2691996.0624 | 1236009.4588
114 | 2692026.4135 | 1236061.4911 | 2692027.2909 | 1236065.919 | 2692030.0374 | 1236070.3648 | 2692034.27 | 1236074.1553 | 2692042.9765 | 1236079.3384 | 2692058.5612 | 1236085.5955 | 2692063.9025 | 1236087.0589
115 | 2692063.9025 | 1236087.0589 | 2692070.951 | 1236088.99 | 2692081.8303 | 1236093.9392
116 | 2692037.8385 | 1236048.036 | 2692034.6378 | 1236042.1266 | 2692035.0545 | 1236036.2399 | 2692036.707 | 1236028.7489 | 2692037.1893 | 1235994.2201 | 2692037.6161 | 1235982.7962 | 2692037.2781 | 1235978.7214 | 2692035.7006 | 1235974.5383 | 2692030.0842 | 1235968.2245
117 | 2691966.3812 | 1236015.1434 | 2691996.0624 | 1236009.4588
118 | 2691939.5828 | 1236020.2759 | 2691966.3812 | 1236015.1434
119 | 2691918.1538 | 1236376.1259 | 2691920.9155 | 1236381.5415
120 | 2691923.3871 | 1236386.3884 | 2691920.9155 | 1236381.5415
121 | 2691923.3871 | 1236386.3884 | 2691933.2483 | 1236381.0386
122 | 2691940.2475 | 1236377.2415 | 2691933.2483 | 1236381.0386
123 | 2691947.13 | 1236373.5077 | 2691940.2475 | 1236377.2415
124 | 2691947.13 | 1236373.5077 | 2691954.1292 | 1236369.7106
125 | 2691967.1804 | 1236362.6302 | 2691960.9884 | 1236365.9894
126 | 2691960.9884 | 1236365.9894 | 2691954.1292 | 1236369.7106
127 | 2692079.0234 | 1236218.0202 | 2692065.6435 | 1236216.9428
128 | 2692079.0234 | 1236218.0202 | 2692078.3915 | 1236229.0074
129 | 2692082.4249 | 1236218.2953 | 2692079.0234 | 1236218.0202
130 | 2692080.5262 | 1236248.9771 | 2692090.4642 | 1236249.5052
131 | 2692082.4249 | 1236218.2953 | 2692081.967 | 1236225.8604 | 2692080.5262 | 1236248.9771 | 2692080.5262 | 1236248.9771
132 | 2692107.3609 | 1236250.403 | 2692090.4642 | 1236249.5052
133 | 2692082.4249 | 1236218.2953 | 2692085.9487 | 1236218.5922
134 | 2692085.9487 | 1236218.5922 | 2692096.7263 | 1236219.5002

## bus_geodata
| x | y | coords
0 | 2691914.5207 | 1236304.6715
1 | 2691918.0147 | 1236309.3367
2 | 2691904.7459 | 1236291.6198
3 | 2691924.7951 | 1236318.3901
4 | 2691898.1201 | 1236336.8392
5 | 2691921.4611 | 1236263.4468
6 | 2691912.3538 | 1236364.7519
7 | 2691938.5785 | 1236260.1426
8 | 2691915.2978 | 1236370.5251
9 | 2691914.1195 | 1236239.5269
10 | 2691929.1412 | 1236223.5536
11 | 2691949.8515 | 1236250.1097
12 | 2691957.2055 | 1236273.7074
13 | 2691939.392 | 1236276.2162
14 | 2691979.0458 | 1236322.7364
15 | 2691989.5575 | 1236286.0394
16 | 2691980.3356 | 1236284.8291
17 | 2691996.1898 | 1236287.7176
18 | 2691978.3651 | 1236284.5206
19 | 2691970.86 | 1236308.3435
20 | 2692016.6751 | 1236294.7657
21 | 2691982.1296 | 1236272.199
22 | 2691963.1936 | 1236325.3933
23 | 2692029.6632 | 1236301.0381
24 | 2692021.8918 | 1236280.1598
25 | 2691933.9774 | 1236219.4069
26 | 2692123.3293 | 1236329.695
27 | 2692124.8845 | 1236304.016
28 | 2692097.4494 | 1236303.5681
29 | 2692130.0626 | 1236304.4077
30 | 2692094.307 | 1236304.0084
31 | 2692098.7465 | 1236325.8443
32 | 2692142.1283 | 1236306.7076
33 | 2692135.7098 | 1236294.0766
34 | 2692068.2645 | 1236307.6577
35 | 2692097.7613 | 1236335.3099
36 | 2692156.6068 | 1236311.5356
37 | 2692138.5613 | 1236327.3272
38 | 2692173.0892 | 1236315.9835
39 | 2692153.9375 | 1236295.2577
40 | 2692164.6667 | 1236325.6821
41 | 2692194.3246 | 1236341.3759
42 | 2692152.2927 | 1236285.2273
43 | 2692054.0028 | 1236340.0492
44 | 2692054.5447 | 1236331.4568
45 | 2692048.8592 | 1236331.5799
46 | 2692019.6858 | 1236353.4551
47 | 2692022.3383 | 1236360.4693
48 | 2692096.7306 | 1236345.2126
49 | 2692088.6902 | 1236426.711
50 | 2692189.6717 | 1236347.9965
51 | 2692192.9206 | 1236364.3555
52 | 2692200.8173 | 1236380.9584
53 | 2692023.0374 | 1236276.9524
54 | 2692024.191 | 1236273.7223
55 | 2691907.3726 | 1236194.2896
56 | 2691922.5424 | 1236178.4572
57 | 2691934.3706 | 1236178.9648
58 | 2691922.3117 | 1236147.4088
59 | 2691955.382 | 1236179.8664
60 | 2691946.5367 | 1236147.6731
61 | 2691950.7824 | 1236197.6926
62 | 2691963.6352 | 1236147.8597
63 | 2691965.6384 | 1236213.6175
64 | 2691989.3679 | 1236214.1123
65 | 2691946.7749 | 1236213.2241
66 | 2692030.8935 | 1236214.9803
67 | 2691937.1474 | 1236216.6888
68 | 2691949.4716 | 1236202.7727
69 | 2692038.5604 | 1236215.1408
70 | 2692041.6952 | 1236215.2064
71 | 2692054.0288 | 1236216.0075
72 | 2692056.9001 | 1236216.2387
73 | 2692062.9224 | 1236216.7237
74 | 2692026.4343 | 1236149.6426
75 | 2692037.737 | 1236149.965
76 | 2692021.4544 | 1236149.5006
77 | 2692052.1908 | 1236150.3773
78 | 2691989.4848 | 1236148.5937
79 | 2692020.4614 | 1236122.1262
80 | 2692068.3398 | 1236151.9079
81 | 2692050.1452 | 1236168.5293
82 | 2691989.8157 | 1236159.4735
83 | 2691977.108 | 1236148.2412
84 | 2692024.9072 | 1236105.5033
85 | 2692082.0042 | 1236153.3844
86 | 2691969.8007 | 1236148.0331
87 | 2692036.5713 | 1236098.7026
88 | 2691970.307 | 1236160.7835
89 | 2692096.0139 | 1236154.8983
90 | 2692105.4702 | 1236155.9202
91 | 2692128.2351 | 1236158.3801
92 | 2692163.5109 | 1236223.6565
93 | 2692143.3101 | 1236222.5302
94 | 2692128.8242 | 1236221.5907
95 | 2692122.1958 | 1236221.2251
96 | 2692119.8123 | 1236246.0729
97 | 2692118.2545 | 1236221.1282
98 | 2692024.0899 | 1236066.3809
99 | 2692021.5105 | 1236053.3187
100 | 2691993.3264 | 1236073.7424
101 | 2691924.0323 | 1236081.0596
102 | 2691930.5276 | 1236080.7748
103 | 2691949.184 | 1236079.9567
104 | 2691954.328 | 1236079.7311
105 | 2691975.3474 | 1236077.5882
106 | 2691976.1397 | 1236077.4187
107 | 2691987.6636 | 1236074.9537
108 | 2692023.3283 | 1236044.7089
109 | 2692023.1225 | 1236004.2763
110 | 2692026.4135 | 1236061.4911
111 | 2692063.9025 | 1236087.0589
112 | 2692081.8303 | 1236093.9392
113 | 2692030.0842 | 1235968.2245
114 | 2691996.0624 | 1236009.4588
115 | 2691939.5828 | 1236020.2759
116 | 2691966.3812 | 1236015.1434
117 | 2692037.8385 | 1236048.036
118 | 2691918.1538 | 1236376.1259
119 | 2691920.9155 | 1236381.5415
120 | 2691923.3871 | 1236386.3884
121 | 2691933.2483 | 1236381.0386
122 | 2691940.2475 | 1236377.2415
123 | 2691947.13 | 1236373.5077
124 | 2691967.1804 | 1236362.6302
125 | 2691960.9884 | 1236365.9894
126 | 2691954.1292 | 1236369.7106
127 | 2692065.6435 | 1236216.9428
128 | 2692079.0234 | 1236218.0202
129 | 2692080.5262 | 1236248.9771
130 | 2692090.4642 | 1236249.5052
131 | 2692082.4249 | 1236218.2953
132 | 2692107.3609 | 1236250.403
133 | 2692085.9487 | 1236218.5922
134 | 2692078.3915 | 1236229.0074
135 | 2692096.7263 | 1236219.5002
136 | 2692041.6952 | 1236215.2064

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98617 | -0.26396 | 0.0017706 | 0.00044375
1 | 0.98615 | -0.26435 | 0.0018491 | 0.00046344
2 | 0.98625 | -0.26237 | 0 | 0
3 | 0.98613 | -0.26472 | 0.0018338 | 0.00045958
4 | 0.98521 | -0.28253 | 0 | 0
5 | 0.98712 | -0.24536 | 0 | 0
6 | 0.98457 | -0.29516 | 0.0020327 | 0.00050946
7 | 0.98771 | -0.23388 | 0 | 0
8 | 0.98444 | -0.29754 | 0.0021006 | 0.00052646
9 | 0.99025 | -0.185 | 0 | 0
10 | 0.99142 | -0.16268 | 0.0023198 | 0.00058139
11 | 0.98768 | -0.23462 | 0.0027043 | 0.00067776
12 | 0.98621 | -0.26286 | 0 | 0
13 | 0.98605 | -0.26596 | 0.0083778 | 0.0020997
14 | 0.98144 | -0.35557 | 0.018577 | 0.0046557
15 | 0.9821 | -0.34274 | 0 | 0
16 | 0.98303 | -0.32465 | 0 | 0
17 | 0.98153 | -0.35381 | 0.0037044 | 0.00092842
18 | 0.98326 | -0.32008 | 0 | 0
19 | 0.98257 | -0.33355 | 0.0098999 | 0.0024811
20 | 0.9798 | -0.38761 | 0 | 0
21 | 0.9832 | -0.32124 | 0.0049962 | 0.0012522
22 | 0.98241 | -0.33678 | 0.0095461 | 0.0023925
23 | 0.97894 | -0.40436 | 0 | 0
24 | 0.97949 | -0.39371 | 0.0063201 | 0.001584
25 | 0.99176 | -0.15614 | 0.0023056 | 0.00057784
26 | 0.97499 | -0.48206 | 0.0022113 | 0.0005542
27 | 0.97504 | -0.48101 | 0 | 0
28 | 0.97575 | -0.46708 | 0 | 0
29 | 0.97492 | -0.48344 | 0 | 0
30 | 0.97586 | -0.46493 | 0.0076085 | 0.0019069
31 | 0.97553 | -0.47145 | 0.0019153 | 0.00048001
32 | 0.97469 | -0.48786 | 0 | 0
33 | 0.97485 | -0.48471 | 0.0058834 | 0.0014745
34 | 0.97695 | -0.44344 | 0.0088581 | 0.0022201
35 | 0.97546 | -0.47275 | 0.0019711 | 0.00049401
36 | 0.97443 | -0.49298 | 0 | 0
37 | 0.97467 | -0.48834 | 0.0012535 | 0.00031416
38 | 0.97431 | -0.4954 | 0 | 0
39 | 0.97427 | -0.49621 | 0.0054854 | 0.0013748
40 | 0.97429 | -0.49579 | 0.0015389 | 0.00038567
41 | 0.97404 | -0.50077 | 0 | 0
42 | 0.97422 | -0.49717 | 0.0051569 | 0.0012924
43 | 0.97854 | -0.41225 | 0.0028611 | 0.00071706
44 | 0.97856 | -0.4118 | 0 | 0
45 | 0.97854 | -0.41233 | 0.0051597 | 0.0012931
46 | 0.97882 | -0.40677 | 0 | 0
47 | 0.9788 | -0.40711 | 0.0024743 | 0.00062012
48 | 0.97541 | -0.47375 | 0.0020896 | 0.0005237
49 | 0.97515 | -0.47884 | 0.0033915 | 0.00084998
50 | 0.97399 | -0.50169 | 0.001746 | 0.00043758
51 | 0.97392 | -0.50316 | 0.0023844 | 0.00059759
52 | 0.97388 | -0.50385 | 0.0020454 | 0.00051263
53 | 0.97944 | -0.39466 | 0.0065067 | 0.0016307
54 | 0.97941 | -0.39522 | 0.0088493 | 0.0022178
55 | 0.98895 | -0.20974 | 0.0022256 | 0.00055779
56 | 0.98899 | -0.20887 | 0 | 0
57 | 0.99012 | -0.18736 | 0.0018109 | 0.00045385
58 | 0.98611 | -0.26427 | 0.0016365 | 0.00041014
59 | 0.99113 | -0.16797 | 0 | 0
60 | 0.98389 | -0.30699 | 0.0012605 | 0.00031591
61 | 0.99202 | -0.15102 | 0.0010022 | 0.00025117
62 | 0.98235 | -0.33688 | 0 | 0
63 | 0.99421 | -0.10946 | 0.0019096 | 0.00047858
64 | 0.99631 | -0.069637 | 0.0014223 | 0.00035645
65 | 0.99255 | -0.14103 | 0 | 0
66 | 1 | 0 | -0.35301 | -0.090293
67 | 0.99199 | -0.1518 | 0.0022216 | 0.00055677
68 | 0.99219 | -0.14777 | 0.0010186 | 0.00025528
69 | 0.99959 | -0.0077703 | 0.0024568 | 0.00061574
70 | 0.99944 | -0.010815 | 0 | 0
71 | 0.99881 | -0.022829 | 0.0029326 | 0.00073498
72 | 0.99867 | -0.025483 | 0.0027903 | 0.00069932
73 | 0.9984 | -0.030756 | 0.0028263 | 0.00070834
74 | 0.9772 | -0.43737 | 0.008037 | 0.0020143
75 | 0.97692 | -0.44284 | 0.0035499 | 0.00088968
76 | 0.97736 | -0.43423 | 0 | 0
77 | 0.97661 | -0.44889 | 0 | 0
78 | 0.98007 | -0.38123 | 0 | 0
79 | 0.9759 | -0.46268 | 0.0055277 | 0.0013854
80 | 0.97632 | -0.4545 | 0.0057133 | 0.0014319
81 | 0.97654 | -0.45023 | 0.0040108 | 0.0010052
82 | 0.98005 | -0.38161 | 0.0019397 | 0.00048614
83 | 0.98114 | -0.36029 | 0.0022361 | 0.00056041
84 | 0.97498 | -0.48078 | 0.0045986 | 0.0011525
85 | 0.97616 | -0.45782 | 0.0036234 | 0.00090811
86 | 0.98179 | -0.34765 | 0 | 0
87 | 0.97434 | -0.49333 | 0.0022624 | 0.00056701
88 | 0.98178 | -0.34797 | 0.0013869 | 0.00034759
89 | 0.97603 | -0.46029 | 0.0063444 | 0.00159
90 | 0.976 | -0.46085 | 0.0018036 | 0.00045202
91 | 0.97597 | -0.46145 | 0.001426 | 0.0003574
92 | 0.99682 | -0.061134 | 0.0029613 | 0.00074218
93 | 0.99688 | -0.060082 | 0.0036625 | 0.0009179
94 | 0.99696 | -0.058396 | 0.0019333 | 0.00048453
95 | 0.99702 | -0.0574 | 0 | 0
96 | 0.99691 | -0.059362 | 0.004481 | 0.001123
97 | 0.99706 | -0.056497 | 0.0023229 | 0.00058218
98 | 0.9728 | -0.52379 | 0 | 0
99 | 0.97245 | -0.53064 | 0.0024566 | 0.00061569
100 | 0.97231 | -0.53344 | 0.0019508 | 0.00048891
101 | 0.97181 | -0.54329 | 0.0022933 | 0.00057476
102 | 0.97183 | -0.54302 | 0.0015804 | 0.00039609
103 | 0.97189 | -0.54168 | 0.0026207 | 0.0006568
104 | 0.97192 | -0.54107 | 0.0016503 | 0.00041359
105 | 0.97209 | -0.53788 | 0.0021319 | 0.00053429
106 | 0.97209 | -0.53773 | 0.0022904 | 0.00057402
107 | 0.97223 | -0.535 | 0.0020232 | 0.00050707
108 | 0.97222 | -0.53519 | 0 | 0
109 | 0.97162 | -0.54711 | 0 | 0
110 | 0.97207 | -0.5382 | 0 | 0
111 | 0.97164 | -0.54668 | 0.0027433 | 0.00068755
112 | 0.97152 | -0.54911 | 0.0068465 | 0.0017159
113 | 0.97139 | -0.55157 | 0 | 0
114 | 0.97138 | -0.55183 | 0.0020742 | 0.00051985
115 | 0.9711 | -0.55743 | 0.0031273 | 0.00078377
116 | 0.97118 | -0.55586 | 0.0040754 | 0.0010214
117 | 0.97088 | -0.56168 | 0.0065702 | 0.0016466
118 | 0.98434 | -0.29961 | 0.0019065 | 0.00047781
119 | 0.98425 | -0.3014 | 0.0019681 | 0.00049325
120 | 0.98417 | -0.30282 | 0 | 0
121 | 0.98402 | -0.30573 | 0.0025424 | 0.00063717
122 | 0.98394 | -0.30743 | 0.0024629 | 0.00061726
123 | 0.98387 | -0.30876 | 0.0024565 | 0.00061567
124 | 0.98377 | -0.31065 | 0.0020678 | 0.00051824
125 | 0.98379 | -0.31038 | 0.0023561 | 0.0005905
126 | 0.98382 | -0.30976 | 0.0025454 | 0.00063795
127 | 0.99828 | -0.033005 | 0.0027438 | 0.00068767
128 | 0.99774 | -0.043425 | 0 | 0
129 | 0.99705 | -0.05671 | 0.0096398 | 0.002416
130 | 0.99696 | -0.05853 | 0.005262 | 0.0013188
131 | 0.99761 | -0.045901 | 0 | 0
132 | 0.99688 | -0.060062 | 0.0051628 | 0.0012939
133 | 0.99754 | -0.047233 | 0.0032919 | 0.00082504
134 | 0.99771 | -0.043962 | 0.0027916 | 0.00069963
135 | 0.99736 | -0.050683 | 0.0028447 | 0.00071294
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.003683 | 0.00092287 | -0.0036829 | -0.0009229 | 6.75e-08 | -3.1164e-08 | 0.0055572 | 0.0055572 | 0.0055572 | 0.98617 | -0.26396 | 0.98615 | -0.26435 | 1.5267
1 | -0.0054536 | -0.0013666 | 0.005454 | 0.0013667 | 4.1405e-07 | 5.6927e-08 | 0.0082288 | 0.0082287 | 0.0082288 | 0.98617 | -0.26396 | 0.98625 | -0.26237 | 2.2607
2 | 0.0018338 | 0.00045946 | -0.0018338 | -0.00045958 | 3.2475e-08 | -1.2352e-07 | 0.002767 | 0.002767 | 0.002767 | 0.98615 | -0.26435 | 0.98613 | -0.26472 | 0.76018
3 | 0.022485 | 0.005651 | -0.022463 | -0.0056378 | 2.1617e-05 | 1.3197e-05 | 0.03393 | 0.03393 | 0.03393 | 0.98625 | -0.26237 | 0.98521 | -0.28253 | 9.3214
4 | -0.027939 | -0.0070177 | 0.027961 | 0.0070318 | 2.2693e-05 | 1.4089e-05 | 0.042159 | 0.042158 | 0.042159 | 0.98625 | -0.26237 | 0.98712 | -0.24536 | 11.582
5 | 0.022463 | 0.0056378 | -0.02245 | -0.0056296 | 1.3527e-05 | 8.2584e-06 | 0.03393 | 0.03393 | 0.03393 | 0.98521 | -0.28253 | 0.98457 | -0.29516 | 9.3215
6 | -0.027961 | -0.0070318 | 0.027977 | 0.0070413 | 1.5344e-05 | 9.5256e-06 | 0.042158 | 0.042158 | 0.042158 | 0.98712 | -0.24536 | 0.98771 | -0.23388 | 11.582
7 | 0.020417 | 0.0051201 | -0.020415 | -0.0051187 | 2.3141e-06 | 1.3986e-06 | 0.030858 | 0.030858 | 0.030858 | 0.98457 | -0.29516 | 0.98444 | -0.29754 | 8.4775
8 | 0.0027044 | 0.00067763 | -0.0027043 | -0.00067776 | 9.4895e-08 | -1.3438e-07 | 0.0040742 | 0.0040742 | 0.0040742 | 0.98771 | -0.23388 | 0.98768 | -0.23462 | 1.1193
9 | 0.14196 | 0.036013 | -0.14176 | -0.035887 | 0.00019752 | 0.00012582 | 0.21402 | 0.21402 | 0.21402 | 0.98771 | -0.23388 | 0.98621 | -0.26286 | 29.3979
10 | -0.17264 | -0.043732 | 0.17304 | 0.043991 | 0.00040631 | 0.00025922 | 0.26025 | 0.26025 | 0.26025 | 0.98771 | -0.23388 | 0.99025 | -0.185 | 35.7485
11 | 0.018314 | 0.0045923 | -0.018312 | -0.0045912 | 1.8067e-06 | 1.0764e-06 | 0.027683 | 0.027683 | 0.027683 | 0.98444 | -0.29754 | 0.98434 | -0.29961 | 7.6052
12 | -0.17304 | -0.043991 | 0.17323 | 0.044109 | 0.00018629 | 0.00011838 | 0.26025 | 0.26025 | 0.26025 | 0.99025 | -0.185 | 0.99142 | -0.16268 | 23.8323
13 | -0.17555 | -0.044691 | 0.17561 | 0.044726 | 5.5387e-05 | 3.5201e-05 | 0.26373 | 0.26373 | 0.26373 | 0.99142 | -0.16268 | 0.99176 | -0.15614 | 24.1511
14 | 0.0083791 | 0.0021002 | -0.0083778 | -0.0020997 | 1.2381e-06 | 5.2887e-07 | 0.012643 | 0.012643 | 0.012643 | 0.98621 | -0.26286 | 0.98605 | -0.26596 | 3.4733
15 | 0.13338 | 0.033787 | -0.13301 | -0.033553 | 0.0003655 | 0.00023361 | 0.20137 | 0.20137 | 0.20137 | 0.98621 | -0.26286 | 0.98326 | -0.32008 | 55.3227
16 | -0.018577 | -0.0046557 | 0.018588 | 0.0046625 | 1.1359e-05 | 6.7867e-06 | 0.028165 | 0.028165 | 0.028165 | 0.98144 | -0.35557 | 0.9821 | -0.34274 | 7.7376
17 | -0.10844 | -0.027344 | 0.10853 | 0.027404 | 9.3991e-05 | 6.0037e-05 | 0.16436 | 0.16436 | 0.16436 | 0.9821 | -0.34274 | 0.98303 | -0.32465 | 45.1544
18 | 0.089852 | 0.022681 | -0.089805 | -0.022651 | 4.7589e-05 | 3.037e-05 | 0.1362 | 0.1362 | 0.1362 | 0.9821 | -0.34274 | 0.98153 | -0.35381 | 37.4168
19 | -0.12799 | -0.032283 | 0.12802 | 0.032301 | 2.8018e-05 | 1.7906e-05 | 0.19381 | 0.19381 | 0.19381 | 0.98303 | -0.32465 | 0.98326 | -0.32008 | 53.2454
20 | 0.019456 | 0.0048793 | -0.019447 | -0.0048743 | 8.2507e-06 | 4.959e-06 | 0.029451 | 0.029452 | 0.029452 | 0.98303 | -0.32465 | 0.98257 | -0.33355 | 8.0911
21 | 0.0861 | 0.021723 | -0.085961 | -0.021634 | 0.00013911 | 8.8753e-05 | 0.13058 | 0.13058 | 0.13058 | 0.98153 | -0.35381 | 0.9798 | -0.38761 | 35.874
22 | 0.0049965 | 0.0012522 | -0.0049962 | -0.0012522 | 2.7624e-07 | 1.3386e-08 | 0.0075614 | 0.0075614 | 0.0075614 | 0.98326 | -0.32008 | 0.9832 | -0.32124 | 2.0773
23 | 0.0095476 | 0.0023932 | -0.0095461 | -0.0023925 | 1.4656e-06 | 7.0125e-07 | 0.014459 | 0.014459 | 0.014459 | 0.98257 | -0.33355 | 0.98241 | -0.33678 | 3.9723
24 | 0.064278 | 0.016197 | -0.064227 | -0.016164 | 5.1453e-05 | 3.2749e-05 | 0.09765 | 0.09765 | 0.09765 | 0.9798 | -0.38761 | 0.97894 | -0.40436 | 26.827
25 | 0.021683 | 0.0054369 | -0.021677 | -0.005433 | 6.3073e-06 | 3.8414e-06 | 0.032931 | 0.032931 | 0.032931 | 0.9798 | -0.38761 | 0.97949 | -0.39371 | 9.047
26 | 0.0024746 | 0.00061956 | -0.0024743 | -0.00062005 | 2.8496e-07 | -4.9282e-07 | 0.0037613 | 0.0037615 | 0.0037615 | 0.97894 | -0.40436 | 0.97882 | -0.40677 | 1.0334
27 | 0.053728 | 0.013533 | -0.053628 | -0.01347 | 0.00010022 | 6.3637e-05 | 0.081692 | 0.081693 | 0.081693 | 0.97894 | -0.40436 | 0.97695 | -0.44344 | 22.443
28 | 0.0080238 | 0.0020113 | -0.008021 | -0.0020101 | 2.8437e-06 | 1.1793e-06 | 0.012197 | 0.012197 | 0.012197 | 0.97894 | -0.40436 | 0.97856 | -0.4118 | 3.3508
29 | 0.015357 | 0.0038491 | -0.015356 | -0.0038487 | 6.9515e-07 | 4.0203e-07 | 0.02333 | 0.02333 | 0.02333 | 0.97949 | -0.39371 | 0.97944 | -0.39466 | 6.4093
30 | -0.17791 | -0.045304 | 0.17795 | 0.045328 | 3.7264e-05 | 2.3687e-05 | 0.26719 | 0.26719 | 0.26719 | 0.99176 | -0.15614 | 0.99199 | -0.1518 | 24.4679
31 | -0.0022113 | -0.0005542 | 0.0022114 | 0.00055394 | 1.099e-07 | -2.5059e-07 | 0.0033748 | 0.0033747 | 0.0033748 | 0.97499 | -0.48206 | 0.97504 | -0.48101 | 0.92715
32 | -0.027722 | -0.0069515 | 0.027741 | 0.0069629 | 1.8422e-05 | 1.1448e-05 | 0.042309 | 0.042308 | 0.042309 | 0.97504 | -0.48101 | 0.97575 | -0.46708 | 11.6232
33 | 0.025511 | 0.0063976 | -0.025508 | -0.0063957 | 2.9434e-06 | 1.8192e-06 | 0.038934 | 0.038934 | 0.038934 | 0.97504 | -0.48101 | 0.97492 | -0.48344 | 10.6961
34 | -0.037112 | -0.0093113 | 0.037115 | 0.0093137 | 3.8118e-06 | 2.3999e-06 | 0.056599 | 0.056599 | 0.056599 | 0.97575 | -0.46708 | 0.97586 | -0.46493 | 15.5492
35 | 0.009371 | 0.0023484 | -0.009369 | -0.0023474 | 1.9493e-06 | 9.2968e-07 | 0.014291 | 0.014291 | 0.014291 | 0.97575 | -0.46708 | 0.97553 | -0.47145 | 3.926
36 | 0.019624 | 0.0049211 | -0.01962 | -0.0049186 | 4.1326e-06 | 2.4918e-06 | 0.029953 | 0.029953 | 0.029953 | 0.97492 | -0.48344 | 0.97469 | -0.48786 | 8.229
37 | 0.0058838 | 0.0014746 | -0.0058834 | -0.0014745 | 3.5608e-07 | 8.1088e-08 | 0.0089804 | 0.0089805 | 0.0089805 | 0.97492 | -0.48344 | 0.97485 | -0.48471 | 2.4672
38 | -0.044724 | -0.011221 | 0.04477 | 0.01125 | 4.5869e-05 | 2.9027e-05 | 0.068201 | 0.068201 | 0.068201 | 0.97586 | -0.46493 | 0.97695 | -0.44344 | 18.7365
39 | 0.0074537 | 0.0018674 | -0.0074533 | -0.0018672 | 4.6131e-07 | 1.7643e-07 | 0.011369 | 0.011369 | 0.011369 | 0.97553 | -0.47145 | 0.97546 | -0.47275 | 3.1235
40 | 0.018366 | 0.0046047 | -0.018362 | -0.004602 | 4.488e-06 | 2.6827e-06 | 0.02804 | 0.02804 | 0.02804 | 0.97469 | -0.48786 | 0.97443 | -0.49298 | 7.7033
41 | 0.0012535 | 0.00031391 | -0.0012535 | -0.00031416 | 2.8738e-08 | -2.4242e-07 | 0.0019136 | 0.0019137 | 0.0019137 | 0.97469 | -0.48786 | 0.97467 | -0.48834 | 0.52574
42 | 0.0054822 | 0.0013732 | -0.0054819 | -0.0013732 | 2.6109e-07 | 4.2822e-08 | 0.0083625 | 0.0083626 | 0.0083626 | 0.97546 | -0.47275 | 0.97541 | -0.47375 | 2.2974
43 | 0.0077178 | 0.001934 | -0.0077169 | -0.0019336 | 8.8677e-07 | 3.5548e-07 | 0.011785 | 0.011786 | 0.011786 | 0.97443 | -0.49298 | 0.97431 | -0.4954 | 3.2378
44 | 0.010644 | 0.0026681 | -0.010643 | -0.0026672 | 1.6343e-06 | 8.4053e-07 | 0.016254 | 0.016255 | 0.016255 | 0.97443 | -0.49298 | 0.97427 | -0.49621 | 4.4655
45 | 0.0015389 | 0.00038552 | -0.0015389 | -0.00038567 | 2.9086e-08 | -1.5626e-07 | 0.0023502 | 0.0023503 | 0.0023503 | 0.97431 | -0.4954 | 0.97429 | -0.49579 | 0.64568
46 | 0.006178 | 0.0015481 | -0.0061764 | -0.0015477 | 1.5805e-06 | 4.2209e-07 | 0.0094353 | 0.0094355 | 0.0094355 | 0.97431 | -0.4954 | 0.97404 | -0.50077 | 2.5922
47 | 0.0051571 | 0.0012925 | -0.0051569 | -0.0012924 | 2.3648e-07 | 2.4776e-08 | 0.0078766 | 0.0078766 | 0.0078766 | 0.97427 | -0.49621 | 0.97422 | -0.49717 | 2.1639
48 | 0.0061764 | 0.0015477 | -0.0061762 | -0.0015476 | 2.7016e-07 | 7.2186e-08 | 0.0094355 | 0.0094355 | 0.0094355 | 0.97404 | -0.50077 | 0.97399 | -0.50169 | 2.5922
49 | -0.0028611 | -0.00071706 | 0.0028612 | 0.00071699 | 6.1152e-08 | -6.9089e-08 | 0.0043507 | 0.0043507 | 0.0043507 | 0.97854 | -0.41225 | 0.97856 | -0.4118 | 1.1953
50 | 0.0051598 | 0.0012931 | -0.0051597 | -0.0012931 | 1.3089e-07 | 1.2542e-08 | 0.007846 | 0.0078461 | 0.0078461 | 0.97856 | -0.4118 | 0.97854 | -0.41233 | 2.1555
51 | 0.0024743 | 0.00062005 | -0.0024743 | -0.00062012 | 3.9789e-08 | -6.8792e-08 | 0.0037615 | 0.0037615 | 0.0037615 | 0.97882 | -0.40677 | 0.9788 | -0.40711 | 1.0334
52 | 0.0033923 | 0.00084949 | -0.0033915 | -0.00084998 | 8.2244e-07 | -4.9557e-07 | 0.0051748 | 0.0051752 | 0.0051752 | 0.97541 | -0.47375 | 0.97515 | -0.47884 | 1.4218
53 | 0.0044302 | 0.00111 | -0.0044299 | -0.00111 | 3.1052e-07 | -2.6225e-08 | 0.0067681 | 0.0067682 | 0.0067682 | 0.97399 | -0.50169 | 0.97392 | -0.50316 | 1.8594
54 | 0.0020455 | 0.00051244 | -0.0020454 | -0.00051263 | 6.7337e-08 | -1.8568e-07 | 0.0031251 | 0.0031252 | 0.0031252 | 0.97392 | -0.50316 | 0.97388 | -0.50385 | 0.85858
55 | 0.0088495 | 0.0022179 | -0.0088493 | -0.0022178 | 2.325e-07 | 1.0563e-07 | 0.013445 | 0.013445 | 0.013445 | 0.97944 | -0.39466 | 0.97941 | -0.39522 | 3.6936
56 | -0.0022256 | -0.00055779 | 0.0022257 | 0.00055757 | 9.2206e-08 | -2.2234e-07 | 0.0033487 | 0.0033486 | 0.0033487 | 0.98895 | -0.20974 | 0.98899 | -0.20887 | 0.91999
57 | -0.10336 | -0.026417 | 0.10347 | 0.026486 | 0.00010762 | 6.8728e-05 | 0.1557 | 0.1557 | 0.1557 | 0.98899 | -0.20887 | 0.99012 | -0.18736 | 42.7738
58 | 0.10113 | 0.025859 | -0.10086 | -0.025687 | 0.00027029 | 0.00017259 | 0.15235 | 0.15235 | 0.15235 | 0.98899 | -0.20887 | 0.98611 | -0.26427 | 41.8539
59 | -0.10528 | -0.026939 | 0.10538 | 0.027002 | 9.8961e-05 | 6.2793e-05 | 0.15842 | 0.15842 | 0.15842 | 0.99012 | -0.18736 | 0.99113 | -0.16797 | 21.7607
60 | 0.099228 | 0.025277 | -0.099024 | -0.025146 | 0.00020408 | 0.0001303 | 0.14988 | 0.14988 | 0.14988 | 0.98611 | -0.26427 | 0.98389 | -0.30699 | 41.1756
61 | -0.10538 | -0.027002 | 0.10546 | 0.027057 | 8.6629e-05 | 5.4968e-05 | 0.15842 | 0.15842 | 0.15842 | 0.99113 | -0.16797 | 0.99202 | -0.15102 | 21.7607
62 | 0.097763 | 0.02483 | -0.097623 | -0.024741 | 0.0001404 | 8.9642e-05 | 0.14797 | 0.14797 | 0.14797 | 0.98389 | -0.30699 | 0.98235 | -0.33688 | 40.6519
63 | -0.10647 | -0.027308 | 0.10648 | 0.027319 | 1.6772e-05 | 1.0531e-05 | 0.15992 | 0.15992 | 0.15992 | 0.99202 | -0.15102 | 0.99219 | -0.14777 | 14.6448
64 | 0.097623 | 0.024741 | -0.097572 | -0.024708 | 5.0498e-05 | 3.2241e-05 | 0.14797 | 0.14797 | 0.14797 | 0.98235 | -0.33688 | 0.98179 | -0.34765 | 40.6519
65 | -0.29015 | -0.0743 | 0.29071 | 0.074658 | 0.00056095 | 0.00035808 | 0.43483 | 0.43483 | 0.43483 | 0.99421 | -0.10946 | 0.99631 | -0.069637 | 39.8194
66 | 0.28824 | 0.073821 | -0.2878 | -0.07354 | 0.00044008 | 0.00028092 | 0.43197 | 0.43197 | 0.43197 | 0.99421 | -0.10946 | 0.99255 | -0.14103 | 39.5577
67 | -0.29213 | -0.075014 | 0.29312 | 0.075647 | 0.00099126 | 0.00063278 | 0.43695 | 0.43695 | 0.43695 | 0.99631 | -0.069637 | 1 | 0 | 40.0139
68 | 0.18026 | 0.045944 | -0.18017 | -0.045884 | 9.3599e-05 | 5.9507e-05 | 0.27052 | 0.27052 | 0.27052 | 0.99255 | -0.14103 | 0.99199 | -0.1518 | 24.7731
69 | 0.10754 | 0.027596 | -0.1075 | -0.027574 | 3.5168e-05 | 2.2089e-05 | 0.16145 | 0.16145 | 0.16145 | 0.99255 | -0.14103 | 0.99219 | -0.14777 | 14.7847
70 | 0.058239 | 0.014646 | -0.058217 | -0.014632 | 2.1606e-05 | 1.3727e-05 | 0.086678 | 0.086678 | 0.086678 | 1 | 0 | 0.99959 | -0.0077703 | 23.8127
71 | 0.055761 | 0.014016 | -0.055753 | -0.014011 | 8.1041e-06 | 5.1455e-06 | 0.083021 | 0.083021 | 0.083021 | 0.99959 | -0.0077703 | 0.99944 | -0.010815 | 22.8079
72 | 0.055753 | 0.014011 | -0.055721 | -0.013991 | 3.1957e-05 | 2.0291e-05 | 0.083021 | 0.083021 | 0.083021 | 0.99944 | -0.010815 | 0.99881 | -0.022829 | 22.808
73 | 0.052788 | 0.013256 | -0.052781 | -0.013252 | 6.6825e-06 | 4.2391e-06 | 0.078652 | 0.078652 | 0.078652 | 0.99881 | -0.022829 | 0.99867 | -0.025483 | 21.6077
74 | 0.049991 | 0.012552 | -0.049978 | -0.012544 | 1.2573e-05 | 7.9678e-06 | 0.074494 | 0.074494 | 0.074494 | 0.99867 | -0.025483 | 0.9984 | -0.030756 | 20.4655
75 | 0.047152 | 0.011836 | -0.047147 | -0.011833 | 5.0566e-06 | 3.2005e-06 | 0.070282 | 0.070282 | 0.070282 | 0.9984 | -0.030756 | 0.99828 | -0.033005 | 19.3083
76 | 0.026494 | 0.006647 | -0.026487 | -0.0066428 | 6.9021e-06 | 4.2757e-06 | 0.040345 | 0.040345 | 0.040345 | 0.9772 | -0.43737 | 0.97692 | -0.44284 | 11.0839
77 | -0.034531 | -0.0086613 | 0.034536 | 0.0086645 | 5.1657e-06 | 3.2436e-06 | 0.052584 | 0.052584 | 0.052584 | 0.9772 | -0.43737 | 0.97736 | -0.43423 | 14.4461
78 | 0.022937 | 0.0057531 | -0.02293 | -0.005749 | 6.6191e-06 | 4.0552e-06 | 0.034938 | 0.034938 | 0.034938 | 0.97692 | -0.44284 | 0.97661 | -0.44889 | 9.5985
79 | -0.091624 | -0.023069 | 0.091857 | 0.023217 | 0.00023282 | 0.0001486 | 0.13953 | 0.13953 | 0.13953 | 0.97736 | -0.43423 | 0.98007 | -0.38123 | 38.3337
80 | 0.057088 | 0.014404 | -0.057011 | -0.014355 | 7.7662e-05 | 4.9361e-05 | 0.086951 | 0.086951 | 0.086951 | 0.97736 | -0.43423 | 0.9759 | -0.46268 | 23.8877
81 | 0.018919 | 0.0047439 | -0.018914 | -0.0047409 | 5.0572e-06 | 3.0336e-06 | 0.028827 | 0.028827 | 0.028827 | 0.97661 | -0.44889 | 0.97632 | -0.4545 | 7.9195
82 | 0.0040111 | 0.0010051 | -0.0040108 | -0.0010052 | 2.5585e-07 | -6.4809e-08 | 0.0061114 | 0.0061115 | 0.0061115 | 0.97661 | -0.44889 | 0.97654 | -0.45023 | 1.679
83 | 0.0019398 | 0.00048603 | -0.0019397 | -0.00048614 | 3.5408e-08 | -1.1452e-07 | 0.0029451 | 0.0029451 | 0.0029451 | 0.98007 | -0.38123 | 0.98005 | -0.38161 | 0.8091
84 | -0.093797 | -0.023703 | 0.093891 | 0.023763 | 9.4258e-05 | 6.0169e-05 | 0.14248 | 0.14248 | 0.14248 | 0.98007 | -0.38123 | 0.98114 | -0.36029 | 39.1428
85 | 0.051483 | 0.012969 | -0.051438 | -0.012941 | 4.4504e-05 | 2.8242e-05 | 0.078523 | 0.078523 | 0.078523 | 0.9759 | -0.46268 | 0.97498 | -0.48078 | 21.5722
86 | 0.013201 | 0.003309 | -0.013199 | -0.0033078 | 2.0863e-06 | 1.1634e-06 | 0.020119 | 0.020119 | 0.020119 | 0.97632 | -0.4545 | 0.97616 | -0.45782 | 5.5273
87 | -0.096127 | -0.024324 | 0.096185 | 0.024361 | 5.8331e-05 | 3.724e-05 | 0.14587 | 0.14587 | 0.14587 | 0.98114 | -0.36029 | 0.98179 | -0.34765 | 40.0744
88 | 0.04684 | 0.011788 | -0.046812 | -0.011771 | 2.8084e-05 | 1.7791e-05 | 0.071504 | 0.071505 | 0.071505 | 0.97498 | -0.48078 | 0.97434 | -0.49333 | 19.6441
89 | 0.0095752 | 0.0023997 | -0.0095741 | -0.0023991 | 1.1258e-06 | 5.4437e-07 | 0.014596 | 0.014596 | 0.014596 | 0.97616 | -0.45782 | 0.97603 | -0.46029 | 4.0099
90 | 0.0013869 | 0.00034744 | -0.0013869 | -0.00034759 | 2.1146e-08 | -1.4785e-07 | 0.002102 | 0.0021021 | 0.0021021 | 0.98179 | -0.34765 | 0.98178 | -0.34797 | 0.57749
91 | 0.044549 | 0.011204 | -0.044485 | -0.011163 | 6.4725e-05 | 4.0961e-05 | 0.068049 | 0.06805 | 0.06805 | 0.97434 | -0.49333 | 0.9728 | -0.52379 | 18.6949
92 | 0.0032298 | 0.0008091 | -0.0032297 | -0.00080916 | 8.6473e-08 | -6.3525e-08 | 0.0049238 | 0.0049239 | 0.0049239 | 0.97603 | -0.46029 | 0.976 | -0.46085 | 1.3527
93 | 0.0014261 | 0.00035714 | -0.001426 | -0.0003574 | 4.0589e-08 | -2.6017e-07 | 0.0021741 | 0.0021742 | 0.0021742 | 0.976 | -0.46085 | 0.97597 | -0.46145 | 0.59731
94 | -0.0029613 | -0.00074218 | 0.0029615 | 0.00074201 | 1.4826e-07 | -1.6888e-07 | 0.0044206 | 0.0044205 | 0.0044206 | 0.99682 | -0.061134 | 0.99688 | -0.060082 | 1.2144
95 | -0.006624 | -0.0016599 | 0.0066245 | 0.0016601 | 5.3217e-07 | 1.5131e-07 | 0.0098874 | 0.0098873 | 0.0098874 | 0.99688 | -0.060082 | 0.99696 | -0.058396 | 2.7163
96 | -0.0085578 | -0.0021446 | 0.0085582 | 0.0021448 | 4.0614e-07 | 1.7336e-07 | 0.012773 | 0.012773 | 0.012773 | 0.99696 | -0.058396 | 0.99702 | -0.0574 | 3.509
97 | 0.0044814 | 0.001123 | -0.004481 | -0.001123 | 4.188e-07 | -5.7509e-08 | 0.0066883 | 0.0066884 | 0.0066884 | 0.99702 | -0.0574 | 0.99691 | -0.059362 | 1.8375
98 | -0.01304 | -0.0032678 | 0.01304 | 0.0032681 | 5.6075e-07 | 3.0739e-07 | 0.019461 | 0.019461 | 0.019461 | 0.99702 | -0.0574 | 0.99706 | -0.056497 | 5.3465
99 | -0.015363 | -0.0038502 | 0.015367 | 0.0038527 | 4.256e-06 | 2.4422e-06 | 0.022928 | 0.022928 | 0.022928 | 0.99706 | -0.056497 | 0.99736 | -0.050683 | 6.2989
100 | 0.027932 | 0.0070107 | -0.027922 | -0.007005 | 9.1157e-06 | 5.6688e-06 | 0.042728 | 0.042729 | 0.042729 | 0.9728 | -0.52379 | 0.97245 | -0.53064 | 11.7386
101 | 0.016553 | 0.004152 | -0.016545 | -0.0041475 | 7.6068e-06 | 4.4758e-06 | 0.025321 | 0.025321 | 0.025321 | 0.9728 | -0.52379 | 0.97231 | -0.53344 | 6.9564
102 | 0.025466 | 0.0063894 | -0.02546 | -0.0063859 | 5.5184e-06 | 3.4116e-06 | 0.03897 | 0.03897 | 0.03897 | 0.97245 | -0.53064 | 0.97222 | -0.53519 | 10.7059
103 | 0.014595 | 0.0036586 | -0.014593 | -0.003658 | 1.0834e-06 | 6.2154e-07 | 0.022336 | 0.022336 | 0.022336 | 0.97231 | -0.53344 | 0.97223 | -0.535 | 6.1362
104 | -0.0022933 | -0.00057476 | 0.0022933 | 0.0005747 | 3.0062e-08 | -6.1316e-08 | 0.0035115 | 0.0035114 | 0.0035115 | 0.97181 | -0.54329 | 0.97183 | -0.54302 | 0.96469
105 | -0.0038737 | -0.00097078 | 0.003874 | 0.00097071 | 2.4636e-07 | -7.373e-08 | 0.0059313 | 0.0059312 | 0.0059313 | 0.97183 | -0.54302 | 0.97189 | -0.54168 | 1.6295
106 | -0.0064947 | -0.0016275 | 0.0064949 | 0.0016276 | 1.9091e-07 | 5.8375e-08 | 0.0099436 | 0.0099436 | 0.0099436 | 0.97189 | -0.54168 | 0.97192 | -0.54107 | 2.7318
107 | -0.0081451 | -0.0020412 | 0.0081464 | 0.0020417 | 1.236e-06 | 5.283e-07 | 0.01247 | 0.01247 | 0.01247 | 0.97192 | -0.54107 | 0.97209 | -0.53788 | 3.4259
108 | -0.010278 | -0.002576 | 0.010278 | 0.002576 | 7.5212e-08 | 3.8091e-08 | 0.015733 | 0.015733 | 0.015733 | 0.97209 | -0.53788 | 0.97209 | -0.53773 | 4.3223
109 | -0.012569 | -0.00315 | 0.01257 | 0.0031509 | 1.6358e-06 | 9.0077e-07 | 0.019239 | 0.019239 | 0.019239 | 0.97209 | -0.53773 | 0.97223 | -0.535 | 5.2855
110 | 0.015864 | 0.0039797 | -0.015855 | -0.0039744 | 9.0155e-06 | 5.2646e-06 | 0.024282 | 0.024282 | 0.024282 | 0.97222 | -0.53519 | 0.97162 | -0.54711 | 6.671
111 | 0.0095959 | 0.0024063 | -0.0095945 | -0.0024056 | 1.3804e-06 | 6.7189e-07 | 0.014687 | 0.014687 | 0.014687 | 0.97222 | -0.53519 | 0.97207 | -0.5382 | 4.035
112 | 0.0065748 | 0.0016481 | -0.0065734 | -0.0016476 | 1.3962e-06 | 4.3886e-07 | 0.010069 | 0.010069 | 0.010069 | 0.97162 | -0.54711 | 0.97139 | -0.55157 | 2.7663
113 | 0.0092806 | 0.0023263 | -0.0092785 | -0.0023253 | 2.0872e-06 | 9.9467e-07 | 0.014213 | 0.014213 | 0.014213 | 0.97162 | -0.54711 | 0.97138 | -0.55183 | 3.9047
114 | 0.0095945 | 0.0024056 | -0.0095907 | -0.0024037 | 3.8738e-06 | 1.8859e-06 | 0.014687 | 0.014688 | 0.014688 | 0.97207 | -0.5382 | 0.97164 | -0.54668 | 4.0351
115 | 0.0068473 | 0.0017162 | -0.0068465 | -0.0017159 | 7.9423e-07 | 2.6979e-07 | 0.010486 | 0.010486 | 0.010486 | 0.97164 | -0.54668 | 0.97152 | -0.54911 | 2.8809
116 | 0.0065734 | 0.0016476 | -0.0065702 | -0.0016466 | 3.1658e-06 | 9.9596e-07 | 0.010069 | 0.01007 | 0.01007 | 0.97139 | -0.55157 | 0.97088 | -0.56168 | 2.7664
117 | 0.0072043 | 0.0018055 | -0.0072029 | -0.001805 | 1.3802e-06 | 5.0932e-07 | 0.011036 | 0.011036 | 0.011036 | 0.97138 | -0.55183 | 0.97118 | -0.55586 | 3.0319
118 | -0.0031273 | -0.00078377 | 0.0031275 | 0.00078358 | 2.3495e-07 | -1.8723e-07 | 0.0047919 | 0.0047918 | 0.0047919 | 0.9711 | -0.55743 | 0.97118 | -0.55586 | 1.3165
119 | 0.016406 | 0.0041134 | -0.016404 | -0.0041126 | 1.4022e-06 | 8.2014e-07 | 0.024801 | 0.024801 | 0.024801 | 0.98434 | -0.29961 | 0.98425 | -0.3014 | 6.8135
120 | 0.014436 | 0.0036193 | -0.014435 | -0.0036187 | 9.7187e-07 | 5.5286e-07 | 0.021826 | 0.021826 | 0.021826 | 0.98425 | -0.3014 | 0.98417 | -0.30282 | 5.996
121 | 0.014435 | 0.0036187 | -0.014433 | -0.0036176 | 2.0041e-06 | 1.1401e-06 | 0.021826 | 0.021826 | 0.021826 | 0.98417 | -0.30282 | 0.98402 | -0.30573 | 5.9961
122 | 0.011891 | 0.0029804 | -0.01189 | -0.0029799 | 9.6546e-07 | 5.1675e-07 | 0.017981 | 0.017981 | 0.017981 | 0.98402 | -0.30573 | 0.98394 | -0.30743 | 4.9399
123 | 0.009427 | 0.0023627 | -0.0094264 | -0.0023624 | 5.9679e-07 | 2.825e-07 | 0.014257 | 0.014257 | 0.014257 | 0.98394 | -0.30743 | 0.98387 | -0.30876 | 3.9166
124 | 0.0069698 | 0.0017467 | -0.0069695 | -0.0017466 | 3.3181e-07 | 1.1124e-07 | 0.010541 | 0.010541 | 0.010541 | 0.98387 | -0.30876 | 0.98382 | -0.30976 | 2.896
125 | -0.0020678 | -0.00051824 | 0.0020678 | 0.00051817 | 2.5841e-08 | -7.2906e-08 | 0.0031277 | 0.0031276 | 0.0031277 | 0.98377 | -0.31065 | 0.98379 | -0.31038 | 0.85925
126 | -0.0044239 | -0.0011087 | 0.0044241 | 0.0011086 | 1.3102e-07 | -1.5232e-08 | 0.0066914 | 0.0066913 | 0.0066914 | 0.98379 | -0.31038 | 0.98382 | -0.30976 | 1.8383
127 | 0.044403 | 0.011145 | -0.044381 | -0.011131 | 2.2055e-05 | 1.394e-05 | 0.066192 | 0.066192 | 0.066192 | 0.99828 | -0.033005 | 0.99774 | -0.043425 | 18.1847
128 | 0.0027916 | 0.00069953 | -0.0027916 | -0.00069963 | 7.1537e-08 | -9.7943e-08 | 0.0041634 | 0.0041634 | 0.0041634 | 0.99774 | -0.043425 | 0.99771 | -0.043962 | 1.1438
129 | 0.041589 | 0.010432 | -0.041585 | -0.010429 | 4.91e-06 | 3.098e-06 | 0.062029 | 0.062029 | 0.062029 | 0.99774 | -0.043425 | 0.99761 | -0.045901 | 17.0409
130 | 0.010426 | 0.0026132 | -0.010425 | -0.0026127 | 9.036e-07 | 4.4852e-07 | 0.01556 | 0.01556 | 0.01556 | 0.99705 | -0.05671 | 0.99696 | -0.05853 | 4.2748
131 | -0.020066 | -0.0050291 | 0.020076 | 0.0050354 | 1.0338e-05 | 6.2152e-06 | 0.029947 | 0.029947 | 0.029947 | 0.99705 | -0.05671 | 0.99761 | -0.045901 | 8.2271
132 | 0.0051632 | 0.0012939 | -0.0051628 | -0.0012939 | 3.7683e-07 | 2.0555e-08 | 0.0077064 | 0.0077064 | 0.0077064 | 0.99696 | -0.05853 | 0.99688 | -0.060062 | 2.1172
133 | 0.021508 | 0.0053933 | -0.021507 | -0.0053924 | 1.3649e-06 | 8.2738e-07 | 0.032082 | 0.032082 | 0.032082 | 0.99761 | -0.045901 | 0.99754 | -0.047233 | 8.8138
134 | 0.018215 | 0.0045674 | -0.018212 | -0.0045656 | 2.9945e-06 | 1.7753e-06 | 0.027172 | 0.027172 | 0.027172 | 0.99754 | -0.047233 | 0.99736 | -0.050683 | 7.4648

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35587 | 0.091009

## res_load
| p_mw | q_mvar
0 | 0.0017706 | 0.00044375
1 | 0.0018491 | 0.00046344
2 | 0.0018338 | 0.00045958
3 | 0.0020327 | 0.00050946
4 | 0.0021006 | 0.00052646
5 | 0.0023198 | 0.00058139
6 | 0.0027043 | 0.00067776
7 | 0.0083778 | 0.0020997
8 | 0.018577 | 0.0046557
9 | 0.0037044 | 0.00092842
10 | 0.0098999 | 0.0024811
11 | 0.0049962 | 0.0012522
12 | 0.0095461 | 0.0023925
13 | 0.0063201 | 0.001584
14 | 0.0023056 | 0.00057784
15 | 0.0022113 | 0.0005542
16 | 0.0076085 | 0.0019069
17 | 0.0019153 | 0.00048001
18 | 0.0058834 | 0.0014745
19 | 0.0088581 | 0.0022201
20 | 0.0019711 | 0.00049401
21 | 0.0012535 | 0.00031416
22 | 0.0054854 | 0.0013748
23 | 0.0015389 | 0.00038567
24 | 0.0051569 | 0.0012924
25 | 0.0028611 | 0.00071706
26 | 0.0051597 | 0.0012931
27 | 0.0024743 | 0.00062012
28 | 0.0020896 | 0.0005237
29 | 0.0033915 | 0.00084998
30 | 0.001746 | 0.00043758
31 | 0.0023844 | 0.00059759
32 | 0.0020454 | 0.00051263
33 | 0.0065067 | 0.0016307
34 | 0.0088493 | 0.0022178
35 | 0.0022256 | 0.00055779
36 | 0.0018109 | 0.00045385
37 | 0.0016365 | 0.00041014
38 | 0.0012605 | 0.00031591
39 | 0.0010022 | 0.00025117
40 | 0.0019096 | 0.00047858
41 | 0.0014223 | 0.00035645
42 | 0.0028566 | 0.00071594
43 | 0.0022216 | 0.00055677
44 | 0.0010186 | 0.00025528
45 | 0.0024568 | 0.00061574
46 | 0.0029326 | 0.00073498
47 | 0.0027903 | 0.00069932
48 | 0.0028263 | 0.00070834
49 | 0.008037 | 0.0020143
50 | 0.0035499 | 0.00088968
51 | 0.0055277 | 0.0013854
52 | 0.0057133 | 0.0014319
53 | 0.0040108 | 0.0010052
54 | 0.0019397 | 0.00048614
55 | 0.0022361 | 0.00056041
56 | 0.0045986 | 0.0011525
57 | 0.0036234 | 0.00090811
58 | 0.0022624 | 0.00056701
59 | 0.0013869 | 0.00034759
60 | 0.0063444 | 0.00159
61 | 0.0018036 | 0.00045202
62 | 0.001426 | 0.0003574
63 | 0.0029613 | 0.00074218
64 | 0.0036625 | 0.0009179
65 | 0.0019333 | 0.00048453
66 | 0.004481 | 0.001123
67 | 0.0023229 | 0.00058218
68 | 0.0024566 | 0.00061569
69 | 0.0019508 | 0.00048891
70 | 0.0022933 | 0.00057476
71 | 0.0015804 | 0.00039609
72 | 0.0026207 | 0.0006568
73 | 0.0016503 | 0.00041359
74 | 0.0021319 | 0.00053429
75 | 0.0022904 | 0.00057402
76 | 0.0020232 | 0.00050707
77 | 0.0027433 | 0.00068755
78 | 0.0068465 | 0.0017159
79 | 0.0020742 | 0.00051985
80 | 0.0031273 | 0.00078377
81 | 0.0040754 | 0.0010214
82 | 0.0065702 | 0.0016466
83 | 0.0019065 | 0.00047781
84 | 0.0019681 | 0.00049325
85 | 0.0025424 | 0.00063717
86 | 0.0024629 | 0.00061726
87 | 0.0024565 | 0.00061567
88 | 0.0020678 | 0.00051824
89 | 0.0023561 | 0.0005905
90 | 0.0025454 | 0.00063795
91 | 0.0027438 | 0.00068767
92 | 0.0096398 | 0.002416
93 | 0.005262 | 0.0013188
94 | 0.0051628 | 0.0012939
95 | 0.0032919 | 0.00082504
96 | 0.0027916 | 0.00069963
97 | 0.0028447 | 0.00071294

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1