## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_156-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_156-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_156-7_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_156-7_0_5_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_156-7_0_5_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_156-7_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_156-7_0_5_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_156-7_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_156-7_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_156-7_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_156-7_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_156-7_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_156-7_0_5_node_120 | 0.4 | n |  | TRUE
13 | bus_LV_156-7_0_5_node_121 | 0.4 | n |  | TRUE
14 | bus_LV_156-7_0_5_node_74 | 0.4 | n |  | TRUE
15 | bus_LV_156-7_0_5_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_156-7_0_5_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_156-7_0_5_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_156-7_0_5_node_122 | 0.4 | n |  | TRUE
19 | bus_LV_156-7_0_5_node_75 | 0.4 | n |  | TRUE
20 | bus_LV_156-7_0_5_node_133 | 0.4 | n |  | TRUE
21 | bus_LV_156-7_0_5_node_83 | 0.4 | n |  | TRUE
22 | bus_LV_156-7_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_156-7_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_156-7_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_156-7_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_156-7_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_156-7_0_5_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_156-7_0_5_node_132 | 0.4 | n |  | TRUE
29 | bus_LV_156-7_0_5_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_156-7_0_5_node_131 | 0.4 | n |  | TRUE
31 | bus_LV_156-7_0_5_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_156-7_0_5_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_156-7_0_5_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_156-7_0_5_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_156-7_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_156-7_0_5_node_84 | 0.4 | n |  | TRUE
37 | bus_LV_156-7_0_5_node_91 | 0.4 | n |  | TRUE
38 | bus_LV_156-7_0_5_node_86 | 0.4 | n |  | TRUE
39 | bus_LV_156-7_0_5_node_85 | 0.4 | n |  | TRUE
40 | bus_LV_156-7_0_5_node_107 | 0.4 | n |  | TRUE
41 | bus_LV_156-7_0_5_node_87 | 0.4 | n |  | TRUE
42 | bus_LV_156-7_0_5_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_156-7_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_156-7_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_156-7_0_5_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_156-7_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_156-7_0_5_node_92 | 0.4 | n |  | TRUE
48 | bus_LV_156-7_0_5_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_156-7_0_5_node_93 | 0.4 | n |  | TRUE
50 | bus_LV_156-7_0_5_node_94 | 0.4 | n |  | TRUE
51 | bus_LV_156-7_0_5_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_156-7_0_5_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_156-7_0_5_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_156-7_0_5_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_156-7_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_156-7_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_156-7_0_5_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_156-7_0_5_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_156-7_0_5_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_156-7_0_5_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_156-7_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_156-7_0_5_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_156-7_0_5_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_156-7_0_5_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_156-7_0_5_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_156-7_0_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_156-7_0_5_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_156-7_0_5_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_156-7_0_5_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_156-7_0_5_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_156-7_0_5_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_156-7_0_5_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_156-7_0_5_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_156-7_0_5_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_156-7_0_5_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_156-7_0_5_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_156-7_0_5_node_123 | 0.4 | n |  | TRUE
78 | bus_LV_156-7_0_5_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_156-7_0_5_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_156-7_0_5_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_156-7_0_5_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_156-7_0_5_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_156-7_0_5_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_156-7_0_5_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_156-7_0_5_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_156-7_0_5_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_156-7_0_5_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_156-7_0_5_node_110 | 0.4 | n |  | TRUE
89 | bus_LV_156-7_0_5_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_156-7_0_5_node_124 | 0.4 | n |  | TRUE
91 | bus_LV_156-7_0_5_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_156-7_0_5_node_105 | 0.4 | n |  | TRUE
93 | bus_LV_156-7_0_5_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_156-7_0_5_node_127 | 0.4 | n |  | TRUE
95 | bus_LV_156-7_0_5_node_128 | 0.4 | n |  | TRUE
96 | bus_LV_156-7_0_5_node_98 | 0.4 | n |  | TRUE
97 | bus_LV_156-7_0_5_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_156-7_0_5_node_70 | 0.4 | n |  | TRUE
99 | bus_LV_156-7_0_5_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_156-7_0_5_node_73 | 0.4 | n |  | TRUE
101 | bus_LV_156-7_0_5_node_119 | 0.4 | n |  | TRUE
102 | bus_LV_156-7_0_5_node_118 | 0.4 | n |  | TRUE
103 | bus_LV_156-7_0_5_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_156-7_0_5_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_156-7_0_5_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_156-7_0_5_node_129 | 0.4 | n |  | TRUE
107 | bus_LV_156-7_0_5_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_156-7_0_5_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_156-7_0_5_node_76 | 0.4 | n |  | TRUE
110 | bus_LV_156-7_0_5_node_77 | 0.4 | n |  | TRUE
111 | bus_LV_156-7_0_5_node_78 | 0.4 | n |  | TRUE
112 | bus_LV_156-7_0_5_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_156-7_0_5_node_126 | 0.4 | n |  | TRUE
114 | bus_LV_156-7_0_5_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_156-7_0_5_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_156-7_0_5_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_156-7_0_5_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_156-7_0_5_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_156-7_0_5_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_156-7_0_5_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_156-7_0_5_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_156-7_0_5_node_100 | 0.4 | n |  | TRUE
123 | bus_LV_156-7_0_5_node_101 | 0.4 | n |  | TRUE
124 | bus_LV_156-7_0_5_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_156-7_0_5_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_156-7_0_5_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_156-7_0_5_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_156-7_0_5_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_156-7_0_5_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_156-7_0_5_node_117 | 0.4 | n |  | TRUE
131 | bus_MV_496_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_156-7_0_5_load_0 | 0 | 0.030391 | 0.0076168 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_156-7_0_5_load_22 | 4 | 0.014205 | 0.0035602 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_156-7_0_5_load_7 | 5 | 0.022891 | 0.0057371 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_156-7_0_5_load_3 | 6 | 0.023255 | 0.0058282 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_156-7_0_5_load_9 | 10 | 0.0047726 | 0.0011961 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_156-7_0_5_load_121 | 13 | 0.014137 | 0.003543 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_156-7_0_5_load_74 | 14 | 0.005252 | 0.0013163 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_156-7_0_5_load_16 | 16 | 0.020794 | 0.0052114 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_156-7_0_5_load_32 | 17 | 0.0051783 | 0.0012978 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_156-7_0_5_load_133 | 20 | 0.0090495 | 0.002268 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_156-7_0_5_load_11 | 22 | 0.0092842 | 0.0023268 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_156-7_0_5_load_13 | 24 | 0.00018627 | 4.6685e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_156-7_0_5_load_33 | 27 | 0.0055259 | 0.0013849 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_156-7_0_5_load_132 | 28 | 0.0020685 | 0.00051841 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_156-7_0_5_load_34 | 29 | 0.0050751 | 0.0012719 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_156-7_0_5_load_131 | 30 | 0.00348 | 0.00087218 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_156-7_0_5_load_82 | 31 | 0.0073824 | 0.0018502 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_156-7_0_5_load_18 | 32 | 0.0033819 | 0.00084759 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_156-7_0_5_load_20 | 34 | 0.0013182 | 0.00033037 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_156-7_0_5_load_84 | 36 | 0.0030715 | 0.00076978 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_156-7_0_5_load_91 | 37 | 0.00084485 | 0.00021174 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_156-7_0_5_load_86 | 38 | 0.0013792 | 0.00034567 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_156-7_0_5_load_107 | 40 | 0.0034961 | 0.0008762 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_156-7_0_5_load_23 | 42 | 0.0070594 | 0.0017692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_156-7_0_5_load_26 | 45 | 0.0086763 | 0.0021745 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_156-7_0_5_load_27 | 46 | 0.0063018 | 0.0015794 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_156-7_0_5_load_93 | 49 | 0.030211 | 0.0075717 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_156-7_0_5_load_94 | 50 | 0.020361 | 0.0051028 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_156-7_0_5_load_28 | 51 | 0.0041771 | 0.0010469 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_156-7_0_5_load_29 | 52 | 0.0098347 | 0.0024648 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_156-7_0_5_load_31 | 53 | 0.0048585 | 0.0012176 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_156-7_0_5_load_36 | 57 | 0.014558 | 0.0036485 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_156-7_0_5_load_57 | 59 | 0.0094957 | 0.0023799 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_156-7_0_5_load_43 | 60 | 0.0089056 | 0.0022319 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_156-7_0_5_load_40 | 61 | 0.0029154 | 0.00073067 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_156-7_0_5_load_58 | 62 | 0.0023421 | 0.00058699 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_156-7_0_5_load_39 | 63 | 0.0091767 | 0.0022999 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_156-7_0_5_load_41 | 64 | 0.011259 | 0.0028217 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_156-7_0_5_load_44 | 68 | 0.013233 | 0.0033164 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_156-7_0_5_load_47 | 70 | 0.0088156 | 0.0022094 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_156-7_0_5_load_48 | 71 | 0.0071535 | 0.0017928 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_156-7_0_5_load_50 | 72 | 0.007685 | 0.001926 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_156-7_0_5_load_51 | 73 | 0.012012 | 0.0030105 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_156-7_0_5_load_68 | 74 | 0.0057818 | 0.0014491 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_156-7_0_5_load_52 | 75 | 0.01163 | 0.0029149 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_156-7_0_5_load_123 | 77 | 0.003597 | 0.0009015 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_156-7_0_5_load_67 | 78 | 0.0029592 | 0.00074165 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_156-7_0_5_load_63 | 81 | 0.0019034 | 0.00047704 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_156-7_0_5_load_59 | 82 | 0.011018 | 0.0027613 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_156-7_0_5_load_54 | 83 | 0.01147 | 0.0028746 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_156-7_0_5_load_55 | 84 | 0.001707 | 0.00042782 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_156-7_0_5_load_56 | 85 | 0.0067878 | 0.0017012 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_156-7_0_5_load_60 | 86 | 0.00065719 | 0.00016471 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_156-7_0_5_load_62 | 87 | 0.0010243 | 0.00025671 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_156-7_0_5_load_110 | 88 | 0.0010146 | 0.00025429 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_156-7_0_5_load_111 | 89 | 0.00085603 | 0.00021454 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_156-7_0_5_load_124 | 90 | 0.0055645 | 0.0013946 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_156-7_0_5_load_104 | 93 | 0.0017091 | 0.00042835 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_156-7_0_5_load_127 | 94 | 0.0035303 | 0.00088478 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_156-7_0_5_load_128 | 95 | 0.019128 | 0.0047939 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_156-7_0_5_load_69 | 97 | 0.0046101 | 0.0011554 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_156-7_0_5_load_70 | 98 | 0.0038802 | 0.00097248 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_156-7_0_5_load_119 | 101 | 0.001193 | 0.000299 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_156-7_0_5_load_118 | 102 | 0.0079851 | 0.0020013 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_156-7_0_5_load_129 | 106 | 0.0069315 | 0.0017372 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_156-7_0_5_load_79 | 107 | 0.0016044 | 0.0004021 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_156-7_0_5_load_80 | 108 | 0.0081884 | 0.0020522 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_156-7_0_5_load_76 | 109 | 0.0015909 | 0.00039872 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_156-7_0_5_load_78 | 111 | 0.0019401 | 0.00048623 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_156-7_0_5_load_126 | 113 | 0.00193 | 0.0004837 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_156-7_0_5_load_88 | 114 | 0.0024494 | 0.00061388 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_156-7_0_5_load_109 | 115 | 0.0052087 | 0.0013054 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_156-7_0_5_load_95 | 116 | 0.0028435 | 0.00071265 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_156-7_0_5_load_96 | 117 | 0.0079813 | 0.0020003 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_156-7_0_5_load_99 | 119 | 0.00049187 | 0.00012327 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_156-7_0_5_load_106 | 120 | 0.0071614 | 0.0017948 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_156-7_0_5_load_100 | 122 | 0.0067593 | 0.001694 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_156-7_0_5_load_101 | 123 | 0.0069269 | 0.0017361 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_156-7_0_5_load_112 | 125 | 0.00034902 | 8.7472e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_156-7_0_5_load_113 | 126 | 0.00037501 | 9.3986e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_156-7_0_5_load_114 | 127 | 0.0018964 | 0.00047528 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_156-7_0_5_load_115 | 128 | 0.001955 | 0.00048996 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_156-7_0_5_load_116 | 129 | 0.00039714 | 9.9534e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_156-7_0_5_load_117 | 130 | 0.00037369 | 9.3657e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_156-7_0_5_line_0 |  | 0 | 1 | 0.019758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_156-7_0_5_line_1 |  | 1 | 2 | 0.026445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_156-7_0_5_line_2 |  | 2 | 3 | 0.020508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_156-7_0_5_line_3 |  | 2 | 4 | 0.019156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_156-7_0_5_line_4 |  | 3 | 5 | 0.0062703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_156-7_0_5_line_5 |  | 5 | 8 | 0.024356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_156-7_0_5_line_6 |  | 6 | 7 | 0.036016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_156-7_0_5_line_7 |  | 7 | 8 | 0.067226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_156-7_0_5_line_8 |  | 7 | 9 | 0.004781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_156-7_0_5_line_9 |  | 8 | 10 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_156-7_0_5_line_10 |  | 8 | 11 | 0.042498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_156-7_0_5_line_11 |  | 9 | 12 | 0.034309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_156-7_0_5_line_12 |  | 9 | 13 | 0.022163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_156-7_0_5_line_13 |  | 10 | 14 | 0.0059601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_156-7_0_5_line_14 |  | 11 | 15 | 0.006074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_156-7_0_5_line_15 |  | 11 | 16 | 0.032091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_156-7_0_5_line_16 |  | 12 | 17 | 0.0022981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_156-7_0_5_line_17 |  | 13 | 18 | 0.018308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_156-7_0_5_line_18 |  | 14 | 19 | 0.023689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_156-7_0_5_line_19 |  | 15 | 20 | 0.022389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_156-7_0_5_line_20 |  | 15 | 21 | 0.015698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_156-7_0_5_line_21 |  | 17 | 48 | 0.015547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_156-7_0_5_line_22 |  | 18 | 124 | 0.004118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_156-7_0_5_line_23 |  | 19 | 104 | 0.010459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_156-7_0_5_line_24 |  | 19 | 105 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_156-7_0_5_line_25 |  | 21 | 31 | 0.019935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_156-7_0_5_line_26 |  | 22 | 23 | 0.020742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_156-7_0_5_line_27 |  | 23 | 24 | 0.004002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_156-7_0_5_line_28 |  | 23 | 25 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_156-7_0_5_line_29 |  | 23 | 26 | 0.035699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_156-7_0_5_line_30 |  | 25 | 27 | 0.039989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_156-7_0_5_line_31 |  | 26 | 28 | 0.033442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_156-7_0_5_line_32 |  | 27 | 29 | 0.0092268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_156-7_0_5_line_33 |  | 28 | 30 | 0.052074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_156-7_0_5_line_34 |  | 29 | 54 | 0.043963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_156-7_0_5_line_35 |  | 32 | 33 | 0.020872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_156-7_0_5_line_36 |  | 33 | 34 | 0.015307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_156-7_0_5_line_37 |  | 33 | 35 | 0.012604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_156-7_0_5_line_38 |  | 34 | 36 | 0.01761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_156-7_0_5_line_39 |  | 35 | 37 | 0.010508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_156-7_0_5_line_40 |  | 35 | 38 | 0.012587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_156-7_0_5_line_41 |  | 36 | 39 | 0.021382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_156-7_0_5_line_42 |  | 37 | 40 | 0.031031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_156-7_0_5_line_43 |  | 38 | 41 | 0.01517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_156-7_0_5_line_44 |  | 39 | 112 | 0.018818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_156-7_0_5_line_45 |  | 41 | 114 | 0.027965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_156-7_0_5_line_46 |  | 41 | 103 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_156-7_0_5_line_47 |  | 41 | 104 | 0.073766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_156-7_0_5_line_48 |  | 42 | 43 | 0.0086856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_156-7_0_5_line_49 |  | 42 | 44 | 0.02604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_156-7_0_5_line_50 |  | 43 | 45 | 0.013296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_156-7_0_5_line_51 |  | 44 | 46 | 0.014565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_156-7_0_5_line_52 |  | 45 | 47 | 0.026987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_156-7_0_5_line_53 |  | 46 | 48 | 0.012387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_156-7_0_5_line_54 |  | 47 | 49 | 0.041355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_156-7_0_5_line_55 |  | 47 | 50 | 0.0037257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_156-7_0_5_line_56 |  | 48 | 51 | 0.011091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_156-7_0_5_line_57 |  | 51 | 52 | 0.0052387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_156-7_0_5_line_58 |  | 52 | 53 | 0.0035143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_156-7_0_5_line_59 |  | 53 | 54 | 0.031807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_156-7_0_5_line_60 |  | 54 | 55 | 0.00943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_156-7_0_5_line_61 |  | 55 | 56 | 0.006558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_156-7_0_5_line_62 |  | 55 | 57 | 0.043129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_156-7_0_5_line_63 |  | 56 | 58 | 0.037408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_156-7_0_5_line_64 |  | 56 | 59 | 0.023895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_156-7_0_5_line_65 |  | 58 | 60 | 0.009579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_156-7_0_5_line_66 |  | 58 | 61 | 0.012965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_156-7_0_5_line_67 |  | 59 | 62 | 0.0018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_156-7_0_5_line_68 |  | 60 | 65 | 0.023042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_156-7_0_5_line_69 |  | 61 | 63 | 0.0024938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_156-7_0_5_line_70 |  | 62 | 85 | 8.6065e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_156-7_0_5_line_71 |  | 63 | 64 | 0.033434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_156-7_0_5_line_72 |  | 65 | 66 | 0.037009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_156-7_0_5_line_73 |  | 65 | 67 | 0.007498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_156-7_0_5_line_74 |  | 66 | 77 | 0.017341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_156-7_0_5_line_75 |  | 67 | 72 | 0.013482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_156-7_0_5_line_76 |  | 67 | 68 | 0.011207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_156-7_0_5_line_77 |  | 68 | 69 | 0.0069948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_156-7_0_5_line_78 |  | 69 | 70 | 0.016594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_156-7_0_5_line_79 |  | 69 | 71 | 0.012407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_156-7_0_5_line_80 |  | 70 | 73 | 5.9363e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_156-7_0_5_line_81 |  | 71 | 74 | 0.0029377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_156-7_0_5_line_82 |  | 73 | 75 | 0.016496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_156-7_0_5_line_83 |  | 74 | 76 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_156-7_0_5_line_84 |  | 75 | 79 | 0.04588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_156-7_0_5_line_85 |  | 76 | 78 | 0.038034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_156-7_0_5_line_86 |  | 77 | 90 | 0.0072216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_156-7_0_5_line_87 |  | 79 | 80 | 0.025116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_156-7_0_5_line_88 |  | 80 | 81 | 0.026063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_156-7_0_5_line_89 |  | 80 | 82 | 0.0039306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_156-7_0_5_line_90 |  | 82 | 86 | 0.01329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_156-7_0_5_line_91 |  | 83 | 84 | 0.0154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_156-7_0_5_line_92 |  | 84 | 85 | 0.00038833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_156-7_0_5_line_93 |  | 86 | 87 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_156-7_0_5_line_94 |  | 87 | 88 | 0.00099047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_156-7_0_5_line_95 |  | 88 | 89 | 0.0044309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_156-7_0_5_line_96 |  | 89 | 125 | 0.039493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_156-7_0_5_line_97 |  | 91 | 92 | 0.02237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_156-7_0_5_line_98 |  | 91 | 93 | 0.016136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_156-7_0_5_line_99 |  | 92 | 94 | 0.026561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_156-7_0_5_line_100 |  | 92 | 95 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_156-7_0_5_line_101 |  | 93 | 96 | 0.021731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_156-7_0_5_line_102 |  | 96 | 120 | 0.031631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_156-7_0_5_line_103 |  | 96 | 118 | 0.004593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_156-7_0_5_line_104 |  | 97 | 98 | 0.0089885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_156-7_0_5_line_105 |  | 97 | 99 | 0.076649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_156-7_0_5_line_106 |  | 99 | 100 | 0.052223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_156-7_0_5_line_107 |  | 100 | 101 | 0.016862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_156-7_0_5_line_108 |  | 100 | 102 | 0.014627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_156-7_0_5_line_109 |  | 102 | 103 | 0.024066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_156-7_0_5_line_110 |  | 104 | 106 | 0.018398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_156-7_0_5_line_111 |  | 105 | 107 | 0.0059799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_156-7_0_5_line_112 |  | 105 | 108 | 0.043113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_156-7_0_5_line_113 |  | 107 | 110 | 0.0052672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_156-7_0_5_line_114 |  | 109 | 110 | 0.012758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_156-7_0_5_line_115 |  | 110 | 111 | 0.004914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_156-7_0_5_line_116 |  | 112 | 113 | 0.009833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_156-7_0_5_line_117 |  | 114 | 115 | 0.0022207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_156-7_0_5_line_118 |  | 116 | 117 | 0.018476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_156-7_0_5_line_119 |  | 116 | 118 | 0.027759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_156-7_0_5_line_120 |  | 118 | 119 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_156-7_0_5_line_121 |  | 119 | 121 | 0.002748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_156-7_0_5_line_122 |  | 121 | 122 | 0.03097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_156-7_0_5_line_123 |  | 122 | 123 | 0.0025095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_156-7_0_5_line_124 |  | 123 | 124 | 0.020875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_156-7_0_5_line_125 |  | 125 | 126 | 3.2697e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_156-7_0_5_line_126 |  | 126 | 127 | 0.0052879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_156-7_0_5_line_127 |  | 127 | 128 | 0.00052403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_156-7_0_5_line_128 |  | 128 | 129 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_156-7_0_5_line_129 |  | 129 | 130 | 6.597e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_156-7_0_5_trafo_122 | 0.63 MVA 20/0.4 kV | 131 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2692022.0872 | 1235800.5342 | 2692041.6974 | 1235798.1251
1 | 2692022.0872 | 1235800.5342 | 2692021.4339 | 1235788.482 | 2692019.5068 | 1235778.5227 | 2692023.1799 | 1235776.4225
2 | 2692041.731 | 1235767.6368 | 2692028.9989 | 1235773.0991 | 2692023.1799 | 1235776.4225
3 | 2692023.1799 | 1235776.4225 | 2692018.2674 | 1235757.9075
4 | 2692041.731 | 1235767.6368 | 2692047.6735 | 1235765.6359
5 | 2692070.8513 | 1235758.1588 | 2692059.9154 | 1235761.514 | 2692047.6735 | 1235765.6359
6 | 2692049.4395 | 1235694.6698 | 2692014.3647 | 1235702.8504
7 | 2692049.4395 | 1235694.6698 | 2692051.7278 | 1235699.3865 | 2692061.7042 | 1235722.291 | 2692068.4538 | 1235748.7704 | 2692070.8513 | 1235758.1588
8 | 2692047.2194 | 1235690.4323 | 2692049.4395 | 1235694.6698
9 | 2692070.8513 | 1235758.1588 | 2692082.8978 | 1235758.3567 | 2692087.6814 | 1235758.3956
10 | 2692070.8513 | 1235758.1588 | 2692073.4244 | 1235767.9391 | 2692078.2576 | 1235788.6513 | 2692080.7842 | 1235799.4761
11 | 2692032.1657 | 1235659.6101 | 2692039.23 | 1235674.5859 | 2692042.2789 | 1235681.0267 | 2692047.2194 | 1235690.4323
12 | 2692047.2194 | 1235690.4323 | 2692058.0647 | 1235687.0757 | 2692063.571 | 1235685.3709 | 2692068.3921 | 1235683.8817
13 | 2692087.6814 | 1235758.3956 | 2692093.4474 | 1235758.4425 | 2692093.6382 | 1235758.4777
14 | 2692080.7842 | 1235799.4761 | 2692082.1684 | 1235805.3908
15 | 2692080.7842 | 1235799.4761 | 2692101.588 | 1235797.6973 | 2692104.5017 | 1235796.7417 | 2692106.1586 | 1235793.8542 | 2692108.1074 | 1235789.4501
16 | 2692032.1657 | 1235659.6101 | 2692031.2918 | 1235657.4846
17 | 2692085.885 | 1235678.4783 | 2692068.3921 | 1235683.8817
18 | 2692116.8043 | 1235763.3526 | 2692109.3192 | 1235761.3685 | 2692093.6382 | 1235758.4777
19 | 2692082.1684 | 1235805.3908 | 2692093.4775 | 1235805.7885 | 2692098.6763 | 1235815.6096
20 | 2692086.0347 | 1235820.6062 | 2692082.1684 | 1235805.3908
21 | 2692028.1706 | 1235642.4357 | 2692028.1616 | 1235645.9492 | 2692028.5353 | 1235649.1796 | 2692029.2992 | 1235652.6384 | 2692031.2918 | 1235657.4846
22 | 2692085.885 | 1235678.4783 | 2692089.8537 | 1235677.339
23 | 2692116.8043 | 1235763.3526 | 2692126.6166 | 1235767.0519
24 | 2692116.8043 | 1235763.3526 | 2692117.4535 | 1235748.3406
25 | 2692086.0347 | 1235820.6062 | 2692067.1377 | 1235826.9543
26 | 2691947.2994 | 1235603.133 | 2691941.108 | 1235583.3363
27 | 2691947.2994 | 1235603.133 | 2691945.3325 | 1235599.6444
28 | 2691946.0731 | 1235622.2056 | 2691944.3071 | 1235611.6039 | 2691946.6864 | 1235608.0159 | 2691947.2994 | 1235603.133
29 | 2691918.7579 | 1235613.8102 | 2691930.0227 | 1235610.7378 | 2691937.5003 | 1235609.308 | 2691944.3071 | 1235611.6039 | 2691946.6864 | 1235608.0159 | 2691947.2994 | 1235603.133
30 | 2691946.0731 | 1235622.2056 | 2691984.571 | 1235611.3885
31 | 2691897.3241 | 1235600.5024 | 2691900.951 | 1235612.6451 | 2691901.7892 | 1235614.7262 | 2691903.3836 | 1235616.8524 | 2691905.6839 | 1235617.3884 | 2691918.7579 | 1235613.8102
32 | 2691984.571 | 1235611.3885 | 2691993.4539 | 1235608.8926
33 | 2691897.3241 | 1235600.5024 | 2691849.3635 | 1235620.7867
34 | 2692034.551 | 1235593.6213 | 2692016.2329 | 1235601.9881 | 2692008.3389 | 1235604.8902 | 2691998.5806 | 1235607.4521 | 2691993.4539 | 1235608.8926
35 | 2692232.8804 | 1235781.8111 | 2692242.4689 | 1235800.3501
36 | 2692232.8804 | 1235781.8111 | 2692244.6099 | 1235774.1543 | 2692245.7292 | 1235773.4934
37 | 2692221.4378 | 1235787.0818 | 2692228.2116 | 1235784.1737 | 2692232.8804 | 1235781.8111
38 | 2692245.7292 | 1235773.4934 | 2692260.8923 | 1235764.539
39 | 2692221.4378 | 1235787.0818 | 2692218.0043 | 1235777.1509
40 | 2692221.4378 | 1235787.0818 | 2692214.2542 | 1235789.5721 | 2692209.4029 | 1235790.713
41 | 2692280.0627 | 1235755.1243 | 2692265.9835 | 1235761.5325 | 2692260.8923 | 1235764.539
42 | 2692200.6057 | 1235756.0693 | 2692207.3874 | 1235756.5527 | 2692210.2259 | 1235757.5196 | 2692212.1228 | 1235760.1399 | 2692218.0043 | 1235777.1509
43 | 2692194.4855 | 1235793.4126 | 2692204.3635 | 1235791.8981 | 2692209.4029 | 1235790.713
44 | 2692280.0627 | 1235755.1243 | 2692286.9734 | 1235772.6333
45 | 2692194.4855 | 1235793.4126 | 2692192.5793 | 1235774.3247 | 2692191.4389 | 1235772.2166 | 2692189.1942 | 1235771.0364 | 2692185.4856 | 1235770.0058
46 | 2692194.4855 | 1235793.4126 | 2692194.8394 | 1235798.8888 | 2692195.8209 | 1235802.4621 | 2692197.797 | 1235806.3178 | 2692199.7729 | 1235810.1846
47 | 2692126.6166 | 1235767.0519 | 2692129.145 | 1235768.0029 | 2692150.8712 | 1235780.927 | 2692161.8226 | 1235786.3341 | 2692170.3574 | 1235788.9461 | 2692178.3657 | 1235791.3499 | 2692186.2134 | 1235792.8839 | 2692194.4855 | 1235793.4126
48 | 2691968.2914 | 1235657.1749 | 2691976.7573 | 1235655.2341
49 | 2692002.1388 | 1235649.4154 | 2691976.7573 | 1235655.2341
50 | 2691968.2914 | 1235657.1749 | 2691955.5325 | 1235660.9152
51 | 2692002.1388 | 1235649.4154 | 2692016.2066 | 1235645.6435
52 | 2691929.6354 | 1235668.5072 | 2691955.5325 | 1235660.9152
53 | 2692028.1706 | 1235642.4357 | 2692016.2066 | 1235645.6435
54 | 2691929.6354 | 1235668.5072 | 2691940.9359 | 1235692.9442 | 2691955.244 | 1235695.2006
55 | 2691929.6354 | 1235668.5072 | 2691926.1092 | 1235669.71
56 | 2692028.1706 | 1235642.4357 | 2692028.8498 | 1235640.6116 | 2692032.0381 | 1235632.0414
57 | 2692032.0381 | 1235632.0414 | 2692033.8647 | 1235627.1315
58 | 2692033.8647 | 1235627.1315 | 2692035.0901 | 1235623.8377
59 | 2692034.551 | 1235593.6213 | 2692037.2823 | 1235601.9919 | 2692038.7607 | 1235605.2505 | 2692039.5662 | 1235608.9545 | 2692039.4163 | 1235611.2984 | 2692038.9593 | 1235613.4373 | 2692035.0901 | 1235623.8377
60 | 2692034.551 | 1235593.6213 | 2692043.1497 | 1235589.696
61 | 2692049.0309 | 1235586.7628 | 2692045.1634 | 1235588.6932 | 2692043.1497 | 1235589.696
62 | 2692043.1497 | 1235589.696 | 2692041.4245 | 1235583.3091 | 2692037.4441 | 1235568.6035 | 2692031.3686 | 1235548.2112
63 | 2692082.6003 | 1235570.1153 | 2692073.1826 | 1235574.1389 | 2692064.0844 | 1235579.0348 | 2692049.0309 | 1235586.7628
64 | 2692049.0309 | 1235586.7628 | 2692056.4888 | 1235597.8308 | 2692063.4801 | 1235605.7304
65 | 2692082.6003 | 1235570.1153 | 2692091.8752 | 1235567.7206
66 | 2692082.6003 | 1235570.1153 | 2692078.7885 | 1235557.7235
67 | 2692063.4801 | 1235605.7304 | 2692064.6867 | 1235607.0936
68 | 2692114.1696 | 1235561.8986 | 2692104.2133 | 1235564.5351 | 2692091.8752 | 1235567.7206
69 | 2692078.0553 | 1235555.3399 | 2692078.7885 | 1235557.7235
70 | 2692064.7437 | 1235607.1581 | 2692064.6867 | 1235607.0936
71 | 2692058.7616 | 1235536.1879 | 2692072.1663 | 1235536.1956 | 2692078.0553 | 1235555.3399
72 | 2692114.1696 | 1235561.8986 | 2692109.2738 | 1235525.2183
73 | 2692121.5701 | 1235560.5679 | 2692114.1696 | 1235561.8986
74 | 2692109.2738 | 1235525.2183 | 2692095.4126 | 1235528.7727 | 2692092.8001 | 1235530.3111
75 | 2692121.5701 | 1235560.5679 | 2692125.346 | 1235573.5103
76 | 2692121.5701 | 1235560.5679 | 2692132.4604 | 1235557.9231
77 | 2692139.2576 | 1235556.2724 | 2692132.4604 | 1235557.9231
78 | 2692139.2576 | 1235556.2724 | 2692155.2848 | 1235551.9723
79 | 2692139.2576 | 1235556.2724 | 2692140.7005 | 1235562.7884 | 2692141.8913 | 1235568.3967
80 | 2692155.3421 | 1235551.9569 | 2692155.2848 | 1235551.9723
81 | 2692141.8913 | 1235568.3967 | 2692142.5014 | 1235571.2704
82 | 2692155.3421 | 1235551.9569 | 2692159.0422 | 1235550.9642 | 2692171.3589 | 1235548.0149
83 | 2692137.5072 | 1235585.1773 | 2692143.8958 | 1235577.8377 | 2692142.5014 | 1235571.2704
84 | 2692216.3318 | 1235539.3223 | 2692207.8512 | 1235540.0135 | 2692199.222 | 1235541.5029 | 2692183.027 | 1235545.221 | 2692171.3589 | 1235548.0149
85 | 2692137.5072 | 1235585.1773 | 2692149.1109 | 1235582.2218 | 2692154.1688 | 1235582.6005 | 2692159.82 | 1235585.2234 | 2692162.7306 | 1235587.3924 | 2692165.8106 | 1235598.1591
86 | 2692094.6978 | 1235537.2789 | 2692092.8001 | 1235530.3111
87 | 2692216.1536 | 1235564.4378 | 2692216.2468 | 1235551.6189 | 2692216.2951 | 1235545.0926 | 2692216.3318 | 1235539.3223
88 | 2692216.1536 | 1235564.4378 | 2692242.2623 | 1235565.7107
89 | 2692216.1536 | 1235564.4378 | 2692216.1273 | 1235568.3683
90 | 2692216.1273 | 1235568.3683 | 2692216.1191 | 1235569.5855 | 2692216.9889 | 1235581.6274
91 | 2692076.7877 | 1235611.9047 | 2692074.6219 | 1235613.601 | 2692072.4012 | 1235614.2782 | 2692070.6372 | 1235613.8172 | 2692065.0011 | 1235607.4489
92 | 2692065.0011 | 1235607.4489 | 2692064.7437 | 1235607.1581
93 | 2692218.3667 | 1235600.7038 | 2692216.9889 | 1235581.6274
94 | 2692218.3667 | 1235600.7038 | 2692218.4381 | 1235601.6917
95 | 2692218.4381 | 1235601.6917 | 2692218.7573 | 1235606.1112
96 | 2692246.5665 | 1235624.9067 | 2692230.4903 | 1235622.8584 | 2692223.6043 | 1235620.7945 | 2692221.2405 | 1235618.5005 | 2692219.3335 | 1235614.09 | 2692218.7573 | 1235606.1112
97 | 2692151.1141 | 1235622.8713 | 2692173.4195 | 1235620.46
98 | 2692151.1141 | 1235622.8713 | 2692155.6407 | 1235638.3594
99 | 2692173.4195 | 1235620.46 | 2692180.0255 | 1235620.0844 | 2692184.0102 | 1235634.9793 | 2692179.6236 | 1235636.2232
100 | 2692168.2159 | 1235600.2201 | 2692173.4195 | 1235620.46
101 | 2692161.7369 | 1235659.2181 | 2692155.6407 | 1235638.3594
102 | 2692161.7369 | 1235659.2181 | 2692173.0828 | 1235658.2378 | 2692180.9169 | 1235657.7367 | 2692184.003 | 1235655.9166 | 2692186.0812 | 1235652.7132 | 2692184.9064 | 1235647.8616
103 | 2692161.7489 | 1235663.8105 | 2692161.7369 | 1235659.2181
104 | 2692150.2931 | 1235869.8716 | 2692146.5081 | 1235868.9344 | 2692141.9069 | 1235869.3856 | 2692141.458 | 1235869.5106
105 | 2692208.056 | 1235879.6971 | 2692186.9835 | 1235886.1192 | 2692182.3568 | 1235887.7264 | 2692169.301 | 1235892.1048 | 2692164.0644 | 1235893.5135 | 2692160.4541 | 1235893.0238 | 2692159.16 | 1235891.069 | 2692159.2079 | 1235887.9786 | 2692159.8605 | 1235885.4313 | 2692157.9173 | 1235879.9416 | 2692154.7802 | 1235877.2577 | 2692153.1455 | 1235874.3191 | 2692152.4726 | 1235871.8402 | 2692150.2931 | 1235869.8716
106 | 2692217.0979 | 1235844.7787 | 2692229.4675 | 1235869.4775 | 2692225.7823 | 1235874.3016 | 2692208.056 | 1235879.6971
107 | 2692217.0979 | 1235844.7787 | 2692206.7381 | 1235849.0543 | 2692201.3942 | 1235851.0284
108 | 2692217.0979 | 1235844.7787 | 2692210.7242 | 1235831.6128
109 | 2692199.7729 | 1235810.1846 | 2692208.1218 | 1235826.237 | 2692210.7242 | 1235831.6128
110 | 2692126.6166 | 1235767.0519 | 2692118.8645 | 1235783.7438
111 | 2692117.4535 | 1235748.3406 | 2692116.9745 | 1235742.3799
112 | 2692117.4535 | 1235748.3406 | 2692137.6562 | 1235747.2642 | 2692152.0109 | 1235746.5085 | 2692160.5179 | 1235746.5846
113 | 2692116.5526 | 1235737.1296 | 2692116.9745 | 1235742.3799
114 | 2692116.5526 | 1235737.1296 | 2692115.5379 | 1235724.4123
115 | 2692116.5526 | 1235737.1296 | 2692120.6888 | 1235734.4585
116 | 2692286.9734 | 1235772.6333 | 2692277.9137 | 1235776.5176
117 | 2692183.346 | 1235769.4112 | 2692185.4856 | 1235770.0058
118 | 2692177.2707 | 1235686.1267 | 2692179.4117 | 1235690.3371 | 2692188.8061 | 1235700.3813
119 | 2692161.7489 | 1235663.8105 | 2692168.6517 | 1235669.177 | 2692177.2707 | 1235686.1267
120 | 2692161.7489 | 1235663.8105 | 2692145.592 | 1235665.6428
121 | 2692142.8614 | 1235665.9524 | 2692145.592 | 1235665.6428
122 | 2692142.8614 | 1235665.9524 | 2692140.4047 | 1235666.2368 | 2692128.5383 | 1235667.5871 | 2692115.7791 | 1235669.9021 | 2692112.332 | 1235670.8909
123 | 2692112.332 | 1235670.8909 | 2692109.9197 | 1235671.5829
124 | 2692089.8537 | 1235677.339 | 2692109.9197 | 1235671.5829
125 | 2692246.5665 | 1235624.9067 | 2692246.5989 | 1235624.9108
126 | 2692246.5989 | 1235624.9108 | 2692251.8444 | 1235625.5791
127 | 2692251.8444 | 1235625.5791 | 2692252.3642 | 1235625.6453
128 | 2692252.3642 | 1235625.6453 | 2692266.6908 | 1235627.4707
129 | 2692266.6908 | 1235627.4707 | 2692266.7563 | 1235627.479

## bus_geodata
| x | y | coords
0 | 2692041.6974 | 1235798.1251
1 | 2692022.0872 | 1235800.5342
2 | 2692023.1799 | 1235776.4225
3 | 2692041.731 | 1235767.6368
4 | 2692018.2674 | 1235757.9075
5 | 2692047.6735 | 1235765.6359
6 | 2692014.3647 | 1235702.8504
7 | 2692049.4395 | 1235694.6698
8 | 2692070.8513 | 1235758.1588
9 | 2692047.2194 | 1235690.4323
10 | 2692087.6814 | 1235758.3956
11 | 2692080.7842 | 1235799.4761
12 | 2692032.1657 | 1235659.6101
13 | 2692068.3921 | 1235683.8817
14 | 2692093.6382 | 1235758.4777
15 | 2692082.1684 | 1235805.3908
16 | 2692108.1074 | 1235789.4501
17 | 2692031.2918 | 1235657.4846
18 | 2692085.885 | 1235678.4783
19 | 2692116.8043 | 1235763.3526
20 | 2692098.6763 | 1235815.6096
21 | 2692086.0347 | 1235820.6062
22 | 2691941.108 | 1235583.3363
23 | 2691947.2994 | 1235603.133
24 | 2691945.3325 | 1235599.6444
25 | 2691946.0731 | 1235622.2056
26 | 2691918.7579 | 1235613.8102
27 | 2691984.571 | 1235611.3885
28 | 2691897.3241 | 1235600.5024
29 | 2691993.4539 | 1235608.8926
30 | 2691849.3635 | 1235620.7867
31 | 2692067.1377 | 1235826.9543
32 | 2692242.4689 | 1235800.3501
33 | 2692232.8804 | 1235781.8111
34 | 2692245.7292 | 1235773.4934
35 | 2692221.4378 | 1235787.0818
36 | 2692260.8923 | 1235764.539
37 | 2692218.0043 | 1235777.1509
38 | 2692209.4029 | 1235790.713
39 | 2692280.0627 | 1235755.1243
40 | 2692200.6057 | 1235756.0693
41 | 2692194.4855 | 1235793.4126
42 | 2691976.7573 | 1235655.2341
43 | 2691968.2914 | 1235657.1749
44 | 2692002.1388 | 1235649.4154
45 | 2691955.5325 | 1235660.9152
46 | 2692016.2066 | 1235645.6435
47 | 2691929.6354 | 1235668.5072
48 | 2692028.1706 | 1235642.4357
49 | 2691955.244 | 1235695.2006
50 | 2691926.1092 | 1235669.71
51 | 2692032.0381 | 1235632.0414
52 | 2692033.8647 | 1235627.1315
53 | 2692035.0901 | 1235623.8377
54 | 2692034.551 | 1235593.6213
55 | 2692043.1497 | 1235589.696
56 | 2692049.0309 | 1235586.7628
57 | 2692031.3686 | 1235548.2112
58 | 2692082.6003 | 1235570.1153
59 | 2692063.4801 | 1235605.7304
60 | 2692091.8752 | 1235567.7206
61 | 2692078.7885 | 1235557.7235
62 | 2692064.6867 | 1235607.0936
63 | 2692078.0553 | 1235555.3399
64 | 2692058.7616 | 1235536.1879
65 | 2692114.1696 | 1235561.8986
66 | 2692109.2738 | 1235525.2183
67 | 2692121.5701 | 1235560.5679
68 | 2692132.4604 | 1235557.9231
69 | 2692139.2576 | 1235556.2724
70 | 2692155.2848 | 1235551.9723
71 | 2692141.8913 | 1235568.3967
72 | 2692125.346 | 1235573.5103
73 | 2692155.3421 | 1235551.9569
74 | 2692142.5014 | 1235571.2704
75 | 2692171.3589 | 1235548.0149
76 | 2692137.5072 | 1235585.1773
77 | 2692092.8001 | 1235530.3111
78 | 2692165.8106 | 1235598.1591
79 | 2692216.3318 | 1235539.3223
80 | 2692216.1536 | 1235564.4378
81 | 2692242.2623 | 1235565.7107
82 | 2692216.1273 | 1235568.3683
83 | 2692076.7877 | 1235611.9047
84 | 2692065.0011 | 1235607.4489
85 | 2692064.7437 | 1235607.1581
86 | 2692216.9889 | 1235581.6274
87 | 2692218.3667 | 1235600.7038
88 | 2692218.4381 | 1235601.6917
89 | 2692218.7573 | 1235606.1112
90 | 2692094.6978 | 1235537.2789
91 | 2692151.1141 | 1235622.8713
92 | 2692173.4195 | 1235620.46
93 | 2692155.6407 | 1235638.3594
94 | 2692179.6236 | 1235636.2232
95 | 2692168.2159 | 1235600.2201
96 | 2692161.7369 | 1235659.2181
97 | 2692150.2931 | 1235869.8716
98 | 2692141.458 | 1235869.5106
99 | 2692208.056 | 1235879.6971
100 | 2692217.0979 | 1235844.7787
101 | 2692201.3942 | 1235851.0284
102 | 2692210.7242 | 1235831.6128
103 | 2692199.7729 | 1235810.1846
104 | 2692126.6166 | 1235767.0519
105 | 2692117.4535 | 1235748.3406
106 | 2692118.8645 | 1235783.7438
107 | 2692116.9745 | 1235742.3799
108 | 2692160.5179 | 1235746.5846
109 | 2692115.5379 | 1235724.4123
110 | 2692116.5526 | 1235737.1296
111 | 2692120.6888 | 1235734.4585
112 | 2692286.9734 | 1235772.6333
113 | 2692277.9137 | 1235776.5176
114 | 2692185.4856 | 1235770.0058
115 | 2692183.346 | 1235769.4112
116 | 2692177.2707 | 1235686.1267
117 | 2692188.8061 | 1235700.3813
118 | 2692161.7489 | 1235663.8105
119 | 2692145.592 | 1235665.6428
120 | 2692184.9064 | 1235647.8616
121 | 2692142.8614 | 1235665.9524
122 | 2692112.332 | 1235670.8909
123 | 2692109.9197 | 1235671.5829
124 | 2692089.8537 | 1235677.339
125 | 2692246.5665 | 1235624.9067
126 | 2692246.5989 | 1235624.9108
127 | 2692251.8444 | 1235625.5791
128 | 2692252.3642 | 1235625.6453
129 | 2692266.6908 | 1235627.4707
130 | 2692266.7563 | 1235627.479
131 | 2692089.8537 | 1235677.339

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98572 | -0.27433 | 0.030391 | 0.0076168
1 | 0.98627 | -0.26356 | 0 | 0
2 | 0.98701 | -0.24917 | 0 | 0
3 | 0.98785 | -0.23282 | 0 | 0
4 | 0.98676 | -0.25404 | 0.014205 | 0.0035602
5 | 0.98811 | -0.22783 | 0.022891 | 0.0057371
6 | 0.99429 | -0.10871 | 0.023255 | 0.0058282
7 | 0.99506 | -0.093953 | 0 | 0
8 | 0.98962 | -0.19853 | 0 | 0
9 | 0.99527 | -0.089766 | 0 | 0
10 | 0.98852 | -0.21983 | 0.0047726 | 0.0011961
11 | 0.98817 | -0.22673 | 0 | 0
12 | 0.99289 | -0.13533 | 0 | 0
13 | 0.99783 | -0.041123 | 0.014137 | 0.003543
14 | 0.98816 | -0.22688 | 0.005252 | 0.0013163
15 | 0.98808 | -0.22851 | 0 | 0
16 | 0.98756 | -0.23865 | 0.020794 | 0.0052114
17 | 0.99273 | -0.13839 | 0.0051783 | 0.0012978
18 | 1 | 0 | -0.57997 | -0.14783
19 | 0.98682 | -0.25272 | 0 | 0
20 | 0.98789 | -0.23213 | 0.0090495 | 0.002268
21 | 0.98797 | -0.23058 | 0 | 0
22 | 0.98543 | -0.2792 | 0.0092842 | 0.0023268
23 | 0.98561 | -0.27575 | 0 | 0
24 | 0.98561 | -0.27576 | 0.00018627 | 4.6685e-05
25 | 0.98588 | -0.27036 | 0 | 0
26 | 0.98542 | -0.2793 | 0 | 0
27 | 0.98644 | -0.25959 | 0.0055259 | 0.0013849
28 | 0.98525 | -0.28263 | 0.0020685 | 0.00051841
29 | 0.98661 | -0.2562 | 0.0050751 | 0.0012719
30 | 0.98509 | -0.28589 | 0.00348 | 0.00087218
31 | 0.98784 | -0.23321 | 0.0073824 | 0.0018502
32 | 0.98303 | -0.32656 | 0.0033819 | 0.00084759
33 | 0.9831 | -0.32529 | 0 | 0
34 | 0.98301 | -0.32703 | 0.0013182 | 0.00033037
35 | 0.98321 | -0.32308 | 0 | 0
36 | 0.98293 | -0.32862 | 0.0030715 | 0.00076978
37 | 0.98317 | -0.3239 | 0.00084485 | 0.00021174
38 | 0.98337 | -0.31989 | 0.0013792 | 0.00034567
39 | 0.98289 | -0.32937 | 0 | 0
40 | 0.98307 | -0.32586 | 0.0034961 | 0.0008762
41 | 0.98359 | -0.31568 | 0 | 0
42 | 0.98836 | -0.22264 | 0.0070594 | 0.0017692
43 | 0.98789 | -0.23182 | 0 | 0
44 | 0.98995 | -0.19188 | 0 | 0
45 | 0.98716 | -0.2459 | 0.0086763 | 0.0021745
46 | 0.99084 | -0.17471 | 0.0063018 | 0.0015794
47 | 0.98591 | -0.27034 | 0 | 0
48 | 0.99166 | -0.15876 | 0 | 0
49 | 0.98476 | -0.29277 | 0.030211 | 0.0075717
50 | 0.98584 | -0.2717 | 0.020361 | 0.0051028
51 | 0.99109 | -0.16974 | 0.0041771 | 0.0010469
52 | 0.99083 | -0.17484 | 0.0098347 | 0.0024648
53 | 0.99066 | -0.17811 | 0.0048585 | 0.0012176
54 | 0.98765 | -0.23605 | 0 | 0
55 | 0.98686 | -0.25113 | 0 | 0
56 | 0.98636 | -0.26078 | 0 | 0
57 | 0.98629 | -0.26237 | 0.014558 | 0.0036485
58 | 0.98176 | -0.35 | 0 | 0
59 | 0.98567 | -0.2744 | 0.0094957 | 0.0023799
60 | 0.98079 | -0.36893 | 0.0089056 | 0.0022319
61 | 0.98148 | -0.35548 | 0.0029154 | 0.00073067
62 | 0.98563 | -0.27513 | 0.0023421 | 0.00058699
63 | 0.98144 | -0.3564 | 0.0091767 | 0.0022999
64 | 0.98109 | -0.36322 | 0.011259 | 0.0028217
65 | 0.97864 | -0.41089 | 0 | 0
66 | 0.97833 | -0.41706 | 0 | 0
67 | 0.97801 | -0.42332 | 0 | 0
68 | 0.97714 | -0.44037 | 0.013233 | 0.0033164
69 | 0.97668 | -0.44934 | 0 | 0
70 | 0.97585 | -0.46581 | 0.0088156 | 0.0022094
71 | 0.9765 | -0.45294 | 0.0071535 | 0.0017928
72 | 0.97791 | -0.42521 | 0.007685 | 0.001926
73 | 0.97584 | -0.46586 | 0.012012 | 0.0030105
74 | 0.97648 | -0.45341 | 0.0057818 | 0.0014491
75 | 0.97533 | -0.47597 | 0.01163 | 0.0029149
76 | 0.97643 | -0.4543 | 0 | 0
77 | 0.97818 | -0.41995 | 0.003597 | 0.0009015
78 | 0.97633 | -0.45636 | 0.0029592 | 0.00074165
79 | 0.9744 | -0.49433 | 0 | 0
80 | 0.97389 | -0.5044 | 0 | 0
81 | 0.97384 | -0.50531 | 0.0019034 | 0.00047704
82 | 0.97382 | -0.50584 | 0.011018 | 0.0027613
83 | 0.98546 | -0.27842 | 0.01147 | 0.0028746
84 | 0.98562 | -0.27525 | 0.001707 | 0.00042782
85 | 0.98563 | -0.27516 | 0.0067878 | 0.0017012
86 | 0.97371 | -0.50801 | 0.00065719 | 0.00016471
87 | 0.97356 | -0.51091 | 0.0010243 | 0.00025671
88 | 0.97355 | -0.51104 | 0.0010146 | 0.00025429
89 | 0.97353 | -0.51155 | 0.00085603 | 0.00021454
90 | 0.97815 | -0.42068 | 0.0055645 | 0.0013946
91 | 0.99571 | -0.082471 | 0 | 0
92 | 0.99525 | -0.091387 | 0 | 0
93 | 0.99604 | -0.076045 | 0.0017091 | 0.00042835
94 | 0.99516 | -0.093037 | 0.0035303 | 0.00088478
95 | 0.99488 | -0.098423 | 0.019128 | 0.0047939
96 | 0.99653 | -0.066745 | 0 | 0
97 | 0.98177 | -0.35137 | 0.0046101 | 0.0011554
98 | 0.98173 | -0.352 | 0.0038802 | 0.00097248
99 | 0.98237 | -0.3396 | 0 | 0
100 | 0.98278 | -0.33159 | 0 | 0
101 | 0.98276 | -0.33196 | 0.001193 | 0.000299
102 | 0.98291 | -0.32904 | 0.0079851 | 0.0020013
103 | 0.9833 | -0.32137 | 0 | 0
104 | 0.98636 | -0.26165 | 0 | 0
105 | 0.98664 | -0.25631 | 0 | 0
106 | 0.98625 | -0.26394 | 0.0069315 | 0.0017372
107 | 0.98661 | -0.25686 | 0.0016044 | 0.0004021
108 | 0.98632 | -0.26263 | 0.0081884 | 0.0020522
109 | 0.98658 | -0.25755 | 0.0015909 | 0.00039872
110 | 0.98659 | -0.25719 | 0 | 0
111 | 0.98659 | -0.25736 | 0.0019401 | 0.00048623
112 | 0.98286 | -0.33002 | 0 | 0
113 | 0.98284 | -0.33036 | 0.00193 | 0.0004837
114 | 0.98339 | -0.31953 | 0.0024494 | 0.00061388
115 | 0.98338 | -0.31974 | 0.0052087 | 0.0013054
116 | 0.99638 | -0.069478 | 0.0028435 | 0.00071265
117 | 0.99625 | -0.072068 | 0.0079813 | 0.0020003
118 | 0.99666 | -0.064204 | 0 | 0
119 | 0.99728 | -0.052125 | 0.00049187 | 0.00012327
120 | 0.99632 | -0.070722 | 0.0071614 | 0.0017948
121 | 0.99739 | -0.050062 | 0 | 0
122 | 0.9986 | -0.026838 | 0.0067593 | 0.001694
123 | 0.99871 | -0.024662 | 0.0069269 | 0.0017361
124 | 0.99979 | -0.004059 | 0 | 0
125 | 0.97333 | -0.51543 | 0.00034902 | 8.7472e-05
126 | 0.97333 | -0.51544 | 0.00037501 | 9.3986e-05
127 | 0.97331 | -0.51589 | 0.0018964 | 0.00047528
128 | 0.97331 | -0.51591 | 0.001955 | 0.00048996
129 | 0.9733 | -0.51612 | 0.00039714 | 9.9534e-05
130 | 0.9733 | -0.51612 | 0.00037369 | 9.3657e-05
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030391 | -0.0076168 | 0.030407 | 0.0076265 | 1.5594e-05 | 9.7284e-06 | 0.045878 | 0.045878 | 0.045878 | 0.98572 | -0.27433 | 0.98627 | -0.26356 | 12.6038
1 | -0.030407 | -0.0076265 | 0.030428 | 0.0076395 | 2.0873e-05 | 1.3021e-05 | 0.045878 | 0.045878 | 0.045878 | 0.98627 | -0.26356 | 0.98701 | -0.24917 | 12.6038
2 | -0.044636 | -0.011202 | 0.044671 | 0.011224 | 3.4831e-05 | 2.203e-05 | 0.067299 | 0.067299 | 0.067299 | 0.98701 | -0.24917 | 0.98785 | -0.23282 | 18.4886
3 | 0.014208 | 0.003562 | -0.014205 | -0.0035602 | 3.2962e-06 | 1.8648e-06 | 0.021421 | 0.021421 | 0.021421 | 0.98701 | -0.24917 | 0.98676 | -0.25404 | 5.8849
4 | -0.044671 | -0.011224 | 0.044682 | 0.01123 | 1.065e-05 | 6.7354e-06 | 0.067299 | 0.067299 | 0.067299 | 0.98785 | -0.23282 | 0.98811 | -0.22783 | 18.4886
5 | -0.067573 | -0.016967 | 0.067668 | 0.017028 | 9.46e-05 | 6.0232e-05 | 0.10177 | 0.10177 | 0.10177 | 0.98811 | -0.22783 | 0.98962 | -0.19853 | 27.9591
6 | -0.023255 | -0.0058282 | 0.023271 | 0.0058382 | 1.6358e-05 | 1.0002e-05 | 0.034802 | 0.034802 | 0.034802 | 0.99429 | -0.10871 | 0.99506 | -0.093953 | 9.5611
7 | 0.17721 | 0.044969 | -0.17632 | -0.044404 | 0.00088648 | 0.00056561 | 0.26519 | 0.2652 | 0.2652 | 0.99506 | -0.093953 | 0.98962 | -0.19853 | 36.4279
8 | -0.20048 | -0.050807 | 0.20052 | 0.050833 | 4.0339e-05 | 2.5568e-05 | 0.3 | 0.3 | 0.3 | 0.99506 | -0.093953 | 0.99527 | -0.089766 | 20.6042
9 | 0.071361 | 0.018006 | -0.071288 | -0.017959 | 7.2729e-05 | 4.633e-05 | 0.10734 | 0.10734 | 0.10734 | 0.98962 | -0.19853 | 0.98852 | -0.21983 | 29.4897
10 | 0.037292 | 0.0093704 | -0.037242 | -0.0093389 | 5.0123e-05 | 3.1534e-05 | 0.056082 | 0.056082 | 0.056082 | 0.98962 | -0.19853 | 0.98817 | -0.22673 | 15.4071
11 | 0.30472 | 0.077744 | -0.30405 | -0.077318 | 0.00066902 | 0.00042639 | 0.45607 | 0.45607 | 0.45607 | 0.99527 | -0.089766 | 0.99289 | -0.13533 | 31.3235
12 | -0.50524 | -0.12858 | 0.50643 | 0.12934 | 0.0011877 | 0.00075899 | 0.75607 | 0.75607 | 0.75607 | 0.99527 | -0.089766 | 0.99783 | -0.041123 | 51.9276
13 | 0.066515 | 0.016763 | -0.066493 | -0.016749 | 2.2421e-05 | 1.4273e-05 | 0.10016 | 0.10016 | 0.10016 | 0.98852 | -0.21983 | 0.98816 | -0.22688 | 27.516
14 | 0.016437 | 0.0041204 | -0.016435 | -0.0041195 | 1.3954e-06 | 8.1524e-07 | 0.024751 | 0.024751 | 0.024751 | 0.98817 | -0.22673 | 0.98808 | -0.22851 | 6.7997
15 | 0.020805 | 0.0052185 | -0.020794 | -0.0052114 | 1.1813e-05 | 7.1495e-06 | 0.031331 | 0.031331 | 0.031331 | 0.98817 | -0.22673 | 0.98756 | -0.23865 | 8.6074
16 | 0.30405 | 0.077318 | -0.30401 | -0.077289 | 4.4814e-05 | 2.8562e-05 | 0.45607 | 0.45607 | 0.45607 | 0.99289 | -0.13533 | 0.99273 | -0.13839 | 31.3236
17 | -0.52056 | -0.13288 | 0.5216 | 0.13354 | 0.0010366 | 0.00066249 | 0.77715 | 0.77715 | 0.77715 | 0.99783 | -0.041123 | 1 | 0 | 53.3755
18 | 0.061241 | 0.015433 | -0.061165 | -0.015384 | 7.5597e-05 | 4.8079e-05 | 0.09225 | 0.09225 | 0.09225 | 0.98816 | -0.22688 | 0.98682 | -0.25272 | 25.3433
19 | 0.009051 | 0.0022687 | -0.0090495 | -0.002268 | 1.5599e-06 | 7.1165e-07 | 0.013631 | 0.013631 | 0.013631 | 0.98808 | -0.22851 | 0.98789 | -0.23213 | 3.7447
20 | 0.0073841 | 0.0018508 | -0.0073834 | -0.0018505 | 7.2796e-07 | 2.6485e-07 | 0.01112 | 0.01112 | 0.01112 | 0.98808 | -0.22851 | 0.98797 | -0.23058 | 3.055
21 | 0.29883 | 0.075991 | -0.29854 | -0.075805 | 0.00029294 | 0.00018668 | 0.44831 | 0.44831 | 0.44831 | 0.99273 | -0.13839 | 0.99166 | -0.15876 | 30.7905
22 | 0.056723 | 0.014287 | -0.056712 | -0.01428 | 1.1008e-05 | 6.9911e-06 | 0.08443 | 0.08443 | 0.08443 | 1 | 0 | 0.99979 | -0.004059 | 23.195
23 | 0.047836 | 0.012043 | -0.047816 | -0.01203 | 2.0418e-05 | 1.2934e-05 | 0.072151 | 0.072151 | 0.072151 | 0.98682 | -0.25272 | 0.98636 | -0.26165 | 19.8217
24 | 0.013329 | 0.0033413 | -0.013326 | -0.0033401 | 2.2765e-06 | 1.265e-06 | 0.020099 | 0.020099 | 0.020099 | 0.98682 | -0.25272 | 0.98664 | -0.25631 | 5.5216
25 | 0.0073834 | 0.0018505 | -0.0073824 | -0.0018502 | 9.2445e-07 | 3.3641e-07 | 0.01112 | 0.01112 | 0.01112 | 0.98797 | -0.23058 | 0.98784 | -0.23321 | 3.0551
26 | -0.0092842 | -0.0023268 | 0.0092857 | 0.0023276 | 1.5288e-06 | 7.141e-07 | 0.014019 | 0.014019 | 0.014019 | 0.98543 | -0.2792 | 0.98561 | -0.27575 | 3.8515
27 | 0.00018627 | 4.6634e-05 | -0.00018627 | -4.6685e-05 | 1.1869e-10 | -5.0927e-08 | 0.00028121 | 0.00028123 | 0.00028123 | 0.98561 | -0.27575 | 0.98561 | -0.27576 | 0.07726
28 | -0.015023 | -0.0037647 | 0.015027 | 0.003767 | 3.8531e-06 | 2.2113e-06 | 0.022681 | 0.022681 | 0.022681 | 0.98561 | -0.27575 | 0.98588 | -0.27036 | 6.2309
29 | 0.0055509 | 0.0013906 | -0.0055499 | -0.0013904 | 9.4017e-07 | 1.4683e-07 | 0.0083802 | 0.0083804 | 0.0083804 | 0.98561 | -0.27575 | 0.98542 | -0.2793 | 2.3023
30 | -0.015027 | -0.003767 | 0.015034 | 0.0037714 | 7.7139e-06 | 4.4267e-06 | 0.022681 | 0.02268 | 0.022681 | 0.98588 | -0.27036 | 0.98644 | -0.25959 | 6.2309
31 | 0.0055499 | 0.0013904 | -0.0055491 | -0.0013903 | 8.8076e-07 | 1.3772e-07 | 0.0083804 | 0.0083805 | 0.0083805 | 0.98542 | -0.2793 | 0.98525 | -0.28263 | 2.3023
32 | -0.02056 | -0.0051563 | 0.020564 | 0.0051583 | 3.3286e-06 | 2.0125e-06 | 0.031016 | 0.031016 | 0.031016 | 0.98644 | -0.25959 | 0.98661 | -0.2562 | 8.5209
33 | 0.0034806 | 0.00087186 | -0.00348 | -0.00087218 | 5.3959e-07 | -3.1772e-07 | 0.0052565 | 0.0052568 | 0.0052568 | 0.98525 | -0.28263 | 0.98509 | -0.28589 | 1.4442
34 | -0.025639 | -0.0064303 | 0.025663 | 0.0064455 | 2.4653e-05 | 1.5216e-05 | 0.03867 | 0.03867 | 0.03867 | 0.98661 | -0.2562 | 0.98765 | -0.23605 | 10.6237
35 | -0.0033819 | -0.00084759 | 0.0033821 | 0.00084745 | 2.0511e-07 | -1.3336e-07 | 0.0051192 | 0.0051191 | 0.0051192 | 0.98303 | -0.32656 | 0.9831 | -0.32529 | 1.4064
36 | 0.0063207 | 0.0015835 | -0.0063202 | -0.0015833 | 5.2537e-07 | 1.4216e-07 | 0.0095668 | 0.0095668 | 0.0095668 | 0.9831 | -0.32529 | 0.98301 | -0.32703 | 2.6283
37 | -0.0097028 | -0.0024309 | 0.0097038 | 0.0024314 | 1.0194e-06 | 4.9258e-07 | 0.014686 | 0.014686 | 0.014686 | 0.9831 | -0.32529 | 0.98321 | -0.32308 | 4.0346
38 | 0.005002 | 0.001253 | -0.0050016 | -0.001253 | 3.7857e-07 | 1.9062e-08 | 0.0075715 | 0.0075716 | 0.0075716 | 0.98301 | -0.32703 | 0.98293 | -0.32862 | 2.0801
39 | 0.0043414 | 0.0010877 | -0.0043412 | -0.0010878 | 1.701e-07 | -2.4393e-08 | 0.0065703 | 0.0065703 | 0.0065703 | 0.98321 | -0.32308 | 0.98317 | -0.3239 | 1.805
40 | -0.014045 | -0.0035192 | 0.014047 | 0.0035204 | 2.1326e-06 | 1.2052e-06 | 0.021256 | 0.021256 | 0.021256 | 0.98321 | -0.32308 | 0.98337 | -0.31989 | 5.8396
41 | 0.0019302 | 0.00048317 | -0.0019301 | -0.0004834 | 6.8451e-08 | -2.272e-07 | 0.0029218 | 0.0029219 | 0.0029219 | 0.98293 | -0.32862 | 0.98289 | -0.32937 | 0.80271
42 | 0.0034964 | 0.00087601 | -0.0034961 | -0.0008762 | 3.2586e-07 | -1.8493e-07 | 0.0052917 | 0.0052918 | 0.0052918 | 0.98317 | -0.3239 | 0.98307 | -0.32586 | 1.4538
43 | -0.015427 | -0.003866 | 0.01543 | 0.0038678 | 3.0998e-06 | 1.7914e-06 | 0.023343 | 0.023343 | 0.023343 | 0.98337 | -0.31989 | 0.98359 | -0.31568 | 6.4129
44 | 0.0019301 | 0.0004834 | -0.00193 | -0.0004836 | 6.0248e-08 | -1.9994e-07 | 0.0029219 | 0.002922 | 0.002922 | 0.98289 | -0.32937 | 0.98286 | -0.33002 | 0.80273
45 | 0.0076596 | 0.0019199 | -0.0076582 | -0.0019193 | 1.4082e-06 | 5.4636e-07 | 0.011588 | 0.011588 | 0.011588 | 0.98359 | -0.31568 | 0.98339 | -0.31953 | 3.1835
46 | 0.017689 | 0.0044386 | -0.017684 | -0.0044358 | 4.7993e-06 | 2.8448e-06 | 0.026763 | 0.026763 | 0.026763 | 0.98359 | -0.31568 | 0.9833 | -0.32137 | 7.3524
47 | -0.040778 | -0.010226 | 0.040884 | 0.010293 | 0.00010529 | 6.6444e-05 | 0.061694 | 0.061693 | 0.061694 | 0.98359 | -0.31568 | 0.98636 | -0.26165 | 16.9488
48 | 0.059407 | 0.014949 | -0.059381 | -0.014933 | 2.6067e-05 | 1.6572e-05 | 0.089461 | 0.089461 | 0.089461 | 0.98836 | -0.22264 | 0.98789 | -0.23182 | 24.5772
49 | -0.066466 | -0.016719 | 0.066564 | 0.016781 | 9.7823e-05 | 6.2273e-05 | 0.10009 | 0.10009 | 0.10009 | 0.98836 | -0.22264 | 0.98995 | -0.19188 | 27.497
50 | 0.059381 | 0.014933 | -0.059341 | -0.014907 | 3.9904e-05 | 2.5368e-05 | 0.089461 | 0.089461 | 0.089461 | 0.98789 | -0.23182 | 0.98716 | -0.2459 | 24.5772
51 | -0.066564 | -0.016781 | 0.066619 | 0.016816 | 5.4715e-05 | 3.483e-05 | 0.10009 | 0.10009 | 0.10009 | 0.98995 | -0.19188 | 0.99084 | -0.17471 | 27.4969
52 | 0.050664 | 0.012733 | -0.050605 | -0.012695 | 5.9044e-05 | 3.7443e-05 | 0.076382 | 0.076383 | 0.076383 | 0.98716 | -0.2459 | 0.98591 | -0.27034 | 20.9842
53 | -0.07292 | -0.018395 | 0.072976 | 0.018431 | 5.5748e-05 | 3.5519e-05 | 0.10955 | 0.10955 | 0.10955 | 0.99084 | -0.17471 | 0.99166 | -0.15876 | 30.0969
54 | 0.030244 | 0.0075918 | -0.030211 | -0.0075717 | 3.2319e-05 | 2.0157e-05 | 0.045651 | 0.045651 | 0.045651 | 0.98591 | -0.27034 | 0.98476 | -0.29277 | 12.5414
55 | 0.020362 | 0.0051036 | -0.020361 | -0.0051028 | 1.3195e-06 | 7.97e-07 | 0.030732 | 0.030732 | 0.030732 | 0.98591 | -0.27034 | 0.98584 | -0.2717 | 8.4429
56 | 0.22556 | 0.057374 | -0.22544 | -0.057298 | 0.00011932 | 7.579e-05 | 0.33876 | 0.33876 | 0.33876 | 0.99166 | -0.15876 | 0.99109 | -0.16974 | 23.2663
57 | 0.22126 | 0.056251 | -0.22121 | -0.056217 | 5.4293e-05 | 3.4477e-05 | 0.33249 | 0.33249 | 0.33249 | 0.99109 | -0.16974 | 0.99083 | -0.17484 | 22.8356
58 | 0.21137 | 0.053752 | -0.21134 | -0.053731 | 3.3258e-05 | 2.1104e-05 | 0.31772 | 0.31772 | 0.31772 | 0.99083 | -0.17484 | 0.99066 | -0.17811 | 21.8212
59 | 0.20648 | 0.052513 | -0.20591 | -0.052146 | 0.00057466 | 0.00036697 | 0.31042 | 0.31042 | 0.31042 | 0.99066 | -0.17811 | 0.98765 | -0.23605 | 42.64
60 | 0.18024 | 0.045701 | -0.18011 | -0.045617 | 0.00013057 | 8.3325e-05 | 0.27175 | 0.27175 | 0.27175 | 0.98765 | -0.23605 | 0.98686 | -0.25113 | 37.3282
61 | 0.16555 | 0.041965 | -0.16547 | -0.041916 | 7.672e-05 | 4.8933e-05 | 0.24979 | 0.24979 | 0.24979 | 0.98686 | -0.25113 | 0.98636 | -0.26078 | 34.3112
62 | 0.014566 | 0.003653 | -0.014558 | -0.0036485 | 7.8018e-06 | 4.4424e-06 | 0.021963 | 0.021963 | 0.021963 | 0.98686 | -0.25113 | 0.98629 | -0.26237 | 6.0339
63 | 0.13365 | 0.033931 | -0.13307 | -0.033566 | 0.0005711 | 0.00036503 | 0.20177 | 0.20177 | 0.20177 | 0.98636 | -0.26078 | 0.98176 | -0.35 | 55.4317
64 | 0.031826 | 0.0079848 | -0.031805 | -0.0079719 | 2.0658e-05 | 1.2917e-05 | 0.048015 | 0.048015 | 0.048015 | 0.98636 | -0.26078 | 0.98567 | -0.2744 | 13.1909
65 | 0.10971 | 0.027707 | -0.10961 | -0.027644 | 9.9417e-05 | 6.3506e-05 | 0.16636 | 0.16636 | 0.16636 | 0.98176 | -0.35 | 0.98079 | -0.36893 | 45.7038
66 | 0.023362 | 0.0058585 | -0.023356 | -0.0058548 | 6.0959e-06 | 3.7375e-06 | 0.03541 | 0.03541 | 0.03541 | 0.98176 | -0.35 | 0.98148 | -0.35548 | 9.7279
67 | 0.022309 | 0.005592 | -0.022309 | -0.0055916 | 7.7438e-07 | 4.724e-07 | 0.03368 | 0.03368 | 0.03368 | 0.98567 | -0.2744 | 0.98563 | -0.27513 | 9.2527
68 | 0.10071 | 0.025412 | -0.10051 | -0.025283 | 0.00020188 | 0.00012891 | 0.15285 | 0.15285 | 0.15285 | 0.98079 | -0.36893 | 0.97864 | -0.41089 | 41.992
69 | 0.02044 | 0.0051241 | -0.020439 | -0.0051236 | 8.9811e-07 | 5.4328e-07 | 0.03099 | 0.03099 | 0.03099 | 0.98148 | -0.35548 | 0.98144 | -0.3564 | 8.5136
70 | 0.019966 | 0.0050046 | -0.019966 | -0.0050046 | 2.9324e-08 | 1.7671e-08 | 0.030144 | 0.030144 | 0.030144 | 0.98563 | -0.27513 | 0.98563 | -0.27516 | 8.2813
71 | 0.011263 | 0.0028237 | -0.011259 | -0.0028217 | 3.656e-06 | 1.9175e-06 | 0.017076 | 0.017076 | 0.017076 | 0.98144 | -0.3564 | 0.98109 | -0.36322 | 4.6913
72 | 0.0091657 | 0.002298 | -0.009163 | -0.0022967 | 2.6956e-06 | 1.2603e-06 | 0.013937 | 0.013937 | 0.013937 | 0.97864 | -0.41089 | 0.97833 | -0.41706 | 3.8288
73 | 0.09134 | 0.022985 | -0.091285 | -0.02295 | 5.4259e-05 | 3.4631e-05 | 0.13891 | 0.13891 | 0.13891 | 0.97864 | -0.41089 | 0.97801 | -0.42332 | 38.1632
74 | 0.009163 | 0.0022967 | -0.0091617 | -0.0022961 | 1.2631e-06 | 5.9067e-07 | 0.013937 | 0.013937 | 0.013937 | 0.97833 | -0.41706 | 0.97818 | -0.41995 | 3.8288
75 | 0.0076857 | 0.0019263 | -0.007685 | -0.001926 | 6.9132e-07 | 2.7328e-07 | 0.011694 | 0.011694 | 0.011694 | 0.97801 | -0.42332 | 0.97791 | -0.42521 | 3.2125
76 | 0.0836 | 0.021024 | -0.083532 | -0.020981 | 6.8019e-05 | 4.3391e-05 | 0.12722 | 0.12722 | 0.12722 | 0.97801 | -0.42332 | 0.97714 | -0.44037 | 34.9507
77 | 0.070299 | 0.017664 | -0.070269 | -0.017645 | 3.007e-05 | 1.9157e-05 | 0.10707 | 0.10707 | 0.10707 | 0.97714 | -0.44037 | 0.97668 | -0.44934 | 29.4148
78 | 0.054371 | 0.01366 | -0.054328 | -0.013633 | 4.2712e-05 | 2.7128e-05 | 0.082849 | 0.082849 | 0.082849 | 0.97668 | -0.44934 | 0.97585 | -0.46581 | 22.7606
79 | 0.015898 | 0.0039848 | -0.015895 | -0.0039832 | 2.7296e-06 | 1.5917e-06 | 0.024221 | 0.024221 | 0.024221 | 0.97668 | -0.44934 | 0.9765 | -0.45294 | 6.6542
80 | 0.045513 | 0.011424 | -0.045513 | -0.011424 | 1.0724e-07 | 6.789e-08 | 0.069406 | 0.069406 | 0.069406 | 0.97585 | -0.46581 | 0.97584 | -0.46586 | 19.0676
81 | 0.0087416 | 0.0021904 | -0.0087414 | -0.0021903 | 1.9547e-07 | 8.8353e-08 | 0.013321 | 0.013321 | 0.013321 | 0.9765 | -0.45294 | 0.97648 | -0.45341 | 3.6595
82 | 0.033501 | 0.008413 | -0.033484 | -0.0084029 | 1.6146e-05 | 1.0128e-05 | 0.051089 | 0.05109 | 0.05109 | 0.97584 | -0.46586 | 0.97533 | -0.47597 | 14.0356
83 | 0.0029597 | 0.00074124 | -0.0029595 | -0.00074136 | 1.2543e-07 | -1.2543e-07 | 0.0045099 | 0.00451 | 0.00451 | 0.97648 | -0.45341 | 0.97643 | -0.4543 | 1.239
84 | 0.021854 | 0.005488 | -0.021835 | -0.0054764 | 1.9131e-05 | 1.1672e-05 | 0.033345 | 0.033346 | 0.033346 | 0.97533 | -0.47597 | 0.9744 | -0.49433 | 9.1609
85 | 0.0029595 | 0.00074136 | -0.0029592 | -0.00074165 | 2.9011e-07 | -2.9001e-07 | 0.00451 | 0.0045102 | 0.0045102 | 0.97643 | -0.4543 | 0.97633 | -0.45636 | 1.2391
86 | 0.0055647 | 0.0013946 | -0.0055645 | -0.0013946 | 1.9406e-07 | 3.3546e-08 | 0.0084651 | 0.0084651 | 0.0084651 | 0.97818 | -0.41995 | 0.97815 | -0.42068 | 2.3256
87 | 0.021835 | 0.0054764 | -0.021824 | -0.00547 | 1.0473e-05 | 6.3899e-06 | 0.033346 | 0.033346 | 0.033346 | 0.9744 | -0.49433 | 0.97389 | -0.5044 | 9.1609
88 | 0.0019035 | 0.00047677 | -0.0019034 | -0.00047704 | 8.267e-08 | -2.7138e-07 | 0.0029083 | 0.0029084 | 0.0029084 | 0.97389 | -0.5044 | 0.97384 | -0.50531 | 0.79901
89 | 0.019921 | 0.0049932 | -0.019919 | -0.0049924 | 1.3656e-06 | 8.2505e-07 | 0.030438 | 0.030438 | 0.030438 | 0.97389 | -0.5044 | 0.97382 | -0.50584 | 8.362
90 | 0.0089017 | 0.0022311 | -0.0089008 | -0.0022306 | 9.2211e-07 | 4.2482e-07 | 0.013602 | 0.013602 | 0.013602 | 0.97382 | -0.50584 | 0.97371 | -0.50801 | 3.7368
91 | -0.01147 | -0.0028746 | 0.011471 | 0.0028755 | 1.7322e-06 | 9.1237e-07 | 0.017319 | 0.017319 | 0.017319 | 0.98546 | -0.27842 | 0.98562 | -0.27525 | 4.758
92 | -0.013179 | -0.0033033 | 0.013179 | 0.0033034 | 5.7646e-08 | 3.1944e-08 | 0.019896 | 0.019896 | 0.019896 | 0.98562 | -0.27525 | 0.98563 | -0.27516 | 5.466
93 | 0.0082436 | 0.0020659 | -0.0082424 | -0.0020654 | 1.1383e-06 | 4.9064e-07 | 0.012598 | 0.012598 | 0.012598 | 0.97371 | -0.50801 | 0.97356 | -0.51091 | 3.461
94 | 0.0072182 | 0.0018087 | -0.0072181 | -0.0018087 | 4.5207e-08 | 1.6617e-08 | 0.011032 | 0.011032 | 0.011032 | 0.97356 | -0.51091 | 0.97355 | -0.51104 | 3.0309
95 | 0.0062035 | 0.0015544 | -0.0062033 | -0.0015544 | 1.4938e-07 | 4.0507e-08 | 0.0094815 | 0.0094816 | 0.0094816 | 0.97355 | -0.51104 | 0.97353 | -0.51155 | 2.6048
96 | 0.0053473 | 0.0013398 | -0.0053463 | -0.0013397 | 9.8933e-07 | 1.4222e-07 | 0.0081731 | 0.0081733 | 0.0081733 | 0.97353 | -0.51155 | 0.97333 | -0.51543 | 2.2454
97 | 0.022675 | 0.0056883 | -0.022665 | -0.0056824 | 9.6334e-06 | 5.8745e-06 | 0.033888 | 0.033888 | 0.033888 | 0.99571 | -0.082471 | 0.99525 | -0.091387 | 9.3098
98 | -0.022675 | -0.0056883 | 0.022682 | 0.0056925 | 6.9487e-06 | 4.2372e-06 | 0.033888 | 0.033887 | 0.033888 | 0.99571 | -0.082471 | 0.99604 | -0.076045 | 9.3098
99 | 0.0035306 | 0.00088461 | -0.0035303 | -0.00088478 | 2.7753e-07 | -1.6751e-07 | 0.0052786 | 0.0052787 | 0.0052787 | 0.99525 | -0.091387 | 0.99516 | -0.093037 | 1.4502
100 | 0.019134 | 0.0047978 | -0.019128 | -0.0047939 | 6.4139e-06 | 3.8335e-06 | 0.028609 | 0.028609 | 0.028609 | 0.99525 | -0.091387 | 0.99488 | -0.098423 | 7.8597
101 | -0.024391 | -0.0061208 | 0.024402 | 0.0061275 | 1.0822e-05 | 6.6428e-06 | 0.036441 | 0.036441 | 0.036441 | 0.99604 | -0.076045 | 0.99653 | -0.066745 | 10.0112
102 | 0.0071627 | 0.0017953 | -0.0071614 | -0.0017948 | 1.3569e-06 | 4.5641e-07 | 0.010695 | 0.010696 | 0.010696 | 0.99653 | -0.066745 | 0.99632 | -0.070722 | 2.9383
103 | -0.031564 | -0.0079228 | 0.031568 | 0.0079251 | 3.8268e-06 | 2.3893e-06 | 0.047136 | 0.047136 | 0.047136 | 0.99653 | -0.066745 | 0.99666 | -0.064204 | 12.9495
104 | 0.0038804 | 0.00097244 | -0.0038802 | -0.00097248 | 1.1659e-07 | -3.904e-08 | 0.0058813 | 0.0058813 | 0.0058813 | 0.98177 | -0.35137 | 0.98173 | -0.352 | 1.6157
105 | -0.0084905 | -0.0021278 | 0.0084952 | 0.0021299 | 4.7598e-06 | 2.0764e-06 | 0.012869 | 0.012868 | 0.012869 | 0.98177 | -0.35137 | 0.98237 | -0.3396 | 3.5353
106 | -0.0084952 | -0.0021299 | 0.0084985 | 0.0021313 | 3.2428e-06 | 1.414e-06 | 0.012868 | 0.012868 | 0.012868 | 0.98237 | -0.3396 | 0.98278 | -0.33159 | 3.5352
107 | 0.0011931 | 0.0002988 | -0.001193 | -0.000299 | 2.0632e-08 | -2.0045e-07 | 0.0018063 | 0.0018064 | 0.0018064 | 0.98278 | -0.33159 | 0.98276 | -0.33196 | 0.49626
108 | -0.0096915 | -0.0024301 | 0.0096927 | 0.0024307 | 1.1812e-06 | 5.7058e-07 | 0.014674 | 0.014674 | 0.014674 | 0.98278 | -0.33159 | 0.98291 | -0.32904 | 4.0314
109 | -0.017678 | -0.004432 | 0.017684 | 0.0044358 | 6.4641e-06 | 3.8318e-06 | 0.026763 | 0.026763 | 0.026763 | 0.98291 | -0.32904 | 0.9833 | -0.32137 | 7.3524
110 | 0.0069322 | 0.0017374 | -0.0069315 | -0.0017372 | 7.5456e-07 | 2.4812e-07 | 0.010458 | 0.010458 | 0.010458 | 0.98636 | -0.26165 | 0.98625 | -0.26394 | 2.8731
111 | 0.0051356 | 0.0012868 | -0.0051355 | -0.0012868 | 1.3452e-07 | 9.7266e-09 | 0.0077452 | 0.0077452 | 0.0077452 | 0.98664 | -0.25631 | 0.98661 | -0.25686 | 2.1278
112 | 0.0081909 | 0.0020532 | -0.0081884 | -0.0020522 | 2.4673e-06 | 1.0286e-06 | 0.012353 | 0.012354 | 0.012354 | 0.98664 | -0.25631 | 0.98632 | -0.26263 | 3.3938
113 | 0.0035311 | 0.00088471 | -0.003531 | -0.00088474 | 5.6019e-08 | -3.1411e-08 | 0.0053255 | 0.0053255 | 0.0053255 | 0.98661 | -0.25686 | 0.98659 | -0.25719 | 1.4631
114 | -0.0015909 | -0.00039872 | 0.0015909 | 0.00039857 | 2.7544e-08 | -1.4528e-07 | 0.0023995 | 0.0023994 | 0.0023995 | 0.98658 | -0.25755 | 0.98659 | -0.25719 | 0.6592
115 | 0.0019401 | 0.00048617 | -0.0019401 | -0.00048623 | 1.5778e-08 | -5.2653e-08 | 0.0029261 | 0.0029261 | 0.0029261 | 0.98659 | -0.25719 | 0.98659 | -0.25736 | 0.80387
116 | 0.00193 | 0.0004836 | -0.00193 | -0.0004837 | 3.1483e-08 | -1.0447e-07 | 0.002922 | 0.002922 | 0.002922 | 0.98286 | -0.33002 | 0.98284 | -0.33036 | 0.80275
117 | 0.0052088 | 0.0013054 | -0.0052087 | -0.0013054 | 5.1732e-08 | 4.9343e-09 | 0.0078817 | 0.0078817 | 0.0078817 | 0.98339 | -0.31953 | 0.98338 | -0.31974 | 2.1653
118 | 0.0079823 | 0.0020007 | -0.0079813 | -0.0020003 | 9.8462e-07 | 3.8955e-07 | 0.011921 | 0.011921 | 0.011921 | 0.99638 | -0.069478 | 0.99625 | -0.072068 | 3.275
119 | -0.010826 | -0.0027133 | 0.010828 | 0.0027147 | 2.7209e-06 | 1.3797e-06 | 0.016167 | 0.016167 | 0.016167 | 0.99638 | -0.069478 | 0.99666 | -0.064204 | 4.4416
120 | -0.042397 | -0.01064 | 0.042421 | 0.010655 | 2.4435e-05 | 1.5427e-05 | 0.063303 | 0.063303 | 0.063303 | 0.99666 | -0.064204 | 0.99728 | -0.052125 | 17.3911
121 | -0.042913 | -0.010779 | 0.042917 | 0.010781 | 4.2259e-06 | 2.6687e-06 | 0.064037 | 0.064037 | 0.064037 | 0.99728 | -0.052125 | 0.99739 | -0.050062 | 17.5927
122 | -0.042917 | -0.010781 | 0.042965 | 0.010811 | 4.7625e-05 | 3.0075e-05 | 0.064037 | 0.064037 | 0.064037 | 0.99739 | -0.050062 | 0.9986 | -0.026838 | 17.5927
123 | -0.049724 | -0.012505 | 0.049729 | 0.012509 | 5.1686e-06 | 3.275e-06 | 0.074109 | 0.074109 | 0.074109 | 0.9986 | -0.026838 | 0.99871 | -0.024662 | 20.3596
124 | -0.056656 | -0.014245 | 0.056712 | 0.01428 | 5.5803e-05 | 3.544e-05 | 0.08443 | 0.08443 | 0.08443 | 0.99871 | -0.024662 | 0.99979 | -0.004059 | 23.195
125 | 0.0049973 | 0.0012522 | -0.0049973 | -0.0012522 | 7.1548e-10 | 4.7243e-11 | 0.0076397 | 0.0076397 | 0.0076397 | 0.97333 | -0.51543 | 0.97333 | -0.51544 | 2.0988
126 | 0.0046223 | 0.0011582 | -0.0046222 | -0.0011582 | 9.9018e-08 | -2.3492e-09 | 0.0070664 | 0.0070665 | 0.0070665 | 0.97333 | -0.51544 | 0.97331 | -0.51589 | 1.9413
127 | 0.0027258 | 0.00068297 | -0.0027258 | -0.00068297 | 3.4128e-09 | -4.3288e-09 | 0.0041672 | 0.0041672 | 0.0041672 | 0.97331 | -0.51589 | 0.97331 | -0.51591 | 1.1448
128 | 0.00077085 | 0.00019301 | -0.00077084 | -0.00019319 | 7.5214e-09 | -1.7468e-07 | 0.0011784 | 0.0011785 | 0.0011785 | 0.97331 | -0.51591 | 0.9733 | -0.51612 | 0.32376
129 | 0.00037369 | 9.3656e-05 | -0.00037369 | -9.3657e-05 | 7.7566e-12 | -8.1633e-10 | 0.00057132 | 0.00057132 | 0.00057132 | 0.9733 | -0.51612 | 0.9733 | -0.51612 | 0.15696

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57997 | 0.14783

## res_load
| p_mw | q_mvar
0 | 0.030391 | 0.0076168
1 | 0.014205 | 0.0035602
2 | 0.022891 | 0.0057371
3 | 0.023255 | 0.0058282
4 | 0.0047726 | 0.0011961
5 | 0.014137 | 0.003543
6 | 0.005252 | 0.0013163
7 | 0.020794 | 0.0052114
8 | 0.0051783 | 0.0012978
9 | 0.0090495 | 0.002268
10 | 0.0092842 | 0.0023268
11 | 0.00018627 | 4.6685e-05
12 | 0.0055259 | 0.0013849
13 | 0.0020685 | 0.00051841
14 | 0.0050751 | 0.0012719
15 | 0.00348 | 0.00087218
16 | 0.0073824 | 0.0018502
17 | 0.0033819 | 0.00084759
18 | 0.0013182 | 0.00033037
19 | 0.0030715 | 0.00076978
20 | 0.00084485 | 0.00021174
21 | 0.0013792 | 0.00034567
22 | 0.0034961 | 0.0008762
23 | 0.0070594 | 0.0017692
24 | 0.0086763 | 0.0021745
25 | 0.0063018 | 0.0015794
26 | 0.030211 | 0.0075717
27 | 0.020361 | 0.0051028
28 | 0.0041771 | 0.0010469
29 | 0.0098347 | 0.0024648
30 | 0.0048585 | 0.0012176
31 | 0.014558 | 0.0036485
32 | 0.0094957 | 0.0023799
33 | 0.0089056 | 0.0022319
34 | 0.0029154 | 0.00073067
35 | 0.0023421 | 0.00058699
36 | 0.0091767 | 0.0022999
37 | 0.011259 | 0.0028217
38 | 0.013233 | 0.0033164
39 | 0.0088156 | 0.0022094
40 | 0.0071535 | 0.0017928
41 | 0.007685 | 0.001926
42 | 0.012012 | 0.0030105
43 | 0.0057818 | 0.0014491
44 | 0.01163 | 0.0029149
45 | 0.003597 | 0.0009015
46 | 0.0029592 | 0.00074165
47 | 0.0019034 | 0.00047704
48 | 0.011018 | 0.0027613
49 | 0.01147 | 0.0028746
50 | 0.001707 | 0.00042782
51 | 0.0067878 | 0.0017012
52 | 0.00065719 | 0.00016471
53 | 0.0010243 | 0.00025671
54 | 0.0010146 | 0.00025429
55 | 0.00085603 | 0.00021454
56 | 0.0055645 | 0.0013946
57 | 0.0017091 | 0.00042835
58 | 0.0035303 | 0.00088478
59 | 0.019128 | 0.0047939
60 | 0.0046101 | 0.0011554
61 | 0.0038802 | 0.00097248
62 | 0.001193 | 0.000299
63 | 0.0079851 | 0.0020013
64 | 0.0069315 | 0.0017372
65 | 0.0016044 | 0.0004021
66 | 0.0081884 | 0.0020522
67 | 0.0015909 | 0.00039872
68 | 0.0019401 | 0.00048623
69 | 0.00193 | 0.0004837
70 | 0.0024494 | 0.00061388
71 | 0.0052087 | 0.0013054
72 | 0.0028435 | 0.00071265
73 | 0.0079813 | 0.0020003
74 | 0.00049187 | 0.00012327
75 | 0.0071614 | 0.0017948
76 | 0.0067593 | 0.001694
77 | 0.0069269 | 0.0017361
78 | 0.00034902 | 8.7472e-05
79 | 0.00037501 | 9.3986e-05
80 | 0.0018964 | 0.00047528
81 | 0.001955 | 0.00048996
82 | 0.00039714 | 9.9534e-05
83 | 0.00037369 | 9.3657e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1