## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_156-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_156-8_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_156-8_0_4_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_156-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_156-8_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_156-8_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_156-8_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_156-8_0_4_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_156-8_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_156-8_0_4_node_143 | 0.4 | n |  | TRUE
10 | bus_LV_156-8_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_156-8_0_4_node_96 | 0.4 | n |  | TRUE
12 | bus_LV_156-8_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_156-8_0_4_node_127 | 0.4 | n |  | TRUE
14 | bus_LV_156-8_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_156-8_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_156-8_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_156-8_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_156-8_0_4_node_113 | 0.4 | n |  | TRUE
19 | bus_LV_156-8_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_156-8_0_4_node_48 | 0.4 | n |  | TRUE
21 | bus_LV_156-8_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_156-8_0_4_node_129 | 0.4 | n |  | TRUE
23 | bus_LV_156-8_0_4_node_75 | 0.4 | n |  | TRUE
24 | bus_LV_156-8_0_4_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_156-8_0_4_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_156-8_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_156-8_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_156-8_0_4_node_73 | 0.4 | n |  | TRUE
29 | bus_LV_156-8_0_4_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_156-8_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_156-8_0_4_node_89 | 0.4 | n |  | TRUE
32 | bus_LV_156-8_0_4_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_156-8_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_156-8_0_4_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_156-8_0_4_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_156-8_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_156-8_0_4_node_135 | 0.4 | n |  | TRUE
38 | bus_LV_156-8_0_4_node_136 | 0.4 | n |  | TRUE
39 | bus_LV_156-8_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_156-8_0_4_node_139 | 0.4 | n |  | TRUE
41 | bus_LV_156-8_0_4_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_156-8_0_4_node_138 | 0.4 | n |  | TRUE
43 | bus_LV_156-8_0_4_node_95 | 0.4 | n |  | TRUE
44 | bus_LV_156-8_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_156-8_0_4_node_142 | 0.4 | n |  | TRUE
46 | bus_LV_156-8_0_4_node_94 | 0.4 | n |  | TRUE
47 | bus_LV_156-8_0_4_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_156-8_0_4_node_21 | 0.4 | n |  | TRUE
49 | bus_LV_156-8_0_4_node_92 | 0.4 | n |  | TRUE
50 | bus_LV_156-8_0_4_node_93 | 0.4 | n |  | TRUE
51 | bus_LV_156-8_0_4_node_140 | 0.4 | n |  | TRUE
52 | bus_LV_156-8_0_4_node_141 | 0.4 | n |  | TRUE
53 | bus_LV_156-8_0_4_node_72 | 0.4 | n |  | TRUE
54 | bus_LV_156-8_0_4_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_156-8_0_4_node_67 | 0.4 | n |  | TRUE
56 | bus_LV_156-8_0_4_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_156-8_0_4_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_156-8_0_4_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_156-8_0_4_node_130 | 0.4 | n |  | TRUE
60 | bus_LV_156-8_0_4_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_156-8_0_4_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_156-8_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_156-8_0_4_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_156-8_0_4_node_137 | 0.4 | n |  | TRUE
65 | bus_LV_156-8_0_4_node_91 | 0.4 | n |  | TRUE
66 | bus_LV_156-8_0_4_node_144 | 0.4 | n |  | TRUE
67 | bus_LV_156-8_0_4_node_111 | 0.4 | n |  | TRUE
68 | bus_LV_156-8_0_4_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_156-8_0_4_node_28 | 0.4 | n |  | TRUE
70 | bus_LV_156-8_0_4_node_29 | 0.4 | n |  | TRUE
71 | bus_LV_156-8_0_4_node_30 | 0.4 | n |  | TRUE
72 | bus_LV_156-8_0_4_node_31 | 0.4 | n |  | TRUE
73 | bus_LV_156-8_0_4_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_156-8_0_4_node_101 | 0.4 | n |  | TRUE
75 | bus_LV_156-8_0_4_node_33 | 0.4 | n |  | TRUE
76 | bus_LV_156-8_0_4_node_34 | 0.4 | n |  | TRUE
77 | bus_LV_156-8_0_4_node_36 | 0.4 | n |  | TRUE
78 | bus_LV_156-8_0_4_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_156-8_0_4_node_38 | 0.4 | n |  | TRUE
80 | bus_LV_156-8_0_4_node_132 | 0.4 | n |  | TRUE
81 | bus_LV_156-8_0_4_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_156-8_0_4_node_41 | 0.4 | n |  | TRUE
83 | bus_LV_156-8_0_4_node_123 | 0.4 | n |  | TRUE
84 | bus_LV_156-8_0_4_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_156-8_0_4_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_156-8_0_4_node_100 | 0.4 | n |  | TRUE
87 | bus_LV_156-8_0_4_node_125 | 0.4 | n |  | TRUE
88 | bus_LV_156-8_0_4_node_87 | 0.4 | n |  | TRUE
89 | bus_LV_156-8_0_4_node_59 | 0.4 | n |  | TRUE
90 | bus_LV_156-8_0_4_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_156-8_0_4_node_99 | 0.4 | n |  | TRUE
92 | bus_LV_156-8_0_4_node_118 | 0.4 | n |  | TRUE
93 | bus_LV_156-8_0_4_node_98 | 0.4 | n |  | TRUE
94 | bus_LV_156-8_0_4_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_156-8_0_4_node_124 | 0.4 | n |  | TRUE
96 | bus_LV_156-8_0_4_node_122 | 0.4 | n |  | TRUE
97 | bus_LV_156-8_0_4_node_112 | 0.4 | n |  | TRUE
98 | bus_LV_156-8_0_4_node_110 | 0.4 | n |  | TRUE
99 | bus_LV_156-8_0_4_node_46 | 0.4 | n |  | TRUE
100 | bus_LV_156-8_0_4_node_47 | 0.4 | n |  | TRUE
101 | bus_LV_156-8_0_4_node_55 | 0.4 | n |  | TRUE
102 | bus_LV_156-8_0_4_node_56 | 0.4 | n |  | TRUE
103 | bus_LV_156-8_0_4_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_156-8_0_4_node_50 | 0.4 | n |  | TRUE
105 | bus_LV_156-8_0_4_node_51 | 0.4 | n |  | TRUE
106 | bus_LV_156-8_0_4_node_52 | 0.4 | n |  | TRUE
107 | bus_LV_156-8_0_4_node_53 | 0.4 | n |  | TRUE
108 | bus_LV_156-8_0_4_node_54 | 0.4 | n |  | TRUE
109 | bus_LV_156-8_0_4_node_133 | 0.4 | n |  | TRUE
110 | bus_LV_156-8_0_4_node_62 | 0.4 | n |  | TRUE
111 | bus_LV_156-8_0_4_node_63 | 0.4 | n |  | TRUE
112 | bus_LV_156-8_0_4_node_64 | 0.4 | n |  | TRUE
113 | bus_LV_156-8_0_4_node_60 | 0.4 | n |  | TRUE
114 | bus_LV_156-8_0_4_node_61 | 0.4 | n |  | TRUE
115 | bus_LV_156-8_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_156-8_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_156-8_0_4_node_134 | 0.4 | n |  | TRUE
118 | bus_LV_156-8_0_4_node_84 | 0.4 | n |  | TRUE
119 | bus_LV_156-8_0_4_node_80 | 0.4 | n |  | TRUE
120 | bus_LV_156-8_0_4_node_131 | 0.4 | n |  | TRUE
121 | bus_LV_156-8_0_4_node_88 | 0.4 | n |  | TRUE
122 | bus_LV_156-8_0_4_node_79 | 0.4 | n |  | TRUE
123 | bus_LV_156-8_0_4_node_81 | 0.4 | n |  | TRUE
124 | bus_LV_156-8_0_4_node_83 | 0.4 | n |  | TRUE
125 | bus_LV_156-8_0_4_node_105 | 0.4 | n |  | TRUE
126 | bus_LV_156-8_0_4_node_104 | 0.4 | n |  | TRUE
127 | bus_LV_156-8_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_156-8_0_4_node_107 | 0.4 | n |  | TRUE
129 | bus_LV_156-8_0_4_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_156-8_0_4_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_156-8_0_4_node_106 | 0.4 | n |  | TRUE
132 | bus_LV_156-8_0_4_node_109 | 0.4 | n |  | TRUE
133 | bus_LV_156-8_0_4_node_108 | 0.4 | n |  | TRUE
134 | bus_LV_156-8_0_4_node_121 | 0.4 | n |  | TRUE
135 | bus_LV_156-8_0_4_node_119 | 0.4 | n |  | TRUE
136 | bus_LV_156-8_0_4_node_120 | 0.4 | n |  | TRUE
137 | bus_MV_496_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_156-8_0_4_load_0 | 0 | 0.019323 | 0.0048429 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_156-8_0_4_load_1 | 2 | 0.0028893 | 0.00072413 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_156-8_0_4_load_3 | 3 | 0.0085916 | 0.0021533 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_156-8_0_4_load_24 | 7 | 0.0032449 | 0.00081324 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_156-8_0_4_load_143 | 9 | 0.0029442 | 0.00073788 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_156-8_0_4_load_127 | 13 | 0.0018141 | 0.00045464 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_156-8_0_4_load_32 | 16 | 0.00857 | 0.0021478 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_156-8_0_4_load_113 | 18 | 0.0056441 | 0.0014145 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_156-8_0_4_load_48 | 20 | 0.0072566 | 0.0018187 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_156-8_0_4_load_129 | 22 | 0.0034376 | 0.00086154 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_156-8_0_4_load_66 | 24 | 0.00088174 | 0.00022099 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_156-8_0_4_load_49 | 25 | 0.0010276 | 0.00025754 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_156-8_0_4_load_77 | 29 | 0.014186 | 0.0035552 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_156-8_0_4_load_89 | 31 | 0.0054935 | 0.0013768 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_156-8_0_4_load_85 | 32 | 0.0042389 | 0.0010624 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_156-8_0_4_load_68 | 34 | 0.0011403 | 0.00028579 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_156-8_0_4_load_70 | 35 | 0.0054685 | 0.0013705 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_156-8_0_4_load_136 | 38 | 0.015639 | 0.0039195 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_156-8_0_4_load_139 | 40 | 0.0034473 | 0.00086398 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_156-8_0_4_load_138 | 42 | 0.016204 | 0.0040612 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_156-8_0_4_load_95 | 43 | 0.0011957 | 0.00029966 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_156-8_0_4_load_25 | 44 | 0.002372 | 0.00059449 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_156-8_0_4_load_142 | 45 | 0.0031864 | 0.0007986 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_156-8_0_4_load_94 | 46 | 0.0016432 | 0.00041182 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_156-8_0_4_load_23 | 47 | 0.021377 | 0.0053575 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_156-8_0_4_load_21 | 48 | 0.0072681 | 0.0018216 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_156-8_0_4_load_92 | 49 | 0.004043 | 0.0010133 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_156-8_0_4_load_140 | 51 | 0.011556 | 0.0028962 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_156-8_0_4_load_141 | 52 | 0.021745 | 0.0054497 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_156-8_0_4_load_67 | 55 | 0.0008173 | 0.00020484 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_156-8_0_4_load_26 | 56 | 0.0015838 | 0.00039693 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_156-8_0_4_load_130 | 59 | 0.0097898 | 0.0024536 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_156-8_0_4_load_71 | 60 | 0.014521 | 0.0036392 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_156-8_0_4_load_69 | 63 | 0.00079119 | 0.00019829 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_156-8_0_4_load_137 | 64 | 0.012751 | 0.0031957 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_156-8_0_4_load_144 | 66 | 0.0079081 | 0.001982 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_156-8_0_4_load_65 | 68 | 0.012691 | 0.0031806 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_156-8_0_4_load_28 | 69 | 0.0027325 | 0.00068482 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_156-8_0_4_load_30 | 71 | 0.0032102 | 0.00080456 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_156-8_0_4_load_31 | 72 | 0.02084 | 0.005223 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_156-8_0_4_load_33 | 75 | 0.0043216 | 0.0010831 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_156-8_0_4_load_34 | 76 | 0.0023605 | 0.00059159 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_156-8_0_4_load_36 | 77 | 0.0041678 | 0.0010445 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_156-8_0_4_load_44 | 78 | 0.0021546 | 0.00054 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_156-8_0_4_load_132 | 80 | 0.012467 | 0.0031246 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_156-8_0_4_load_126 | 84 | 0.0053033 | 0.0013291 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_156-8_0_4_load_125 | 87 | 0.0057804 | 0.0014487 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_156-8_0_4_load_57 | 90 | 0.0043837 | 0.0010986 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_156-8_0_4_load_118 | 92 | 0.0026686 | 0.00066881 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_156-8_0_4_load_98 | 93 | 0.0030185 | 0.0007565 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_156-8_0_4_load_97 | 94 | 0.0018702 | 0.00046871 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_156-8_0_4_load_124 | 95 | 0.011699 | 0.002932 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_156-8_0_4_load_122 | 96 | 0.0056902 | 0.0014261 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_156-8_0_4_load_112 | 97 | 0.0091705 | 0.0022983 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_156-8_0_4_load_46 | 99 | 0.0029729 | 0.00074508 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_156-8_0_4_load_47 | 100 | 0.0016984 | 0.00042565 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_156-8_0_4_load_55 | 101 | 0.0038007 | 0.00095254 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_156-8_0_4_load_56 | 102 | 0.0028196 | 0.00070666 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_156-8_0_4_load_103 | 103 | 0.015571 | 0.0039026 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_156-8_0_4_load_50 | 104 | 0.0032052 | 0.00080329 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_156-8_0_4_load_52 | 106 | 0.0053024 | 0.0013289 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_156-8_0_4_load_53 | 107 | 0.0027591 | 0.0006915 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_156-8_0_4_load_54 | 108 | 0.0030656 | 0.0007683 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_156-8_0_4_load_133 | 109 | 0.0032793 | 0.00082187 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_156-8_0_4_load_63 | 111 | 0.0010847 | 0.00027184 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_156-8_0_4_load_60 | 113 | 0.0036758 | 0.00092124 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_156-8_0_4_load_61 | 114 | 0.0017673 | 0.00044292 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_156-8_0_4_load_115 | 115 | 0.0011346 | 0.00028436 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_156-8_0_4_load_116 | 116 | 0.0012007 | 0.00030093 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_156-8_0_4_load_134 | 117 | 0.0030716 | 0.00076981 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_156-8_0_4_load_84 | 118 | 0.0015151 | 0.00037972 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_156-8_0_4_load_80 | 119 | 0.0026295 | 0.00065902 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_156-8_0_4_load_131 | 120 | 0.0017381 | 0.00043561 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_156-8_0_4_load_79 | 122 | 0.0017753 | 0.00044493 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_156-8_0_4_load_81 | 123 | 0.001485 | 0.00037218 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_156-8_0_4_load_83 | 124 | 0.0040565 | 0.0010167 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_156-8_0_4_load_105 | 125 | 0.0021791 | 0.00054614 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_156-8_0_4_load_104 | 126 | 0.002776 | 0.00069574 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_156-8_0_4_load_114 | 127 | 0.0032525 | 0.00081516 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_156-8_0_4_load_117 | 129 | 0.0023869 | 0.00059821 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_156-8_0_4_load_128 | 130 | 0.0017448 | 0.00043729 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_156-8_0_4_load_109 | 132 | 0.0081747 | 0.0020488 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_156-8_0_4_load_108 | 133 | 0.0047778 | 0.0011974 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_156-8_0_4_load_121 | 134 | 0.0012262 | 0.00030731 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_156-8_0_4_load_120 | 136 | 0.0015466 | 0.00038761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 117 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_156-8_0_4_line_0 |  | 0 | 1 | 0.1033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_156-8_0_4_line_1 |  | 1 | 3 | 0.017992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_156-8_0_4_line_2 |  | 1 | 4 | 0.075931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_156-8_0_4_line_3 |  | 1 | 2 | 0.022796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_156-8_0_4_line_4 |  | 4 | 14 | 0.031088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_156-8_0_4_line_5 |  | 4 | 15 | 0.093624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_156-8_0_4_line_6 |  | 4 | 5 | 0.077655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_156-8_0_4_line_7 |  | 5 | 6 | 0.03143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_156-8_0_4_line_8 |  | 5 | 7 | 0.0072386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_156-8_0_4_line_9 |  | 6 | 11 | 0.02173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_156-8_0_4_line_10 |  | 6 | 43 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_156-8_0_4_line_11 |  | 7 | 44 | 0.034746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_156-8_0_4_line_12 |  | 8 | 9 | 0.034172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_156-8_0_4_line_13 |  | 8 | 10 | 0.05881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_156-8_0_4_line_14 |  | 8 | 11 | 0.051755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_156-8_0_4_line_15 |  | 10 | 12 | 0.0499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_156-8_0_4_line_16 |  | 10 | 13 | 0.014387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_156-8_0_4_line_17 |  | 11 | 45 | 0.035177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_156-8_0_4_line_18 |  | 12 | 16 | 0.038393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_156-8_0_4_line_19 |  | 13 | 46 | 0.015846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_156-8_0_4_line_20 |  | 14 | 47 | 0.0080935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_156-8_0_4_line_21 |  | 14 | 48 | 0.041687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_156-8_0_4_line_22 |  | 15 | 17 | 0.10728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_156-8_0_4_line_23 |  | 15 | 18 | 0.029009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_156-8_0_4_line_24 |  | 17 | 19 | 0.046577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_156-8_0_4_line_25 |  | 17 | 20 | 0.051334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_156-8_0_4_line_26 |  | 19 | 24 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_156-8_0_4_line_27 |  | 19 | 25 | 0.019853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_156-8_0_4_line_28 |  | 19 | 21 | 0.032347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_156-8_0_4_line_29 |  | 21 | 22 | 0.044649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_156-8_0_4_line_30 |  | 21 | 23 | 0.024003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_156-8_0_4_line_31 |  | 23 | 51 | 0.010753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_156-8_0_4_line_32 |  | 23 | 52 | 0.012535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_156-8_0_4_line_33 |  | 23 | 53 | 0.027038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_156-8_0_4_line_34 |  | 24 | 55 | 0.00051332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_156-8_0_4_line_35 |  | 26 | 27 | 0.020748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_156-8_0_4_line_36 |  | 26 | 28 | 0.040541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_156-8_0_4_line_37 |  | 26 | 29 | 0.010263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_156-8_0_4_line_38 |  | 27 | 42 | 0.004317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_156-8_0_4_line_39 |  | 27 | 37 | 0.018282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_156-8_0_4_line_40 |  | 28 | 60 | 0.021854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_156-8_0_4_line_41 |  | 28 | 53 | 0.027455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_156-8_0_4_line_42 |  | 28 | 57 | 0.039995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_156-8_0_4_line_43 |  | 29 | 61 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_156-8_0_4_line_44 |  | 30 | 31 | 0.0069438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_156-8_0_4_line_45 |  | 30 | 32 | 0.014003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_156-8_0_4_line_46 |  | 31 | 41 | 0.030735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_156-8_0_4_line_47 |  | 32 | 62 | 0.015337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_156-8_0_4_line_48 |  | 33 | 34 | 0.020305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_156-8_0_4_line_49 |  | 33 | 35 | 0.019269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_156-8_0_4_line_50 |  | 34 | 55 | 0.025018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_156-8_0_4_line_51 |  | 35 | 63 | 0.012589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_156-8_0_4_line_52 |  | 36 | 37 | 0.017446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_156-8_0_4_line_53 |  | 36 | 38 | 0.005555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_156-8_0_4_line_54 |  | 37 | 64 | 0.005195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_156-8_0_4_line_55 |  | 39 | 40 | 0.032366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_156-8_0_4_line_56 |  | 39 | 41 | 0.048966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_156-8_0_4_line_57 |  | 44 | 56 | 0.056002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_156-8_0_4_line_58 |  | 46 | 50 | 0.005415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_156-8_0_4_line_59 |  | 47 | 68 | 0.011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_156-8_0_4_line_60 |  | 49 | 50 | 0.014213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_156-8_0_4_line_61 |  | 53 | 54 | 0.036252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_156-8_0_4_line_62 |  | 54 | 117 | 0.004858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_156-8_0_4_line_63 |  | 54 | 73 | 0.021362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_156-8_0_4_line_64 |  | 57 | 58 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_156-8_0_4_line_65 |  | 57 | 59 | 0.024764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_156-8_0_4_line_66 |  | 58 | 118 | 0.006438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_156-8_0_4_line_67 |  | 58 | 119 | 0.012905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_156-8_0_4_line_68 |  | 59 | 120 | 0.014557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_156-8_0_4_line_69 |  | 59 | 121 | 0.031807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_156-8_0_4_line_70 |  | 61 | 122 | 0.016466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_156-8_0_4_line_71 |  | 62 | 122 | 0.010869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_156-8_0_4_line_72 |  | 65 | 66 | 0.028363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_156-8_0_4_line_73 |  | 65 | 67 | 0.03751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_156-8_0_4_line_74 |  | 67 | 127 | 0.011496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_156-8_0_4_line_75 |  | 67 | 128 | 0.008429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_156-8_0_4_line_76 |  | 69 | 70 | 0.028798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_156-8_0_4_line_77 |  | 70 | 71 | 0.0064809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_156-8_0_4_line_78 |  | 70 | 72 | 0.012267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_156-8_0_4_line_79 |  | 71 | 73 | 0.021169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_156-8_0_4_line_80 |  | 73 | 74 | 0.055523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_156-8_0_4_line_81 |  | 74 | 103 | 0.019389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_156-8_0_4_line_82 |  | 74 | 100 | 0.014654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_156-8_0_4_line_83 |  | 75 | 76 | 0.0061633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_156-8_0_4_line_84 |  | 76 | 77 | 0.0061933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_156-8_0_4_line_85 |  | 77 | 78 | 0.032174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_156-8_0_4_line_86 |  | 78 | 85 | 0.0093851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_156-8_0_4_line_87 |  | 79 | 80 | 0.048241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_156-8_0_4_line_88 |  | 79 | 81 | 0.094564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_156-8_0_4_line_89 |  | 81 | 89 | 0.026152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_156-8_0_4_line_90 |  | 81 | 90 | 0.018551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_156-8_0_4_line_91 |  | 82 | 83 | 0.008082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_156-8_0_4_line_92 |  | 82 | 84 | 0.013386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_156-8_0_4_line_93 |  | 83 | 95 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_156-8_0_4_line_94 |  | 83 | 96 | 0.021023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_156-8_0_4_line_95 |  | 84 | 87 | 6.6318e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_156-8_0_4_line_96 |  | 85 | 99 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_156-8_0_4_line_97 |  | 85 | 100 | 0.0092353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_156-8_0_4_line_98 |  | 86 | 87 | 0.019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_156-8_0_4_line_99 |  | 86 | 88 | 0.040604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_156-8_0_4_line_100 |  | 88 | 121 | 0.018969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_156-8_0_4_line_101 |  | 88 | 125 | 0.057737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_156-8_0_4_line_102 |  | 88 | 91 | 0.018373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_156-8_0_4_line_103 |  | 89 | 109 | 0.02081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_156-8_0_4_line_104 |  | 89 | 110 | 0.01784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_156-8_0_4_line_105 |  | 91 | 92 | 0.024358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_156-8_0_4_line_106 |  | 92 | 129 | 0.014139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_156-8_0_4_line_107 |  | 93 | 94 | 0.021046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_156-8_0_4_line_108 |  | 94 | 112 | 0.040272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_156-8_0_4_line_109 |  | 97 | 98 | 0.009261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_156-8_0_4_line_110 |  | 98 | 132 | 0.013961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_156-8_0_4_line_111 |  | 99 | 101 | 0.00012175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_156-8_0_4_line_112 |  | 101 | 102 | 0.020712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_156-8_0_4_line_113 |  | 102 | 108 | 0.0014274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_156-8_0_4_line_114 |  | 103 | 130 | 0.035997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_156-8_0_4_line_115 |  | 104 | 105 | 0.0086766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_156-8_0_4_line_116 |  | 104 | 106 | 0.0051959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_156-8_0_4_line_117 |  | 105 | 107 | 0.014601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_156-8_0_4_line_118 |  | 105 | 108 | 0.0090159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_156-8_0_4_line_119 |  | 110 | 111 | 0.038932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_156-8_0_4_line_120 |  | 110 | 112 | 0.037213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_156-8_0_4_line_121 |  | 110 | 113 | 0.016342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_156-8_0_4_line_122 |  | 111 | 115 | 0.0084088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_156-8_0_4_line_123 |  | 113 | 114 | 0.0009102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_156-8_0_4_line_124 |  | 115 | 116 | 0.019446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_156-8_0_4_line_125 |  | 116 | 134 | 0.0090108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_156-8_0_4_line_126 |  | 119 | 123 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_156-8_0_4_line_127 |  | 123 | 124 | 0.0048487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_156-8_0_4_line_128 |  | 125 | 126 | 0.010581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_156-8_0_4_line_129 |  | 126 | 131 | 0.010729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_156-8_0_4_line_130 |  | 127 | 133 | 0.0071346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_156-8_0_4_line_131 |  | 128 | 132 | 0.01685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_156-8_0_4_line_132 |  | 128 | 131 | 0.01789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_156-8_0_4_line_133 |  | 129 | 135 | 0.01862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_156-8_0_4_line_134 |  | 134 | 135 | 0.0033615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_156-8_0_4_line_135 |  | 135 | 136 | 0.023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_156-8_0_4_trafo_134 | 0.63 MVA 20/0.4 kV | 137 | 117 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2691811.3932 | 1235753.7187 | 2691818.9808 | 1235751.5232 | 2691826.0969 | 1235752.4116 | 2691834.6727 | 1235752.3886 | 2691843.3835 | 1235750.9777 | 2691852.0869 | 1235748.0879 | 2691863.4624 | 1235740.7807 | 2691865.1679 | 1235736.2149 | 2691864.092 | 1235730.9055 | 2691847.0018 | 1235697.1353
1 | 2691811.3932 | 1235753.7187 | 2691818.9808 | 1235751.5232 | 2691826.0969 | 1235752.4116 | 2691829.019 | 1235752.4037
2 | 2691741.3648 | 1235776.8538 | 2691749.42 | 1235776.2333 | 2691755.7345 | 1235775.6081 | 2691768.8107 | 1235774.3091 | 2691781.2358 | 1235772.5331 | 2691794.2879 | 1235766.9195 | 2691811.3932 | 1235753.7187
3 | 2691811.3932 | 1235753.7187 | 2691797.0548 | 1235735.9972
4 | 2691741.3648 | 1235776.8538 | 2691721.3647 | 1235791.7781 | 2691718.0147 | 1235796.9746
5 | 2691732.8429 | 1235851.2874 | 2691738.0768 | 1235846.6204 | 2691742.9565 | 1235840.8805 | 2691756.2585 | 1235824.9632 | 2691752.4804 | 1235818.6781 | 2691750.5979 | 1235814.1346 | 2691749.5587 | 1235808.8925 | 2691749.42 | 1235776.2333 | 2691741.3648 | 1235776.8538
6 | 2691741.3648 | 1235776.8538 | 2691749.42 | 1235776.2333 | 2691749.1129 | 1235746.1512 | 2691747.236 | 1235741.7301 | 2691744.4523 | 1235738.1956 | 2691742.043 | 1235734.9227 | 2691747.9883 | 1235727.8205 | 2691748.1996 | 1235723.4539 | 2691749.6861 | 1235720.319 | 2691742.7745 | 1235714.5192
7 | 2691764.2618 | 1235691.5454 | 2691754.4675 | 1235701.3569 | 2691742.7745 | 1235714.5192
8 | 2691742.7745 | 1235714.5192 | 2691737.2689 | 1235709.8197 | 2691737.2689 | 1235709.8197
9 | 2691764.2618 | 1235691.5454 | 2691772.1724 | 1235685.1074 | 2691781.5861 | 1235678.3812
10 | 2691764.2618 | 1235691.5454 | 2691752.4203 | 1235679.5975
11 | 2691737.2689 | 1235709.8197 | 2691725.0213 | 1235726.0646 | 2691716.6661 | 1235737.794
12 | 2691827.579 | 1235654.619 | 2691823.3776 | 1235648.7832 | 2691820.386 | 1235641.0758 | 2691811.7495 | 1235624.4525
13 | 2691827.579 | 1235654.619 | 2691830.3043 | 1235653.6048 | 2691834.0004 | 1235652.4722 | 2691839.2826 | 1235651.064 | 2691843.9265 | 1235649.8126 | 2691851.4663 | 1235647.7832 | 2691853.3473 | 1235652.916 | 2691880.818 | 1235645.3797
14 | 2691827.579 | 1235654.619 | 2691823.6871 | 1235656.1822 | 2691804.6399 | 1235664.7497 | 2691783.6218 | 1235676.9338 | 2691781.5861 | 1235678.3812
15 | 2691880.818 | 1235645.3797 | 2691892.9877 | 1235642.0322 | 2691900.9972 | 1235668.3418 | 2691903.2885 | 1235671.4128 | 2691908.4191 | 1235674.4166
16 | 2691880.818 | 1235645.3797 | 2691884.3442 | 1235659.3278
17 | 2691781.5861 | 1235678.3812 | 2691759.9828 | 1235650.5718
18 | 2691908.4191 | 1235674.4166 | 2691906.1623 | 1235684.2777 | 2691903.8557 | 1235686.11 | 2691905.9547 | 1235693.2922 | 2691909.2373 | 1235701.7491 | 2691911.3755 | 1235706.3967 | 2691913.0984 | 1235709.6273
19 | 2691884.3442 | 1235659.3278 | 2691888.228 | 1235674.6901
20 | 2691718.0147 | 1235796.9746 | 2691713.6319 | 1235803.7787
21 | 2691718.0147 | 1235796.9746 | 2691705.3477 | 1235787.4611 | 2691703.786 | 1235785.1798 | 2691703.6559 | 1235782.3313 | 2691715.3524 | 1235765.8266
22 | 2691832.3737 | 1235832.5224 | 2691792.6104 | 1235838.2232 | 2691779.8819 | 1235840.5394 | 2691764.319 | 1235842.6005 | 2691757.816 | 1235842.7001 | 2691754.3302 | 1235841.9902 | 2691751.1997 | 1235840.8188 | 2691735.313 | 1235854.5391 | 2691733.785 | 1235852.5251 | 2691732.8429 | 1235851.2874
23 | 2691732.8429 | 1235851.2874 | 2691730.1429 | 1235853.603 | 2691716.8043 | 1235864.0603 | 2691709.995 | 1235869.1524
24 | 2691832.3737 | 1235832.5224 | 2691836.8876 | 1235826.4544 | 2691858.1267 | 1235824.4146 | 2691864.1185 | 1235824.5851 | 2691870.7222 | 1235825.8103 | 2691872.2561 | 1235821.0861
25 | 2691832.3737 | 1235832.5224 | 2691810.9166 | 1235845.2334 | 2691794.807 | 1235853.2903 | 2691787.0996 | 1235856.5852
26 | 2691872.2561 | 1235821.0861 | 2691877.8456 | 1235812.0327
27 | 2691872.2561 | 1235821.0861 | 2691867.3061 | 1235818.6412 | 2691863.5727 | 1235817.7939 | 2691853.1127 | 1235818.7554
28 | 2691872.2561 | 1235821.0861 | 2691870.7222 | 1235825.8103 | 2691876.4094 | 1235828.0554 | 2691882.5155 | 1235831.5969 | 2691894.1434 | 1235839.7604
29 | 2691894.1434 | 1235839.7604 | 2691889.1652 | 1235845.0095 | 2691882.0403 | 1235847.1453 | 2691866.3849 | 1235851.2729 | 2691853.7541 | 1235857.0596
30 | 2691894.1434 | 1235839.7604 | 2691907.3202 | 1235848.5817 | 2691913.2348 | 1235842.9803
31 | 2691913.2348 | 1235842.9803 | 2691916.8743 | 1235842.0692 | 2691923.9015 | 1235842.3337
32 | 2691913.2348 | 1235842.9803 | 2691914.0166 | 1235838.4335 | 2691912.206 | 1235830.7221
33 | 2691923.0215 | 1235859.0878 | 2691907.3202 | 1235848.5817 | 2691913.2348 | 1235842.9803
34 | 2691878.3483 | 1235811.9287 | 2691877.8456 | 1235812.0327 | 2691877.8456 | 1235812.0327
35 | 2691980.7578 | 1235872.1241 | 2691979.9109 | 1235869.6314 | 2691978.4489 | 1235865.3168 | 2691976.415 | 1235859.3142 | 2691981.6727 | 1235857.5277 | 2691983.2552 | 1235856.9962
36 | 2691945.8533 | 1235874.43 | 2691957.5621 | 1235882.7284 | 2691967.7208 | 1235874.8132 | 2691980.7578 | 1235872.1241
37 | 2691980.7578 | 1235872.1241 | 2691990.6704 | 1235869.4638
38 | 2691983.2552 | 1235856.9962 | 2691987.1446 | 1235855.0995
39 | 2691974.2606 | 1235841.0676 | 2691978.2127 | 1235848.3119 | 2691983.2552 | 1235856.9962
40 | 2691945.8533 | 1235874.43 | 2691958.0912 | 1235870.561 | 2691961.6043 | 1235867.5465 | 2691957.2167 | 1235867.4008
41 | 2691923.0215 | 1235859.0878 | 2691932.5163 | 1235865.6951 | 2691945.8533 | 1235874.43
42 | 2691945.8533 | 1235874.43 | 2691957.5621 | 1235882.7284 | 2691978.4869 | 1235897.5519
43 | 2692006.2187 | 1235865.2911 | 2691990.6704 | 1235869.4638
44 | 2692027.4628 | 1235837.5333 | 2692025.1961 | 1235830.9699
45 | 2692027.4628 | 1235837.5333 | 2692030.1101 | 1235844.9686 | 2692030.3959 | 1235851.0727
46 | 2692022.0872 | 1235800.5342 | 2692023.7178 | 1235826.6896 | 2692025.1961 | 1235830.9699
47 | 2692030.9814 | 1235866.3977 | 2692030.7185 | 1235857.9652 | 2692030.3959 | 1235851.0727
48 | 2691922.9448 | 1235803.9132 | 2691902.8925 | 1235807.1055
49 | 2691922.9448 | 1235803.9132 | 2691915.8646 | 1235792.3953 | 2691912.3682 | 1235787.8312
50 | 2691902.8925 | 1235807.1055 | 2691897.6103 | 1235807.9464 | 2691878.3483 | 1235811.9287
51 | 2691906.9885 | 1235776.5003 | 2691911.2872 | 1235786.4201 | 2691912.3682 | 1235787.8312
52 | 2691974.2606 | 1235841.0676 | 2691969.887 | 1235835.1289 | 2691964.7991 | 1235829.3793 | 2691962.9691 | 1235827.8054
53 | 2691966.375 | 1235823.4105 | 2691962.9691 | 1235827.8054
54 | 2691978.604 | 1235838.1994 | 2691974.2606 | 1235841.0676
55 | 2691996.0045 | 1235791.3014 | 2691990.3797 | 1235775.7474 | 2691986.3785 | 1235760.4299
56 | 2691996.0045 | 1235791.3014 | 2692019.5068 | 1235778.5227 | 2692021.4339 | 1235788.482 | 2692022.0872 | 1235800.5342
57 | 2691716.6661 | 1235737.794 | 2691713.2307 | 1235742.6169 | 2691698.6008 | 1235763.6508 | 2691685.4224 | 1235782.3499 | 2691684.5278 | 1235783.6559
58 | 2691889.5552 | 1235679.9399 | 2691888.228 | 1235674.6901
59 | 2691707.3132 | 1235813.5882 | 2691713.6319 | 1235803.7787
60 | 2691889.5552 | 1235679.9399 | 2691895.6471 | 1235692.7812
61 | 2691923.0215 | 1235859.0878 | 2691918.8924 | 1235864.2499 | 2691914.4967 | 1235868.0513 | 2691908.5398 | 1235871.495 | 2691900.4981 | 1235876.1407 | 2691893.663 | 1235879.6042
62 | 2691890.7181 | 1235875.7336 | 2691893.663 | 1235879.6042
63 | 2691874.6145 | 1235889.2722 | 2691877.3457 | 1235887.8689 | 2691893.663 | 1235879.6042
64 | 2691968.2025 | 1235910.1686 | 2691972.3099 | 1235907.3857 | 2691978.4869 | 1235897.5519
65 | 2691978.4869 | 1235897.5519 | 2691998.645 | 1235912.019
66 | 2691968.2025 | 1235910.1686 | 2691970.2878 | 1235916.2608
67 | 2691968.2025 | 1235910.1686 | 2691962.6986 | 1235912.2182 | 2691955.9882 | 1235914.3192
68 | 2691998.645 | 1235912.019 | 2691995.6325 | 1235921.3124 | 2691991.397 | 1235923.5707
69 | 2692024.5369 | 1235930.6001 | 2691998.645 | 1235912.019
70 | 2692006.2187 | 1235865.2911 | 2692010.7712 | 1235864.0719 | 2692016.9426 | 1235863.4003 | 2692022.3758 | 1235862.2925
71 | 2692030.9814 | 1235866.3977 | 2692026.4714 | 1235861.4575 | 2692022.3758 | 1235862.2925
72 | 2692086.0347 | 1235820.6062 | 2692059.0782 | 1235829.6617
73 | 2692086.0347 | 1235820.6062 | 2692095.751 | 1235856.8387
74 | 2692095.751 | 1235856.8387 | 2692085.4167 | 1235861.8741
75 | 2692095.751 | 1235856.8387 | 2692097.6121 | 1235861.7711 | 2692098.8689 | 1235864.6705
76 | 2691885.2404 | 1235914.7328 | 2691889.5734 | 1235920.3594 | 2691892.2573 | 1235922.5025 | 2691895.4543 | 1235921.8181 | 2691909.8549 | 1235917.6489
77 | 2691885.2404 | 1235914.7328 | 2691884.2091 | 1235913.3936 | 2691882.4384 | 1235908.9422
78 | 2691885.2404 | 1235914.7328 | 2691881.8979 | 1235916.9939 | 2691879.4 | 1235920.4355 | 2691877.9425 | 1235924.1379
79 | 2691874.6145 | 1235889.2722 | 2691882.4384 | 1235908.9422
80 | 2691821.6 | 1235906.1538 | 2691854.0344 | 1235896.6705 | 2691866.2987 | 1235892.5571 | 2691874.6145 | 1235889.2722
81 | 2691821.6 | 1235906.1538 | 2691822.5239 | 1235916.3978 | 2691825.1901 | 1235925.1023
82 | 2691821.6 | 1235906.1538 | 2691818.1208 | 1235906.9785 | 2691807.4735 | 1235910.0399
83 | 2691753.6735 | 1235928.7301 | 2691747.9725 | 1235931.072
84 | 2691753.6735 | 1235928.7301 | 2691759.4023 | 1235926.3767
85 | 2691789.7153 | 1235915.6219 | 2691765.3553 | 1235923.9312 | 2691759.4023 | 1235926.3767
86 | 2691798.5978 | 1235912.592 | 2691789.7153 | 1235915.6219
87 | 2691766.5777 | 1236034.8418 | 2691760.1011 | 1236005.8207 | 2691760.3066 | 1236001.8321 | 2691763.4044 | 1235999.2336 | 2691773.3052 | 1235995.7284
88 | 2691766.5777 | 1236034.8418 | 2691795.7214 | 1236027.6534 | 2691857.8772 | 1236009.3229
89 | 2691857.8772 | 1236009.3229 | 2691882.8627 | 1236001.3701
90 | 2691857.8772 | 1236009.3229 | 2691852.0776 | 1235991.702
91 | 2692071.0331 | 1235987.5507 | 2692079.1393 | 1235987.5319
92 | 2692079.1393 | 1235987.5319 | 2692079.0671 | 1235978.5242 | 2692079.0468 | 1235974.1466
93 | 2692071.0331 | 1235987.5507 | 2692069.3159 | 1236007.5053 | 2692069.2187 | 1236008.949
94 | 2692071.0331 | 1235987.5507 | 2692050.0098 | 1235987.6074
95 | 2692079.0465 | 1235974.0803 | 2692079.0468 | 1235974.1466
96 | 2691798.5978 | 1235912.592 | 2691804.1079 | 1235927.7735
97 | 2691798.5978 | 1235912.592 | 2691807.4735 | 1235910.0399
98 | 2692079.0214 | 1235954.1391 | 2692078.982 | 1235960.0984 | 2692079.0465 | 1235974.0803
99 | 2692079.0214 | 1235954.1391 | 2692069.1018 | 1235951.5168 | 2692058.7396 | 1235948.1538 | 2692040.8096 | 1235940.3481
100 | 2692024.5369 | 1235930.6001 | 2692033.3183 | 1235935.851 | 2692040.8096 | 1235940.3481
101 | 2692040.8096 | 1235940.3481 | 2692050.8762 | 1235922.7468 | 2692068.6861 | 1235901.2071 | 2692073.6302 | 1235895.2349 | 2692074.7515 | 1235893.8808
102 | 2692029.8344 | 1235955.0444 | 2692034.2078 | 1235950.242 | 2692040.8096 | 1235940.3481
103 | 2691882.8627 | 1236001.3701 | 2691878.6918 | 1235987.2287 | 2691876.8638 | 1235985.5325 | 2691873.3398 | 1235984.8553
104 | 2691882.8627 | 1236001.3701 | 2691892.2922 | 1235998.0024 | 2691899.7246 | 1235995.5489
105 | 2692029.8344 | 1235955.0444 | 2692019.596 | 1235957.8545 | 2692006.5177 | 1235962.0704
106 | 2691993.0459 | 1235966.3606 | 2691999.6516 | 1235964.2837 | 2692006.5177 | 1235962.0704
107 | 2691940.5786 | 1236020.0852 | 2691961.2488 | 1236016.1264
108 | 2691901.0012 | 1236026.0242 | 2691905.6518 | 1236026.7744 | 2691940.5786 | 1236020.0852
109 | 2692112.0758 | 1235892.5066 | 2692116.4342 | 1235900.6779
110 | 2692112.0758 | 1235892.5066 | 2692106.0916 | 1235879.8937
111 | 2691804.1494 | 1235927.888 | 2691804.1079 | 1235927.7735
112 | 2691804.1494 | 1235927.888 | 2691811.2159 | 1235947.3577
113 | 2691811.2159 | 1235947.3577 | 2691811.7029 | 1235948.6995
114 | 2691846.7072 | 1235943.2022 | 2691837.0752 | 1235945.9553 | 2691833.0513 | 1235945.3037 | 2691830.2474 | 1235941.6133 | 2691825.1901 | 1235925.1023
115 | 2691814.7788 | 1235957.1744 | 2691807.2424 | 1235961.474
116 | 2691802.7294 | 1235964.0488 | 2691807.2424 | 1235961.474
117 | 2691829.4227 | 1235957.2563 | 2691814.7788 | 1235957.1744
118 | 2691814.7788 | 1235957.1744 | 2691811.7029 | 1235948.6995
119 | 2691899.7246 | 1235995.5489 | 2691936.8857 | 1235983.9403
120 | 2691901.0012 | 1236026.0242 | 2691898.1266 | 1236019.0858 | 2691894.8333 | 1236007.4152 | 2691892.2922 | 1235998.0024 | 2691899.7246 | 1235995.5489
121 | 2691899.7246 | 1235995.5489 | 2691894.713 | 1235979.9947
122 | 2691936.8857 | 1235983.9403 | 2691944.9119 | 1235981.433
123 | 2691894.4279 | 1235979.1303 | 2691894.6262 | 1235979.7252 | 2691894.713 | 1235979.9947
124 | 2691963.4738 | 1235975.6345 | 2691944.9119 | 1235981.433
125 | 2691963.4738 | 1235975.6345 | 2691972.0747 | 1235972.9477
126 | 2691955.9882 | 1235914.3192 | 2691943.5359 | 1235918.2178
127 | 2691938.9087 | 1235919.6666 | 2691943.5359 | 1235918.2178
128 | 2692079.4218 | 1235884.4067 | 2692075.1574 | 1235893.3906 | 2692074.7515 | 1235893.8808
129 | 2692084.0223 | 1235874.7144 | 2692079.4218 | 1235884.4067
130 | 2692085.4167 | 1235861.8741 | 2692079.0029 | 1235864.9992
131 | 2692098.8689 | 1235864.6705 | 2692106.0916 | 1235879.8937
132 | 2692084.0223 | 1235874.7144 | 2692098.8689 | 1235864.6705
133 | 2691975.2833 | 1235971.9453 | 2691993.0459 | 1235966.3606
134 | 2691975.2833 | 1235971.9453 | 2691972.0747 | 1235972.9477
135 | 2691975.2833 | 1235971.9453 | 2691976.7507 | 1235976.4046 | 2691978.3615 | 1235985.2805 | 2691977.7563 | 1235994.5445

## bus_geodata
| x | y | coords
0 | 2691847.0018 | 1235697.1353
1 | 2691811.3932 | 1235753.7187
2 | 2691797.0548 | 1235735.9972
3 | 2691829.019 | 1235752.4037
4 | 2691741.3648 | 1235776.8538
5 | 2691742.7745 | 1235714.5192
6 | 2691764.2618 | 1235691.5454
7 | 2691737.2689 | 1235709.8197
8 | 2691827.579 | 1235654.619
9 | 2691811.7495 | 1235624.4525
10 | 2691880.818 | 1235645.3797
11 | 2691781.5861 | 1235678.3812
12 | 2691908.4191 | 1235674.4166
13 | 2691884.3442 | 1235659.3278
14 | 2691718.0147 | 1235796.9746
15 | 2691732.8429 | 1235851.2875
16 | 2691913.0984 | 1235709.6273
17 | 2691832.3737 | 1235832.5224
18 | 2691709.995 | 1235869.1524
19 | 2691872.2561 | 1235821.0861
20 | 2691787.0996 | 1235856.5852
21 | 2691894.1434 | 1235839.7604
22 | 2691853.7541 | 1235857.0596
23 | 2691913.2348 | 1235842.9803
24 | 2691877.8456 | 1235812.0327
25 | 2691853.1127 | 1235818.7554
26 | 2691980.7578 | 1235872.1241
27 | 2691983.2552 | 1235856.9962
28 | 2691945.8533 | 1235874.43
29 | 2691990.6704 | 1235869.4639
30 | 2692027.4628 | 1235837.5333
31 | 2692025.1961 | 1235830.9699
32 | 2692030.3959 | 1235851.0727
33 | 2691922.9448 | 1235803.9132
34 | 2691902.8925 | 1235807.1055
35 | 2691912.3682 | 1235787.8312
36 | 2691962.9691 | 1235827.8054
37 | 2691974.2606 | 1235841.0676
38 | 2691966.375 | 1235823.4105
39 | 2691996.0045 | 1235791.3014
40 | 2691986.3785 | 1235760.4299
41 | 2692022.0872 | 1235800.5342
42 | 2691987.1446 | 1235855.0995
43 | 2691752.4203 | 1235679.5975
44 | 2691716.6661 | 1235737.794
45 | 2691759.9828 | 1235650.5718
46 | 2691888.228 | 1235674.6901
47 | 2691713.6319 | 1235803.7787
48 | 2691715.3524 | 1235765.8266
49 | 2691895.6471 | 1235692.7812
50 | 2691889.5552 | 1235679.9399
51 | 2691923.9015 | 1235842.3337
52 | 2691912.206 | 1235830.7221
53 | 2691923.0215 | 1235859.0878
54 | 2691893.663 | 1235879.6042
55 | 2691878.3483 | 1235811.9287
56 | 2691684.5278 | 1235783.6559
57 | 2691978.4869 | 1235897.5519
58 | 2691968.2025 | 1235910.1686
59 | 2691998.645 | 1235912.019
60 | 2691957.2167 | 1235867.4008
61 | 2692006.2187 | 1235865.2911
62 | 2692030.9814 | 1235866.3977
63 | 2691906.9885 | 1235776.5003
64 | 2691978.604 | 1235838.1994
65 | 2692086.0347 | 1235820.6062
66 | 2692059.0782 | 1235829.6617
67 | 2692095.751 | 1235856.8387
68 | 2691707.3132 | 1235813.5882
69 | 2691909.8549 | 1235917.6489
70 | 2691885.2404 | 1235914.7328
71 | 2691882.4384 | 1235908.9422
72 | 2691877.9425 | 1235924.1379
73 | 2691874.6145 | 1235889.2722
74 | 2691821.6 | 1235906.1538
75 | 2691747.9725 | 1235931.072
76 | 2691753.6735 | 1235928.7301
77 | 2691759.4023 | 1235926.3767
78 | 2691789.7153 | 1235915.6219
79 | 2691766.5777 | 1236034.8418
80 | 2691773.3052 | 1235995.7284
81 | 2691857.8772 | 1236009.3229
82 | 2692079.1393 | 1235987.5319
83 | 2692071.0331 | 1235987.5508
84 | 2692079.0468 | 1235974.1466
85 | 2691798.5978 | 1235912.592
86 | 2692079.0214 | 1235954.1391
87 | 2692079.0465 | 1235974.0803
88 | 2692040.8096 | 1235940.3481
89 | 2691882.8627 | 1236001.3701
90 | 2691852.0776 | 1235991.702
91 | 2692029.8344 | 1235955.0444
92 | 2692006.5177 | 1235962.0704
93 | 2691961.2488 | 1236016.1264
94 | 2691940.5786 | 1236020.0852
95 | 2692069.2187 | 1236008.949
96 | 2692050.0098 | 1235987.6074
97 | 2692116.4343 | 1235900.6779
98 | 2692112.0758 | 1235892.5066
99 | 2691804.1079 | 1235927.7735
100 | 2691807.4735 | 1235910.0399
101 | 2691804.1494 | 1235927.888
102 | 2691811.2159 | 1235947.3577
103 | 2691825.1901 | 1235925.1023
104 | 2691807.2424 | 1235961.474
105 | 2691814.7788 | 1235957.1744
106 | 2691802.7294 | 1235964.0488
107 | 2691829.4227 | 1235957.2563
108 | 2691811.7029 | 1235948.6995
109 | 2691873.3398 | 1235984.8553
110 | 2691899.7246 | 1235995.5489
111 | 2691936.8857 | 1235983.9403
112 | 2691901.0012 | 1236026.0242
113 | 2691894.713 | 1235979.9947
114 | 2691894.4279 | 1235979.1303
115 | 2691944.9119 | 1235981.433
116 | 2691963.4738 | 1235975.6345
117 | 2691890.7181 | 1235875.7336
118 | 2691970.2878 | 1235916.2608
119 | 2691955.9882 | 1235914.3192
120 | 2691991.397 | 1235923.5707
121 | 2692024.5369 | 1235930.6001
122 | 2692022.3758 | 1235862.2925
123 | 2691943.5359 | 1235918.2178
124 | 2691938.9086 | 1235919.6666
125 | 2692074.7515 | 1235893.8808
126 | 2692079.4218 | 1235884.4067
127 | 2692085.4167 | 1235861.8741
128 | 2692098.8689 | 1235864.6705
129 | 2691993.0459 | 1235966.3606
130 | 2691846.7072 | 1235943.2022
131 | 2692084.0223 | 1235874.7144
132 | 2692106.0916 | 1235879.8937
133 | 2692079.0029 | 1235864.9992
134 | 2691972.0747 | 1235972.9477
135 | 2691975.2833 | 1235971.9453
136 | 2691977.7563 | 1235994.5445
137 | 2691893.663 | 1235879.6042

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97397 | -0.50146 | 0.019323 | 0.0048429
1 | 0.97583 | -0.46485 | 0 | 0
2 | 0.97577 | -0.46606 | 0.0028893 | 0.00072413
3 | 0.97568 | -0.46768 | 0.0085916 | 0.0021533
4 | 0.978 | -0.42213 | 0 | 0
5 | 0.97579 | -0.46555 | 0 | 0
6 | 0.97511 | -0.47902 | 0 | 0
7 | 0.97574 | -0.4665 | 0.0032449 | 0.00081324
8 | 0.97374 | -0.50596 | 0 | 0
9 | 0.97365 | -0.50781 | 0.0029442 | 0.00073788
10 | 0.97286 | -0.52335 | 0 | 0
11 | 0.97466 | -0.48788 | 0 | 0
12 | 0.97246 | -0.53123 | 0 | 0
13 | 0.97276 | -0.52534 | 0.0018141 | 0.00045464
14 | 0.97681 | -0.44558 | 0 | 0
15 | 0.98695 | -0.2484 | 0 | 0
16 | 0.97215 | -0.5373 | 0.00857 | 0.0021478
17 | 0.99236 | -0.1449 | 0 | 0
18 | 0.9868 | -0.25133 | 0.0056441 | 0.0014145
19 | 0.99362 | -0.12109 | 0 | 0
20 | 0.99202 | -0.1515 | 0.0072566 | 0.0018187
21 | 0.99456 | -0.10314 | 0 | 0
22 | 0.99442 | -0.10585 | 0.0034376 | 0.00086154
23 | 0.99528 | -0.089487 | 0 | 0
24 | 0.99353 | -0.1228 | 0.00088174 | 0.00022099
25 | 0.9936 | -0.12145 | 0.0010276 | 0.00025754
26 | 0.9908 | -0.17578 | 0 | 0
27 | 0.98995 | -0.19223 | 0 | 0
28 | 0.99353 | -0.12285 | 0 | 0
29 | 0.99052 | -0.1811 | 0.014186 | 0.0035552
30 | 0.98964 | -0.19813 | 0 | 0
31 | 0.98959 | -0.19924 | 0.0054935 | 0.0013768
32 | 0.98976 | -0.1959 | 0.0042389 | 0.0010624
33 | 0.99324 | -0.12839 | 0 | 0
34 | 0.99335 | -0.12614 | 0.0011403 | 0.00028579
35 | 0.99313 | -0.13052 | 0.0054685 | 0.0013705
36 | 0.98922 | -0.20632 | 0 | 0
37 | 0.98947 | -0.20146 | 0 | 0
38 | 0.98914 | -0.20787 | 0.015639 | 0.0039195
39 | 0.98934 | -0.20413 | 0 | 0
40 | 0.98923 | -0.20612 | 0.0034473 | 0.00086398
41 | 0.98949 | -0.20112 | 0 | 0
42 | 0.98988 | -0.19347 | 0.016204 | 0.0040612
43 | 0.97509 | -0.47939 | 0.0011957 | 0.00029966
44 | 0.97562 | -0.46902 | 0.002372 | 0.00059449
45 | 0.97455 | -0.48993 | 0.0031864 | 0.0007986
46 | 0.97267 | -0.527 | 0.0016432 | 0.00041182
47 | 0.97656 | -0.45061 | 0.021377 | 0.0053575
48 | 0.97653 | -0.45111 | 0.0072681 | 0.0018216
49 | 0.9726 | -0.52846 | 0.004043 | 0.0010133
50 | 0.97265 | -0.5274 | 0 | 0
51 | 0.99517 | -0.091674 | 0.011556 | 0.0028962
52 | 0.99503 | -0.094284 | 0.021745 | 0.0054497
53 | 0.9963 | -0.070172 | 0 | 0
54 | 0.99948 | -0.0098111 | 0 | 0
55 | 0.99352 | -0.12287 | 0.0008173 | 0.00020484
56 | 0.97553 | -0.47064 | 0.0015838 | 0.00039693
57 | 0.98873 | -0.21487 | 0 | 0
58 | 0.98858 | -0.21773 | 0 | 0
59 | 0.98597 | -0.26799 | 0.0097898 | 0.0024536
60 | 0.99325 | -0.12846 | 0.014521 | 0.0036392
61 | 0.9903 | -0.18538 | 0 | 0
62 | 0.98994 | -0.1923 | 0 | 0
63 | 0.99312 | -0.1307 | 0.00079119 | 0.00019829
64 | 0.98941 | -0.20264 | 0.012751 | 0.0031957
65 | 0.97717 | -0.43949 | 0 | 0
66 | 0.97696 | -0.44358 | 0.0079081 | 0.001982
67 | 0.97745 | -0.43408 | 0 | 0
68 | 0.97642 | -0.45332 | 0.012691 | 0.0031806
69 | 0.99714 | -0.054685 | 0.0027325 | 0.00068482
70 | 0.99722 | -0.053306 | 0 | 0
71 | 0.99736 | -0.050628 | 0.0032102 | 0.00080456
72 | 0.99698 | -0.057787 | 0.02084 | 0.005223
73 | 0.99787 | -0.040698 | 0 | 0
74 | 0.99504 | -0.095232 | 0 | 0
75 | 0.99372 | -0.12073 | 0.0043216 | 0.0010831
76 | 0.99374 | -0.12026 | 0.0023605 | 0.00059159
77 | 0.99378 | -0.11953 | 0.0041678 | 0.0010445
78 | 0.9941 | -0.11337 | 0.0021546 | 0.00054
79 | 0.97387 | -0.50423 | 0 | 0
80 | 0.97331 | -0.51529 | 0.012467 | 0.0031246
81 | 0.97497 | -0.48258 | 0 | 0
82 | 0.97904 | -0.40278 | 0 | 0
83 | 0.97891 | -0.40533 | 0 | 0
84 | 0.97926 | -0.39854 | 0.0053033 | 0.0013291
85 | 0.99421 | -0.11122 | 0 | 0
86 | 0.97979 | -0.3882 | 0 | 0
87 | 0.97926 | -0.39852 | 0.0057804 | 0.0014487
88 | 0.98086 | -0.36723 | 0 | 0
89 | 0.97538 | -0.4745 | 0 | 0
90 | 0.9749 | -0.48408 | 0.0043837 | 0.0010986
91 | 0.98015 | -0.38113 | 0 | 0
92 | 0.9792 | -0.39959 | 0.0026686 | 0.00066881
93 | 0.97531 | -0.47603 | 0.0030185 | 0.0007565
94 | 0.97537 | -0.47487 | 0.0018702 | 0.00046871
95 | 0.97868 | -0.4099 | 0.011699 | 0.002932
96 | 0.9788 | -0.40751 | 0.0056902 | 0.0014261
97 | 0.9771 | -0.44084 | 0.0091705 | 0.0022983
98 | 0.97718 | -0.43929 | 0 | 0
99 | 0.99386 | -0.11803 | 0.0029729 | 0.00074508
100 | 0.99452 | -0.1052 | 0.0016984 | 0.00042565
101 | 0.99385 | -0.11808 | 0.0038007 | 0.00095254
102 | 0.99353 | -0.12435 | 0.0028196 | 0.00070666
103 | 0.99473 | -0.10114 | 0.015571 | 0.0039026
104 | 0.99335 | -0.12781 | 0.0032052 | 0.00080329
105 | 0.99342 | -0.1265 | 0 | 0
106 | 0.99333 | -0.12829 | 0.0053024 | 0.0013289
107 | 0.99338 | -0.12722 | 0.0027591 | 0.0006915
108 | 0.99351 | -0.12471 | 0.0030656 | 0.0007683
109 | 0.97532 | -0.47575 | 0.0032793 | 0.00082187
110 | 0.97572 | -0.46793 | 0 | 0
111 | 0.97682 | -0.44623 | 0.0010847 | 0.00027184
112 | 0.97555 | -0.47126 | 0 | 0
113 | 0.97563 | -0.46955 | 0.0036758 | 0.00092124
114 | 0.97563 | -0.46958 | 0.0017673 | 0.00044292
115 | 0.97707 | -0.44138 | 0.0011346 | 0.00028436
116 | 0.97766 | -0.42978 | 0.0012007 | 0.00030093
117 | 1 | 0 | -0.47128 | -0.12019
118 | 0.98857 | -0.2179 | 0.0015151 | 0.00037972
119 | 0.98848 | -0.21961 | 0.0026295 | 0.00065902
120 | 0.98595 | -0.26844 | 0.0017381 | 0.00043561
121 | 0.98277 | -0.33004 | 0 | 0
122 | 0.99008 | -0.18976 | 0.0017753 | 0.00044493
123 | 0.98842 | -0.2209 | 0.001485 | 0.00037218
124 | 0.9884 | -0.22125 | 0.0040565 | 0.0010167
125 | 0.97881 | -0.40732 | 0.0021791 | 0.00054614
126 | 0.97846 | -0.41426 | 0.002776 | 0.00069574
127 | 0.97736 | -0.43576 | 0.0032525 | 0.00081516
128 | 0.97757 | -0.43162 | 0 | 0
129 | 0.97869 | -0.40963 | 0.0023869 | 0.00059821
130 | 0.99467 | -0.10225 | 0.0017448 | 0.00043729
131 | 0.97812 | -0.42077 | 0 | 0
132 | 0.9773 | -0.43696 | 0.0081747 | 0.0020488
133 | 0.97733 | -0.43638 | 0.0047778 | 0.0011974
134 | 0.97794 | -0.42422 | 0.0012262 | 0.00030731
135 | 0.97805 | -0.42206 | 0 | 0
136 | 0.97802 | -0.42271 | 0.0015466 | 0.00038761
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.019323 | -0.0048429 | 0.019357 | 0.0048632 | 3.3761e-05 | 2.0319e-05 | 0.029522 | 0.029521 | 0.029522 | 0.97397 | -0.50146 | 0.97583 | -0.46485 | 8.1104
1 | 0.0085928 | 0.0021538 | -0.0085916 | -0.0021533 | 1.1584e-06 | 5.1664e-07 | 0.013103 | 0.013103 | 0.013103 | 0.97583 | -0.46485 | 0.97568 | -0.46768 | 3.5997
2 | -0.030839 | -0.0077409 | 0.030902 | 0.0077803 | 6.298e-05 | 3.9357e-05 | 0.04703 | 0.04703 | 0.04703 | 0.97583 | -0.46485 | 0.978 | -0.42213 | 12.9204
3 | 0.0028895 | 0.00072395 | -0.0028893 | -0.00072413 | 1.6595e-07 | -1.7855e-07 | 0.004406 | 0.0044061 | 0.0044061 | 0.97583 | -0.46485 | 0.97577 | -0.46606 | 1.2105
4 | 0.041394 | 0.010396 | -0.041347 | -0.010366 | 4.6252e-05 | 2.9212e-05 | 0.062987 | 0.062987 | 0.062987 | 0.978 | -0.42213 | 0.97681 | -0.44558 | 17.3042
5 | -0.10302 | -0.025918 | 0.10388 | 0.026469 | 0.00086295 | 0.00055111 | 0.15678 | 0.15678 | 0.15678 | 0.978 | -0.42213 | 0.98695 | -0.2484 | 43.0709
6 | 0.030724 | 0.0077423 | -0.03066 | -0.0077026 | 6.3675e-05 | 3.978e-05 | 0.046761 | 0.046761 | 0.046761 | 0.978 | -0.42213 | 0.97579 | -0.46555 | 12.8465
7 | 0.023458 | 0.0058985 | -0.023443 | -0.0058893 | 1.5088e-05 | 9.2643e-06 | 0.035779 | 0.03578 | 0.03578 | 0.97579 | -0.46555 | 0.97511 | -0.47902 | 9.8296
8 | 0.0072016 | 0.001804 | -0.0072013 | -0.0018039 | 3.2736e-07 | 1.1909e-07 | 0.010982 | 0.010982 | 0.010982 | 0.97579 | -0.46555 | 0.97574 | -0.4665 | 3.0169
9 | 0.022248 | 0.0055898 | -0.022238 | -0.0055841 | 9.3951e-06 | 5.7419e-06 | 0.033955 | 0.033955 | 0.033955 | 0.97511 | -0.47902 | 0.97466 | -0.48788 | 9.3283
10 | 0.0011957 | 0.00029946 | -0.0011957 | -0.00029966 | 2.1001e-08 | -1.964e-07 | 0.0018245 | 0.0018246 | 0.0018246 | 0.97511 | -0.47902 | 0.97509 | -0.47939 | 0.50127
11 | 0.0039564 | 0.00099067 | -0.0039559 | -0.0009908 | 4.7429e-07 | -1.3039e-07 | 0.0060333 | 0.0060334 | 0.0060334 | 0.97574 | -0.4665 | 0.97562 | -0.46902 | 1.6575
12 | 0.0029444 | 0.00073762 | -0.0029442 | -0.00073788 | 2.5943e-07 | -2.59e-07 | 0.0044994 | 0.0044995 | 0.0044995 | 0.97374 | -0.50596 | 0.97365 | -0.50781 | 1.2361
13 | 0.016091 | 0.0040382 | -0.016077 | -0.0040304 | 1.3336e-05 | 7.8044e-06 | 0.024591 | 0.024591 | 0.024591 | 0.97374 | -0.50596 | 0.97286 | -0.52335 | 6.7558
14 | -0.019035 | -0.0047758 | 0.019052 | 0.0047857 | 1.6424e-05 | 9.8669e-06 | 0.02909 | 0.02909 | 0.02909 | 0.97374 | -0.50596 | 0.97466 | -0.48788 | 7.9918
15 | 0.0085757 | 0.0021504 | -0.0085724 | -0.0021489 | 3.2197e-06 | 1.4413e-06 | 0.013117 | 0.013117 | 0.013117 | 0.97286 | -0.52335 | 0.97246 | -0.53123 | 3.6037
16 | 0.0075017 | 0.00188 | -0.007501 | -0.0018798 | 7.1028e-07 | 2.7596e-07 | 0.011474 | 0.011474 | 0.011474 | 0.97286 | -0.52335 | 0.97276 | -0.52534 | 3.1522
17 | 0.0031868 | 0.00079836 | -0.0031864 | -0.0007986 | 3.1224e-07 | -2.3852e-07 | 0.0048651 | 0.0048653 | 0.0048653 | 0.97466 | -0.48788 | 0.97455 | -0.48993 | 1.3366
18 | 0.0085724 | 0.0021489 | -0.00857 | -0.0021478 | 2.4773e-06 | 1.1093e-06 | 0.013117 | 0.013118 | 0.013118 | 0.97246 | -0.53123 | 0.97215 | -0.5373 | 3.6037
19 | 0.0056869 | 0.0014251 | -0.0056865 | -0.001425 | 4.4967e-07 | 9.1097e-08 | 0.0086991 | 0.0086992 | 0.0086992 | 0.97276 | -0.52534 | 0.97267 | -0.527 | 2.3899
20 | 0.034077 | 0.0085442 | -0.034069 | -0.008539 | 8.1793e-06 | 5.1334e-06 | 0.051913 | 0.051913 | 0.051913 | 0.97681 | -0.44558 | 0.97656 | -0.45061 | 14.2617
21 | 0.00727 | 0.0018223 | -0.0072681 | -0.0018216 | 1.9174e-06 | 7.0545e-07 | 0.011075 | 0.011075 | 0.011075 | 0.97681 | -0.44558 | 0.97653 | -0.45111 | 3.0426
22 | -0.10953 | -0.027884 | 0.11008 | 0.028233 | 0.00054957 | 0.00034897 | 0.16529 | 0.16529 | 0.16529 | 0.98695 | -0.2484 | 0.99236 | -0.1449 | 22.7044
23 | 0.0056449 | 0.0014147 | -0.0056441 | -0.0014145 | 7.8795e-07 | 1.3363e-07 | 0.0085107 | 0.0085108 | 0.0085108 | 0.98695 | -0.2484 | 0.9868 | -0.25133 | 2.3381
24 | -0.11734 | -0.030052 | 0.11747 | 0.030137 | 0.00013552 | 8.4325e-05 | 0.17617 | 0.17617 | 0.17617 | 0.99236 | -0.1449 | 0.99362 | -0.12109 | 12.0997
25 | 0.0072589 | 0.0018195 | -0.0072566 | -0.0018187 | 2.2807e-06 | 7.9663e-07 | 0.010884 | 0.010885 | 0.010885 | 0.99236 | -0.1449 | 0.99202 | -0.1515 | 2.9903
26 | 0.0091022 | 0.0022814 | -0.0091015 | -0.002281 | 7.414e-07 | 3.3669e-07 | 0.013631 | 0.013631 | 0.013631 | 0.99362 | -0.12109 | 0.99353 | -0.1228 | 3.7449
27 | 0.0010276 | 0.00025729 | -0.0010276 | -0.00025754 | 1.7631e-08 | -2.4586e-07 | 0.0015388 | 0.0015389 | 0.0015389 | 0.99362 | -0.12109 | 0.9936 | -0.12145 | 0.42278
28 | -0.1276 | -0.032675 | 0.12771 | 0.032745 | 0.00011103 | 6.9379e-05 | 0.19134 | 0.19134 | 0.19134 | 0.99362 | -0.12109 | 0.99456 | -0.10314 | 13.1415
29 | 0.003438 | 0.00086124 | -0.0034376 | -0.00086154 | 4.43e-07 | -2.9581e-07 | 0.0051437 | 0.0051439 | 0.0051439 | 0.99456 | -0.10314 | 0.99442 | -0.10585 | 1.4131
30 | -0.13115 | -0.033606 | 0.13124 | 0.03366 | 8.6874e-05 | 5.4353e-05 | 0.19648 | 0.19648 | 0.19648 | 0.99456 | -0.10314 | 0.99528 | -0.089487 | 13.4948
31 | 0.011557 | 0.0028968 | -0.011556 | -0.0028962 | 1.2039e-06 | 6.3077e-07 | 0.017279 | 0.017279 | 0.017279 | 0.99528 | -0.089487 | 0.99517 | -0.091674 | 4.7469
32 | 0.02175 | 0.0054527 | -0.021745 | -0.0054497 | 4.9705e-06 | 3.0183e-06 | 0.032518 | 0.032518 | 0.032518 | 0.99528 | -0.089487 | 0.99503 | -0.094284 | 8.9335
33 | -0.16454 | -0.04201 | 0.1647 | 0.042107 | 0.00015375 | 9.699e-05 | 0.24628 | 0.24628 | 0.24628 | 0.99528 | -0.089487 | 0.9963 | -0.070172 | 16.9148
34 | 0.0082198 | 0.00206 | -0.0082197 | -0.00206 | 2.9174e-08 | 1.2024e-08 | 0.012311 | 0.012311 | 0.012311 | 0.99353 | -0.1228 | 0.99352 | -0.12287 | 3.3821
35 | 0.044648 | 0.01121 | -0.044613 | -0.011188 | 3.4991e-05 | 2.2127e-05 | 0.067061 | 0.067061 | 0.067061 | 0.9908 | -0.17578 | 0.98995 | -0.19223 | 18.4234
36 | -0.073808 | -0.018523 | 0.073995 | 0.018642 | 0.00018683 | 0.00011905 | 0.11086 | 0.11086 | 0.11086 | 0.9908 | -0.17578 | 0.99353 | -0.12285 | 30.4553
37 | 0.029161 | 0.0073135 | -0.029153 | -0.0073089 | 7.3824e-06 | 4.5926e-06 | 0.043796 | 0.043796 | 0.043796 | 0.9908 | -0.17578 | 0.99052 | -0.1811 | 12.032
38 | 0.016205 | 0.0040617 | -0.016204 | -0.0040612 | 9.6054e-07 | 5.5924e-07 | 0.024358 | 0.024359 | 0.024359 | 0.98995 | -0.19223 | 0.98988 | -0.19347 | 6.6919
39 | 0.028408 | 0.0071261 | -0.028395 | -0.0071183 | 1.2502e-05 | 7.7661e-06 | 0.042703 | 0.042703 | 0.042703 | 0.98995 | -0.19223 | 0.98947 | -0.20146 | 11.7315
40 | 0.014524 | 0.0036414 | -0.014521 | -0.0036392 | 3.8782e-06 | 2.1991e-06 | 0.021754 | 0.021754 | 0.021754 | 0.99353 | -0.12285 | 0.99325 | -0.12846 | 5.9763
41 | -0.21996 | -0.055913 | 0.22052 | 0.05627 | 0.0005596 | 0.00035743 | 0.32971 | 0.32971 | 0.32971 | 0.99353 | -0.12285 | 0.9963 | -0.070172 | 45.2895
42 | 0.13144 | 0.033629 | -0.13085 | -0.033256 | 0.00058263 | 0.00037237 | 0.1971 | 0.1971 | 0.1971 | 0.99353 | -0.12285 | 0.98873 | -0.21487 | 54.1476
43 | 0.014968 | 0.0037537 | -0.014965 | -0.0037519 | 3.0524e-06 | 1.7464e-06 | 0.022486 | 0.022486 | 0.022486 | 0.99052 | -0.1811 | 0.9903 | -0.18538 | 6.1775
44 | 0.0089424 | 0.0022403 | -0.0089419 | -0.0022401 | 4.7073e-07 | 2.1205e-07 | 0.013445 | 0.013445 | 0.013445 | 0.98964 | -0.19813 | 0.98959 | -0.19924 | 3.6938
45 | -0.0089424 | -0.0022403 | 0.0089434 | 0.0022407 | 9.4931e-07 | 4.2761e-07 | 0.013445 | 0.013445 | 0.013445 | 0.98964 | -0.19813 | 0.98976 | -0.1959 | 3.6938
46 | 0.0034485 | 0.00086326 | -0.0034481 | -0.00086346 | 3.0986e-07 | -1.9651e-07 | 0.005185 | 0.0051851 | 0.0051851 | 0.98959 | -0.19924 | 0.98949 | -0.20112 | 1.4245
47 | -0.013182 | -0.0033031 | 0.013184 | 0.0033043 | 2.2588e-06 | 1.2485e-06 | 0.019818 | 0.019818 | 0.019818 | 0.98976 | -0.1959 | 0.98994 | -0.1923 | 5.4445
48 | -0.0062603 | -0.0015688 | 0.006261 | 0.001569 | 6.6976e-07 | 1.6582e-07 | 0.0093788 | 0.0093787 | 0.0093788 | 0.99324 | -0.12839 | 0.99335 | -0.12614 | 2.5766
49 | 0.0062603 | 0.0015688 | -0.0062597 | -0.0015687 | 6.3562e-07 | 1.5743e-07 | 0.0093788 | 0.0093789 | 0.0093789 | 0.99324 | -0.12839 | 0.99313 | -0.13052 | 2.5766
50 | -0.0074013 | -0.0018548 | 0.0074024 | 0.0018552 | 1.1532e-06 | 4.1411e-07 | 0.011087 | 0.011087 | 0.011087 | 0.99335 | -0.12614 | 0.99352 | -0.12287 | 3.0458
51 | 0.0007912 | 0.00019813 | -0.00079119 | -0.00019829 | 6.6339e-09 | -1.5865e-07 | 0.0011854 | 0.0011855 | 0.0011855 | 0.99313 | -0.13052 | 0.99312 | -0.1307 | 0.32568
52 | -0.01564 | -0.0039201 | 0.015644 | 0.0039222 | 3.621e-06 | 2.0934e-06 | 0.023526 | 0.023526 | 0.023526 | 0.98922 | -0.20632 | 0.98947 | -0.20146 | 6.4632
53 | 0.01564 | 0.0039201 | -0.015639 | -0.0039195 | 1.153e-06 | 6.6659e-07 | 0.023526 | 0.023526 | 0.023526 | 0.98922 | -0.20632 | 0.98914 | -0.20787 | 6.4632
54 | 0.012752 | 0.0031961 | -0.012751 | -0.0031957 | 7.1642e-07 | 3.9179e-07 | 0.019177 | 0.019177 | 0.019177 | 0.98947 | -0.20146 | 0.98941 | -0.20264 | 5.2683
55 | 0.0034477 | 0.00086377 | -0.0034473 | -0.00086398 | 3.2635e-07 | -2.067e-07 | 0.0051854 | 0.0051855 | 0.0051855 | 0.98934 | -0.20413 | 0.98923 | -0.20612 | 1.4246
56 | -0.0034477 | -0.00086377 | 0.0034481 | 0.00086346 | 4.937e-07 | -3.129e-07 | 0.0051854 | 0.0051851 | 0.0051854 | 0.98934 | -0.20413 | 0.98949 | -0.20112 | 1.4245
57 | 0.0015839 | 0.00039631 | -0.0015838 | -0.00039693 | 1.2255e-07 | -6.2082e-07 | 0.0024155 | 0.0024158 | 0.0024158 | 0.97562 | -0.46902 | 0.97553 | -0.47064 | 0.66368
58 | 0.0040433 | 0.0010132 | -0.0040432 | -0.0010132 | 7.769e-08 | -1.7488e-08 | 0.0061854 | 0.0061854 | 0.0061854 | 0.97267 | -0.527 | 0.97265 | -0.5274 | 1.6993
59 | 0.012692 | 0.0031815 | -0.012691 | -0.0031806 | 1.6367e-06 | 9.015e-07 | 0.01934 | 0.01934 | 0.01934 | 0.97656 | -0.45061 | 0.97642 | -0.45332 | 5.3132
60 | -0.004043 | -0.0010133 | 0.0040432 | 0.0010132 | 2.0392e-07 | -4.5886e-08 | 0.0061855 | 0.0061854 | 0.0061855 | 0.9726 | -0.52846 | 0.97265 | -0.5274 | 1.6993
61 | -0.38521 | -0.098377 | 0.38634 | 0.099097 | 0.0011275 | 0.00071973 | 0.57599 | 0.57599 | 0.57599 | 0.9963 | -0.070172 | 0.99948 | -0.0098111 | 39.5595
62 | -0.46941 | -0.12004 | 0.46963 | 0.12019 | 0.00022298 | 0.00014245 | 0.6997 | 0.6997 | 0.6997 | 0.99948 | -0.0098111 | 1 | 0 | 48.0566
63 | 0.08307 | 0.020948 | -0.082948 | -0.02087 | 0.00012261 | 7.8194e-05 | 0.12372 | 0.12372 | 0.12372 | 0.99948 | -0.0098111 | 0.99787 | -0.040698 | 33.9889
64 | 0.0096886 | 0.0024285 | -0.0096873 | -0.0024278 | 1.3201e-06 | 6.3256e-07 | 0.014581 | 0.014581 | 0.014581 | 0.98873 | -0.21487 | 0.98858 | -0.21773 | 4.0059
65 | 0.12116 | 0.030828 | -0.12086 | -0.03063 | 0.00030935 | 0.00019767 | 0.18252 | 0.18252 | 0.18252 | 0.98873 | -0.21487 | 0.98597 | -0.26799 | 50.1418
66 | 0.0015151 | 0.00037965 | -0.0015151 | -0.00037972 | 1.2557e-08 | -7.4507e-08 | 0.0022806 | 0.0022806 | 0.0022806 | 0.98858 | -0.21773 | 0.98857 | -0.2179 | 0.62654
67 | 0.0081722 | 0.0020482 | -0.0081715 | -0.0020479 | 7.3224e-07 | 3.0319e-07 | 0.012301 | 0.012301 | 0.012301 | 0.98858 | -0.21773 | 0.98848 | -0.21961 | 3.3794
68 | 0.0017381 | 0.00043545 | -0.0017381 | -0.00043561 | 3.7562e-08 | -1.6161e-07 | 0.0026231 | 0.0026232 | 0.0026232 | 0.98597 | -0.26799 | 0.98595 | -0.26844 | 0.72066
69 | 0.10933 | 0.027741 | -0.109 | -0.027534 | 0.0003252 | 0.00020772 | 0.16512 | 0.16512 | 0.16512 | 0.98597 | -0.26799 | 0.98277 | -0.33004 | 45.3622
70 | 0.014965 | 0.0037519 | -0.014961 | -0.0037501 | 3.1221e-06 | 1.7863e-06 | 0.022486 | 0.022486 | 0.022486 | 0.9903 | -0.18538 | 0.99008 | -0.18976 | 6.1775
71 | -0.013184 | -0.0033043 | 0.013186 | 0.0033052 | 1.6008e-06 | 8.8476e-07 | 0.019818 | 0.019818 | 0.019818 | 0.98994 | -0.1923 | 0.99008 | -0.18976 | 5.4445
72 | 0.0079097 | 0.0019826 | -0.0079081 | -0.001982 | 1.5431e-06 | 6.3233e-07 | 0.012045 | 0.012045 | 0.012045 | 0.97717 | -0.43949 | 0.97696 | -0.44358 | 3.309
73 | -0.0079097 | -0.0019826 | 0.0079117 | 0.0019834 | 2.0407e-06 | 8.3599e-07 | 0.012045 | 0.012045 | 0.012045 | 0.97717 | -0.43949 | 0.97745 | -0.43408 | 3.309
74 | 0.0080312 | 0.0020129 | -0.0080305 | -0.0020126 | 6.4441e-07 | 2.6834e-07 | 0.012226 | 0.012226 | 0.012226 | 0.97745 | -0.43408 | 0.97736 | -0.43576 | 3.3589
75 | -0.015943 | -0.0039963 | 0.015945 | 0.0039974 | 1.862e-06 | 1.086e-06 | 0.024271 | 0.024271 | 0.024271 | 0.97745 | -0.43408 | 0.97757 | -0.43162 | 6.6678
76 | -0.0027325 | -0.00068482 | 0.0027327 | 0.00068456 | 1.7955e-07 | -2.6077e-07 | 0.0040776 | 0.0040775 | 0.0040776 | 0.99714 | -0.054685 | 0.99722 | -0.053306 | 1.1202
77 | -0.023577 | -0.0059103 | 0.02358 | 0.0059121 | 3.0082e-06 | 1.8407e-06 | 0.035182 | 0.035182 | 0.035182 | 0.99722 | -0.053306 | 0.99736 | -0.050628 | 9.6653
78 | 0.020845 | 0.0052257 | -0.02084 | -0.005223 | 4.4505e-06 | 2.6883e-06 | 0.031104 | 0.031104 | 0.031104 | 0.99722 | -0.053306 | 0.99698 | -0.057787 | 8.5451
79 | -0.026791 | -0.0067167 | 0.026803 | 0.0067245 | 1.2683e-05 | 7.8408e-06 | 0.039971 | 0.039971 | 0.039971 | 0.99736 | -0.050628 | 0.99787 | -0.040698 | 10.9811
80 | 0.056144 | 0.014145 | -0.055998 | -0.014053 | 0.00014604 | 9.2739e-05 | 0.083748 | 0.083749 | 0.083749 | 0.99787 | -0.040698 | 0.99504 | -0.095232 | 23.0079
81 | 0.017321 | 0.0043423 | -0.017316 | -0.0043395 | 4.8787e-06 | 2.8706e-06 | 0.025903 | 0.025903 | 0.025903 | 0.99504 | -0.095232 | 0.99473 | -0.10114 | 7.1163
82 | 0.038677 | 0.0097104 | -0.038659 | -0.0096988 | 1.8388e-05 | 1.1578e-05 | 0.057845 | 0.057845 | 0.057845 | 0.99504 | -0.095232 | 0.99452 | -0.1052 | 15.8916
83 | -0.0043216 | -0.0010831 | 0.0043217 | 0.0010831 | 9.6789e-08 | -1.7902e-08 | 0.0064713 | 0.0064713 | 0.0064713 | 0.99372 | -0.12073 | 0.99374 | -0.12026 | 1.7778
84 | -0.0066822 | -0.0016747 | 0.0066825 | 0.0016747 | 2.3252e-07 | 6.8572e-08 | 0.010006 | 0.010006 | 0.010006 | 0.99374 | -0.12026 | 0.99378 | -0.11953 | 2.7489
85 | -0.01085 | -0.0027193 | 0.010853 | 0.0027209 | 3.1845e-06 | 1.6211e-06 | 0.016246 | 0.016246 | 0.016246 | 0.99378 | -0.11953 | 0.9941 | -0.11337 | 4.4633
86 | -0.013008 | -0.0032609 | 0.013009 | 0.0032617 | 1.3343e-06 | 7.3228e-07 | 0.019471 | 0.019471 | 0.019471 | 0.9941 | -0.11337 | 0.99421 | -0.11122 | 5.3493
87 | 0.012474 | 0.0031282 | -0.012467 | -0.0031246 | 6.572e-06 | 3.6062e-06 | 0.01906 | 0.01906 | 0.01906 | 0.97387 | -0.50423 | 0.97331 | -0.51529 | 5.2363
88 | -0.012474 | -0.0031282 | 0.012487 | 0.0031353 | 1.2882e-05 | 7.0667e-06 | 0.01906 | 0.01906 | 0.01906 | 0.97387 | -0.50423 | 0.97497 | -0.48258 | 5.2362
89 | -0.016871 | -0.0042339 | 0.016877 | 0.0042377 | 6.5028e-06 | 3.8355e-06 | 0.02575 | 0.02575 | 0.02575 | 0.97497 | -0.48258 | 0.97538 | -0.4745 | 7.0743
90 | 0.004384 | 0.0010986 | -0.0043837 | -0.0010986 | 3.1143e-07 | -3.2011e-08 | 0.0066908 | 0.0066909 | 0.0066909 | 0.97497 | -0.48258 | 0.9749 | -0.48408 | 1.8382
91 | 0.017394 | 0.0043608 | -0.017392 | -0.0043595 | 2.1183e-06 | 1.2541e-06 | 0.026437 | 0.026437 | 0.026437 | 0.97904 | -0.40278 | 0.97891 | -0.40533 | 7.263
92 | -0.017394 | -0.0043608 | 0.017398 | 0.0043629 | 3.5083e-06 | 2.077e-06 | 0.026437 | 0.026437 | 0.026437 | 0.97904 | -0.40278 | 0.97926 | -0.39854 | 7.263
93 | 0.011701 | 0.0029333 | -0.011699 | -0.002932 | 2.5479e-06 | 1.3607e-06 | 0.017787 | 0.017787 | 0.017787 | 0.97891 | -0.40533 | 0.97868 | -0.4099 | 4.8866
94 | 0.0056907 | 0.0014262 | -0.0056902 | -0.0014261 | 5.8993e-07 | 1.1328e-07 | 0.0086503 | 0.0086504 | 0.0086504 | 0.97891 | -0.40533 | 0.9788 | -0.40751 | 2.3765
95 | -0.022701 | -0.005692 | 0.022701 | 0.005692 | 2.9595e-08 | 1.8106e-08 | 0.034496 | 0.034496 | 0.034496 | 0.97926 | -0.39854 | 0.97926 | -0.39852 | 9.4769
96 | 0.02394 | 0.0060049 | -0.023933 | -0.0060001 | 7.7765e-06 | 4.7676e-06 | 0.035833 | 0.035833 | 0.035833 | 0.99421 | -0.11122 | 0.99386 | -0.11803 | 9.8442
97 | -0.03695 | -0.0092665 | 0.03696 | 0.0092732 | 1.0593e-05 | 6.6594e-06 | 0.055304 | 0.055304 | 0.055304 | 0.99421 | -0.11122 | 0.99452 | -0.1052 | 15.1935
98 | 0.028495 | 0.0071494 | -0.028481 | -0.0071407 | 1.4007e-05 | 8.7135e-06 | 0.043279 | 0.043279 | 0.043279 | 0.97979 | -0.3882 | 0.97926 | -0.39852 | 11.8899
99 | -0.028495 | -0.0071494 | 0.028524 | 0.0071672 | 2.852e-05 | 1.7741e-05 | 0.043279 | 0.043279 | 0.043279 | 0.97979 | -0.3882 | 0.98086 | -0.36723 | 11.8899
100 | -0.10881 | -0.02741 | 0.109 | 0.027534 | 0.00019394 | 0.00012388 | 0.16512 | 0.16512 | 0.16512 | 0.98086 | -0.36723 | 0.98277 | -0.33004 | 45.3622
101 | 0.038364 | 0.0096608 | -0.038291 | -0.0096146 | 7.3381e-05 | 4.6237e-05 | 0.058217 | 0.058217 | 0.058217 | 0.98086 | -0.36723 | 0.97881 | -0.40732 | 15.9937
102 | 0.04192 | 0.010582 | -0.041893 | -0.010564 | 2.7889e-05 | 1.7617e-05 | 0.063623 | 0.063623 | 0.063623 | 0.98086 | -0.36723 | 0.98015 | -0.38113 | 17.4788
103 | 0.0032795 | 0.00082174 | -0.0032793 | -0.00082187 | 1.9533e-07 | -1.3471e-07 | 0.005003 | 0.0050031 | 0.0050031 | 0.97538 | -0.4745 | 0.97532 | -0.47575 | 1.3745
104 | -0.020157 | -0.0050595 | 0.020163 | 0.0050633 | 6.327e-06 | 3.8266e-06 | 0.030753 | 0.030753 | 0.030753 | 0.97538 | -0.4745 | 0.97572 | -0.46793 | 8.4487
105 | 0.041893 | 0.010564 | -0.041856 | -0.010541 | 3.6974e-05 | 2.3357e-05 | 0.063623 | 0.063623 | 0.063623 | 0.98015 | -0.38113 | 0.9792 | -0.39959 | 17.4788
106 | 0.039187 | 0.0098719 | -0.039168 | -0.00986 | 1.8813e-05 | 1.1863e-05 | 0.059568 | 0.059568 | 0.059568 | 0.9792 | -0.39959 | 0.97869 | -0.40963 | 16.3648
107 | -0.0030185 | -0.0007565 | 0.0030186 | 0.00075635 | 1.6738e-07 | -1.5553e-07 | 0.0046053 | 0.0046052 | 0.0046053 | 0.97531 | -0.47603 | 0.97537 | -0.47487 | 1.2652
108 | -0.0048888 | -0.0012251 | 0.0048897 | 0.0012251 | 8.4006e-07 | 3.491e-08 | 0.0074583 | 0.0074581 | 0.0074583 | 0.97537 | -0.47487 | 0.97555 | -0.47126 | 2.049
109 | -0.0091705 | -0.0022983 | 0.0091712 | 0.0022987 | 6.7734e-07 | 3.1749e-07 | 0.013966 | 0.013966 | 0.013966 | 0.9771 | -0.44084 | 0.97718 | -0.43929 | 3.8367
110 | -0.0091712 | -0.0022987 | 0.0091722 | 0.0022991 | 1.0211e-06 | 4.7856e-07 | 0.013966 | 0.013965 | 0.013966 | 0.97718 | -0.43929 | 0.9773 | -0.43696 | 3.8367
111 | 0.02096 | 0.005255 | -0.02096 | -0.005255 | 4.4963e-08 | 2.7198e-08 | 0.031382 | 0.031382 | 0.031382 | 0.99386 | -0.11803 | 0.99385 | -0.11808 | 8.6214
112 | 0.017159 | 0.0043024 | -0.017154 | -0.0042994 | 5.1267e-06 | 3.0128e-06 | 0.025691 | 0.025692 | 0.025692 | 0.99385 | -0.11808 | 0.99353 | -0.12435 | 7.0581
113 | 0.014334 | 0.0035928 | -0.014334 | -0.0035926 | 2.4672e-07 | 1.3941e-07 | 0.021469 | 0.021469 | 0.021469 | 0.99353 | -0.12435 | 0.99351 | -0.12471 | 5.898
114 | 0.0017449 | 0.00043688 | -0.0017448 | -0.00043729 | 9.1965e-08 | -4.0841e-07 | 0.0026101 | 0.0026102 | 0.0026102 | 0.99473 | -0.10114 | 0.99467 | -0.10225 | 0.71709
115 | -0.0085077 | -0.0021322 | 0.0085083 | 0.0021324 | 5.2847e-07 | 2.2589e-07 | 0.012744 | 0.012744 | 0.012744 | 0.99335 | -0.12781 | 0.99342 | -0.1265 | 3.5012
116 | 0.0053026 | 0.0013289 | -0.0053024 | -0.0013289 | 1.2293e-07 | 1.1416e-08 | 0.0079431 | 0.0079431 | 0.0079431 | 0.99335 | -0.12781 | 0.99333 | -0.12829 | 2.1822
117 | 0.0027592 | 0.00069137 | -0.0027591 | -0.0006915 | 9.3526e-08 | -1.2918e-07 | 0.0041329 | 0.004133 | 0.004133 | 0.99342 | -0.1265 | 0.99338 | -0.12722 | 1.1354
118 | -0.011267 | -0.0028238 | 0.011268 | 0.0028243 | 9.6303e-07 | 4.996e-07 | 0.016877 | 0.016877 | 0.016877 | 0.99342 | -0.1265 | 0.99351 | -0.12471 | 4.6366
119 | -0.030497 | -0.0076526 | 0.030529 | 0.0076724 | 3.1585e-05 | 1.9728e-05 | 0.046513 | 0.046513 | 0.046513 | 0.97572 | -0.46793 | 0.97682 | -0.44623 | 12.7782
120 | 0.0048904 | 0.0012251 | -0.0048897 | -0.0012251 | 7.7621e-07 | 3.2067e-08 | 0.007458 | 0.0074581 | 0.0074581 | 0.97572 | -0.46793 | 0.97555 | -0.47126 | 2.0489
121 | 0.0054435 | 0.0013642 | -0.0054431 | -0.0013642 | 4.2233e-07 | 6.6203e-08 | 0.0083016 | 0.0083016 | 0.0083016 | 0.97572 | -0.46793 | 0.97563 | -0.46955 | 2.2807
122 | -0.031613 | -0.0079442 | 0.031621 | 0.0079488 | 7.3152e-06 | 4.5764e-06 | 0.048165 | 0.048165 | 0.048165 | 0.97682 | -0.44623 | 0.97707 | -0.44138 | 13.2321
123 | 0.0017673 | 0.00044291 | -0.0017673 | -0.00044292 | 2.4798e-09 | -9.7794e-09 | 0.0026954 | 0.0026954 | 0.0026954 | 0.97563 | -0.46955 | 0.97563 | -0.46958 | 0.74049
124 | -0.032755 | -0.0082331 | 0.032773 | 0.0082445 | 1.8153e-05 | 1.1374e-05 | 0.049893 | 0.049893 | 0.049893 | 0.97707 | -0.44138 | 0.97766 | -0.42978 | 13.7068
125 | -0.033974 | -0.0085454 | 0.033983 | 0.0085511 | 9.0389e-06 | 5.6719e-06 | 0.05172 | 0.05172 | 0.05172 | 0.97766 | -0.42978 | 0.97794 | -0.42422 | 14.2089
126 | 0.0055419 | 0.0013889 | -0.0055416 | -0.0013888 | 3.4056e-07 | 5.0703e-08 | 0.0083426 | 0.0083426 | 0.0083426 | 0.98848 | -0.21961 | 0.98842 | -0.2209 | 2.2919
127 | 0.0040566 | 0.0010166 | -0.0040565 | -0.0010167 | 6.7814e-08 | -1.8745e-08 | 0.006107 | 0.006107 | 0.006107 | 0.98842 | -0.2209 | 0.9884 | -0.22125 | 1.6778
128 | 0.036112 | 0.0090684 | -0.0361 | -0.0090609 | 1.1961e-05 | 7.5222e-06 | 0.054904 | 0.054904 | 0.054904 | 0.97881 | -0.40732 | 0.97846 | -0.41426 | 15.0836
129 | 0.033324 | 0.0083652 | -0.033313 | -0.0083587 | 1.0335e-05 | 6.4795e-06 | 0.050683 | 0.050683 | 0.050683 | 0.97846 | -0.41426 | 0.97812 | -0.42077 | 13.9238
130 | 0.004778 | 0.0011974 | -0.0047778 | -0.0011974 | 1.4158e-07 | 1.2018e-09 | 0.0072744 | 0.0072744 | 0.0072744 | 0.97736 | -0.43576 | 0.97733 | -0.43638 | 1.9985
131 | 0.017351 | 0.0043505 | -0.017347 | -0.0043479 | 4.4078e-06 | 2.6098e-06 | 0.026412 | 0.026412 | 0.026412 | 0.97757 | -0.43162 | 0.9773 | -0.43696 | 7.2561
132 | -0.033296 | -0.0083479 | 0.033313 | 0.0083587 | 1.7233e-05 | 1.0805e-05 | 0.050683 | 0.050683 | 0.050683 | 0.97757 | -0.43162 | 0.97812 | -0.42077 | 13.9238
133 | 0.036781 | 0.0092618 | -0.036759 | -0.009248 | 2.1849e-05 | 1.375e-05 | 0.055939 | 0.055939 | 0.055939 | 0.97869 | -0.40963 | 0.97805 | -0.42206 | 15.3678
134 | -0.035209 | -0.0088584 | 0.035213 | 0.0088607 | 3.6197e-06 | 2.2744e-06 | 0.053586 | 0.053586 | 0.053586 | 0.97794 | -0.42422 | 0.97805 | -0.42206 | 14.7214
135 | 0.0015466 | 0.00038735 | -0.0015466 | -0.00038761 | 4.7753e-08 | -2.5807e-07 | 0.0023529 | 0.002353 | 0.002353 | 0.97805 | -0.42206 | 0.97802 | -0.42271 | 0.64644

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47436 | 0.12096

## res_load
| p_mw | q_mvar
0 | 0.019323 | 0.0048429
1 | 0.0028893 | 0.00072413
2 | 0.0085916 | 0.0021533
3 | 0.0032449 | 0.00081324
4 | 0.0029442 | 0.00073788
5 | 0.0018141 | 0.00045464
6 | 0.00857 | 0.0021478
7 | 0.0056441 | 0.0014145
8 | 0.0072566 | 0.0018187
9 | 0.0034376 | 0.00086154
10 | 0.00088174 | 0.00022099
11 | 0.0010276 | 0.00025754
12 | 0.014186 | 0.0035552
13 | 0.0054935 | 0.0013768
14 | 0.0042389 | 0.0010624
15 | 0.0011403 | 0.00028579
16 | 0.0054685 | 0.0013705
17 | 0.015639 | 0.0039195
18 | 0.0034473 | 0.00086398
19 | 0.016204 | 0.0040612
20 | 0.0011957 | 0.00029966
21 | 0.002372 | 0.00059449
22 | 0.0031864 | 0.0007986
23 | 0.0016432 | 0.00041182
24 | 0.021377 | 0.0053575
25 | 0.0072681 | 0.0018216
26 | 0.004043 | 0.0010133
27 | 0.011556 | 0.0028962
28 | 0.021745 | 0.0054497
29 | 0.0008173 | 0.00020484
30 | 0.0015838 | 0.00039693
31 | 0.0097898 | 0.0024536
32 | 0.014521 | 0.0036392
33 | 0.00079119 | 0.00019829
34 | 0.012751 | 0.0031957
35 | 0.0079081 | 0.001982
36 | 0.012691 | 0.0031806
37 | 0.0027325 | 0.00068482
38 | 0.0032102 | 0.00080456
39 | 0.02084 | 0.005223
40 | 0.0043216 | 0.0010831
41 | 0.0023605 | 0.00059159
42 | 0.0041678 | 0.0010445
43 | 0.0021546 | 0.00054
44 | 0.012467 | 0.0031246
45 | 0.0053033 | 0.0013291
46 | 0.0057804 | 0.0014487
47 | 0.0043837 | 0.0010986
48 | 0.0026686 | 0.00066881
49 | 0.0030185 | 0.0007565
50 | 0.0018702 | 0.00046871
51 | 0.011699 | 0.002932
52 | 0.0056902 | 0.0014261
53 | 0.0091705 | 0.0022983
54 | 0.0029729 | 0.00074508
55 | 0.0016984 | 0.00042565
56 | 0.0038007 | 0.00095254
57 | 0.0028196 | 0.00070666
58 | 0.015571 | 0.0039026
59 | 0.0032052 | 0.00080329
60 | 0.0053024 | 0.0013289
61 | 0.0027591 | 0.0006915
62 | 0.0030656 | 0.0007683
63 | 0.0032793 | 0.00082187
64 | 0.0010847 | 0.00027184
65 | 0.0036758 | 0.00092124
66 | 0.0017673 | 0.00044292
67 | 0.0011346 | 0.00028436
68 | 0.0012007 | 0.00030093
69 | 0.0030716 | 0.00076981
70 | 0.0015151 | 0.00037972
71 | 0.0026295 | 0.00065902
72 | 0.0017381 | 0.00043561
73 | 0.0017753 | 0.00044493
74 | 0.001485 | 0.00037218
75 | 0.0040565 | 0.0010167
76 | 0.0021791 | 0.00054614
77 | 0.002776 | 0.00069574
78 | 0.0032525 | 0.00081516
79 | 0.0023869 | 0.00059821
80 | 0.0017448 | 0.00043729
81 | 0.0081747 | 0.0020488
82 | 0.0047778 | 0.0011974
83 | 0.0012262 | 0.00030731
84 | 0.0015466 | 0.00038761

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1