## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_158-16_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_158-16_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_158-16_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_158-16_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_158-16_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_158-16_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_158-16_0_6_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_158-16_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_158-16_0_6_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_158-16_0_6_node_143 | 0.4 | n |  | TRUE
10 | bus_LV_158-16_0_6_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_158-16_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_158-16_0_6_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_158-16_0_6_node_144 | 0.4 | n |  | TRUE
14 | bus_LV_158-16_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_158-16_0_6_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_158-16_0_6_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_158-16_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_158-16_0_6_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_158-16_0_6_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_158-16_0_6_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_158-16_0_6_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_158-16_0_6_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_158-16_0_6_node_103 | 0.4 | n |  | TRUE
24 | bus_LV_158-16_0_6_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_158-16_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_158-16_0_6_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_158-16_0_6_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_158-16_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_158-16_0_6_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_158-16_0_6_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_158-16_0_6_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_158-16_0_6_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_158-16_0_6_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_158-16_0_6_node_154 | 0.4 | n |  | TRUE
35 | bus_LV_158-16_0_6_node_104 | 0.4 | n |  | TRUE
36 | bus_LV_158-16_0_6_node_153 | 0.4 | n |  | TRUE
37 | bus_LV_158-16_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_158-16_0_6_node_105 | 0.4 | n |  | TRUE
39 | bus_LV_158-16_0_6_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_158-16_0_6_node_95 | 0.4 | n |  | TRUE
41 | bus_LV_158-16_0_6_node_93 | 0.4 | n |  | TRUE
42 | bus_LV_158-16_0_6_node_155 | 0.4 | n |  | TRUE
43 | bus_LV_158-16_0_6_node_56 | 0.4 | n |  | TRUE
44 | bus_LV_158-16_0_6_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_158-16_0_6_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_158-16_0_6_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_158-16_0_6_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_158-16_0_6_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_158-16_0_6_node_94 | 0.4 | n |  | TRUE
50 | bus_LV_158-16_0_6_node_102 | 0.4 | n |  | TRUE
51 | bus_LV_158-16_0_6_node_97 | 0.4 | n |  | TRUE
52 | bus_LV_158-16_0_6_node_99 | 0.4 | n |  | TRUE
53 | bus_LV_158-16_0_6_node_96 | 0.4 | n |  | TRUE
54 | bus_LV_158-16_0_6_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_158-16_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_158-16_0_6_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_158-16_0_6_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_158-16_0_6_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_158-16_0_6_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_158-16_0_6_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_158-16_0_6_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_158-16_0_6_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_158-16_0_6_node_147 | 0.4 | n |  | TRUE
64 | bus_LV_158-16_0_6_node_87 | 0.4 | n |  | TRUE
65 | bus_LV_158-16_0_6_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_158-16_0_6_node_112 | 0.4 | n |  | TRUE
67 | bus_LV_158-16_0_6_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_158-16_0_6_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_158-16_0_6_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_158-16_0_6_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_158-16_0_6_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_158-16_0_6_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_158-16_0_6_node_91 | 0.4 | n |  | TRUE
74 | bus_LV_158-16_0_6_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_158-16_0_6_node_92 | 0.4 | n |  | TRUE
76 | bus_LV_158-16_0_6_node_152 | 0.4 | n |  | TRUE
77 | bus_LV_158-16_0_6_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_158-16_0_6_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_158-16_0_6_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_158-16_0_6_node_78 | 0.4 | n |  | TRUE
81 | bus_LV_158-16_0_6_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_158-16_0_6_node_58 | 0.4 | n |  | TRUE
83 | bus_LV_158-16_0_6_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_158-16_0_6_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_158-16_0_6_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_158-16_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_158-16_0_6_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_158-16_0_6_node_63 | 0.4 | n |  | TRUE
89 | bus_LV_158-16_0_6_node_127 | 0.4 | n |  | TRUE
90 | bus_LV_158-16_0_6_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_158-16_0_6_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_158-16_0_6_node_110 | 0.4 | n |  | TRUE
93 | bus_LV_158-16_0_6_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_158-16_0_6_node_129 | 0.4 | n |  | TRUE
95 | bus_LV_158-16_0_6_node_66 | 0.4 | n |  | TRUE
96 | bus_LV_158-16_0_6_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_158-16_0_6_node_126 | 0.4 | n |  | TRUE
98 | bus_LV_158-16_0_6_node_67 | 0.4 | n |  | TRUE
99 | bus_LV_158-16_0_6_node_111 | 0.4 | n |  | TRUE
100 | bus_LV_158-16_0_6_node_108 | 0.4 | n |  | TRUE
101 | bus_LV_158-16_0_6_node_128 | 0.4 | n |  | TRUE
102 | bus_LV_158-16_0_6_node_70 | 0.4 | n |  | TRUE
103 | bus_LV_158-16_0_6_node_76 | 0.4 | n |  | TRUE
104 | bus_LV_158-16_0_6_node_71 | 0.4 | n |  | TRUE
105 | bus_LV_158-16_0_6_node_68 | 0.4 | n |  | TRUE
106 | bus_LV_158-16_0_6_node_69 | 0.4 | n |  | TRUE
107 | bus_LV_158-16_0_6_node_72 | 0.4 | n |  | TRUE
108 | bus_LV_158-16_0_6_node_74 | 0.4 | n |  | TRUE
109 | bus_LV_158-16_0_6_node_135 | 0.4 | n |  | TRUE
110 | bus_LV_158-16_0_6_node_140 | 0.4 | n |  | TRUE
111 | bus_LV_158-16_0_6_node_136 | 0.4 | n |  | TRUE
112 | bus_LV_158-16_0_6_node_133 | 0.4 | n |  | TRUE
113 | bus_LV_158-16_0_6_node_138 | 0.4 | n |  | TRUE
114 | bus_LV_158-16_0_6_node_98 | 0.4 | n |  | TRUE
115 | bus_LV_158-16_0_6_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_158-16_0_6_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_158-16_0_6_node_139 | 0.4 | n |  | TRUE
118 | bus_LV_158-16_0_6_node_137 | 0.4 | n |  | TRUE
119 | bus_LV_158-16_0_6_node_80 | 0.4 | n |  | TRUE
120 | bus_LV_158-16_0_6_node_81 | 0.4 | n |  | TRUE
121 | bus_LV_158-16_0_6_node_82 | 0.4 | n |  | TRUE
122 | bus_LV_158-16_0_6_node_83 | 0.4 | n |  | TRUE
123 | bus_LV_158-16_0_6_node_85 | 0.4 | n |  | TRUE
124 | bus_LV_158-16_0_6_node_146 | 0.4 | n |  | TRUE
125 | bus_LV_158-16_0_6_node_86 | 0.4 | n |  | TRUE
126 | bus_LV_158-16_0_6_node_88 | 0.4 | n |  | TRUE
127 | bus_LV_158-16_0_6_node_145 | 0.4 | n |  | TRUE
128 | bus_LV_158-16_0_6_node_149 | 0.4 | n |  | TRUE
129 | bus_LV_158-16_0_6_node_148 | 0.4 | n |  | TRUE
130 | bus_LV_158-16_0_6_node_109 | 0.4 | n |  | TRUE
131 | bus_LV_158-16_0_6_node_113 | 0.4 | n |  | TRUE
132 | bus_LV_158-16_0_6_node_114 | 0.4 | n |  | TRUE
133 | bus_LV_158-16_0_6_node_115 | 0.4 | n |  | TRUE
134 | bus_LV_158-16_0_6_node_116 | 0.4 | n |  | TRUE
135 | bus_LV_158-16_0_6_node_117 | 0.4 | n |  | TRUE
136 | bus_LV_158-16_0_6_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_158-16_0_6_node_118 | 0.4 | n |  | TRUE
138 | bus_LV_158-16_0_6_node_119 | 0.4 | n |  | TRUE
139 | bus_LV_158-16_0_6_node_120 | 0.4 | n |  | TRUE
140 | bus_LV_158-16_0_6_node_142 | 0.4 | n |  | TRUE
141 | bus_LV_158-16_0_6_node_121 | 0.4 | n |  | TRUE
142 | bus_LV_158-16_0_6_node_122 | 0.4 | n |  | TRUE
143 | bus_LV_158-16_0_6_node_124 | 0.4 | n |  | TRUE
144 | bus_LV_158-16_0_6_node_132 | 0.4 | n |  | TRUE
145 | bus_LV_158-16_0_6_node_131 | 0.4 | n |  | TRUE
146 | bus_LV_158-16_0_6_node_130 | 0.4 | n |  | TRUE
147 | bus_LV_158-16_0_6_node_134 | 0.4 | n |  | TRUE
148 | bus_LV_158-16_0_6_node_141 | 0.4 | n |  | TRUE
149 | bus_MV_361_1_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_158-16_0_6_load_0 | 0 | 0.0059346 | 0.0014873 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_158-16_0_6_load_1 | 1 | 0.0046546 | 0.0011665 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_158-16_0_6_load_4 | 4 | 0.0052993 | 0.0013281 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_158-16_0_6_load_5 | 5 | 0.0080235 | 0.0020109 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_158-16_0_6_load_10 | 6 | 0.0027918 | 0.00069969 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_158-16_0_6_load_14 | 8 | 0.0016731 | 0.00041933 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_158-16_0_6_load_143 | 9 | 0.00075415 | 0.00018901 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_158-16_0_6_load_11 | 10 | 0.0012142 | 0.00030431 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_158-16_0_6_load_6 | 11 | 0.0083263 | 0.0020868 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_158-16_0_6_load_15 | 12 | 0.0016772 | 0.00042033 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_158-16_0_6_load_144 | 13 | 0.00069362 | 0.00017384 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_158-16_0_6_load_9 | 14 | 0.0019808 | 0.00049645 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_158-16_0_6_load_40 | 16 | 0.005938 | 0.0014882 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_158-16_0_6_load_13 | 17 | 0.0039401 | 0.00098748 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_158-16_0_6_load_16 | 20 | 0.0016332 | 0.00040931 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_158-16_0_6_load_46 | 21 | 0.0024104 | 0.00060411 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_158-16_0_6_load_43 | 22 | 0.0012308 | 0.00030846 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_158-16_0_6_load_103 | 23 | 0.0026583 | 0.00066623 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_158-16_0_6_load_44 | 24 | 0.001287 | 0.00032254 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_158-16_0_6_load_19 | 25 | 0.0042199 | 0.0010576 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_158-16_0_6_load_21 | 27 | 0.0070542 | 0.001768 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_158-16_0_6_load_26 | 31 | 0.0030233 | 0.00075771 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_158-16_0_6_load_48 | 32 | 0.0013757 | 0.00034479 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_158-16_0_6_load_154 | 34 | 0.0026194 | 0.0006565 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_158-16_0_6_load_153 | 36 | 0.0025802 | 0.00064665 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_158-16_0_6_load_27 | 37 | 0.003103 | 0.00077768 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_158-16_0_6_load_105 | 38 | 0.016254 | 0.0040736 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_158-16_0_6_load_47 | 39 | 0.0043213 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_158-16_0_6_load_95 | 40 | 0.0015156 | 0.00037985 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_158-16_0_6_load_93 | 41 | 0.0050284 | 0.0012602 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_158-16_0_6_load_155 | 42 | 0.0024116 | 0.00060441 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_158-16_0_6_load_56 | 43 | 0.0015581 | 0.00039049 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_158-16_0_6_load_28 | 44 | 0.0031492 | 0.00078927 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_158-16_0_6_load_29 | 45 | 0.0029185 | 0.00073145 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_158-16_0_6_load_30 | 46 | 0.0034087 | 0.00085431 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_158-16_0_6_load_94 | 49 | 0.0050887 | 0.0012754 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_158-16_0_6_load_102 | 50 | 0.0045777 | 0.0011473 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_158-16_0_6_load_99 | 52 | 0.003277 | 0.00082129 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_158-16_0_6_load_96 | 53 | 0.0035959 | 0.00090121 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_158-16_0_6_load_34 | 54 | 0.0042615 | 0.001068 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_158-16_0_6_load_37 | 56 | 0.0045263 | 0.0011344 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_158-16_0_6_load_106 | 58 | 0.0051162 | 0.0012822 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_158-16_0_6_load_147 | 63 | 0.0024109 | 0.00060423 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_158-16_0_6_load_112 | 66 | 0.0023893 | 0.0005988 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_158-16_0_6_load_52 | 68 | 0.0075456 | 0.0018911 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_158-16_0_6_load_45 | 69 | 0.0008153 | 0.00020433 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_158-16_0_6_load_50 | 71 | 0.0045028 | 0.0011285 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_158-16_0_6_load_51 | 72 | 0.0048268 | 0.0012097 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_158-16_0_6_load_91 | 73 | 0.0055791 | 0.0013983 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_158-16_0_6_load_151 | 74 | 0.0024239 | 0.00060749 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_158-16_0_6_load_92 | 75 | 0.0056838 | 0.0014245 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_158-16_0_6_load_152 | 76 | 0.0022251 | 0.00055766 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_158-16_0_6_load_53 | 77 | 0.0058736 | 0.0014721 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_158-16_0_6_load_55 | 78 | 0.0014887 | 0.00037311 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_158-16_0_6_load_79 | 79 | 0.0020534 | 0.00051464 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_158-16_0_6_load_78 | 80 | 0.0049832 | 0.0012489 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_158-16_0_6_load_57 | 81 | 0.0045713 | 0.0011457 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_158-16_0_6_load_64 | 86 | 0.0056638 | 0.0014195 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_158-16_0_6_load_65 | 87 | 0.0022208 | 0.0005566 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_158-16_0_6_load_127 | 89 | 0.0039224 | 0.00098306 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_158-16_0_6_load_77 | 91 | 0.001448 | 0.0003629 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_158-16_0_6_load_110 | 92 | 0.0014498 | 0.00036336 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_158-16_0_6_load_107 | 93 | 0.0022798 | 0.00057136 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_158-16_0_6_load_129 | 94 | 0.0023819 | 0.00059696 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_158-16_0_6_load_75 | 96 | 0.004099 | 0.0010273 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_158-16_0_6_load_126 | 97 | 0.0019259 | 0.00048267 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_158-16_0_6_load_67 | 98 | 0.0020475 | 0.00051315 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_158-16_0_6_load_111 | 99 | 0.0023864 | 0.0005981 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_158-16_0_6_load_108 | 100 | 0.0012158 | 0.0003047 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_158-16_0_6_load_128 | 101 | 0.0024281 | 0.00060853 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_158-16_0_6_load_76 | 103 | 0.0038444 | 0.0009635 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_158-16_0_6_load_71 | 104 | 0.007462 | 0.0018702 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_158-16_0_6_load_68 | 105 | 0.0047658 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_158-16_0_6_load_74 | 108 | 0.0038912 | 0.00097523 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_158-16_0_6_load_140 | 110 | 0.0045674 | 0.0011447 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_158-16_0_6_load_136 | 111 | 0.0073907 | 0.0018523 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_158-16_0_6_load_133 | 112 | 0.0075922 | 0.0019028 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_158-16_0_6_load_100 | 115 | 0.0034131 | 0.00085542 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_158-16_0_6_load_139 | 117 | 0.0040652 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_158-16_0_6_load_137 | 118 | 0.0045798 | 0.0011478 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_158-16_0_6_load_80 | 119 | 0.003592 | 0.00090025 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_158-16_0_6_load_81 | 120 | 0.0016472 | 0.00041284 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_158-16_0_6_load_85 | 123 | 0.0020462 | 0.00051282 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_158-16_0_6_load_146 | 124 | 0.0083273 | 0.002087 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_158-16_0_6_load_86 | 125 | 0.0068176 | 0.0017087 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_158-16_0_6_load_88 | 126 | 0.0033112 | 0.00082985 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_158-16_0_6_load_145 | 127 | 0.0034503 | 0.00086473 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_158-16_0_6_load_149 | 128 | 0.0041765 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_158-16_0_6_load_148 | 129 | 0.0015596 | 0.00039087 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_158-16_0_6_load_109 | 130 | 0.0065219 | 0.0016346 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_158-16_0_6_load_113 | 131 | 0.0018522 | 0.00046421 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_158-16_0_6_load_114 | 132 | 0.0036923 | 0.00092539 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_158-16_0_6_load_115 | 133 | 0.0081419 | 0.0020406 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_158-16_0_6_load_116 | 134 | 0.0020694 | 0.00051863 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_158-16_0_6_load_117 | 135 | 0.0034377 | 0.00086156 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_158-16_0_6_load_125 | 136 | 0.003024 | 0.00075788 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_158-16_0_6_load_118 | 137 | 0.0097768 | 0.0024503 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_158-16_0_6_load_120 | 139 | 0.0084497 | 0.0021177 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_158-16_0_6_load_142 | 140 | 0.0075752 | 0.0018985 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_158-16_0_6_load_121 | 141 | 0.0034158 | 0.00085609 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_158-16_0_6_load_122 | 142 | 0.0018576 | 0.00046555 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_158-16_0_6_load_124 | 143 | 0.0030627 | 0.00076758 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_158-16_0_6_load_132 | 144 | 0.0020413 | 0.00051159 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_158-16_0_6_load_131 | 145 | 0.00098906 | 0.00024788 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_158-16_0_6_load_134 | 147 | 0.0078174 | 0.0019592 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_158-16_0_6_load_141 | 148 | 0.0043113 | 0.0010805 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_158-16_0_6_line_0 |  | 0 | 1 | 0.0066739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_158-16_0_6_line_1 |  | 0 | 2 | 0.016134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_158-16_0_6_line_2 |  | 1 | 3 | 0.020866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_158-16_0_6_line_3 |  | 2 | 4 | 0.024699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_158-16_0_6_line_4 |  | 2 | 5 | 0.041429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_158-16_0_6_line_5 |  | 3 | 6 | 0.035821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_158-16_0_6_line_6 |  | 3 | 7 | 0.057205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_158-16_0_6_line_7 |  | 4 | 8 | 0.015855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_158-16_0_6_line_8 |  | 5 | 9 | 0.017968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_158-16_0_6_line_9 |  | 6 | 10 | 0.025906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_158-16_0_6_line_10 |  | 7 | 11 | 0.05849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_158-16_0_6_line_11 |  | 8 | 12 | 0.01958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_158-16_0_6_line_12 |  | 9 | 13 | 0.000391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_158-16_0_6_line_13 |  | 12 | 20 | 0.0079504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_158-16_0_6_line_14 |  | 13 | 16 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_158-16_0_6_line_15 |  | 14 | 15 | 0.020992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_158-16_0_6_line_16 |  | 15 | 16 | 0.0051107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_158-16_0_6_line_17 |  | 17 | 18 | 0.015691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_158-16_0_6_line_18 |  | 18 | 19 | 0.010601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_158-16_0_6_line_19 |  | 18 | 20 | 0.0114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_158-16_0_6_line_20 |  | 19 | 21 | 0.03297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_158-16_0_6_line_21 |  | 19 | 22 | 0.017951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_158-16_0_6_line_22 |  | 21 | 23 | 0.012366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_158-16_0_6_line_23 |  | 22 | 24 | 0.0052061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_158-16_0_6_line_24 |  | 23 | 29 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_158-16_0_6_line_25 |  | 24 | 69 | 0.018709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_158-16_0_6_line_26 |  | 25 | 26 | 0.030833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_158-16_0_6_line_27 |  | 25 | 27 | 0.024069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_158-16_0_6_line_28 |  | 26 | 28 | 0.026019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_158-16_0_6_line_29 |  | 26 | 29 | 0.005111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_158-16_0_6_line_30 |  | 28 | 30 | 0.003687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_158-16_0_6_line_31 |  | 28 | 31 | 0.021899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_158-16_0_6_line_32 |  | 30 | 32 | 0.012764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_158-16_0_6_line_33 |  | 31 | 37 | 0.011664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_158-16_0_6_line_34 |  | 32 | 39 | 0.029407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_158-16_0_6_line_35 |  | 33 | 34 | 0.0072537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_158-16_0_6_line_36 |  | 33 | 35 | 0.003375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_158-16_0_6_line_37 |  | 33 | 36 | 0.0059111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_158-16_0_6_line_38 |  | 34 | 42 | 0.0053021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_158-16_0_6_line_39 |  | 35 | 38 | 0.002838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_158-16_0_6_line_40 |  | 36 | 43 | 0.0077637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_158-16_0_6_line_41 |  | 37 | 44 | 0.01561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_158-16_0_6_line_42 |  | 39 | 70 | 0.010064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_158-16_0_6_line_43 |  | 40 | 41 | 0.022236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_158-16_0_6_line_44 |  | 41 | 49 | 0.017146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_158-16_0_6_line_45 |  | 42 | 76 | 0.0049117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_158-16_0_6_line_46 |  | 43 | 62 | 0.0209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_158-16_0_6_line_47 |  | 44 | 45 | 0.013584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_158-16_0_6_line_48 |  | 45 | 46 | 0.021229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_158-16_0_6_line_49 |  | 46 | 47 | 0.01832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_158-16_0_6_line_50 |  | 47 | 48 | 0.004352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_158-16_0_6_line_51 |  | 48 | 49 | 0.0219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_158-16_0_6_line_52 |  | 48 | 50 | 0.011469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_158-16_0_6_line_53 |  | 51 | 52 | 0.014238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_158-16_0_6_line_54 |  | 51 | 53 | 0.0025806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_158-16_0_6_line_55 |  | 53 | 114 | 0.024911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_158-16_0_6_line_56 |  | 54 | 55 | 0.0038752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_158-16_0_6_line_57 |  | 55 | 56 | 0.022803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_158-16_0_6_line_58 |  | 55 | 57 | 0.027906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_158-16_0_6_line_59 |  | 57 | 58 | 0.05975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_158-16_0_6_line_60 |  | 58 | 59 | 0.04794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_158-16_0_6_line_61 |  | 59 | 60 | 0.00466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_158-16_0_6_line_62 |  | 59 | 61 | 0.019644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_158-16_0_6_line_63 |  | 60 | 63 | 0.005926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_158-16_0_6_line_64 |  | 60 | 64 | 0.019252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_158-16_0_6_line_65 |  | 61 | 62 | 0.011466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_158-16_0_6_line_66 |  | 62 | 68 | 0.034113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_158-16_0_6_line_67 |  | 63 | 129 | 0.0097497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_158-16_0_6_line_68 |  | 64 | 125 | 0.021361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_158-16_0_6_line_69 |  | 64 | 126 | 0.011291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_158-16_0_6_line_70 |  | 65 | 66 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_158-16_0_6_line_71 |  | 65 | 67 | 0.003104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_158-16_0_6_line_72 |  | 66 | 99 | 0.001039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_158-16_0_6_line_73 |  | 67 | 125 | 0.029349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_158-16_0_6_line_74 |  | 68 | 77 | 0.015403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_158-16_0_6_line_75 |  | 70 | 71 | 0.017258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_158-16_0_6_line_76 |  | 70 | 72 | 0.024793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_158-16_0_6_line_77 |  | 71 | 73 | 0.034341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_158-16_0_6_line_78 |  | 72 | 74 | 0.0059463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_158-16_0_6_line_79 |  | 73 | 75 | 0.0086351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_158-16_0_6_line_80 |  | 74 | 76 | 0.0065316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_158-16_0_6_line_81 |  | 75 | 115 | 0.027457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_158-16_0_6_line_82 |  | 78 | 79 | 0.0024246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_158-16_0_6_line_83 |  | 79 | 80 | 0.00050957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_158-16_0_6_line_84 |  | 80 | 91 | 0.013876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_158-16_0_6_line_85 |  | 81 | 82 | 0.019684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_158-16_0_6_line_86 |  | 81 | 83 | 0.021323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_158-16_0_6_line_87 |  | 82 | 84 | 0.033017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_158-16_0_6_line_88 |  | 82 | 85 | 0.02532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_158-16_0_6_line_89 |  | 83 | 86 | 0.018793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_158-16_0_6_line_90 |  | 83 | 87 | 0.03228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_158-16_0_6_line_91 |  | 84 | 88 | 0.003897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_158-16_0_6_line_92 |  | 84 | 89 | 0.01904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_158-16_0_6_line_93 |  | 85 | 90 | 0.026665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_158-16_0_6_line_94 |  | 85 | 91 | 0.013235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_158-16_0_6_line_95 |  | 86 | 95 | 0.014886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_158-16_0_6_line_96 |  | 87 | 96 | 0.014793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_158-16_0_6_line_97 |  | 88 | 94 | 0.021926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_158-16_0_6_line_98 |  | 89 | 97 | 0.017573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_158-16_0_6_line_99 |  | 90 | 92 | 0.012326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_158-16_0_6_line_100 |  | 90 | 93 | 0.013877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_158-16_0_6_line_101 |  | 92 | 99 | 0.01361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_158-16_0_6_line_102 |  | 93 | 100 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_158-16_0_6_line_103 |  | 94 | 101 | 0.026218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_158-16_0_6_line_104 |  | 95 | 98 | 0.010865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_158-16_0_6_line_105 |  | 96 | 102 | 0.013046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_158-16_0_6_line_106 |  | 97 | 136 | 0.0069828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_158-16_0_6_line_107 |  | 98 | 103 | 0.022393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_158-16_0_6_line_108 |  | 100 | 130 | 0.0046232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_158-16_0_6_line_109 |  | 101 | 146 | 0.047513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_158-16_0_6_line_110 |  | 102 | 108 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_158-16_0_6_line_111 |  | 103 | 104 | 0.0018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_158-16_0_6_line_112 |  | 104 | 106 | 0.01588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_158-16_0_6_line_113 |  | 105 | 106 | 0.019251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_158-16_0_6_line_114 |  | 106 | 107 | 0.041291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_158-16_0_6_line_115 |  | 107 | 109 | 0.001691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_158-16_0_6_line_116 |  | 107 | 110 | 0.01814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_158-16_0_6_line_117 |  | 109 | 111 | 0.015656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_158-16_0_6_line_118 |  | 109 | 112 | 0.025224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_158-16_0_6_line_119 |  | 110 | 113 | 0.005617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_158-16_0_6_line_120 |  | 112 | 147 | 0.015897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_158-16_0_6_line_121 |  | 113 | 148 | 0.01546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_158-16_0_6_line_122 |  | 113 | 118 | 0.02084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_158-16_0_6_line_123 |  | 114 | 115 | 0.0079578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_158-16_0_6_line_124 |  | 116 | 117 | 0.014622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_158-16_0_6_line_125 |  | 116 | 118 | 0.0039436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_158-16_0_6_line_126 |  | 119 | 120 | 0.017456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_158-16_0_6_line_127 |  | 119 | 121 | 0.0065695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_158-16_0_6_line_128 |  | 120 | 122 | 0.024269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_158-16_0_6_line_129 |  | 121 | 123 | 0.012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_158-16_0_6_line_130 |  | 122 | 124 | 0.0097889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_158-16_0_6_line_131 |  | 123 | 126 | 0.012763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_158-16_0_6_line_132 |  | 127 | 128 | 0.0017716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_158-16_0_6_line_133 |  | 128 | 129 | 0.0057136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_158-16_0_6_line_134 |  | 131 | 132 | 0.0010533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_158-16_0_6_line_135 |  | 131 | 133 | 0.037639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_158-16_0_6_line_136 |  | 132 | 134 | 0.02403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_158-16_0_6_line_137 |  | 133 | 135 | 0.002295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_158-16_0_6_line_138 |  | 134 | 136 | 0.022798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_158-16_0_6_line_139 |  | 135 | 137 | 0.029618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_158-16_0_6_line_140 |  | 137 | 138 | 0.015591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
141 | LV_158-16_0_6_line_141 |  | 138 | 139 | 0.021368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_158-16_0_6_line_142 |  | 139 | 140 | 0.03563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
143 | LV_158-16_0_6_line_143 |  | 141 | 142 | 0.02194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_158-16_0_6_line_144 |  | 142 | 143 | 0.018087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
145 | LV_158-16_0_6_line_145 |  | 143 | 144 | 0.012704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
146 | LV_158-16_0_6_line_146 |  | 144 | 145 | 0.033231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
147 | LV_158-16_0_6_line_147 |  | 145 | 146 | 0.052004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_158-16_0_6_trafo_133 | 0.63 MVA 20/0.4 kV | 149 | 112 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2697367.2572 | 1233437.9497 | 2697364.5106 | 1233431.8672
1 | 2697375.9393 | 1233451.4395 | 2697369.5355 | 1233442.995 | 2697367.2572 | 1233437.9497
2 | 2697355.9231 | 1233412.8499 | 2697364.5106 | 1233431.8672
3 | 2697375.9393 | 1233451.4395 | 2697385.8031 | 1233444.6627 | 2697398.0568 | 1233441.2073
4 | 2697375.9393 | 1233451.4395 | 2697387.1033 | 1233466.5001 | 2697394.4679 | 1233476.8395 | 2697397.8239 | 1233483.6662 | 2697398.6628 | 1233485.8941
5 | 2697355.9231 | 1233412.8499 | 2697388.8737 | 1233398.8002
6 | 2697355.9231 | 1233412.8499 | 2697303.1423 | 1233435.2688
7 | 2697413.3168 | 1233436.9042 | 2697398.0568 | 1233441.2073
8 | 2697398.6628 | 1233485.8941 | 2697402.3443 | 1233495.6713 | 2697407.0909 | 1233501.2754 | 2697407.181 | 1233501.427
9 | 2697388.8737 | 1233398.8002 | 2697412.7043 | 1233388.6392
10 | 2697303.1423 | 1233435.2688 | 2697314.6975 | 1233461.5884 | 2697330.6179 | 1233460.4149 | 2697331.0212 | 1233474.1907
11 | 2697432.3408 | 1233432.4329 | 2697425.8624 | 1233433.3664 | 2697413.3168 | 1233436.9042
12 | 2697407.3808 | 1233501.7631 | 2697407.181 | 1233501.427
13 | 2697432.3408 | 1233432.4329 | 2697440.2099 | 1233431.2989
14 | 2697412.747 | 1233510.9753 | 2697411.7773 | 1233509.158 | 2697407.3808 | 1233501.7631
15 | 2697412.4754 | 1233515.9967 | 2697392.7521 | 1233508.8098
16 | 2697412.4754 | 1233515.9967 | 2697413.0594 | 1233513.6268 | 2697412.747 | 1233510.9753
17 | 2697451.4937 | 1233429.6728 | 2697451.9081 | 1233413.9877
18 | 2697451.4937 | 1233429.6728 | 2697452.4487 | 1233440.2295
19 | 2697451.4937 | 1233429.6728 | 2697440.2099 | 1233431.2989
20 | 2697452.4487 | 1233440.2295 | 2697470.5675 | 1233450.9011 | 2697480.9974 | 1233456.7171
21 | 2697452.4487 | 1233440.2295 | 2697450.702 | 1233455.312 | 2697449.8321 | 1233457.9399
22 | 2697492.2377 | 1233461.7924 | 2697486.7245 | 1233459.7615 | 2697485.319 | 1233459.1269 | 2697480.9974 | 1233456.7171
23 | 2697449.8321 | 1233457.9399 | 2697448.1961 | 1233462.8823
24 | 2697507.234 | 1233467.7816 | 2697497.7508 | 1233463.8231 | 2697492.2377 | 1233461.7924
25 | 2697440.3203 | 1233479.8043 | 2697446.6787 | 1233467.4661 | 2697448.1961 | 1233462.8823
26 | 2697509.6478 | 1233463.2734 | 2697498.8461 | 1233434.3941
27 | 2697496.2187 | 1233412.7715 | 2697494.7374 | 1233416.2943 | 2697493.3025 | 1233416.9824 | 2697495.1356 | 1233421.0932 | 2697494.5747 | 1233422.9743 | 2697498.8461 | 1233434.3941
28 | 2697523.0829 | 1233440.9886 | 2697519.0474 | 1233446.9601 | 2697509.6478 | 1233463.2734
29 | 2697507.234 | 1233467.7816 | 2697509.6478 | 1233463.2734
30 | 2697523.0829 | 1233440.9886 | 2697524.1456 | 1233444.5197
31 | 2697523.0829 | 1233440.9886 | 2697527.2572 | 1233435.7866 | 2697531.4512 | 1233432.1527 | 2697539.3994 | 1233426.6281
32 | 2697524.1456 | 1233444.5197 | 2697527.851 | 1233456.7343
33 | 2697539.3994 | 1233426.6281 | 2697539.5778 | 1233426.5041 | 2697549.3875 | 1233420.6052
34 | 2697536.3878 | 1233484.8752 | 2697527.851 | 1233456.7343
35 | 2697486.2089 | 1233507.7884 | 2697493.2262 | 1233505.9516
36 | 2697482.8614 | 1233508.2894 | 2697486.2089 | 1233507.7884
37 | 2697486.2089 | 1233507.7884 | 2697483.0289 | 1233512.7712
38 | 2697493.2262 | 1233505.9516 | 2697498.3555 | 1233504.6089
39 | 2697482.8614 | 1233508.2894 | 2697481.4339 | 1233510.7422
40 | 2697479.3764 | 1233519.6199 | 2697482.7116 | 1233513.2684 | 2697483.0289 | 1233512.7712
41 | 2697562.7653 | 1233412.5606 | 2697549.3875 | 1233420.6052
42 | 2697539.3092 | 1233494.5053 | 2697536.3878 | 1233484.8752
43 | 2697577.8543 | 1233410.4657 | 2697570.7328 | 1233414.7512 | 2697564.0205 | 1233414.9634 | 2697557.8363 | 1233418.6685
44 | 2697577.8543 | 1233410.4657 | 2697592.545 | 1233401.6253
45 | 2697503.1071 | 1233503.3651 | 2697498.3555 | 1233504.6089
46 | 2697478.1226 | 1233538.6674 | 2697475.4382 | 1233534.7539 | 2697474.8558 | 1233530.5634 | 2697475.9271 | 1233526.1889 | 2697479.3764 | 1233519.6199
47 | 2697574.4065 | 1233405.5604 | 2697562.7653 | 1233412.5606
48 | 2697574.4065 | 1233405.5604 | 2697592.5991 | 1233394.6205
49 | 2697608.299 | 1233385.1796 | 2697592.5991 | 1233394.6205
50 | 2697609.8907 | 1233389.2309 | 2697608.299 | 1233385.1796
51 | 2697609.8907 | 1233389.2309 | 2697600.0892 | 1233394.4961 | 2697598.1802 | 1233398.2341 | 2697592.545 | 1233401.6253
52 | 2697609.8907 | 1233389.2309 | 2697618.4123 | 1233381.6764 | 2697618.4646 | 1233381.6146
53 | 2697640.5959 | 1233447.7005 | 2697644.2574 | 1233448.3611 | 2697648.6584 | 1233449.1785 | 2697651.6 | 1233454.4862
54 | 2697640.5959 | 1233447.7005 | 2697639.7804 | 1233450.1488
55 | 2697632.7424 | 1233474.0353 | 2697633.3476 | 1233471.7658 | 2697634.0173 | 1233469.7197 | 2697637.4098 | 1233457.2663 | 2697639.7804 | 1233450.1488
56 | 2697338.2138 | 1233524.0972 | 2697334.3789 | 1233524.6542
57 | 2697338.2138 | 1233524.0972 | 2697360.8318 | 1233521.2012
58 | 2697338.2138 | 1233524.0972 | 2697349.5731 | 1233498.5978
59 | 2697349.5731 | 1233498.5978 | 2697405.9866 | 1233518.2839
60 | 2697451.2496 | 1233534.079 | 2697405.9866 | 1233518.2839
61 | 2697451.2496 | 1233534.079 | 2697449.7838 | 1233538.5026
62 | 2697451.2496 | 1233534.079 | 2697452.6629 | 1233530.0881 | 2697467.4797 | 1233534.323
63 | 2697449.7838 | 1233538.5026 | 2697447.166 | 1233541.6064 | 2697446.2695 | 1233543.2425
64 | 2697449.7838 | 1233538.5026 | 2697468.0746 | 1233544.6737
65 | 2697467.4797 | 1233534.323 | 2697478.1226 | 1233538.6674
66 | 2697478.1226 | 1233538.6674 | 2697490.5779 | 1233543.3084 | 2697495.942 | 1233545.8761 | 2697500.5829 | 1233549.1435 | 2697506.794 | 1233555.9282
67 | 2697446.2695 | 1233543.2425 | 2697442.069 | 1233550.9075 | 2697441.4587 | 1233551.7114
68 | 2697468.0746 | 1233544.6737 | 2697488.2091 | 1233551.808
69 | 2697468.0746 | 1233544.6737 | 2697466.8663 | 1233548.6346 | 2697468.5049 | 1233555.5938
70 | 2697511.7725 | 1233569.998 | 2697522.2761 | 1233585.6409
71 | 2697509.1775 | 1233571.7122 | 2697511.7725 | 1233569.998
72 | 2697522.8553 | 1233586.5035 | 2697522.2761 | 1233585.6409
73 | 2697509.1775 | 1233571.7122 | 2697501.7386 | 1233562.6947 | 2697496.9562 | 1233557.4346 | 2697491.6676 | 1233553.0335 | 2697488.2091 | 1233551.808
74 | 2697506.794 | 1233555.9282 | 2697506.794 | 1233555.9282 | 2697515.552 | 1233568.599
75 | 2697539.3092 | 1233494.5053 | 2697556.1677 | 1233490.8118
76 | 2697539.3092 | 1233494.5053 | 2697515.2216 | 1233500.3767
77 | 2697556.1677 | 1233490.8118 | 2697589.7135 | 1233483.4624
78 | 2697509.4445 | 1233501.7849 | 2697515.2216 | 1233500.3767
79 | 2697598.1486 | 1233481.6144 | 2697589.7135 | 1233483.4624
80 | 2697503.1071 | 1233503.3651 | 2697505.0758 | 1233502.8498 | 2697509.4445 | 1233501.7849
81 | 2697598.1486 | 1233481.6144 | 2697624.969 | 1233475.7384
82 | 2697537.8979 | 1233601.5645 | 2697537.7882 | 1233601.4146 | 2697536.4667 | 1233599.6074
83 | 2697538.1987 | 1233601.9758 | 2697537.8979 | 1233601.5645
84 | 2697538.1987 | 1233601.9758 | 2697543.7571 | 1233609.5742 | 2697545.5093 | 1233612.1493 | 2697546.0652 | 1233613.3757
85 | 2697570.4325 | 1233642.7587 | 2697571.6986 | 1233641.7342 | 2697581.7844 | 1233633.427 | 2697585.0486 | 1233629.6545
86 | 2697601.2915 | 1233616.7017 | 2697596.2733 | 1233621.6562 | 2697590.151 | 1233623.7573 | 2697585.0486 | 1233629.6545
87 | 2697590.1961 | 1233666.634 | 2697590.0717 | 1233659.46 | 2697588.1381 | 1233658.2496 | 2697572.2847 | 1233645.2353 | 2697570.4325 | 1233642.7587
88 | 2697552.9914 | 1233624.5256 | 2697555.9399 | 1233627.5651 | 2697563.8226 | 1233634.444 | 2697568.9802 | 1233640.8223 | 2697570.4325 | 1233642.7587
89 | 2697601.2915 | 1233616.7017 | 2697584.1634 | 1233608.9686
90 | 2697601.2915 | 1233616.7017 | 2697607.8848 | 1233611.2726 | 2697616.0441 | 1233608.2377 | 2697628.5064 | 1233605.9852 | 2697630.0502 | 1233604.1883
91 | 2697590.1961 | 1233666.634 | 2697591.4834 | 1233670.3134
92 | 2697590.1961 | 1233666.634 | 2697606.3988 | 1233656.6345
93 | 2697537.3161 | 1233608.034 | 2697550.1946 | 1233627.0038 | 2697552.9914 | 1233624.5256
94 | 2697552.9914 | 1233624.5256 | 2697548.7536 | 1233619.3078 | 2697546.0652 | 1233613.3757
95 | 2697570.596 | 1233602.8431 | 2697584.1634 | 1233608.9686
96 | 2697637.2584 | 1233591.3756 | 2697632.397 | 1233601.4568 | 2697630.0502 | 1233604.1883
97 | 2697591.4834 | 1233670.3134 | 2697592.9612 | 1233672.5394 | 2697595.6714 | 1233676.2533 | 2697604.6828 | 1233687.8127
98 | 2697621.3533 | 1233647.4052 | 2697606.3988 | 1233656.6345
99 | 2697537.3161 | 1233608.034 | 2697536.7912 | 1233607.2581 | 2697530.4421 | 1233597.8025
100 | 2697537.3161 | 1233608.034 | 2697525.211 | 1233614.8181 | 2697525.211 | 1233614.8181
101 | 2697530.4421 | 1233597.8025 | 2697522.8553 | 1233586.5035
102 | 2697525.211 | 1233614.8181 | 2697521.2977 | 1233611.0512 | 2697518.5738 | 1233610.4727 | 2697513.3296 | 1233613.8783
103 | 2697620.802 | 1233708.4897 | 2697604.6828 | 1233687.8127
104 | 2697570.596 | 1233602.8431 | 2697575.26 | 1233593.0296
105 | 2697642.9248 | 1233579.6248 | 2697637.2584 | 1233591.3756
106 | 2697621.3533 | 1233647.4052 | 2697627.2955 | 1233643.7379
107 | 2697575.26 | 1233593.0296 | 2697584.872 | 1233572.8048
108 | 2697513.3296 | 1233613.8783 | 2697511.6934 | 1233614.9409 | 2697510.7885 | 1233617.4553
109 | 2697639.5871 | 1233747.6493 | 2697637.2301 | 1233744.5639 | 2697640.6996 | 1233741.6966 | 2697627.0297 | 1233724.3815 | 2697620.802 | 1233708.4897
110 | 2697642.9248 | 1233579.6248 | 2697648.8406 | 1233567.3595
111 | 2697585.669 | 1233571.1277 | 2697584.872 | 1233572.8048
112 | 2697593.8243 | 1233557.8023 | 2697590.721 | 1233560.4978 | 2697585.669 | 1233571.1277
113 | 2697593.8243 | 1233557.8023 | 2697611.4158 | 1233565.6208
114 | 2697592.342 | 1233518.9827 | 2697595.2638 | 1233534.709 | 2697595.839 | 1233544.4033 | 2697596.9614 | 1233546.6011 | 2697598.0122 | 1233549.0091 | 2697598.1888 | 1233551.625 | 2697597.481 | 1233554.1486 | 2697595.9692 | 1233556.292 | 2697593.8243 | 1233557.8023
115 | 2697592.342 | 1233518.9827 | 2697590.6854 | 1233519.3447
116 | 2697592.342 | 1233518.9827 | 2697610.0682 | 1233515.1308
117 | 2697587.5072 | 1233504.0146 | 2697590.6854 | 1233519.3447
118 | 2697590.6854 | 1233519.3447 | 2697566.0414 | 1233524.7219
119 | 2697615.5571 | 1233513.938 | 2697610.0682 | 1233515.1308
120 | 2697566.0414 | 1233524.7219 | 2697566.0414 | 1233524.7219 | 2697562.9857 | 1233509.1213
121 | 2697612.0489 | 1233498.8804 | 2697615.5571 | 1233513.938
122 | 2697615.5571 | 1233513.938 | 2697635.9215 | 1233509.5136
123 | 2697632.7424 | 1233474.0353 | 2697624.969 | 1233475.7384
124 | 2697636.7469 | 1233494.3716 | 2697639.7752 | 1233508.6764
125 | 2697639.7752 | 1233508.6764 | 2697635.9215 | 1233509.5136
126 | 2697470.6138 | 1233578.7482 | 2697456.8494 | 1233577.2025 | 2697453.2594 | 1233577.5363
127 | 2697477.1423 | 1233579.4814 | 2697470.6138 | 1233578.7482
128 | 2697429.0943 | 1233579.7827 | 2697453.2594 | 1233577.5363
129 | 2697477.1423 | 1233579.4814 | 2697476.715 | 1233575.994 | 2697472.5963 | 1233567.5993
130 | 2697429.0943 | 1233579.7827 | 2697419.3989 | 1233581.1329
131 | 2697472.5963 | 1233567.5993 | 2697470.1649 | 1233562.6435 | 2697468.5049 | 1233555.5938
132 | 2697437.9675 | 1233556.2337 | 2697436.8547 | 1233557.6122
133 | 2697441.4587 | 1233551.7114 | 2697438.9424 | 1233555.0259 | 2697437.9675 | 1233556.2337
134 | 2697666.2952 | 1233616.1686 | 2697665.4869 | 1233616.8439
135 | 2697666.2952 | 1233616.1686 | 2697676.0464 | 1233608.0233 | 2697692.3042 | 1233589.1189
136 | 2697665.4869 | 1233616.8439 | 2697650.251 | 1233629.5708 | 2697646.6959 | 1233631.7649
137 | 2697693.8006 | 1233587.3789 | 2697692.3042 | 1233589.1189
138 | 2697646.6959 | 1233631.7649 | 2697627.2955 | 1233643.7379
139 | 2697713.1127 | 1233564.9229 | 2697693.8006 | 1233587.3789
140 | 2697724.035 | 1233553.8054 | 2697714.5742 | 1233563.2235 | 2697713.1127 | 1233564.9229
141 | 2697724.035 | 1233553.8054 | 2697708.1533 | 1233539.5105
142 | 2697698.8461 | 1233514.9738 | 2697690.6005 | 1233523.7114 | 2697708.1533 | 1233539.5105
143 | 2697750.9396 | 1233666.5524 | 2697750.8763 | 1233666.5744 | 2697737.6128 | 1233673.3501 | 2697731.992 | 1233677.4876
144 | 2697731.992 | 1233677.4876 | 2697718.804 | 1233687.1955 | 2697717.4417 | 1233688.2304
145 | 2697707.3253 | 1233695.9151 | 2697717.4417 | 1233688.2304
146 | 2697680.8634 | 1233716.0162 | 2697707.3253 | 1233695.9151
147 | 2697639.5871 | 1233747.6493 | 2697673.543 | 1233721.5769 | 2697680.8634 | 1233716.0162

## bus_geodata
| x | y | coords
0 | 2697367.2572 | 1233437.9497
1 | 2697364.5106 | 1233431.8672
2 | 2697375.9393 | 1233451.4395
3 | 2697355.9231 | 1233412.8499
4 | 2697398.0568 | 1233441.2073
5 | 2697398.6628 | 1233485.8941
6 | 2697388.8737 | 1233398.8002
7 | 2697303.1423 | 1233435.2688
8 | 2697413.3168 | 1233436.9042
9 | 2697407.181 | 1233501.427
10 | 2697412.7043 | 1233388.6392
11 | 2697331.0212 | 1233474.1907
12 | 2697432.3408 | 1233432.4329
13 | 2697407.3808 | 1233501.7631
14 | 2697392.7521 | 1233508.8098
15 | 2697412.4754 | 1233515.9967
16 | 2697412.747 | 1233510.9753
17 | 2697451.9081 | 1233413.9877
18 | 2697451.4937 | 1233429.6728
19 | 2697452.4487 | 1233440.2295
20 | 2697440.2099 | 1233431.2989
21 | 2697480.9974 | 1233456.7171
22 | 2697449.8321 | 1233457.9399
23 | 2697492.2377 | 1233461.7924
24 | 2697448.1961 | 1233462.8823
25 | 2697498.8461 | 1233434.3941
26 | 2697509.6478 | 1233463.2734
27 | 2697496.2187 | 1233412.7715
28 | 2697523.0829 | 1233440.9886
29 | 2697507.234 | 1233467.7816
30 | 2697524.1456 | 1233444.5197
31 | 2697539.3994 | 1233426.6281
32 | 2697527.851 | 1233456.7343
33 | 2697486.2089 | 1233507.7884
34 | 2697493.2262 | 1233505.9516
35 | 2697482.8614 | 1233508.2894
36 | 2697483.0289 | 1233512.7712
37 | 2697549.3875 | 1233420.6052
38 | 2697481.4339 | 1233510.7422
39 | 2697536.3878 | 1233484.8752
40 | 2697557.8363 | 1233418.6685
41 | 2697577.8543 | 1233410.4657
42 | 2697498.3555 | 1233504.6089
43 | 2697479.3764 | 1233519.6199
44 | 2697562.7653 | 1233412.5606
45 | 2697574.4065 | 1233405.5604
46 | 2697592.5991 | 1233394.6205
47 | 2697608.299 | 1233385.1796
48 | 2697609.8907 | 1233389.2309
49 | 2697592.545 | 1233401.6253
50 | 2697618.4646 | 1233381.6146
51 | 2697640.5959 | 1233447.7005
52 | 2697651.6 | 1233454.4862
53 | 2697639.7804 | 1233450.1488
54 | 2697334.3789 | 1233524.6542
55 | 2697338.2138 | 1233524.0972
56 | 2697360.8318 | 1233521.2012
57 | 2697349.5731 | 1233498.5978
58 | 2697405.9866 | 1233518.2839
59 | 2697451.2496 | 1233534.079
60 | 2697449.7838 | 1233538.5026
61 | 2697467.4797 | 1233534.323
62 | 2697478.1226 | 1233538.6674
63 | 2697446.2695 | 1233543.2425
64 | 2697468.0746 | 1233544.6737
65 | 2697511.7725 | 1233569.998
66 | 2697522.2761 | 1233585.6409
67 | 2697509.1775 | 1233571.7122
68 | 2697506.794 | 1233555.9282
69 | 2697440.3203 | 1233479.8043
70 | 2697539.3092 | 1233494.5053
71 | 2697556.1677 | 1233490.8118
72 | 2697515.2216 | 1233500.3767
73 | 2697589.7135 | 1233483.4624
74 | 2697509.4445 | 1233501.7849
75 | 2697598.1486 | 1233481.6144
76 | 2697503.1071 | 1233503.3651
77 | 2697515.552 | 1233568.599
78 | 2697536.4667 | 1233599.6074
79 | 2697537.8979 | 1233601.5645
80 | 2697538.1987 | 1233601.9758
81 | 2697585.0486 | 1233629.6545
82 | 2697570.4325 | 1233642.7587
83 | 2697601.2915 | 1233616.7017
84 | 2697590.1961 | 1233666.634
85 | 2697552.9914 | 1233624.5256
86 | 2697584.1634 | 1233608.9686
87 | 2697630.0502 | 1233604.1883
88 | 2697591.4834 | 1233670.3134
89 | 2697606.3988 | 1233656.6345
90 | 2697537.3161 | 1233608.034
91 | 2697546.0652 | 1233613.3757
92 | 2697530.4421 | 1233597.8025
93 | 2697525.211 | 1233614.8181
94 | 2697604.6828 | 1233687.8127
95 | 2697570.596 | 1233602.843
96 | 2697637.2584 | 1233591.3756
97 | 2697621.3533 | 1233647.4052
98 | 2697575.26 | 1233593.0296
99 | 2697522.8553 | 1233586.5035
100 | 2697513.3296 | 1233613.8783
101 | 2697620.802 | 1233708.4897
102 | 2697642.9248 | 1233579.6248
103 | 2697584.872 | 1233572.8048
104 | 2697585.669 | 1233571.1277
105 | 2697611.4158 | 1233565.6208
106 | 2697593.8243 | 1233557.8023
107 | 2697592.342 | 1233518.9827
108 | 2697648.8406 | 1233567.3595
109 | 2697590.6854 | 1233519.3447
110 | 2697610.0682 | 1233515.1308
111 | 2697587.5072 | 1233504.0146
112 | 2697566.0414 | 1233524.7219
113 | 2697615.5571 | 1233513.938
114 | 2697632.7424 | 1233474.0353
115 | 2697624.969 | 1233475.7384
116 | 2697639.7752 | 1233508.6764
117 | 2697636.7469 | 1233494.3716
118 | 2697635.9215 | 1233509.5136
119 | 2697470.6138 | 1233578.7482
120 | 2697453.2594 | 1233577.5363
121 | 2697477.1423 | 1233579.4814
122 | 2697429.0943 | 1233579.7827
123 | 2697472.5963 | 1233567.5993
124 | 2697419.3989 | 1233581.1329
125 | 2697488.2091 | 1233551.808
126 | 2697468.5049 | 1233555.5938
127 | 2697436.8547 | 1233557.6122
128 | 2697437.9675 | 1233556.2337
129 | 2697441.4587 | 1233551.7114
130 | 2697510.7885 | 1233617.4553
131 | 2697666.2952 | 1233616.1686
132 | 2697665.4869 | 1233616.8439
133 | 2697692.3042 | 1233589.1189
134 | 2697646.6959 | 1233631.7649
135 | 2697693.8006 | 1233587.3789
136 | 2697627.2955 | 1233643.7379
137 | 2697713.1127 | 1233564.9229
138 | 2697724.035 | 1233553.8054
139 | 2697708.1533 | 1233539.5105
140 | 2697698.8461 | 1233514.9739
141 | 2697750.9396 | 1233666.5524
142 | 2697731.992 | 1233677.4876
143 | 2697717.4417 | 1233688.2303
144 | 2697707.3253 | 1233695.9151
145 | 2697680.8634 | 1233716.0162
146 | 2697639.5871 | 1233747.6493
147 | 2697562.9857 | 1233509.1213
148 | 2697612.0489 | 1233498.8804
149 | 2697562.9606 | 1233508.993

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97125 | -0.55536 | 0.0059346 | 0.0014873
1 | 0.97114 | -0.55745 | 0.0046546 | 0.0011665
2 | 0.97159 | -0.54853 | 0 | 0
3 | 0.9709 | -0.56221 | 0 | 0
4 | 0.97252 | -0.53016 | 0.0052993 | 0.0013281
5 | 0.97092 | -0.56184 | 0.0080235 | 0.0020109
6 | 0.97077 | -0.56487 | 0.0027918 | 0.00069969
7 | 0.97046 | -0.57103 | 0 | 0
8 | 0.97286 | -0.52349 | 0.0016731 | 0.00041933
9 | 0.97076 | -0.56495 | 0.00075415 | 0.00018901
10 | 0.97074 | -0.56545 | 0.0012142 | 0.00030431
11 | 0.97 | -0.58004 | 0.0083263 | 0.0020868
12 | 0.97303 | -0.52008 | 0.0016772 | 0.00042033
13 | 0.97076 | -0.56501 | 0.00069362 | 0.00017384
14 | 0.97063 | -0.56753 | 0.0019808 | 0.00049645
15 | 0.97067 | -0.56676 | 0 | 0
16 | 0.97068 | -0.56658 | 0.005938 | 0.0014882
17 | 0.97316 | -0.51766 | 0.0039401 | 0.00098748
18 | 0.97321 | -0.51653 | 0 | 0
19 | 0.97332 | -0.5144 | 0 | 0
20 | 0.97311 | -0.51865 | 0.0016332 | 0.00040931
21 | 0.97368 | -0.50738 | 0.0024104 | 0.00060411
22 | 0.97327 | -0.5155 | 0.0012308 | 0.00030846
23 | 0.97382 | -0.50463 | 0.0026583 | 0.00066623
24 | 0.97326 | -0.5157 | 0.001287 | 0.00032254
25 | 0.97374 | -0.5061 | 0.0042199 | 0.0010576
26 | 0.97407 | -0.49971 | 0 | 0
27 | 0.97359 | -0.50922 | 0.0070542 | 0.001768
28 | 0.97443 | -0.49262 | 0 | 0
29 | 0.97401 | -0.5009 | 0 | 0
30 | 0.9745 | -0.49118 | 0 | 0
31 | 0.97378 | -0.50542 | 0.0030233 | 0.00075771
32 | 0.97475 | -0.48622 | 0.0013757 | 0.00034479
33 | 0.97701 | -0.44185 | 0 | 0
34 | 0.97681 | -0.44589 | 0.0026194 | 0.0006565
35 | 0.97696 | -0.44285 | 0 | 0
36 | 0.9772 | -0.43821 | 0.0025802 | 0.00064665
37 | 0.97346 | -0.51159 | 0.003103 | 0.00077768
38 | 0.97692 | -0.44369 | 0.016254 | 0.0040736
39 | 0.97534 | -0.47463 | 0.0043213 | 0.001083
40 | 0.9717 | -0.54646 | 0.0015156 | 0.00037985
41 | 0.97173 | -0.54584 | 0.0050284 | 0.0012602
42 | 0.97666 | -0.44879 | 0.0024116 | 0.00060441
43 | 0.97744 | -0.43336 | 0.0015581 | 0.00039049
44 | 0.97309 | -0.51897 | 0.0031492 | 0.00078927
45 | 0.97281 | -0.52461 | 0.0029185 | 0.00073145
46 | 0.97242 | -0.53229 | 0.0034087 | 0.00085431
47 | 0.97214 | -0.53776 | 0 | 0
48 | 0.97207 | -0.53906 | 0 | 0
49 | 0.97184 | -0.54376 | 0.0050887 | 0.0012754
50 | 0.97202 | -0.54003 | 0.0045777 | 0.0011473
51 | 0.9752 | -0.4774 | 0 | 0
52 | 0.97516 | -0.47825 | 0.003277 | 0.00082129
53 | 0.97521 | -0.47724 | 0.0035959 | 0.00090121
54 | 0.97785 | -0.42558 | 0.0042615 | 0.001068
55 | 0.97786 | -0.42528 | 0 | 0
56 | 0.97777 | -0.42716 | 0.0045263 | 0.0011344
57 | 0.97809 | -0.42081 | 0 | 0
58 | 0.97858 | -0.41124 | 0.0051162 | 0.0012822
59 | 0.9792 | -0.39911 | 0 | 0
60 | 0.97937 | -0.39572 | 0 | 0
61 | 0.97851 | -0.41242 | 0 | 0
62 | 0.97812 | -0.42019 | 0 | 0
63 | 0.97931 | -0.39697 | 0.0024109 | 0.00060423
64 | 0.98013 | -0.38092 | 0 | 0
65 | 0.98248 | -0.33519 | 0 | 0
66 | 0.98331 | -0.31905 | 0.0023893 | 0.0005988
67 | 0.98234 | -0.33786 | 0 | 0
68 | 0.97769 | -0.42854 | 0.0075456 | 0.0018911
69 | 0.97324 | -0.51598 | 0.0008153 | 0.00020433
70 | 0.97555 | -0.47051 | 0 | 0
71 | 0.97547 | -0.47216 | 0.0045028 | 0.0011285
72 | 0.97619 | -0.458 | 0.0048268 | 0.0012097
73 | 0.97533 | -0.47487 | 0.0055791 | 0.0013983
74 | 0.97635 | -0.4549 | 0.0024239 | 0.00060749
75 | 0.9753 | -0.47538 | 0.0056838 | 0.0014245
76 | 0.97652 | -0.45143 | 0.0022251 | 0.00055766
77 | 0.97761 | -0.43019 | 0.0058736 | 0.0014721
78 | 0.98555 | -0.27575 | 0.0014887 | 0.00037311
79 | 0.98555 | -0.27569 | 0.0020534 | 0.00051464
80 | 0.98555 | -0.27566 | 0.0049832 | 0.0012489
81 | 0.98824 | -0.22376 | 0.0045713 | 0.0011457
82 | 0.98703 | -0.24724 | 0 | 0
83 | 0.98958 | -0.19804 | 0 | 0
84 | 0.9866 | -0.25553 | 0 | 0
85 | 0.98578 | -0.27117 | 0 | 0
86 | 0.9908 | -0.17475 | 0.0056638 | 0.0014195
87 | 0.98928 | -0.20391 | 0.0022208 | 0.0005566
88 | 0.98659 | -0.25576 | 0 | 0
89 | 0.98641 | -0.25921 | 0.0039224 | 0.00098306
90 | 0.98453 | -0.29546 | 0 | 0
91 | 0.98566 | -0.27353 | 0.001448 | 0.0003629
92 | 0.98397 | -0.30627 | 0.0014498 | 0.00036336
93 | 0.9845 | -0.29596 | 0.0022798 | 0.00057136
94 | 0.98652 | -0.25703 | 0.0023819 | 0.00059696
95 | 0.99177 | -0.15604 | 0 | 0
96 | 0.98917 | -0.20602 | 0.004099 | 0.0010273
97 | 0.98625 | -0.26236 | 0.0019259 | 0.00048267
98 | 0.99249 | -0.14241 | 0.0020475 | 0.00051315
99 | 0.98336 | -0.31815 | 0.0023864 | 0.0005981
100 | 0.98448 | -0.29637 | 0.0012158 | 0.0003047
101 | 0.98646 | -0.25833 | 0.0024281 | 0.00060853
102 | 0.98912 | -0.20692 | 0 | 0
103 | 0.99397 | -0.11421 | 0.0038444 | 0.0009635
104 | 0.99409 | -0.11185 | 0.007462 | 0.0018702
105 | 0.99509 | -0.092896 | 0.0047658 | 0.0011944
106 | 0.99517 | -0.091281 | 0 | 0
107 | 0.99802 | -0.03731 | 0 | 0
108 | 0.98908 | -0.20787 | 0.0038912 | 0.00097523
109 | 0.99814 | -0.035003 | 0 | 0
110 | 0.99796 | -0.038423 | 0.0045674 | 0.0011447
111 | 0.99812 | -0.035408 | 0.0073907 | 0.0018523
112 | 1 | 0 | -0.41373 | -0.10597
113 | 0.99795 | -0.038678 | 0 | 0
114 | 0.97524 | -0.47661 | 0 | 0
115 | 0.97525 | -0.47641 | 0.0034131 | 0.00085542
116 | 0.99788 | -0.04001 | 0 | 0
117 | 0.99783 | -0.041051 | 0.0040652 | 0.0010188
118 | 0.9979 | -0.039729 | 0.0045798 | 0.0011478
119 | 0.98 | -0.38338 | 0.003592 | 0.00090025
120 | 0.97997 | -0.38401 | 0.0016472 | 0.00041284
121 | 0.98002 | -0.38306 | 0 | 0
122 | 0.97993 | -0.38475 | 0 | 0
123 | 0.98005 | -0.38242 | 0.0020462 | 0.00051282
124 | 0.97992 | -0.38504 | 0.0083273 | 0.002087
125 | 0.98104 | -0.36306 | 0.0068176 | 0.0017087
126 | 0.98009 | -0.3817 | 0.0033112 | 0.00082985
127 | 0.97918 | -0.3995 | 0.0034503 | 0.00086473
128 | 0.97918 | -0.39939 | 0.0041765 | 0.0010467
129 | 0.97922 | -0.3986 | 0.0015596 | 0.00039087
130 | 0.98447 | -0.2965 | 0.0065219 | 0.0016346
131 | 0.9858 | -0.27109 | 0.0018522 | 0.00046421
132 | 0.98581 | -0.27094 | 0.0036923 | 0.00092539
133 | 0.98554 | -0.27614 | 0.0081419 | 0.0020406
134 | 0.986 | -0.26724 | 0.0020694 | 0.00051863
135 | 0.98553 | -0.27638 | 0.0034377 | 0.00086156
136 | 0.98619 | -0.26356 | 0.003024 | 0.00075788
137 | 0.98539 | -0.27912 | 0.0097768 | 0.0024503
138 | 0.98534 | -0.28002 | 0 | 0
139 | 0.98528 | -0.28125 | 0.0084497 | 0.0021177
140 | 0.98523 | -0.28222 | 0.0075752 | 0.0018985
141 | 0.98613 | -0.26469 | 0.0034158 | 0.00085609
142 | 0.98615 | -0.26435 | 0.0018576 | 0.00046555
143 | 0.98617 | -0.26401 | 0.0030627 | 0.00076758
144 | 0.98619 | -0.26363 | 0.0020413 | 0.00051159
145 | 0.98625 | -0.26239 | 0.00098906 | 0.00024788
146 | 0.98636 | -0.26027 | 0 | 0
147 | 0.99989 | -0.0021663 | 0.0078174 | 0.0019592
148 | 0.99794 | -0.038912 | 0.0043113 | 0.0010805
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.016999 | 0.0042625 | -0.016997 | -0.0042615 | 1.6976e-06 | 1.0039e-06 | 0.026044 | 0.026044 | 0.026044 | 0.97125 | -0.55536 | 0.97114 | -0.55745 | 7.1551
1 | -0.022934 | -0.0057499 | 0.022941 | 0.0057545 | 7.4694e-06 | 4.5807e-06 | 0.035137 | 0.035137 | 0.035137 | 0.97125 | -0.55536 | 0.97159 | -0.54853 | 9.6529
2 | 0.012343 | 0.003095 | -0.01234 | -0.0030935 | 2.7989e-06 | 1.5332e-06 | 0.018913 | 0.018913 | 0.018913 | 0.97114 | -0.55745 | 0.9709 | -0.56221 | 5.1958
3 | -0.040344 | -0.01012 | 0.04038 | 0.010142 | 3.5364e-05 | 2.2327e-05 | 0.061791 | 0.061791 | 0.061791 | 0.97159 | -0.54853 | 0.97252 | -0.53016 | 16.9757
4 | 0.017403 | 0.0043656 | -0.017392 | -0.004359 | 1.1038e-05 | 6.5516e-06 | 0.026655 | 0.026655 | 0.026655 | 0.97159 | -0.54853 | 0.97092 | -0.56184 | 7.3228
5 | 0.0040066 | 0.0010036 | -0.0040061 | -0.0010037 | 5.0648e-07 | -1.1879e-07 | 0.0061403 | 0.0061405 | 0.0061405 | 0.9709 | -0.56221 | 0.97077 | -0.56487 | 1.6869
6 | 0.0083334 | 0.0020899 | -0.0083299 | -0.0020883 | 3.4996e-06 | 1.5326e-06 | 0.012772 | 0.012773 | 0.012773 | 0.9709 | -0.56221 | 0.97046 | -0.57103 | 3.509
7 | -0.045679 | -0.011471 | 0.045694 | 0.011479 | 1.4525e-05 | 8.9024e-06 | 0.0699 | 0.069899 | 0.0699 | 0.97252 | -0.53016 | 0.97286 | -0.52349 | 9.6016
8 | 0.0093687 | 0.0023481 | -0.0093673 | -0.0023475 | 1.3891e-06 | 6.6685e-07 | 0.014358 | 0.014358 | 0.014358 | 0.97092 | -0.56184 | 0.97076 | -0.56495 | 3.9446
9 | 0.0012143 | 0.00030402 | -0.0012142 | -0.00030431 | 3.3653e-08 | -2.9875e-07 | 0.0018611 | 0.0018613 | 0.0018613 | 0.97077 | -0.56487 | 0.97074 | -0.56545 | 0.51133
10 | 0.0083299 | 0.0020883 | -0.0083263 | -0.0020868 | 3.5783e-06 | 1.5678e-06 | 0.012773 | 0.012773 | 0.012773 | 0.97046 | -0.57103 | 0.97 | -0.58004 | 3.509
11 | -0.047367 | -0.011899 | 0.047374 | 0.011902 | 7.71e-06 | 3.7186e-06 | 0.072459 | 0.072458 | 0.072459 | 0.97286 | -0.52349 | 0.97303 | -0.52008 | 3.9812
12 | 0.0086131 | 0.0021585 | -0.0086131 | -0.0021585 | 2.5557e-08 | 1.1523e-08 | 0.013202 | 0.013202 | 0.013202 | 0.97076 | -0.56495 | 0.97076 | -0.56501 | 3.627
13 | -0.049052 | -0.012323 | 0.049055 | 0.012324 | 3.3561e-06 | 1.6541e-06 | 0.075023 | 0.075023 | 0.075023 | 0.97303 | -0.52008 | 0.97311 | -0.51865 | 4.1221
14 | 0.0079195 | 0.0019846 | -0.0079189 | -0.0019844 | 5.8924e-07 | 2.4529e-07 | 0.012139 | 0.012139 | 0.012139 | 0.97076 | -0.56501 | 0.97068 | -0.56658 | 3.335
15 | -0.0019808 | -0.00049645 | 0.0019809 | 0.00049623 | 7.2589e-08 | -2.1301e-07 | 0.0030367 | 0.0030366 | 0.0030367 | 0.97063 | -0.56753 | 0.97067 | -0.56676 | 0.83426
16 | -0.0019809 | -0.00049623 | 0.0019809 | 0.00049618 | 1.7672e-08 | -5.1864e-08 | 0.0030366 | 0.0030366 | 0.0030366 | 0.97067 | -0.56676 | 0.97068 | -0.56658 | 0.83423
17 | -0.0039401 | -0.00098748 | 0.0039403 | 0.00098742 | 2.1356e-07 | -5.8276e-08 | 0.0060247 | 0.0060246 | 0.0060247 | 0.97316 | -0.51766 | 0.97321 | -0.51653 | 1.6551
18 | -0.054633 | -0.013724 | 0.054639 | 0.013727 | 5.5493e-06 | 2.8929e-06 | 0.083544 | 0.083544 | 0.083544 | 0.97321 | -0.51653 | 0.97332 | -0.5144 | 4.5903
19 | 0.050693 | 0.012736 | -0.050688 | -0.012734 | 5.1381e-06 | 2.5802e-06 | 0.07752 | 0.07752 | 0.07752 | 0.97321 | -0.51653 | 0.97311 | -0.51865 | 4.2593
20 | -0.057972 | -0.014562 | 0.057992 | 0.014572 | 1.9428e-05 | 1.0384e-05 | 0.08864 | 0.088639 | 0.08864 | 0.97332 | -0.5144 | 0.97368 | -0.50738 | 4.8703
21 | 0.0033332 | 0.00083494 | -0.0033331 | -0.00083506 | 1.748e-07 | -1.1123e-07 | 0.0050957 | 0.0050958 | 0.0050958 | 0.97332 | -0.5144 | 0.97327 | -0.5155 | 1.3999
22 | -0.060402 | -0.015176 | 0.06041 | 0.01518 | 7.9049e-06 | 4.29e-06 | 0.092323 | 0.092322 | 0.092323 | 0.97368 | -0.50738 | 0.97382 | -0.50463 | 5.0727
23 | 0.0021023 | 0.0005266 | -0.0021023 | -0.00052665 | 2.0168e-08 | -5.179e-08 | 0.0032141 | 0.0032141 | 0.0032141 | 0.97327 | -0.5155 | 0.97326 | -0.5157 | 0.88299
24 | -0.063068 | -0.015847 | 0.06308 | 0.015853 | 1.1253e-05 | 6.1973e-06 | 0.096384 | 0.096384 | 0.096384 | 0.97382 | -0.50463 | 0.97401 | -0.5009 | 5.2958
25 | 0.00081531 | 0.00020411 | -0.0008153 | -0.00020433 | 1.0901e-08 | -2.2551e-07 | 0.0012465 | 0.0012465 | 0.0012465 | 0.97326 | -0.5157 | 0.97324 | -0.51598 | 0.34246
26 | -0.011275 | -0.0028259 | 0.011279 | 0.0028278 | 3.4326e-06 | 1.8132e-06 | 0.01723 | 0.01723 | 0.01723 | 0.97374 | -0.5061 | 0.97407 | -0.49971 | 4.7336
27 | 0.0070553 | 0.0017683 | -0.0070542 | -0.001768 | 1.0492e-06 | 3.7213e-07 | 0.010781 | 0.010782 | 0.010782 | 0.97374 | -0.5061 | 0.97359 | -0.50922 | 2.962
28 | -0.074362 | -0.018683 | 0.074387 | 0.018697 | 2.5189e-05 | 1.4501e-05 | 0.11361 | 0.11361 | 0.11361 | 0.97407 | -0.49971 | 0.97443 | -0.49262 | 6.2425
29 | 0.063083 | 0.015855 | -0.06308 | -0.015853 | 3.561e-06 | 1.961e-06 | 0.096384 | 0.096384 | 0.096384 | 0.97407 | -0.49971 | 0.97401 | -0.5009 | 5.2958
30 | -0.10626 | -0.026706 | 0.10627 | 0.02671 | 7.2833e-06 | 4.4316e-06 | 0.16229 | 0.16229 | 0.16229 | 0.97443 | -0.49262 | 0.9745 | -0.49118 | 8.9171
31 | 0.031872 | 0.0080087 | -0.031853 | -0.0079965 | 1.9459e-05 | 1.2181e-05 | 0.048678 | 0.048678 | 0.048678 | 0.97443 | -0.49262 | 0.97378 | -0.50542 | 13.3732
32 | -0.10627 | -0.02671 | 0.10629 | 0.026725 | 2.5214e-05 | 1.5342e-05 | 0.16229 | 0.16229 | 0.16229 | 0.9745 | -0.49118 | 0.97475 | -0.48622 | 8.9171
33 | 0.028829 | 0.0072388 | -0.028821 | -0.0072335 | 8.4907e-06 | 5.289e-06 | 0.044059 | 0.044059 | 0.044059 | 0.97378 | -0.50542 | 0.97346 | -0.51159 | 12.104
34 | -0.10767 | -0.02707 | 0.10773 | 0.027107 | 5.9604e-05 | 3.6312e-05 | 0.16439 | 0.16439 | 0.16439 | 0.97475 | -0.48622 | 0.97534 | -0.47463 | 9.0325
35 | 0.15283 | 0.038487 | -0.1528 | -0.038468 | 2.9493e-05 | 1.8421e-05 | 0.23283 | 0.23283 | 0.23283 | 0.97701 | -0.44185 | 0.97681 | -0.44589 | 12.793
36 | 0.016255 | 0.0040744 | -0.016254 | -0.0040739 | 7.7573e-07 | 4.542e-07 | 0.024757 | 0.024757 | 0.024757 | 0.97701 | -0.44185 | 0.97696 | -0.44285 | 6.8014
37 | -0.16909 | -0.042561 | 0.16912 | 0.04258 | 2.9416e-05 | 1.8456e-05 | 0.25759 | 0.25759 | 0.25759 | 0.97701 | -0.44185 | 0.9772 | -0.43821 | 14.1533
38 | 0.15018 | 0.037812 | -0.15016 | -0.037799 | 2.0825e-05 | 1.2996e-05 | 0.22884 | 0.22884 | 0.22884 | 0.97681 | -0.44589 | 0.97666 | -0.44879 | 12.5738
39 | 0.016254 | 0.0040739 | -0.016254 | -0.0040736 | 6.5229e-07 | 3.8193e-07 | 0.024757 | 0.024757 | 0.024757 | 0.97696 | -0.44285 | 0.97692 | -0.44369 | 6.8014
40 | -0.1717 | -0.043226 | 0.17174 | 0.043251 | 3.9823e-05 | 2.5001e-05 | 0.26152 | 0.26152 | 0.26152 | 0.9772 | -0.43821 | 0.97744 | -0.43336 | 14.3692
41 | 0.025718 | 0.0064558 | -0.025709 | -0.0064502 | 9.0484e-06 | 5.597e-06 | 0.039316 | 0.039316 | 0.039316 | 0.97346 | -0.51159 | 0.97309 | -0.51897 | 10.801
42 | -0.11205 | -0.02819 | 0.11207 | 0.028203 | 2.2066e-05 | 1.3494e-05 | 0.17098 | 0.17098 | 0.17098 | 0.97534 | -0.47463 | 0.97555 | -0.47051 | 9.3947
43 | -0.0015156 | -0.00037985 | 0.0015157 | 0.00037961 | 4.4917e-08 | -2.4671e-07 | 0.002321 | 0.0023209 | 0.002321 | 0.9717 | -0.54646 | 0.97173 | -0.54584 | 0.63763
44 | -0.0065441 | -0.0016398 | 0.0065447 | 0.00164 | 6.4564e-07 | 2.0079e-07 | 0.010021 | 0.010021 | 0.010021 | 0.97173 | -0.54584 | 0.97184 | -0.54376 | 2.753
45 | 0.14775 | 0.037194 | -0.14773 | -0.037183 | 1.8677e-05 | 1.1646e-05 | 0.22517 | 0.22517 | 0.22517 | 0.97666 | -0.44879 | 0.97652 | -0.45143 | 12.3719
46 | -0.17329 | -0.043642 | 0.1734 | 0.04371 | 0.00010916 | 6.8549e-05 | 0.26389 | 0.26389 | 0.26389 | 0.97744 | -0.43336 | 0.97812 | -0.42019 | 14.4995
47 | 0.02256 | 0.0056609 | -0.022554 | -0.0056572 | 6.063e-06 | 3.7116e-06 | 0.0345 | 0.0345 | 0.0345 | 0.97309 | -0.51897 | 0.97281 | -0.52461 | 9.478
48 | 0.019635 | 0.0049258 | -0.019628 | -0.0049214 | 7.1818e-06 | 4.3329e-06 | 0.030036 | 0.030036 | 0.030036 | 0.97281 | -0.52461 | 0.97242 | -0.53229 | 8.2516
49 | 0.016219 | 0.0040671 | -0.016215 | -0.0040646 | 4.2321e-06 | 2.4813e-06 | 0.02482 | 0.02482 | 0.02482 | 0.97242 | -0.53229 | 0.97214 | -0.53776 | 6.8186
50 | 0.016215 | 0.0040646 | -0.016214 | -0.0040641 | 1.0054e-06 | 5.8947e-07 | 0.02482 | 0.02482 | 0.02482 | 0.97214 | -0.53776 | 0.97207 | -0.53906 | 6.8186
51 | 0.011636 | 0.0029168 | -0.011633 | -0.0029154 | 2.6057e-06 | 1.3962e-06 | 0.017812 | 0.017812 | 0.017812 | 0.97207 | -0.53906 | 0.97184 | -0.54376 | 4.8935
52 | 0.0045779 | 0.0011473 | -0.0045777 | -0.0011473 | 2.1121e-07 | -6.9995e-09 | 0.0070077 | 0.0070077 | 0.0070077 | 0.97207 | -0.53906 | 0.97202 | -0.54003 | 1.9252
53 | 0.0032771 | 0.0008212 | -0.003277 | -0.00082129 | 1.335e-07 | -9.2194e-08 | 0.0050004 | 0.0050004 | 0.0050004 | 0.9752 | -0.4774 | 0.97516 | -0.47825 | 1.3737
54 | -0.0032771 | -0.0008212 | 0.0032771 | 0.00082118 | 2.4197e-08 | -1.6712e-08 | 0.0050004 | 0.0050004 | 0.0050004 | 0.9752 | -0.4774 | 0.97521 | -0.47724 | 1.3737
55 | -0.006873 | -0.0017224 | 0.0068732 | 0.001721 | 2.0546e-07 | -1.4226e-06 | 0.010487 | 0.010487 | 0.010487 | 0.97521 | -0.47724 | 0.97524 | -0.47661 | 0.57621
56 | -0.0042615 | -0.001068 | 0.0042616 | 0.001068 | 6.1111e-08 | -9.5019e-09 | 0.0064848 | 0.0064848 | 0.0064848 | 0.97785 | -0.42558 | 0.97786 | -0.42528 | 1.7815
57 | 0.0045267 | 0.0011344 | -0.0045263 | -0.0011344 | 4.0573e-07 | -2.6359e-08 | 0.0068882 | 0.0068884 | 0.0068884 | 0.97786 | -0.42528 | 0.97777 | -0.42716 | 1.8924
58 | -0.0087883 | -0.0022024 | 0.0087901 | 0.0022032 | 1.8715e-06 | 8.4759e-07 | 0.013373 | 0.013373 | 0.013373 | 0.97786 | -0.42528 | 0.97809 | -0.42081 | 3.6739
59 | -0.0087901 | -0.0022032 | 0.0087941 | 0.0022051 | 4.0069e-06 | 1.8142e-06 | 0.013373 | 0.013373 | 0.013373 | 0.97809 | -0.42081 | 0.97858 | -0.41124 | 3.6739
60 | -0.01391 | -0.0034873 | 0.013918 | 0.0034918 | 8.0434e-06 | 4.5451e-06 | 0.021152 | 0.021152 | 0.021152 | 0.97858 | -0.41124 | 0.9792 | -0.39911 | 5.8111
61 | -0.20094 | -0.050687 | 0.20097 | 0.050708 | 3.2612e-05 | 2.0578e-05 | 0.30547 | 0.30547 | 0.30547 | 0.9792 | -0.39911 | 0.97937 | -0.39572 | 16.7838
62 | 0.18702 | 0.047195 | -0.1869 | -0.04712 | 0.00011909 | 7.4985e-05 | 0.28431 | 0.28431 | 0.28431 | 0.9792 | -0.39911 | 0.97851 | -0.41242 | 15.6217
63 | 0.011599 | 0.0029074 | -0.011598 | -0.002907 | 6.9019e-07 | 3.6715e-07 | 0.017623 | 0.017623 | 0.017623 | 0.97937 | -0.39572 | 0.97931 | -0.39697 | 4.8416
64 | -0.21257 | -0.053615 | 0.21272 | 0.05371 | 0.00015072 | 9.5251e-05 | 0.32309 | 0.32309 | 0.32309 | 0.97937 | -0.39572 | 0.98013 | -0.38092 | 17.7521
65 | 0.1869 | 0.04712 | -0.18683 | -0.047077 | 6.9514e-05 | 4.3769e-05 | 0.28431 | 0.28431 | 0.28431 | 0.97851 | -0.41242 | 0.97812 | -0.42019 | 15.6217
66 | 0.013425 | 0.0033663 | -0.01342 | -0.0033633 | 5.3364e-06 | 2.9873e-06 | 0.020424 | 0.020424 | 0.020424 | 0.97812 | -0.42019 | 0.97769 | -0.42854 | 5.6111
67 | 0.0091874 | 0.0023028 | -0.0091867 | -0.0023024 | 7.1252e-07 | 3.3335e-07 | 0.01396 | 0.01396 | 0.01396 | 0.97931 | -0.39697 | 0.97922 | -0.3986 | 3.8352
68 | -0.23164 | -0.058449 | 0.23184 | 0.058574 | 0.0001983 | 0.00012557 | 0.35182 | 0.35182 | 0.35182 | 0.98013 | -0.38092 | 0.98104 | -0.36306 | 19.3308
69 | 0.018926 | 0.0047384 | -0.018926 | -0.0047387 | 6.9906e-07 | -2.6405e-07 | 0.028732 | 0.028732 | 0.028732 | 0.98013 | -0.38092 | 0.98009 | -0.3817 | 1.5787
70 | -0.23898 | -0.060485 | 0.23916 | 0.060603 | 0.00018535 | 0.00011743 | 0.36216 | 0.36216 | 0.36216 | 0.98248 | -0.33519 | 0.98331 | -0.31905 | 19.8989
71 | 0.23898 | 0.060485 | -0.23895 | -0.060466 | 3.0534e-05 | 1.9345e-05 | 0.36216 | 0.36216 | 0.36216 | 0.98248 | -0.33519 | 0.98234 | -0.33786 | 19.8989
72 | -0.24155 | -0.061202 | 0.24156 | 0.061208 | 1.0426e-05 | 6.6067e-06 | 0.36578 | 0.36578 | 0.36578 | 0.98331 | -0.31905 | 0.98336 | -0.31815 | 20.0976
73 | 0.23895 | 0.060466 | -0.23866 | -0.060283 | 0.0002887 | 0.00018291 | 0.36216 | 0.36216 | 0.36216 | 0.98234 | -0.33786 | 0.98104 | -0.36306 | 19.899
74 | 0.0058741 | 0.0014722 | -0.0058736 | -0.0014721 | 4.6167e-07 | 1.0232e-07 | 0.0089402 | 0.0089402 | 0.0089402 | 0.97769 | -0.42854 | 0.97761 | -0.43019 | 2.4561
75 | 0.026058 | 0.0065254 | -0.026056 | -0.0065251 | 2.0446e-06 | 2.3124e-07 | 0.039744 | 0.039745 | 0.039745 | 0.97555 | -0.47051 | 0.97547 | -0.47216 | 2.1838
76 | -0.13813 | -0.034728 | 0.13821 | 0.03478 | 8.2571e-05 | 5.1297e-05 | 0.21073 | 0.21073 | 0.21073 | 0.97555 | -0.47051 | 0.97619 | -0.458 | 11.5784
77 | 0.021553 | 0.0053966 | -0.02155 | -0.005397 | 2.7839e-06 | -3.6154e-07 | 0.032876 | 0.032877 | 0.032877 | 0.97547 | -0.47216 | 0.97533 | -0.47487 | 1.8064
78 | -0.14304 | -0.035989 | 0.14306 | 0.036003 | 2.1211e-05 | 1.3203e-05 | 0.21808 | 0.21808 | 0.21808 | 0.97619 | -0.458 | 0.97635 | -0.4549 | 11.9827
79 | 0.015971 | 0.0039987 | -0.015971 | -0.003999 | 3.8447e-07 | -2.9276e-07 | 0.024365 | 0.024365 | 0.024365 | 0.97533 | -0.47487 | 0.9753 | -0.47538 | 1.3387
80 | -0.14548 | -0.03661 | 0.14551 | 0.036625 | 2.4095e-05 | 1.5012e-05 | 0.22178 | 0.22178 | 0.22178 | 0.97635 | -0.4549 | 0.97652 | -0.45143 | 12.1856
81 | 0.010287 | 0.0025745 | -0.010286 | -0.0025759 | 5.0718e-07 | -1.3885e-06 | 0.015693 | 0.015694 | 0.015694 | 0.9753 | -0.47538 | 0.97525 | -0.47641 | 0.86231
82 | -0.0014887 | -0.00037311 | 0.0014887 | 0.00037308 | 4.5936e-09 | -2.7957e-08 | 0.0022477 | 0.0022477 | 0.0022477 | 0.98555 | -0.27575 | 0.98555 | -0.27569 | 0.6175
83 | -0.0035421 | -0.00088771 | 0.0035421 | 0.00088771 | 5.4653e-09 | -2.9957e-09 | 0.005348 | 0.005348 | 0.005348 | 0.98555 | -0.27569 | 0.98555 | -0.27566 | 1.4692
84 | -0.0085254 | -0.0021366 | 0.0085262 | 0.002137 | 8.6211e-07 | 3.7491e-07 | 0.012872 | 0.012872 | 0.012872 | 0.98555 | -0.27566 | 0.98566 | -0.27353 | 3.5362
85 | 0.33677 | 0.08555 | -0.33639 | -0.085308 | 0.00038022 | 0.00024208 | 0.5075 | 0.5075 | 0.5075 | 0.98824 | -0.22376 | 0.98703 | -0.24724 | 27.8844
86 | -0.34135 | -0.086696 | 0.34177 | 0.086965 | 0.00042313 | 0.00026943 | 0.51438 | 0.51438 | 0.51438 | 0.98824 | -0.22376 | 0.98958 | -0.19804 | 28.2626
87 | 0.070127 | 0.017576 | -0.070099 | -0.01756 | 2.7678e-05 | 1.5605e-05 | 0.10572 | 0.10572 | 0.10572 | 0.98703 | -0.24724 | 0.9866 | -0.25553 | 5.8089
88 | 0.26627 | 0.067732 | -0.26596 | -0.067538 | 0.00030654 | 0.00019457 | 0.40178 | 0.40178 | 0.40178 | 0.98703 | -0.24724 | 0.98578 | -0.27117 | 22.0756
89 | -0.35198 | -0.089526 | 0.35238 | 0.089778 | 0.00039553 | 0.00025193 | 0.52974 | 0.52974 | 0.52974 | 0.98958 | -0.19804 | 0.9908 | -0.17475 | 29.1065
90 | 0.010215 | 0.0025608 | -0.010212 | -0.0025593 | 2.8561e-06 | 1.4133e-06 | 0.01536 | 0.015361 | 0.015361 | 0.98958 | -0.19804 | 0.98928 | -0.20391 | 4.2199
91 | 0.016182 | 0.0040426 | -0.016181 | -0.0040427 | 1.7402e-07 | -1.3745e-07 | 0.024401 | 0.024401 | 0.024401 | 0.9866 | -0.25553 | 0.98659 | -0.25576 | 1.3407
92 | 0.053918 | 0.013518 | -0.053908 | -0.013513 | 9.4436e-06 | 4.8285e-06 | 0.081322 | 0.081322 | 0.081322 | 0.9866 | -0.25553 | 0.98641 | -0.25921 | 4.4682
93 | 0.25598 | 0.065037 | -0.25569 | -0.064848 | 0.00029908 | 0.00018972 | 0.38672 | 0.38672 | 0.38672 | 0.98578 | -0.27117 | 0.98453 | -0.29546 | 21.2483
94 | 0.0099753 | 0.0025004 | -0.0099742 | -0.0024999 | 1.1253e-06 | 5.5148e-07 | 0.015058 | 0.015058 | 0.015058 | 0.98578 | -0.27117 | 0.98566 | -0.27353 | 4.1367
95 | -0.35804 | -0.091198 | 0.35837 | 0.091404 | 0.00032345 | 0.00020605 | 0.53824 | 0.53824 | 0.53824 | 0.9908 | -0.17475 | 0.99177 | -0.15604 | 29.5739
96 | 0.0079914 | 0.0020027 | -0.0079906 | -0.0020024 | 8.0153e-07 | 3.2306e-07 | 0.01202 | 0.01202 | 0.01202 | 0.98928 | -0.20391 | 0.98917 | -0.20602 | 3.3023
97 | 0.016181 | 0.0040427 | -0.01618 | -0.0040435 | 9.7915e-07 | -7.7322e-07 | 0.024401 | 0.024401 | 0.024401 | 0.98659 | -0.25576 | 0.98652 | -0.25703 | 1.3407
98 | 0.049986 | 0.01253 | -0.049978 | -0.012526 | 7.494e-06 | 3.6747e-06 | 0.075405 | 0.075405 | 0.075405 | 0.98641 | -0.25921 | 0.98625 | -0.26236 | 4.1432
99 | 0.24567 | 0.062339 | -0.24554 | -0.062258 | 0.00012764 | 8.0907e-05 | 0.37158 | 0.37158 | 0.37158 | 0.98453 | -0.29546 | 0.98397 | -0.30627 | 20.4164
100 | 0.010018 | 0.0025089 | -0.010018 | -0.0025096 | 2.3858e-07 | -7.2959e-07 | 0.01514 | 0.015141 | 0.015141 | 0.98453 | -0.29546 | 0.9845 | -0.29596 | 0.83191
101 | 0.24409 | 0.061895 | -0.24395 | -0.061806 | 0.00013928 | 8.8273e-05 | 0.36939 | 0.36939 | 0.36939 | 0.98397 | -0.30627 | 0.98336 | -0.31815 | 20.296
102 | 0.0077379 | 0.0019382 | -0.0077378 | -0.001939 | 1.4843e-07 | -8.2493e-07 | 0.011695 | 0.011695 | 0.011695 | 0.9845 | -0.29596 | 0.98448 | -0.29637 | 0.6426
103 | 0.013798 | 0.0034465 | -0.013798 | -0.0034477 | 8.5145e-07 | -1.1287e-06 | 0.020809 | 0.020809 | 0.020809 | 0.98652 | -0.25703 | 0.98646 | -0.25833 | 1.1434
104 | -0.35837 | -0.091404 | 0.3586 | 0.091554 | 0.00023608 | 0.00015039 | 0.53824 | 0.53824 | 0.53824 | 0.99177 | -0.15604 | 0.99249 | -0.14241 | 29.5738
105 | 0.0038916 | 0.00097511 | -0.0038914 | -0.00097517 | 1.6765e-07 | -6.0158e-08 | 0.005854 | 0.0058541 | 0.0058541 | 0.98917 | -0.20602 | 0.98912 | -0.20692 | 1.6083
106 | 0.048052 | 0.012043 | -0.04805 | -0.012042 | 2.7527e-06 | 1.3162e-06 | 0.0725 | 0.0725 | 0.0725 | 0.98625 | -0.26236 | 0.98619 | -0.26356 | 3.9835
107 | -0.36065 | -0.092067 | 0.36114 | 0.092381 | 0.00049211 | 0.0003135 | 0.54131 | 0.54131 | 0.54131 | 0.99249 | -0.14241 | 0.99397 | -0.11421 | 29.7425
108 | 0.006522 | 0.0016343 | -0.0065219 | -0.0016346 | 4.2118e-08 | -2.0818e-07 | 0.0098577 | 0.0098578 | 0.0098578 | 0.98448 | -0.29637 | 0.98447 | -0.2965 | 0.67705
109 | 0.01137 | 0.0028391 | -0.011368 | -0.0028415 | 1.0478e-06 | -2.362e-06 | 0.017147 | 0.017148 | 0.017148 | 0.98646 | -0.25833 | 0.98636 | -0.26027 | 0.94218
110 | 0.0038914 | 0.00097517 | -0.0038912 | -0.00097523 | 1.75e-07 | -6.2776e-08 | 0.0058541 | 0.0058541 | 0.0058541 | 0.98912 | -0.20692 | 0.98908 | -0.20787 | 1.6083
111 | -0.36499 | -0.093344 | 0.36503 | 0.093371 | 4.1678e-05 | 2.6554e-05 | 0.54707 | 0.54707 | 0.54707 | 0.99397 | -0.11421 | 0.99409 | -0.11185 | 30.0587
112 | -0.37249 | -0.095241 | 0.37286 | 0.095477 | 0.00037115 | 0.0002365 | 0.55824 | 0.55824 | 0.55824 | 0.99409 | -0.11185 | 0.99517 | -0.091281 | 30.6724
113 | -0.0047658 | -0.0011944 | 0.0047662 | 0.0011944 | 3.6664e-07 | -1.5452e-08 | 0.0071266 | 0.0071265 | 0.0071266 | 0.99509 | -0.092896 | 0.99517 | -0.091281 | 1.9579
114 | -0.37763 | -0.096672 | 0.37862 | 0.097303 | 0.00098985 | 0.00063082 | 0.56536 | 0.56536 | 0.56536 | 0.99517 | -0.091281 | 0.99802 | -0.03731 | 31.0639
115 | -0.39614 | -0.10169 | 0.39619 | 0.10172 | 4.4371e-05 | 2.8287e-05 | 0.59149 | 0.59149 | 0.59149 | 0.99802 | -0.03731 | 0.99814 | -0.035003 | 32.4995
116 | 0.017525 | 0.0043894 | -0.017524 | -0.00439 | 9.2884e-07 | -5.9068e-07 | 0.026129 | 0.026129 | 0.026129 | 0.99802 | -0.03731 | 0.99796 | -0.038423 | 1.4357
117 | 0.0073908 | 0.0018513 | -0.0073907 | -0.0018523 | 1.4254e-07 | -9.3192e-07 | 0.011018 | 0.011018 | 0.011018 | 0.99814 | -0.035003 | 0.99812 | -0.035408 | 0.60539
118 | -0.40358 | -0.10357 | 0.40426 | 0.10401 | 0.00068675 | 0.00043787 | 0.60251 | 0.60251 | 0.60251 | 0.99814 | -0.035003 | 1 | 0 | 33.1049
119 | 0.012957 | 0.0032453 | -0.012957 | -0.0032455 | 1.5723e-07 | -2.6633e-07 | 0.019319 | 0.019319 | 0.019319 | 0.99796 | -0.038423 | 0.99795 | -0.038678 | 1.0615
120 | 0.0078182 | 0.0019595 | -0.0078174 | -0.0019592 | 8.0683e-07 | 3.0784e-07 | 0.011634 | 0.011634 | 0.011634 | 1 | 0 | 0.99989 | -0.0021663 | 3.1961
121 | 0.0043113 | 0.0010795 | -0.0043113 | -0.0010805 | 4.7914e-08 | -9.7929e-07 | 0.0064281 | 0.0064285 | 0.0064285 | 0.99795 | -0.038678 | 0.99794 | -0.038912 | 0.35321
122 | 0.0086456 | 0.002166 | -0.0086452 | -0.0021665 | 4.3289e-07 | -5.3975e-07 | 0.012891 | 0.012891 | 0.012891 | 0.99795 | -0.038678 | 0.9979 | -0.039729 | 1.1805
123 | -0.0068732 | -0.001721 | 0.0068733 | 0.0017205 | 6.5631e-08 | -4.5448e-07 | 0.010487 | 0.010486 | 0.010487 | 0.97524 | -0.47661 | 0.97525 | -0.47641 | 0.57618
124 | 0.0040654 | 0.0010188 | -0.0040652 | -0.0010188 | 2.0151e-07 | -6.2044e-08 | 0.0060621 | 0.0060622 | 0.0060622 | 0.99788 | -0.04001 | 0.99783 | -0.041051 | 1.6654
125 | -0.0040654 | -0.0010188 | 0.0040654 | 0.0010187 | 5.4347e-08 | -1.6737e-08 | 0.0060621 | 0.0060621 | 0.0060621 | 0.99788 | -0.04001 | 0.9979 | -0.039729 | 1.6654
126 | 0.0099753 | 0.0024971 | -0.009975 | -0.002498 | 3.0031e-07 | -9.075e-07 | 0.015145 | 0.015146 | 0.015146 | 0.98 | -0.38338 | 0.97997 | -0.38401 | 0.83217
127 | -0.013567 | -0.0033973 | 0.013567 | 0.003397 | 2.0907e-07 | -2.8008e-07 | 0.020599 | 0.020599 | 0.020599 | 0.98 | -0.38338 | 0.98002 | -0.38306 | 1.1318
128 | 0.0083277 | 0.0020851 | -0.0083274 | -0.0020865 | 2.9103e-07 | -1.3425e-06 | 0.012644 | 0.012645 | 0.012645 | 0.97997 | -0.38401 | 0.97993 | -0.38475 | 0.69477
129 | -0.013567 | -0.003397 | 0.013568 | 0.0033965 | 4.0938e-07 | -5.4847e-07 | 0.020599 | 0.020599 | 0.020599 | 0.98002 | -0.38306 | 0.98005 | -0.38242 | 1.1318
130 | 0.0083274 | 0.0020865 | -0.0083273 | -0.002087 | 1.1739e-07 | -5.4146e-07 | 0.012645 | 0.012645 | 0.012645 | 0.97993 | -0.38475 | 0.97992 | -0.38504 | 0.69479
131 | -0.015614 | -0.0039093 | 0.015615 | 0.0039088 | 5.379e-07 | -4.599e-07 | 0.023706 | 0.023705 | 0.023706 | 0.98005 | -0.38242 | 0.98009 | -0.3817 | 1.3025
132 | -0.0034503 | -0.00086473 | 0.0034503 | 0.00086472 | 1.8265e-08 | -1.0595e-08 | 0.0052433 | 0.0052433 | 0.0052433 | 0.97918 | -0.3995 | 0.97918 | -0.39939 | 1.4405
133 | -0.0076269 | -0.0019115 | 0.0076272 | 0.0019116 | 2.8782e-07 | 1.1233e-07 | 0.01159 | 0.01159 | 0.01159 | 0.97918 | -0.39939 | 0.97922 | -0.3986 | 3.1841
134 | -0.039248 | -0.0098332 | 0.039248 | 0.0098333 | 2.7725e-07 | 1.1029e-07 | 0.059242 | 0.059242 | 0.059242 | 0.9858 | -0.27109 | 0.98581 | -0.27094 | 3.255
135 | 0.037396 | 0.009369 | -0.037387 | -0.0093656 | 8.9945e-06 | 3.3577e-06 | 0.056446 | 0.056447 | 0.056447 | 0.9858 | -0.27109 | 0.98554 | -0.27614 | 3.1015
136 | -0.042941 | -0.010759 | 0.042948 | 0.010762 | 7.5711e-06 | 3.3134e-06 | 0.064815 | 0.064815 | 0.064815 | 0.98581 | -0.27094 | 0.986 | -0.26724 | 3.5613
137 | 0.029245 | 0.0073251 | -0.029245 | -0.007325 | 3.3557e-07 | 6.8544e-08 | 0.044154 | 0.044154 | 0.044154 | 0.98554 | -0.27614 | 0.98553 | -0.27638 | 2.426
138 | -0.045018 | -0.011281 | 0.045026 | 0.011284 | 7.8916e-06 | 3.5965e-06 | 0.067938 | 0.067937 | 0.067938 | 0.986 | -0.26724 | 0.98619 | -0.26356 | 3.7328
139 | 0.025807 | 0.0064634 | -0.025804 | -0.0064632 | 3.3724e-06 | 2.7159e-07 | 0.038964 | 0.038964 | 0.038964 | 0.98553 | -0.27638 | 0.98539 | -0.27912 | 2.1409
140 | 0.016027 | 0.0040129 | -0.016026 | -0.0040134 | 6.8483e-07 | -5.547e-07 | 0.0242 | 0.024201 | 0.024201 | 0.98539 | -0.27912 | 0.98534 | -0.28002 | 1.3297
141 | 0.016026 | 0.0040134 | -0.016025 | -0.0040142 | 9.3861e-07 | -7.6006e-07 | 0.024201 | 0.024201 | 0.024201 | 0.98534 | -0.28002 | 0.98528 | -0.28125 | 1.3297
142 | 0.0075756 | 0.0018965 | -0.0075752 | -0.0018985 | 3.4977e-07 | -2.0449e-06 | 0.01144 | 0.011441 | 0.011441 | 0.98528 | -0.28125 | 0.98523 | -0.28222 | 0.62863
143 | -0.0034158 | -0.00085609 | 0.0034159 | 0.000855 | 5.4641e-08 | -1.0847e-06 | 0.0051543 | 0.0051539 | 0.0051543 | 0.98613 | -0.26469 | 0.98615 | -0.26435 | 0.354
144 | -0.0052735 | -0.0013206 | 0.0052735 | 0.0013195 | 8.5877e-08 | -1.0988e-06 | 0.0079568 | 0.0079564 | 0.0079568 | 0.98615 | -0.26435 | 0.98617 | -0.26401 | 0.43719
145 | -0.0083362 | -0.002087 | 0.0083364 | 0.0020863 | 1.5073e-07 | -7.14e-07 | 0.012578 | 0.012577 | 0.012578 | 0.98617 | -0.26401 | 0.98619 | -0.26363 | 0.69108
146 | -0.010378 | -0.0025979 | 0.010378 | 0.0025962 | 6.1097e-07 | -1.7291e-06 | 0.015657 | 0.015657 | 0.015657 | 0.98619 | -0.26363 | 0.98625 | -0.26239 | 0.8603
147 | -0.011367 | -0.0028441 | 0.011368 | 0.0028415 | 1.1469e-06 | -2.5844e-06 | 0.017149 | 0.017148 | 0.017149 | 0.98625 | -0.26239 | 0.98636 | -0.26027 | 0.94225

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42132 | 0.10787

## res_load
| p_mw | q_mvar
0 | 0.0059346 | 0.0014873
1 | 0.0046546 | 0.0011665
2 | 0.0052993 | 0.0013281
3 | 0.0080235 | 0.0020109
4 | 0.0027918 | 0.00069969
5 | 0.0016731 | 0.00041933
6 | 0.00075415 | 0.00018901
7 | 0.0012142 | 0.00030431
8 | 0.0083263 | 0.0020868
9 | 0.0016772 | 0.00042033
10 | 0.00069362 | 0.00017384
11 | 0.0019808 | 0.00049645
12 | 0.005938 | 0.0014882
13 | 0.0039401 | 0.00098748
14 | 0.0016332 | 0.00040931
15 | 0.0024104 | 0.00060411
16 | 0.0012308 | 0.00030846
17 | 0.0026583 | 0.00066623
18 | 0.001287 | 0.00032254
19 | 0.0042199 | 0.0010576
20 | 0.0070542 | 0.001768
21 | 0.0030233 | 0.00075771
22 | 0.0013757 | 0.00034479
23 | 0.0026194 | 0.0006565
24 | 0.0025802 | 0.00064665
25 | 0.003103 | 0.00077768
26 | 0.016254 | 0.0040736
27 | 0.0043213 | 0.001083
28 | 0.0015156 | 0.00037985
29 | 0.0050284 | 0.0012602
30 | 0.0024116 | 0.00060441
31 | 0.0015581 | 0.00039049
32 | 0.0031492 | 0.00078927
33 | 0.0029185 | 0.00073145
34 | 0.0034087 | 0.00085431
35 | 0.0050887 | 0.0012754
36 | 0.0045777 | 0.0011473
37 | 0.003277 | 0.00082129
38 | 0.0035959 | 0.00090121
39 | 0.0042615 | 0.001068
40 | 0.0045263 | 0.0011344
41 | 0.0051162 | 0.0012822
42 | 0.0024109 | 0.00060423
43 | 0.0023893 | 0.0005988
44 | 0.0075456 | 0.0018911
45 | 0.0008153 | 0.00020433
46 | 0.0045028 | 0.0011285
47 | 0.0048268 | 0.0012097
48 | 0.0055791 | 0.0013983
49 | 0.0024239 | 0.00060749
50 | 0.0056838 | 0.0014245
51 | 0.0022251 | 0.00055766
52 | 0.0058736 | 0.0014721
53 | 0.0014887 | 0.00037311
54 | 0.0020534 | 0.00051464
55 | 0.0049832 | 0.0012489
56 | 0.0045713 | 0.0011457
57 | 0.0056638 | 0.0014195
58 | 0.0022208 | 0.0005566
59 | 0.0039224 | 0.00098306
60 | 0.001448 | 0.0003629
61 | 0.0014498 | 0.00036336
62 | 0.0022798 | 0.00057136
63 | 0.0023819 | 0.00059696
64 | 0.004099 | 0.0010273
65 | 0.0019259 | 0.00048267
66 | 0.0020475 | 0.00051315
67 | 0.0023864 | 0.0005981
68 | 0.0012158 | 0.0003047
69 | 0.0024281 | 0.00060853
70 | 0.0038444 | 0.0009635
71 | 0.007462 | 0.0018702
72 | 0.0047658 | 0.0011944
73 | 0.0038912 | 0.00097523
74 | 0.0045674 | 0.0011447
75 | 0.0073907 | 0.0018523
76 | 0.0075922 | 0.0019028
77 | 0.0034131 | 0.00085542
78 | 0.0040652 | 0.0010188
79 | 0.0045798 | 0.0011478
80 | 0.003592 | 0.00090025
81 | 0.0016472 | 0.00041284
82 | 0.0020462 | 0.00051282
83 | 0.0083273 | 0.002087
84 | 0.0068176 | 0.0017087
85 | 0.0033112 | 0.00082985
86 | 0.0034503 | 0.00086473
87 | 0.0041765 | 0.0010467
88 | 0.0015596 | 0.00039087
89 | 0.0065219 | 0.0016346
90 | 0.0018522 | 0.00046421
91 | 0.0036923 | 0.00092539
92 | 0.0081419 | 0.0020406
93 | 0.0020694 | 0.00051863
94 | 0.0034377 | 0.00086156
95 | 0.003024 | 0.00075788
96 | 0.0097768 | 0.0024503
97 | 0.0084497 | 0.0021177
98 | 0.0075752 | 0.0018985
99 | 0.0034158 | 0.00085609
100 | 0.0018576 | 0.00046555
101 | 0.0030627 | 0.00076758
102 | 0.0020413 | 0.00051159
103 | 0.00098906 | 0.00024788
104 | 0.0078174 | 0.0019592
105 | 0.0043113 | 0.0010805

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1