## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_158-18_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_158-18_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_158-18_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_158-18_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_158-18_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_158-18_0_4_node_119 | 0.4 | n |  | TRUE
6 | bus_LV_158-18_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_158-18_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_158-18_0_4_node_82 | 0.4 | n |  | TRUE
9 | bus_LV_158-18_0_4_node_80 | 0.4 | n |  | TRUE
10 | bus_LV_158-18_0_4_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_158-18_0_4_node_78 | 0.4 | n |  | TRUE
12 | bus_LV_158-18_0_4_node_75 | 0.4 | n |  | TRUE
13 | bus_LV_158-18_0_4_node_76 | 0.4 | n |  | TRUE
14 | bus_LV_158-18_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_158-18_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_158-18_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_158-18_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_158-18_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_158-18_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_158-18_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_158-18_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_158-18_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_158-18_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_158-18_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_158-18_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_158-18_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_158-18_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_158-18_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_158-18_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_158-18_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_158-18_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_158-18_0_4_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_158-18_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_158-18_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_158-18_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_158-18_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_158-18_0_4_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_158-18_0_4_node_52 | 0.4 | n |  | TRUE
39 | bus_LV_158-18_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_158-18_0_4_node_55 | 0.4 | n |  | TRUE
41 | bus_LV_158-18_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_158-18_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_158-18_0_4_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_158-18_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_158-18_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_158-18_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_158-18_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_158-18_0_4_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_158-18_0_4_node_118 | 0.4 | n |  | TRUE
50 | bus_LV_158-18_0_4_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_158-18_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_158-18_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_158-18_0_4_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_158-18_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_158-18_0_4_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_158-18_0_4_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_158-18_0_4_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_158-18_0_4_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_158-18_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_158-18_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_158-18_0_4_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_158-18_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_158-18_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_158-18_0_4_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_158-18_0_4_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_158-18_0_4_node_104 | 0.4 | n |  | TRUE
67 | bus_LV_158-18_0_4_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_158-18_0_4_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_158-18_0_4_node_120 | 0.4 | n |  | TRUE
70 | bus_LV_158-18_0_4_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_158-18_0_4_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_158-18_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_158-18_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_158-18_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_158-18_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_158-18_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_158-18_0_4_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_158-18_0_4_node_105 | 0.4 | n |  | TRUE
79 | bus_LV_158-18_0_4_node_116 | 0.4 | n |  | TRUE
80 | bus_LV_158-18_0_4_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_158-18_0_4_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_158-18_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_158-18_0_4_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_158-18_0_4_node_111 | 0.4 | n |  | TRUE
85 | bus_LV_158-18_0_4_node_81 | 0.4 | n |  | TRUE
86 | bus_LV_158-18_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_158-18_0_4_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_158-18_0_4_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_158-18_0_4_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_158-18_0_4_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_158-18_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_158-18_0_4_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_158-18_0_4_node_108 | 0.4 | n |  | TRUE
94 | bus_LV_158-18_0_4_node_106 | 0.4 | n |  | TRUE
95 | bus_LV_158-18_0_4_node_109 | 0.4 | n |  | TRUE
96 | bus_LV_158-18_0_4_node_107 | 0.4 | n |  | TRUE
97 | bus_LV_158-18_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_158-18_0_4_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_158-18_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_158-18_0_4_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_158-18_0_4_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_158-18_0_4_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_158-18_0_4_node_114 | 0.4 | n |  | TRUE
104 | bus_LV_158-18_0_4_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_158-18_0_4_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_158-18_0_4_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_158-18_0_4_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_158-18_0_4_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_158-18_0_4_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_158-18_0_4_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_158-18_0_4_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_158-18_0_4_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_158-18_0_4_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_158-18_0_4_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_158-18_0_4_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_158-18_0_4_node_122 | 0.4 | n |  | TRUE
117 | bus_MV_361_1_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_158-18_0_4_load_0 | 0 | 0.0024716 | 0.00061944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_158-18_0_4_load_1 | 1 | 0.002864 | 0.00071779 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_158-18_0_4_load_119 | 5 | 0.005893 | 0.0014769 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_158-18_0_4_load_7 | 7 | 0.0020734 | 0.00051965 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_158-18_0_4_load_82 | 8 | 0.0097082 | 0.0024331 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_158-18_0_4_load_83 | 10 | 0.0055673 | 0.0013953 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_158-18_0_4_load_78 | 11 | 0.012199 | 0.0030575 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_158-18_0_4_load_75 | 12 | 0.011804 | 0.0029583 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_158-18_0_4_load_76 | 13 | 0.0058618 | 0.0014691 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_158-18_0_4_load_8 | 14 | 0.00087984 | 0.00022051 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_158-18_0_4_load_14 | 15 | 0.0017408 | 0.0004363 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_158-18_0_4_load_11 | 16 | 0.0020316 | 0.00050916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_158-18_0_4_load_12 | 18 | 0.0041073 | 0.0010294 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_158-18_0_4_load_13 | 19 | 0.0066879 | 0.0016761 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_158-18_0_4_load_15 | 20 | 0.0028856 | 0.00072319 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_158-18_0_4_load_16 | 21 | 0.0020798 | 0.00052124 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_158-18_0_4_load_18 | 22 | 0.0040068 | 0.0010042 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_158-18_0_4_load_19 | 23 | 0.0030011 | 0.00075215 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_158-18_0_4_load_20 | 24 | 0.0038273 | 0.00095921 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_158-18_0_4_load_31 | 25 | 0.0071964 | 0.0018036 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_158-18_0_4_load_32 | 26 | 0.0018368 | 0.00046035 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_158-18_0_4_load_21 | 27 | 0.0021733 | 0.00054469 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_158-18_0_4_load_24 | 30 | 0.0031393 | 0.00078678 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_158-18_0_4_load_27 | 31 | 0.0025243 | 0.00063265 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_158-18_0_4_load_53 | 32 | 0.0036943 | 0.00092587 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_158-18_0_4_load_51 | 33 | 0.0028728 | 0.00072 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_158-18_0_4_load_25 | 34 | 0.001774 | 0.00044461 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_158-18_0_4_load_26 | 36 | 0.0043532 | 0.001091 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_158-18_0_4_load_52 | 38 | 0.0025721 | 0.00064462 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_158-18_0_4_load_55 | 40 | 0.0055407 | 0.0013886 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_158-18_0_4_load_34 | 43 | 0.0064082 | 0.001606 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_158-18_0_4_load_41 | 44 | 0.0014864 | 0.00037252 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_158-18_0_4_load_38 | 45 | 0.007763 | 0.0019456 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_158-18_0_4_load_35 | 46 | 0.007096 | 0.0017784 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_158-18_0_4_load_36 | 47 | 0.0079349 | 0.0019887 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_158-18_0_4_load_50 | 48 | 0.023041 | 0.0057747 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_158-18_0_4_load_118 | 49 | 0.006649 | 0.0016664 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_158-18_0_4_load_64 | 50 | 0.0036299 | 0.00090975 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_158-18_0_4_load_39 | 51 | 0.003168 | 0.00079398 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_158-18_0_4_load_40 | 52 | 0.0080134 | 0.0020083 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_158-18_0_4_load_42 | 53 | 0.0030704 | 0.00076951 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_158-18_0_4_load_43 | 54 | 0.0044595 | 0.0011177 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_158-18_0_4_load_44 | 58 | 0.0092208 | 0.0023109 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_158-18_0_4_load_45 | 59 | 0.0085319 | 0.0021383 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_158-18_0_4_load_46 | 61 | 0.0020912 | 0.00052409 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_158-18_0_4_load_49 | 63 | 0.0005826 | 0.00014601 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_158-18_0_4_load_68 | 64 | 0.0064825 | 0.0016247 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_158-18_0_4_load_73 | 65 | 0.0029153 | 0.00073065 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_158-18_0_4_load_104 | 66 | 0.0055693 | 0.0013958 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_158-18_0_4_load_120 | 69 | 0.0062199 | 0.0015589 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_158-18_0_4_load_56 | 70 | 0.0017746 | 0.00044476 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_158-18_0_4_load_57 | 71 | 0.0028359 | 0.00071073 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_158-18_0_4_load_58 | 72 | 0.0034668 | 0.00086887 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_158-18_0_4_load_59 | 73 | 0.0029662 | 0.00074341 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_158-18_0_4_load_60 | 74 | 0.0030536 | 0.0007653 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_158-18_0_4_load_61 | 75 | 0.0020345 | 0.00050989 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_158-18_0_4_load_62 | 76 | 0.0030773 | 0.00077125 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_158-18_0_4_load_65 | 77 | 0.0030868 | 0.00077363 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_158-18_0_4_load_105 | 78 | 0.011844 | 0.0029683 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_158-18_0_4_load_116 | 79 | 0.0021211 | 0.00053159 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_158-18_0_4_load_69 | 81 | 0.0031198 | 0.0007819 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_158-18_0_4_load_71 | 82 | 0.0021113 | 0.00052913 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_158-18_0_4_load_74 | 83 | 0.010909 | 0.0027341 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_158-18_0_4_load_86 | 87 | 0.0088184 | 0.0022101 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_158-18_0_4_load_79 | 89 | 0.010972 | 0.0027498 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_158-18_0_4_load_87 | 90 | 0.0040228 | 0.0010082 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_158-18_0_4_load_84 | 91 | 0.017294 | 0.0043342 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_158-18_0_4_load_88 | 92 | 0.0032241 | 0.00080803 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_158-18_0_4_load_108 | 93 | 0.039879 | 0.0099947 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_158-18_0_4_load_106 | 94 | 0.005683 | 0.0014243 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_158-18_0_4_load_109 | 95 | 0.0052436 | 0.0013142 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_158-18_0_4_load_107 | 96 | 0.01394 | 0.0034936 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_158-18_0_4_load_89 | 97 | 0.00054075 | 0.00013553 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_158-18_0_4_load_90 | 98 | 0.0083634 | 0.0020961 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_158-18_0_4_load_93 | 99 | 0.00032627 | 8.1772e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_158-18_0_4_load_91 | 100 | 0.00034612 | 8.6746e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_158-18_0_4_load_92 | 102 | 0.00018212 | 4.5644e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_158-18_0_4_load_114 | 103 | 0.00099061 | 0.00024827 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_158-18_0_4_load_96 | 105 | 0.00019474 | 4.8807e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_158-18_0_4_load_100 | 107 | 0.00045411 | 0.00011381 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_158-18_0_4_load_98 | 108 | 0.00021485 | 5.3847e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_158-18_0_4_load_99 | 109 | 0.00038256 | 9.5879e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_158-18_0_4_load_102 | 111 | 0.0035121 | 0.00088021 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_158-18_0_4_load_110 | 112 | 0.0095725 | 0.0023991 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_158-18_0_4_load_112 | 113 | 0.0015808 | 0.00039618 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_158-18_0_4_load_113 | 114 | 0.010129 | 0.0025386 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_158-18_0_4_load_121 | 115 | 0.0014542 | 0.00036447 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_158-18_0_4_load_122 | 116 | 0.0016822 | 0.0004216 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_158-18_0_4_line_0 |  | 0 | 1 | 0.00038436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_158-18_0_4_line_1 |  | 1 | 2 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_158-18_0_4_line_2 |  | 2 | 3 | 0.007354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_158-18_0_4_line_3 |  | 3 | 4 | 0.021136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_158-18_0_4_line_4 |  | 3 | 5 | 0.033006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_158-18_0_4_line_5 |  | 4 | 6 | 0.003081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_158-18_0_4_line_6 |  | 4 | 7 | 0.012215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_158-18_0_4_line_7 |  | 5 | 8 | 0.02945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_158-18_0_4_line_8 |  | 6 | 15 | 0.044075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_158-18_0_4_line_9 |  | 6 | 16 | 0.022381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_158-18_0_4_line_10 |  | 7 | 14 | 0.0016857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_158-18_0_4_line_11 |  | 9 | 10 | 0.023011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_158-18_0_4_line_12 |  | 9 | 11 | 0.027428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_158-18_0_4_line_13 |  | 10 | 69 | 0.013613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_158-18_0_4_line_14 |  | 11 | 89 | 0.036771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_158-18_0_4_line_15 |  | 12 | 13 | 0.018858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_158-18_0_4_line_16 |  | 13 | 86 | 0.010989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_158-18_0_4_line_17 |  | 15 | 17 | 0.014587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_158-18_0_4_line_18 |  | 17 | 22 | 0.023619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_158-18_0_4_line_19 |  | 17 | 23 | 0.015335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_158-18_0_4_line_20 |  | 17 | 24 | 0.017339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_158-18_0_4_line_21 |  | 18 | 19 | 0.027437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_158-18_0_4_line_22 |  | 19 | 20 | 0.0087196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_158-18_0_4_line_23 |  | 20 | 21 | 0.025719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_158-18_0_4_line_24 |  | 21 | 25 | 0.0080108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_158-18_0_4_line_25 |  | 24 | 27 | 0.0019103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_158-18_0_4_line_26 |  | 25 | 26 | 0.01272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_158-18_0_4_line_27 |  | 26 | 41 | 0.010208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_158-18_0_4_line_28 |  | 27 | 28 | 0.014843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_158-18_0_4_line_29 |  | 28 | 29 | 0.031173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_158-18_0_4_line_30 |  | 28 | 30 | 0.021766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_158-18_0_4_line_31 |  | 29 | 31 | 0.014644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_158-18_0_4_line_32 |  | 29 | 32 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_158-18_0_4_line_33 |  | 30 | 33 | 0.016492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_158-18_0_4_line_34 |  | 31 | 36 | 0.029467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_158-18_0_4_line_35 |  | 32 | 37 | 0.024319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_158-18_0_4_line_36 |  | 33 | 38 | 0.0068107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_158-18_0_4_line_37 |  | 34 | 35 | 0.034267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_158-18_0_4_line_38 |  | 35 | 39 | 0.026335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_158-18_0_4_line_39 |  | 36 | 39 | 0.028909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_158-18_0_4_line_40 |  | 37 | 40 | 0.018596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_158-18_0_4_line_41 |  | 38 | 70 | 0.0084623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_158-18_0_4_line_42 |  | 41 | 42 | 0.030077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_158-18_0_4_line_43 |  | 41 | 43 | 0.033738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_158-18_0_4_line_44 |  | 42 | 44 | 0.024059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_158-18_0_4_line_45 |  | 42 | 45 | 0.012328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_158-18_0_4_line_46 |  | 43 | 46 | 0.0038197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_158-18_0_4_line_47 |  | 44 | 50 | 0.014915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_158-18_0_4_line_48 |  | 45 | 51 | 0.011343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_158-18_0_4_line_49 |  | 46 | 47 | 0.041774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_158-18_0_4_line_50 |  | 47 | 48 | 0.009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_158-18_0_4_line_51 |  | 48 | 49 | 0.034128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_158-18_0_4_line_52 |  | 49 | 69 | 0.033989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_158-18_0_4_line_53 |  | 50 | 55 | 0.0098329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_158-18_0_4_line_54 |  | 51 | 52 | 0.02082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_158-18_0_4_line_55 |  | 52 | 53 | 0.0053808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_158-18_0_4_line_56 |  | 53 | 54 | 0.025385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_158-18_0_4_line_57 |  | 54 | 56 | 0.0030276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_158-18_0_4_line_58 |  | 55 | 77 | 0.020639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_158-18_0_4_line_59 |  | 55 | 76 | 0.0018676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_158-18_0_4_line_60 |  | 56 | 57 | 0.014366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_158-18_0_4_line_61 |  | 57 | 66 | 0.05196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_158-18_0_4_line_62 |  | 57 | 62 | 0.034301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_158-18_0_4_line_63 |  | 58 | 59 | 0.028885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_158-18_0_4_line_64 |  | 59 | 60 | 0.041802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_158-18_0_4_line_65 |  | 60 | 63 | 0.043255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_158-18_0_4_line_66 |  | 61 | 62 | 0.026993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_158-18_0_4_line_67 |  | 62 | 64 | 0.05091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_158-18_0_4_line_68 |  | 63 | 65 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_158-18_0_4_line_69 |  | 64 | 67 | 0.10042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_158-18_0_4_line_70 |  | 65 | 68 | 0.012622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_158-18_0_4_line_71 |  | 66 | 78 | 0.0093557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_158-18_0_4_line_72 |  | 67 | 79 | 0.039529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_158-18_0_4_line_73 |  | 67 | 80 | 0.091806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_158-18_0_4_line_74 |  | 68 | 83 | 0.028315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_158-18_0_4_line_75 |  | 68 | 81 | 0.031391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_158-18_0_4_line_76 |  | 70 | 71 | 0.0236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_158-18_0_4_line_77 |  | 71 | 72 | 0.0010771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_158-18_0_4_line_78 |  | 72 | 73 | 0.025758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_158-18_0_4_line_79 |  | 73 | 74 | 0.0028216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_158-18_0_4_line_80 |  | 74 | 75 | 0.024127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_158-18_0_4_line_81 |  | 75 | 76 | 0.0094969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_158-18_0_4_line_82 |  | 80 | 103 | 0.07687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_158-18_0_4_line_83 |  | 81 | 82 | 0.099885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_158-18_0_4_line_84 |  | 83 | 84 | 0.039079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_158-18_0_4_line_85 |  | 84 | 85 | 0.036256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_158-18_0_4_line_86 |  | 85 | 88 | 0.010862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_158-18_0_4_line_87 |  | 85 | 89 | 0.02991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_158-18_0_4_line_88 |  | 86 | 87 | 0.025503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_158-18_0_4_line_89 |  | 87 | 92 | 0.027856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_158-18_0_4_line_90 |  | 87 | 91 | 0.029173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_158-18_0_4_line_91 |  | 88 | 90 | 0.038768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_158-18_0_4_line_92 |  | 88 | 91 | 0.022396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_158-18_0_4_line_93 |  | 90 | 93 | 0.0062195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_158-18_0_4_line_94 |  | 92 | 94 | 0.014742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_158-18_0_4_line_95 |  | 93 | 95 | 0.013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_158-18_0_4_line_96 |  | 94 | 96 | 0.038356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_158-18_0_4_line_97 |  | 95 | 112 | 0.024507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_158-18_0_4_line_98 |  | 97 | 98 | 0.019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_158-18_0_4_line_99 |  | 97 | 99 | 0.09388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_158-18_0_4_line_100 |  | 98 | 100 | 0.055867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_158-18_0_4_line_101 |  | 99 | 101 | 0.019417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_158-18_0_4_line_102 |  | 100 | 102 | 0.055889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_158-18_0_4_line_103 |  | 101 | 104 | 0.052802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_158-18_0_4_line_104 |  | 102 | 103 | 2.9036e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_158-18_0_4_line_105 |  | 104 | 107 | 0.011132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_158-18_0_4_line_106 |  | 105 | 106 | 0.048439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_158-18_0_4_line_107 |  | 106 | 108 | 0.0013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_158-18_0_4_line_108 |  | 106 | 109 | 0.051861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_158-18_0_4_line_109 |  | 107 | 108 | 0.01 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_158-18_0_4_line_110 |  | 109 | 110 | 0.054733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_158-18_0_4_line_111 |  | 110 | 111 | 0.009694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_158-18_0_4_line_112 |  | 112 | 113 | 0.0026023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_158-18_0_4_line_113 |  | 113 | 114 | 0.021533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_158-18_0_4_line_114 |  | 114 | 115 | 0.058589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_158-18_0_4_line_115 |  | 115 | 116 | 0.0014673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_158-18_0_4_trafo_50 | 0.63 MVA 20/0.4 kV | 117 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2696928.136 | 1233186.5186 | 2696927.7517 | 1233186.5128
1 | 2696916.9772 | 1233187.5558 | 2696921.5089 | 1233186.4177 | 2696927.7517 | 1233186.5128
2 | 2696916.9772 | 1233187.5558 | 2696918.4562 | 1233190.6599 | 2696918.9228 | 1233194.5482
3 | 2696918.1393 | 1233215.6509 | 2696918.8752 | 1233206.7452 | 2696918.9228 | 1233194.5482
4 | 2696889.315 | 1233188.0607 | 2696895.2793 | 1233185.9008 | 2696898.7818 | 1233186.1136 | 2696902.4277 | 1233187.285 | 2696905.2696 | 1233188.9993 | 2696908.3616 | 1233190.2395 | 2696911.5525 | 1233190.058 | 2696913.6909 | 1233190.8046 | 2696915.1842 | 1233192.0965 | 2696916.1305 | 1233194.4359 | 2696918.9228 | 1233194.5482
5 | 2696917.1904 | 1233218.582 | 2696918.1393 | 1233215.6509
6 | 2696918.1393 | 1233215.6509 | 2696929.5004 | 1233220.1373
7 | 2696889.315 | 1233188.0607 | 2696877.719 | 1233191.4854 | 2696868.9996 | 1233191.7101 | 2696860.3937 | 1233191.4808 | 2696860.3661 | 1233191.4789
8 | 2696917.1904 | 1233218.582 | 2696919.1727 | 1233220.538 | 2696919.0549 | 1233256.5291 | 2696919.8509 | 1233261.7678
9 | 2696917.1904 | 1233218.582 | 2696914.6934 | 1233221.2544 | 2696911.216 | 1233224.1442 | 2696899.2789 | 1233231.8387
10 | 2696929.5004 | 1233220.1373 | 2696931.0683 | 1233220.7564
11 | 2696805.9822 | 1233188.0475 | 2696804.0487 | 1233210.9772
12 | 2696805.9822 | 1233188.0475 | 2696778.613 | 1233186.2593
13 | 2696793.7717 | 1233218.6432 | 2696799.4029 | 1233217.2618 | 2696804.0487 | 1233210.9772 | 2696804.0487 | 1233210.9772
14 | 2696778.613 | 1233186.2593 | 2696762.4501 | 1233185.2033 | 2696741.9896 | 1233183.0488
15 | 2696789.8412 | 1233179.2546 | 2696789.5273 | 1233179.2397 | 2696779.3671 | 1233178.6628 | 2696771.0437 | 1233177.8062
16 | 2696760.1128 | 1233176.6812 | 2696771.0437 | 1233177.8062
17 | 2696923.6547 | 1233275.8072 | 2696920.525 | 1233266.2047 | 2696919.8509 | 1233261.7678
18 | 2696923.6547 | 1233275.8072 | 2696917.5115 | 1233273.6165 | 2696900.6144 | 1233276.621
19 | 2696923.6547 | 1233275.8072 | 2696930.3965 | 1233271.9365 | 2696937.8655 | 1233270.7614
20 | 2696923.6547 | 1233275.8072 | 2696928.0756 | 1233292.5735
21 | 2696860.5522 | 1233256.8013 | 2696852.0608 | 1233262.2748 | 2696836.3163 | 1233269.5258
22 | 2696828.3963 | 1233273.1733 | 2696836.3163 | 1233269.5258
23 | 2696828.3963 | 1233273.1733 | 2696824.3354 | 1233275.0436 | 2696814.0779 | 1233280.4471 | 2696806.0165 | 1233285.7589
24 | 2696799.7851 | 1233290.7714 | 2696804.1808 | 1233286.9685 | 2696806.0165 | 1233285.7589
25 | 2696928.0756 | 1233292.5735 | 2696928.5627 | 1233294.4207
26 | 2696799.7851 | 1233290.7714 | 2696797.9366 | 1233292.3708 | 2696790.0648 | 1233298.9751
27 | 2696782.2446 | 1233305.536 | 2696790.0648 | 1233298.9751
28 | 2696932.3472 | 1233308.7731 | 2696928.5627 | 1233294.4207
29 | 2696932.3472 | 1233308.7731 | 2696933.1411 | 1233339.9312
30 | 2696932.3472 | 1233308.7731 | 2696911.3888 | 1233314.648
31 | 2696933.1411 | 1233339.9312 | 2696947.5452 | 1233337.2919
32 | 2696933.1411 | 1233339.9312 | 2696936.5365 | 1233357.5042
33 | 2696911.3888 | 1233314.648 | 2696895.509 | 1233319.0993
34 | 2696947.5452 | 1233337.2919 | 2696976.53 | 1233331.9811
35 | 2696941.1498 | 1233381.3811 | 2696936.5365 | 1233357.5042
36 | 2696888.9511 | 1233320.9375 | 2696895.509 | 1233319.0993
37 | 2697002.0231 | 1233300.6038 | 2696993.3078 | 1233299.1938 | 2696967.9341 | 1233301.0145
38 | 2697002.0231 | 1233300.6038 | 2697004.9653 | 1233326.771
39 | 2697004.9653 | 1233326.771 | 2696976.53 | 1233331.9811
40 | 2696941.1498 | 1233381.3811 | 2696959.2927 | 1233377.2996
41 | 2696888.9511 | 1233320.9375 | 2696880.8029 | 1233323.2215
42 | 2696763.0991 | 1233328.5078 | 2696768.4959 | 1233319.8004 | 2696776.1306 | 1233310.8515 | 2696782.2446 | 1233305.536
43 | 2696782.2446 | 1233305.536 | 2696765.9671 | 1233287.7135 | 2696762.5206 | 1233286.8568 | 2696756.4897 | 1233286.3768
44 | 2696763.0991 | 1233328.5078 | 2696775.0763 | 1233334.6629 | 2696785.0029 | 1233330.9663
45 | 2696763.0991 | 1233328.5078 | 2696756.6073 | 1233338.9881
46 | 2696756.4897 | 1233286.3768 | 2696752.682 | 1233286.0738
47 | 2696792.3164 | 1233343.9655 | 2696785.0029 | 1233330.9663
48 | 2696756.6073 | 1233338.9881 | 2696750.634 | 1233348.6313
49 | 2696752.682 | 1233286.0738 | 2696752.682 | 1233286.0738 | 2696753.2136 | 1233258.0842 | 2696739.4492 | 1233257.439
50 | 2696739.4492 | 1233257.439 | 2696738.671 | 1233257.4025 | 2696739.4497 | 1233249.2186
51 | 2696739.4497 | 1233249.2186 | 2696740.3063 | 1233240.2165 | 2696742.0966 | 1233239.0893 | 2696753.924 | 1233228.4184 | 2696760.761 | 1233226.7412
52 | 2696760.761 | 1233226.7412 | 2696793.7717 | 1233218.6432
53 | 2696797.1378 | 1233352.5352 | 2696792.3164 | 1233343.9655
54 | 2696739.236 | 1233366.0403 | 2696743.6109 | 1233359.9693 | 2696750.634 | 1233348.6313
55 | 2696739.236 | 1233366.0403 | 2696736.0901 | 1233370.4057
56 | 2696736.0901 | 1233370.4057 | 2696721.2488 | 1233391.0004
57 | 2696719.4787 | 1233393.4567 | 2696721.2488 | 1233391.0004
58 | 2696784.4888 | 1233368.0962 | 2696789.6138 | 1233357.95 | 2696796.3449 | 1233352.867 | 2696797.1378 | 1233352.5352
59 | 2696797.1378 | 1233352.5352 | 2696798.8605 | 1233351.8139
60 | 2696719.4787 | 1233393.4567 | 2696717.5534 | 1233395.9049 | 2696713.8673 | 1233400.9264 | 2696710.0282 | 1233404.1886
61 | 2696710.0282 | 1233404.1886 | 2696713.0151 | 1233413.2772 | 2696725.618 | 1233453.7532
62 | 2696710.0282 | 1233404.1886 | 2696708.2468 | 1233405.7051 | 2696703.4021 | 1233409.8071 | 2696689.6605 | 1233419.4796 | 2696685.0476 | 1233421.4393 | 2696681.285 | 1233422.3232
63 | 2696661.1469 | 1233342.974 | 2696656.6374 | 1233326.5187 | 2696651.9021 | 1233315.6854
64 | 2696638.0951 | 1233276.614 | 2696638.6318 | 1233284.5841 | 2696650.308 | 1233312.0385 | 2696651.9021 | 1233315.6854
65 | 2696638.0951 | 1233276.614 | 2696632.2414 | 1233269.1911 | 2696623.911 | 1233250.631 | 2696621.0616 | 1233242.8568 | 2696620.8793 | 1233237.6824
66 | 2696681.285 | 1233422.3232 | 2696678.1871 | 1233405.1713 | 2696675.6618 | 1233395.9471
67 | 2696681.285 | 1233422.3232 | 2696682.64 | 1233468.8683 | 2696683.6062 | 1233473.1046
68 | 2696621.6878 | 1233221.4394 | 2696622.6902 | 1233223.7359 | 2696620.7508 | 1233234.0341 | 2696620.8793 | 1233237.6824
69 | 2696679.6498 | 1233572.0954 | 2696689.2829 | 1233519.8915 | 2696689.7183 | 1233509.4243 | 2696685.99 | 1233483.5558 | 2696683.6062 | 1233473.1046
70 | 2696616.6384 | 1233209.8718 | 2696621.6878 | 1233221.4394
71 | 2696728.3993 | 1233462.686 | 2696725.618 | 1233453.7532
72 | 2696679.6498 | 1233572.0954 | 2696709.0077 | 1233598.5659
73 | 2696628.8732 | 1233621.9063 | 2696629.6351 | 1233623.4754 | 2696634.5979 | 1233634.9089 | 2696640.9354 | 1233627.929 | 2696648.3411 | 1233615.7961 | 2696655.14 | 1233602.7971 | 2696679.6498 | 1233572.0954
74 | 2696616.6384 | 1233209.8718 | 2696643.0777 | 1233199.7389
75 | 2696616.6384 | 1233209.8718 | 2696610.8933 | 1233212.0578 | 2696586.7823 | 1233219.5372
76 | 2696858.0861 | 1233329.6161 | 2696858.4994 | 1233329.4734 | 2696880.8029 | 1233323.2215
77 | 2696857.068 | 1233329.9675 | 2696858.0861 | 1233329.6161
78 | 2696857.068 | 1233329.9675 | 2696832.7199 | 1233338.3717
79 | 2696832.7199 | 1233338.3717 | 2696830.0527 | 1233339.2923
80 | 2696807.6205 | 1233348.146 | 2696822.7243 | 1233341.8219 | 2696830.0527 | 1233339.2923
81 | 2696807.6205 | 1233348.146 | 2696798.8605 | 1233351.8139
82 | 2696628.8732 | 1233621.9063 | 2696625.0681 | 1233613.3159 | 2696617.0219 | 1233598.2629 | 2696594.0985 | 1233562.175 | 2696590.5338 | 1233555.4026
83 | 2696586.7823 | 1233219.5372 | 2696493.2953 | 1233254.7103
84 | 2696679.7514 | 1233186.2473 | 2696657.4117 | 1233194.2454 | 2696643.0777 | 1233199.7389
85 | 2696679.7514 | 1233186.2473 | 2696699.7594 | 1233178.2113 | 2696714.2901 | 1233175.4568
86 | 2696713.876 | 1233164.6088 | 2696714.3494 | 1233172.7447 | 2696714.2901 | 1233175.4568
87 | 2696714.2901 | 1233175.4568 | 2696717.751 | 1233179.6162 | 2696723.6327 | 1233180.2012 | 2696727.9261 | 1233181.1384 | 2696740.0896 | 1233182.8487 | 2696741.9896 | 1233183.0488
88 | 2696763.1982 | 1233151.3684 | 2696760.1128 | 1233176.6812
89 | 2696763.1982 | 1233151.3684 | 2696791.0481 | 1233150.7926
90 | 2696763.1982 | 1233151.3684 | 2696752.6708 | 1233152.8759 | 2696747.7602 | 1233154.9642 | 2696740.9167 | 1233155.7756 | 2696734.6179 | 1233156.1623
91 | 2696713.876 | 1233164.6088 | 2696708.5154 | 1233152.9463 | 2696692.8749 | 1233132.2619
92 | 2696713.876 | 1233164.6088 | 2696734.6179 | 1233156.1623
93 | 2696689.1237 | 1233127.301 | 2696692.8749 | 1233132.2619
94 | 2696805.7561 | 1233150.0463 | 2696804.1817 | 1233150.3127 | 2696798.9895 | 1233150.6284 | 2696791.0481 | 1233150.7926
95 | 2696689.1237 | 1233127.301 | 2696689.1237 | 1233127.301 | 2696679.8543 | 1233117.8987
96 | 2696822.9887 | 1233122.5987 | 2696823.186 | 1233129.5403 | 2696822.9178 | 1233140.8887 | 2696819.9283 | 1233144.5093 | 2696814.7843 | 1233147.4388 | 2696809.8766 | 1233149.3492 | 2696805.7561 | 1233150.0463
97 | 2696662.5988 | 1233100.4973 | 2696666.6191 | 1233104.4738 | 2696679.8543 | 1233117.8987
98 | 2696554.7173 | 1233432.2418 | 2696565.0579 | 1233448.2503
99 | 2696554.7173 | 1233432.2418 | 2696476.3763 | 1233483.9724
100 | 2696565.0579 | 1233448.2503 | 2696569.3712 | 1233454.9278 | 2696576.5984 | 1233475.6605 | 2696579.8061 | 1233491.2018 | 2696580.9149 | 1233501.2332
101 | 2696483.9472 | 1233501.8528 | 2696476.3763 | 1233483.9724
102 | 2696580.9149 | 1233501.2332 | 2696584.1758 | 1233530.7351 | 2696584.2931 | 1233543.5464 | 2696590.5324 | 1233555.4
103 | 2696483.9472 | 1233501.8528 | 2696492.1073 | 1233525.3025 | 2696491.6955 | 1233535.2698 | 2696483.4699 | 1233543.3533 | 2696478.8378 | 1233547.9037
104 | 2696590.5338 | 1233555.4026 | 2696590.5324 | 1233555.4
105 | 2696478.8378 | 1233547.9037 | 2696468.8019 | 1233552.7216
106 | 2696458.6072 | 1233557.6158 | 2696439.8308 | 1233535.5949 | 2696425.4243 | 1233522.4536
107 | 2696458.6072 | 1233557.6158 | 2696459.7866 | 1233557.0496
108 | 2696458.6072 | 1233557.6158 | 2696449.4472 | 1233564.0274 | 2696435.3704 | 1233574.3399 | 2696418.9755 | 1233582.3909 | 2696414.2861 | 1233584.0221
109 | 2696468.8019 | 1233552.7216 | 2696459.7866 | 1233557.0496
110 | 2696361.5749 | 1233598.672 | 2696404.9872 | 1233587.2565 | 2696414.2861 | 1233584.0221
111 | 2696361.5749 | 1233598.672 | 2696352.0777 | 1233600.6156
112 | 2696662.5988 | 1233100.4973 | 2696660.7486 | 1233098.6674
113 | 2696645.0613 | 1233083.9231 | 2696654.5834 | 1233092.5694 | 2696660.7486 | 1233098.6674
114 | 2696645.0613 | 1233083.9231 | 2696642.9872 | 1233082.0398 | 2696632.734 | 1233068.5521 | 2696622.7739 | 1233051.9336 | 2696621.2487 | 1233048.8732 | 2696619.4444 | 1233044.3406 | 2696617.95 | 1233039.3793 | 2696618.6854 | 1233033.4338
115 | 2696618.8655 | 1233031.9776 | 2696618.6854 | 1233033.4338

## bus_geodata
| x | y | coords
0 | 2696928.136 | 1233186.5186
1 | 2696927.7517 | 1233186.5128
2 | 2696916.9772 | 1233187.5558
3 | 2696918.9228 | 1233194.5482
4 | 2696918.1393 | 1233215.6509
5 | 2696889.315 | 1233188.0607
6 | 2696917.1904 | 1233218.582
7 | 2696929.5004 | 1233220.1373
8 | 2696860.3661 | 1233191.4789
9 | 2696805.9822 | 1233188.0475
10 | 2696804.0487 | 1233210.9772
11 | 2696778.613 | 1233186.2593
12 | 2696789.8412 | 1233179.2546
13 | 2696771.0437 | 1233177.8062
14 | 2696931.0683 | 1233220.7564
15 | 2696919.8509 | 1233261.7678
16 | 2696899.2789 | 1233231.8387
17 | 2696923.6547 | 1233275.8072
18 | 2696860.5522 | 1233256.8013
19 | 2696836.3163 | 1233269.5258
20 | 2696828.3963 | 1233273.1733
21 | 2696806.0165 | 1233285.7589
22 | 2696900.6144 | 1233276.621
23 | 2696937.8655 | 1233270.7613
24 | 2696928.0756 | 1233292.5735
25 | 2696799.7851 | 1233290.7714
26 | 2696790.0648 | 1233298.9751
27 | 2696928.5627 | 1233294.4207
28 | 2696932.3472 | 1233308.7731
29 | 2696933.1411 | 1233339.9312
30 | 2696911.3888 | 1233314.648
31 | 2696947.5452 | 1233337.2919
32 | 2696936.5365 | 1233357.5042
33 | 2696895.509 | 1233319.0993
34 | 2696967.9341 | 1233301.0145
35 | 2697002.0231 | 1233300.6038
36 | 2696976.53 | 1233331.9811
37 | 2696941.1498 | 1233381.3811
38 | 2696888.9511 | 1233320.9375
39 | 2697004.9653 | 1233326.771
40 | 2696959.2927 | 1233377.2996
41 | 2696782.2446 | 1233305.536
42 | 2696763.0991 | 1233328.5078
43 | 2696756.4897 | 1233286.3768
44 | 2696785.0029 | 1233330.9663
45 | 2696756.6073 | 1233338.9881
46 | 2696752.682 | 1233286.0738
47 | 2696739.4492 | 1233257.439
48 | 2696739.4497 | 1233249.2186
49 | 2696760.761 | 1233226.7412
50 | 2696792.3164 | 1233343.9655
51 | 2696750.634 | 1233348.6313
52 | 2696739.236 | 1233366.0403
53 | 2696736.0901 | 1233370.4057
54 | 2696721.2488 | 1233391.0004
55 | 2696797.1378 | 1233352.5352
56 | 2696719.4787 | 1233393.4567
57 | 2696710.0282 | 1233404.1886
58 | 2696661.1469 | 1233342.974
59 | 2696651.9021 | 1233315.6854
60 | 2696638.0951 | 1233276.614
61 | 2696675.6618 | 1233395.9471
62 | 2696681.285 | 1233422.3232
63 | 2696620.8793 | 1233237.6824
64 | 2696683.6062 | 1233473.1046
65 | 2696621.6878 | 1233221.4394
66 | 2696725.618 | 1233453.7532
67 | 2696679.6498 | 1233572.0954
68 | 2696616.6384 | 1233209.8718
69 | 2696793.7717 | 1233218.6432
70 | 2696880.8029 | 1233323.2215
71 | 2696858.0861 | 1233329.6161
72 | 2696857.068 | 1233329.9675
73 | 2696832.7199 | 1233338.3717
74 | 2696830.0527 | 1233339.2923
75 | 2696807.6205 | 1233348.146
76 | 2696798.8605 | 1233351.8139
77 | 2696784.4888 | 1233368.0962
78 | 2696728.3993 | 1233462.686
79 | 2696709.0077 | 1233598.5659
80 | 2696628.8732 | 1233621.9063
81 | 2696586.7823 | 1233219.5372
82 | 2696493.2953 | 1233254.7103
83 | 2696643.0777 | 1233199.7389
84 | 2696679.7514 | 1233186.2473
85 | 2696714.2901 | 1233175.4568
86 | 2696760.1128 | 1233176.6812
87 | 2696763.1982 | 1233151.3684
88 | 2696713.876 | 1233164.6088
89 | 2696741.9896 | 1233183.0488
90 | 2696692.8749 | 1233132.2619
91 | 2696734.6179 | 1233156.1623
92 | 2696791.0481 | 1233150.7926
93 | 2696689.1237 | 1233127.301
94 | 2696805.7561 | 1233150.0463
95 | 2696679.8543 | 1233117.8987
96 | 2696822.9887 | 1233122.5987
97 | 2696554.7173 | 1233432.2418
98 | 2696565.0579 | 1233448.2503
99 | 2696476.3763 | 1233483.9724
100 | 2696580.9149 | 1233501.2332
101 | 2696483.9472 | 1233501.8528
102 | 2696590.5324 | 1233555.4
103 | 2696590.5338 | 1233555.4026
104 | 2696478.8378 | 1233547.9037
105 | 2696425.4243 | 1233522.4536
106 | 2696458.6072 | 1233557.6158
107 | 2696468.8019 | 1233552.7216
108 | 2696459.7866 | 1233557.0496
109 | 2696414.2861 | 1233584.0221
110 | 2696361.5749 | 1233598.672
111 | 2696352.0777 | 1233600.6156
112 | 2696662.5988 | 1233100.4973
113 | 2696660.7486 | 1233098.6674
114 | 2696645.0613 | 1233083.9231
115 | 2696618.6854 | 1233033.4338
116 | 2696618.8655 | 1233031.9776
117 | 2696782.2446 | 1233305.536

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97281 | -0.52487 | 0.0024716 | 0.00061944
1 | 0.97281 | -0.52486 | 0.002864 | 0.00071779
2 | 0.97287 | -0.52378 | 0 | 0
3 | 0.9729 | -0.52306 | 0 | 0
4 | 0.97331 | -0.51492 | 0 | 0
5 | 0.97242 | -0.53255 | 0.005893 | 0.0014769
6 | 0.97338 | -0.51356 | 0 | 0
7 | 0.97328 | -0.51558 | 0.0020734 | 0.00051965
8 | 0.97216 | -0.53782 | 0.0097082 | 0.0024331
9 | 0.98973 | -0.19491 | 0 | 0
10 | 0.99188 | -0.1539 | 0.0055673 | 0.0013953
11 | 0.98718 | -0.24403 | 0.012199 | 0.0030575
12 | 0.97655 | -0.45095 | 0.011804 | 0.0029583
13 | 0.97676 | -0.44688 | 0.0058618 | 0.0014691
14 | 0.97328 | -0.51561 | 0.00087984 | 0.00022051
15 | 0.97445 | -0.49256 | 0.0017408 | 0.0004363
16 | 0.97334 | -0.5144 | 0.0020316 | 0.00050916
17 | 0.97482 | -0.48516 | 0 | 0
18 | 0.99078 | -0.17575 | 0.0041073 | 0.0010294
19 | 0.99088 | -0.17375 | 0.0066879 | 0.0016761
20 | 0.99097 | -0.17208 | 0.0028856 | 0.00072319
21 | 0.99129 | -0.16584 | 0.0020798 | 0.00052124
22 | 0.97474 | -0.48689 | 0.0040068 | 0.0010042
23 | 0.97478 | -0.486 | 0.0030011 | 0.00075215
24 | 0.97538 | -0.47414 | 0.0038273 | 0.00095921
25 | 0.9914 | -0.1636 | 0.0071964 | 0.0018036
26 | 0.99167 | -0.15842 | 0.0018368 | 0.00046035
27 | 0.97545 | -0.47279 | 0.0021733 | 0.00054469
28 | 0.97602 | -0.46173 | 0 | 0
29 | 0.9755 | -0.47194 | 0 | 0
30 | 0.9772 | -0.43844 | 0.0031393 | 0.00078678
31 | 0.97538 | -0.47427 | 0.0025243 | 0.00063265
32 | 0.97534 | -0.47497 | 0.0036943 | 0.00092587
33 | 0.97815 | -0.41988 | 0.0028728 | 0.00072
34 | 0.97506 | -0.48049 | 0.001774 | 0.00044461
35 | 0.97512 | -0.47938 | 0 | 0
36 | 0.97521 | -0.47758 | 0.0043532 | 0.001091
37 | 0.97522 | -0.47744 | 0 | 0
38 | 0.97856 | -0.41187 | 0.0025721 | 0.00064462
39 | 0.97516 | -0.47852 | 0 | 0
40 | 0.97512 | -0.47933 | 0.0055407 | 0.0013886
41 | 0.9919 | -0.15393 | 0 | 0
42 | 0.98961 | -0.19791 | 0 | 0
43 | 0.99486 | -0.097472 | 0.0064082 | 0.001606
44 | 0.9875 | -0.2385 | 0.0014864 | 0.00037252
45 | 0.98881 | -0.21331 | 0.007763 | 0.0019456
46 | 0.9952 | -0.090885 | 0.007096 | 0.0017784
47 | 0.99912 | -0.016559 | 0.0079349 | 0.0019887
48 | 1 | 0 | -0.43932 | -0.11261
49 | 0.99653 | -0.065427 | 0.006649 | 0.0016664
50 | 0.98621 | -0.26335 | 0.0036299 | 0.00090975
51 | 0.98816 | -0.22593 | 0.003168 | 0.00079398
52 | 0.98702 | -0.24795 | 0.0080134 | 0.0020083
53 | 0.98677 | -0.25288 | 0.0030704 | 0.00076951
54 | 0.98564 | -0.27476 | 0.0044595 | 0.0011177
55 | 0.98539 | -0.27912 | 0 | 0
56 | 0.98552 | -0.27714 | 0 | 0
57 | 0.98494 | -0.28839 | 0 | 0
58 | 0.976 | -0.46185 | 0.0092208 | 0.0023109
59 | 0.97625 | -0.45698 | 0.0085319 | 0.0021383
60 | 0.97694 | -0.44341 | 0 | 0
61 | 0.98406 | -0.30559 | 0.0020912 | 0.00052409
62 | 0.98411 | -0.30457 | 0 | 0
63 | 0.97765 | -0.4294 | 0.0005826 | 0.00014601
64 | 0.98297 | -0.32671 | 0.0064825 | 0.0016247
65 | 0.97793 | -0.42384 | 0.0029153 | 0.00073065
66 | 0.98411 | -0.30467 | 0.0055693 | 0.0013958
67 | 0.98133 | -0.35874 | 0 | 0
68 | 0.97818 | -0.41895 | 0 | 0
69 | 0.99318 | -0.12905 | 0.0062199 | 0.0015589
70 | 0.97909 | -0.40153 | 0.0017746 | 0.00044476
71 | 0.9806 | -0.37199 | 0.0028359 | 0.00071073
72 | 0.98067 | -0.37059 | 0.0034668 | 0.00086887
73 | 0.98248 | -0.33554 | 0.0029662 | 0.00074341
74 | 0.98268 | -0.33155 | 0.0030536 | 0.0007653
75 | 0.9845 | -0.29623 | 0.0020345 | 0.00050989
76 | 0.98524 | -0.28202 | 0.0030773 | 0.00077125
77 | 0.98533 | -0.28027 | 0.0030868 | 0.00077363
78 | 0.984 | -0.30666 | 0.011844 | 0.0029683
79 | 0.98125 | -0.36026 | 0.0021211 | 0.00053159
80 | 0.98001 | -0.38458 | 0 | 0
81 | 0.97803 | -0.42194 | 0.0031198 | 0.0007819
82 | 0.97784 | -0.42579 | 0.0021113 | 0.00052913
83 | 0.97888 | -0.40529 | 0.010909 | 0.0027341
84 | 0.98023 | -0.37874 | 0 | 0
85 | 0.98149 | -0.35418 | 0 | 0
86 | 0.97694 | -0.44334 | 0 | 0
87 | 0.97736 | -0.43511 | 0.0088184 | 0.0022101
88 | 0.98008 | -0.38177 | 0 | 0
89 | 0.98396 | -0.30624 | 0.010972 | 0.0027498
90 | 0.97743 | -0.43366 | 0.0040228 | 0.0010082
91 | 0.97869 | -0.40889 | 0.017294 | 0.0043342
92 | 0.97677 | -0.44673 | 0.0032241 | 0.00080803
93 | 0.97703 | -0.44156 | 0.039879 | 0.0099947
94 | 0.9765 | -0.45202 | 0.005683 | 0.0014243
95 | 0.97667 | -0.44871 | 0.0052436 | 0.0013142
96 | 0.976 | -0.4618 | 0.01394 | 0.0034936
97 | 0.97733 | -0.43708 | 0.00054075 | 0.00013553
98 | 0.97743 | -0.43512 | 0.0083634 | 0.0020961
99 | 0.97689 | -0.44581 | 0.00032627 | 8.1772e-05
100 | 0.97816 | -0.42086 | 0.00034612 | 8.6746e-05
101 | 0.97681 | -0.4475 | 0 | 0
102 | 0.9789 | -0.40626 | 0.00018212 | 4.5644e-05
103 | 0.9789 | -0.40626 | 0.00099061 | 0.00024827
104 | 0.97657 | -0.4521 | 0 | 0
105 | 0.97647 | -0.45413 | 0.00019474 | 4.8807e-05
106 | 0.97648 | -0.45395 | 0 | 0
107 | 0.97652 | -0.45307 | 0.00045411 | 0.00011381
108 | 0.97648 | -0.45385 | 0.00021485 | 5.3847e-05
109 | 0.97629 | -0.45765 | 0.00038256 | 9.5879e-05
110 | 0.97611 | -0.46116 | 0 | 0
111 | 0.97608 | -0.46179 | 0.0035121 | 0.00088021
112 | 0.97611 | -0.45965 | 0.0095725 | 0.0023991
113 | 0.97607 | -0.46036 | 0.0015808 | 0.00039618
114 | 0.97581 | -0.46559 | 0.010129 | 0.0025386
115 | 0.97564 | -0.46896 | 0.0014542 | 0.00036447
116 | 0.97564 | -0.469 | 0.0016822 | 0.0004216
117 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0024716 | -0.00061944 | 0.0024716 | 0.00061943 | 2.0606e-09 | -3.4538e-09 | 0.0037805 | 0.0037805 | 0.0037805 | 0.97281 | -0.52487 | 0.97281 | -0.52486 | 1.0386
1 | -0.0053356 | -0.0013372 | 0.0053359 | 0.0013373 | 2.7265e-07 | 3.8963e-08 | 0.0081613 | 0.0081613 | 0.0081613 | 0.97281 | -0.52486 | 0.97287 | -0.52378 | 2.2421
2 | -0.0053359 | -0.0013373 | 0.005336 | 0.0013373 | 1.8368e-07 | 2.624e-08 | 0.0081613 | 0.0081613 | 0.0081613 | 0.97287 | -0.52378 | 0.9729 | -0.52306 | 2.2421
3 | -0.020947 | -0.0052526 | 0.020955 | 0.0052576 | 8.1356e-06 | 4.9442e-06 | 0.032038 | 0.032038 | 0.032038 | 0.9729 | -0.52306 | 0.97331 | -0.51492 | 8.8017
4 | 0.015611 | 0.0039153 | -0.015604 | -0.0039112 | 7.0564e-06 | 4.1065e-06 | 0.023877 | 0.023877 | 0.023877 | 0.9729 | -0.52306 | 0.97242 | -0.53255 | 6.5597
5 | -0.023908 | -0.0059976 | 0.02391 | 0.0059985 | 1.5437e-06 | 9.497e-07 | 0.036553 | 0.036553 | 0.036553 | 0.97331 | -0.51492 | 0.97338 | -0.51356 | 10.0421
6 | 0.0029533 | 0.00074004 | -0.0029533 | -0.00074013 | 9.3379e-08 | -9.2043e-08 | 0.0045151 | 0.0045151 | 0.0045151 | 0.97331 | -0.51492 | 0.97328 | -0.51558 | 1.2404
7 | 0.0097106 | 0.0024343 | -0.0097082 | -0.0024331 | 2.4385e-06 | 1.1954e-06 | 0.01486 | 0.01486 | 0.01486 | 0.97242 | -0.53255 | 0.97216 | -0.53782 | 4.0823
8 | -0.025941 | -0.0065075 | 0.025967 | 0.0065236 | 2.5996e-05 | 1.6089e-05 | 0.039659 | 0.039659 | 0.039659 | 0.97338 | -0.51356 | 0.97445 | -0.49256 | 10.8953
9 | 0.0020316 | 0.00050893 | -0.0020316 | -0.00050916 | 8.0954e-08 | -2.2638e-07 | 0.0031057 | 0.0031058 | 0.0031058 | 0.97338 | -0.51356 | 0.97334 | -0.5144 | 0.85324
10 | 0.00087984 | 0.00022049 | -0.00087984 | -0.00022051 | 1.1439e-09 | -2.0218e-08 | 0.0013452 | 0.0013452 | 0.0013452 | 0.97328 | -0.51558 | 0.97328 | -0.51561 | 0.36955
11 | -0.20296 | -0.051715 | 0.20336 | 0.051973 | 0.00040254 | 0.00025703 | 0.30545 | 0.30545 | 0.30545 | 0.98973 | -0.19491 | 0.99188 | -0.1539 | 41.9568
12 | 0.20296 | 0.051715 | -0.20248 | -0.051409 | 0.0004798 | 0.00030637 | 0.30545 | 0.30545 | 0.30545 | 0.98973 | -0.19491 | 0.98718 | -0.24403 | 41.9569
13 | -0.20893 | -0.053368 | 0.20918 | 0.053528 | 0.00025134 | 0.00016051 | 0.3138 | 0.3138 | 0.3138 | 0.99188 | -0.1539 | 0.99318 | -0.12905 | 43.104
14 | 0.19028 | 0.048352 | -0.18971 | -0.047989 | 0.00056812 | 0.00036266 | 0.28706 | 0.28706 | 0.28706 | 0.98718 | -0.24403 | 0.98396 | -0.30624 | 39.431
15 | -0.011804 | -0.0029583 | 0.011806 | 0.0029595 | 2.2877e-06 | 1.2281e-06 | 0.017986 | 0.017986 | 0.017986 | 0.97655 | -0.45095 | 0.97676 | -0.44688 | 4.9412
16 | -0.017668 | -0.0044286 | 0.017671 | 0.0044304 | 2.9853e-06 | 1.773e-06 | 0.026916 | 0.026916 | 0.026916 | 0.97676 | -0.44688 | 0.97694 | -0.44334 | 7.3944
17 | -0.027708 | -0.0069599 | 0.027718 | 0.006966 | 9.7958e-06 | 6.0875e-06 | 0.042317 | 0.042317 | 0.042317 | 0.97445 | -0.49256 | 0.97482 | -0.48516 | 11.6256
18 | 0.0040071 | 0.0010041 | -0.0040068 | -0.0010042 | 3.3138e-07 | -8.235e-08 | 0.0061166 | 0.0061167 | 0.0061167 | 0.97482 | -0.48516 | 0.97474 | -0.48689 | 1.6804
19 | 0.0030012 | 0.00075203 | -0.0030011 | -0.00075215 | 1.2069e-07 | -1.1393e-07 | 0.0045812 | 0.0045812 | 0.0045812 | 0.97482 | -0.48516 | 0.97478 | -0.486 | 1.2586
20 | -0.034726 | -0.0087221 | 0.034745 | 0.0087336 | 1.8275e-05 | 1.148e-05 | 0.053015 | 0.053015 | 0.053015 | 0.97482 | -0.48516 | 0.97538 | -0.47414 | 14.5645
21 | -0.0041073 | -0.0010294 | 0.0041077 | 0.0010293 | 3.915e-07 | -1.0282e-07 | 0.0061686 | 0.0061685 | 0.0061686 | 0.99078 | -0.17575 | 0.99088 | -0.17375 | 1.6947
22 | -0.010796 | -0.0027054 | 0.010796 | 0.0027059 | 8.5938e-07 | 4.3768e-07 | 0.016212 | 0.016212 | 0.016212 | 0.99088 | -0.17375 | 0.99097 | -0.17208 | 4.4538
23 | -0.013682 | -0.0034291 | 0.013686 | 0.0034313 | 4.0708e-06 | 2.2738e-06 | 0.020545 | 0.020545 | 0.020545 | 0.99097 | -0.17208 | 0.99129 | -0.16584 | 5.6441
24 | -0.015766 | -0.0039526 | 0.015768 | 0.0039535 | 1.6826e-06 | 9.7356e-07 | 0.023666 | 0.023666 | 0.023666 | 0.99129 | -0.16584 | 0.9914 | -0.1636 | 6.5018
25 | -0.038572 | -0.0096928 | 0.038574 | 0.0096944 | 2.4813e-06 | 1.5642e-06 | 0.058853 | 0.058853 | 0.058853 | 0.97538 | -0.47414 | 0.97545 | -0.47279 | 16.1685
26 | -0.022964 | -0.0057571 | 0.02297 | 0.0057606 | 5.6667e-06 | 3.4626e-06 | 0.034468 | 0.034468 | 0.034468 | 0.9914 | -0.1636 | 0.99167 | -0.15842 | 9.4691
27 | -0.024806 | -0.0062209 | 0.024812 | 0.0062242 | 5.304e-06 | 3.2629e-06 | 0.037224 | 0.037224 | 0.037224 | 0.99167 | -0.15842 | 0.9919 | -0.15393 | 10.2263
28 | -0.040748 | -0.010239 | 0.040769 | 0.010253 | 2.1513e-05 | 1.3583e-05 | 0.062169 | 0.062169 | 0.062169 | 0.97545 | -0.47279 | 0.97602 | -0.46173 | 17.0793
29 | 0.0179 | 0.0044885 | -0.017891 | -0.0044833 | 8.7064e-06 | 5.1827e-06 | 0.027291 | 0.027291 | 0.027291 | 0.97602 | -0.46173 | 0.9755 | -0.47194 | 7.4974
30 | -0.058669 | -0.014741 | 0.058734 | 0.014783 | 6.5323e-05 | 4.1534e-05 | 0.089459 | 0.089459 | 0.089459 | 0.97602 | -0.46173 | 0.9772 | -0.43844 | 24.5767
31 | 0.0086537 | 0.002168 | -0.0086527 | -0.0021676 | 9.5683e-07 | 4.2958e-07 | 0.0132 | 0.0132 | 0.0132 | 0.9755 | -0.47194 | 0.97538 | -0.47427 | 3.6264
32 | 0.0092374 | 0.0023153 | -0.0092361 | -0.0023147 | 1.3326e-06 | 6.2947e-07 | 0.014091 | 0.014091 | 0.014091 | 0.9755 | -0.47194 | 0.97534 | -0.47497 | 3.8711
33 | -0.061874 | -0.015569 | 0.061929 | 0.015604 | 5.4925e-05 | 3.4945e-05 | 0.094239 | 0.094239 | 0.094239 | 0.9772 | -0.43844 | 0.97815 | -0.41988 | 25.89
34 | 0.0061284 | 0.0015349 | -0.0061275 | -0.0015347 | 9.6585e-07 | 2.5042e-07 | 0.009349 | 0.0093492 | 0.0093492 | 0.97538 | -0.47427 | 0.97521 | -0.47758 | 2.5685
35 | 0.0055418 | 0.0013888 | -0.0055412 | -0.0013887 | 6.5189e-07 | 1.1374e-07 | 0.0084547 | 0.0084548 | 0.0084548 | 0.97534 | -0.47497 | 0.97522 | -0.47744 | 2.3228
36 | -0.064801 | -0.016324 | 0.064826 | 0.01634 | 2.4835e-05 | 1.5809e-05 | 0.09861 | 0.09861 | 0.09861 | 0.97815 | -0.41988 | 0.97856 | -0.41187 | 27.0906
37 | -0.001774 | -0.00044461 | 0.0017741 | 0.00044424 | 9.4179e-08 | -3.6717e-07 | 0.0027073 | 0.0027071 | 0.0027073 | 0.97506 | -0.48049 | 0.97512 | -0.47938 | 0.74376
38 | -0.0017741 | -0.00044424 | 0.0017742 | 0.00044396 | 7.2371e-08 | -2.8222e-07 | 0.0027071 | 0.002707 | 0.0027071 | 0.97512 | -0.47938 | 0.97516 | -0.47852 | 0.74372
39 | 0.0017743 | 0.00044365 | -0.0017742 | -0.00044396 | 7.9436e-08 | -3.0984e-07 | 0.0027069 | 0.002707 | 0.002707 | 0.97521 | -0.47758 | 0.97516 | -0.47852 | 0.74368
40 | 0.0055412 | 0.0013887 | -0.0055407 | -0.0013886 | 4.9851e-07 | 8.704e-08 | 0.0084548 | 0.0084549 | 0.0084549 | 0.97522 | -0.47744 | 0.97512 | -0.47933 | 2.3228
41 | -0.067398 | -0.016985 | 0.067432 | 0.017006 | 3.3354e-05 | 2.124e-05 | 0.10252 | 0.10252 | 0.10252 | 0.97856 | -0.41187 | 0.97909 | -0.40153 | 28.165
42 | 0.1665 | 0.042429 | -0.16615 | -0.042204 | 0.00035254 | 0.00022485 | 0.25003 | 0.25003 | 0.25003 | 0.9919 | -0.15393 | 0.98961 | -0.19791 | 34.3444
43 | -0.19131 | -0.048653 | 0.19183 | 0.048986 | 0.00052197 | 0.00033319 | 0.28725 | 0.28725 | 0.28725 | 0.9919 | -0.15393 | 0.99486 | -0.097472 | 39.4574
44 | 0.095665 | 0.0244 | -0.095478 | -0.024281 | 0.00018708 | 0.00011942 | 0.144 | 0.144 | 0.144 | 0.98961 | -0.19791 | 0.9875 | -0.2385 | 39.5599
45 | 0.070482 | 0.017804 | -0.07043 | -0.017771 | 5.1972e-05 | 3.3104e-05 | 0.10603 | 0.10603 | 0.10603 | 0.98961 | -0.19791 | 0.98881 | -0.21331 | 29.1289
46 | -0.19824 | -0.050592 | 0.1983 | 0.050632 | 6.3105e-05 | 4.0288e-05 | 0.29683 | 0.29683 | 0.29683 | 0.99486 | -0.097472 | 0.9952 | -0.090885 | 40.774
47 | 0.093992 | 0.023908 | -0.09388 | -0.023836 | 0.0001124 | 7.1745e-05 | 0.14176 | 0.14176 | 0.14176 | 0.9875 | -0.2385 | 0.98621 | -0.26335 | 38.9446
48 | 0.062667 | 0.015825 | -0.062629 | -0.015801 | 3.7864e-05 | 2.4088e-05 | 0.094347 | 0.094347 | 0.094347 | 0.98881 | -0.21331 | 0.98816 | -0.22593 | 25.9195
49 | -0.2054 | -0.052411 | 0.20614 | 0.052884 | 0.00074036 | 0.00047274 | 0.30744 | 0.30744 | 0.30744 | 0.9952 | -0.090885 | 0.99912 | -0.016559 | 42.2313
50 | -0.21408 | -0.054872 | 0.21425 | 0.054982 | 0.000172 | 0.00010985 | 0.31926 | 0.31926 | 0.31926 | 0.99912 | -0.016559 | 1 | 0 | 43.8546
51 | 0.22343 | 0.057632 | -0.22272 | -0.057179 | 0.00070976 | 0.00045335 | 0.33304 | 0.33304 | 0.33304 | 1 | 0 | 0.99653 | -0.065427 | 45.7478
52 | 0.21607 | 0.055512 | -0.2154 | -0.055087 | 0.00066537 | 0.00042495 | 0.32312 | 0.32312 | 0.32312 | 0.99653 | -0.065427 | 0.99318 | -0.12905 | 44.3841
53 | 0.09025 | 0.022927 | -0.090181 | -0.022883 | 6.8484e-05 | 4.3704e-05 | 0.13628 | 0.13628 | 0.13628 | 0.98621 | -0.26335 | 0.98539 | -0.27912 | 37.44
54 | 0.059461 | 0.015007 | -0.059398 | -0.014967 | 6.2647e-05 | 3.9828e-05 | 0.089576 | 0.089577 | 0.089577 | 0.98816 | -0.22593 | 0.98702 | -0.24795 | 24.6089
55 | 0.051385 | 0.012959 | -0.051373 | -0.012951 | 1.2118e-05 | 7.6869e-06 | 0.077496 | 0.077496 | 0.077496 | 0.98702 | -0.24795 | 0.98677 | -0.25288 | 21.2901
56 | 0.048303 | 0.012182 | -0.048252 | -0.01215 | 5.0543e-05 | 3.2024e-05 | 0.072866 | 0.072866 | 0.072866 | 0.98677 | -0.25288 | 0.98564 | -0.27476 | 20.0181
57 | 0.043792 | 0.011032 | -0.043787 | -0.011029 | 4.9656e-06 | 3.1394e-06 | 0.066133 | 0.066133 | 0.066133 | 0.98564 | -0.27476 | 0.98552 | -0.27714 | 18.1685
58 | 0.003087 | 0.00077348 | -0.0030868 | -0.00077363 | 1.6818e-07 | -1.5526e-07 | 0.0046615 | 0.0046616 | 0.0046616 | 0.98539 | -0.27912 | 0.98533 | -0.28027 | 1.2807
59 | 0.087094 | 0.022109 | -0.087082 | -0.022102 | 1.2132e-05 | 7.741e-06 | 0.13162 | 0.13162 | 0.13162 | 0.98539 | -0.27912 | 0.98524 | -0.28202 | 36.1594
60 | 0.043787 | 0.011029 | -0.043764 | -0.011014 | 2.3562e-05 | 1.4897e-05 | 0.066133 | 0.066133 | 0.066133 | 0.98552 | -0.27714 | 0.98494 | -0.28839 | 18.1685
61 | 0.017428 | 0.0043727 | -0.017414 | -0.0043647 | 1.3509e-05 | 7.9852e-06 | 0.026331 | 0.026331 | 0.026331 | 0.98494 | -0.28839 | 0.98411 | -0.30467 | 7.2338
62 | 0.026336 | 0.0066413 | -0.026316 | -0.0066287 | 2.0378e-05 | 1.2606e-05 | 0.039803 | 0.039803 | 0.039803 | 0.98494 | -0.28839 | 0.98411 | -0.30457 | 10.9348
63 | -0.0092208 | -0.0023109 | 0.0092229 | 0.002312 | 2.1407e-06 | 1.009e-06 | 0.014058 | 0.014058 | 0.014058 | 0.976 | -0.46185 | 0.97625 | -0.45698 | 3.8621
64 | -0.017755 | -0.0044502 | 0.017766 | 0.0044571 | 1.1481e-05 | 6.8245e-06 | 0.027062 | 0.027062 | 0.027062 | 0.97625 | -0.45698 | 0.97694 | -0.44341 | 7.4347
65 | -0.017766 | -0.0044571 | 0.017778 | 0.0044641 | 1.1879e-05 | 7.0607e-06 | 0.027062 | 0.027062 | 0.027062 | 0.97694 | -0.44341 | 0.97765 | -0.4294 | 7.4347
66 | -0.0020912 | -0.00052409 | 0.0020913 | 0.00052381 | 1.0121e-07 | -2.7817e-07 | 0.0031621 | 0.003162 | 0.0031621 | 0.98406 | -0.30559 | 0.98411 | -0.30457 | 0.8687
67 | 0.024225 | 0.0061049 | -0.024199 | -0.0060891 | 2.5631e-05 | 1.5758e-05 | 0.036641 | 0.036641 | 0.036641 | 0.98411 | -0.30457 | 0.98297 | -0.32671 | 10.0662
68 | -0.018361 | -0.0046101 | 0.018366 | 0.0046131 | 4.8729e-06 | 2.91e-06 | 0.027949 | 0.027949 | 0.027949 | 0.97765 | -0.4294 | 0.97793 | -0.42384 | 7.6782
69 | 0.017717 | 0.0044644 | -0.017689 | -0.0044484 | 2.7103e-05 | 1.6075e-05 | 0.026828 | 0.026828 | 0.026828 | 0.98297 | -0.32671 | 0.98133 | -0.35874 | 7.3704
70 | -0.021281 | -0.0053437 | 0.021286 | 0.0053467 | 4.9639e-06 | 3.0185e-06 | 0.032385 | 0.032385 | 0.032385 | 0.97793 | -0.42384 | 0.97818 | -0.41895 | 8.8969
71 | 0.011845 | 0.0029689 | -0.011844 | -0.0029683 | 1.1254e-06 | 6.0139e-07 | 0.01791 | 0.01791 | 0.01791 | 0.98411 | -0.30467 | 0.984 | -0.30666 | 4.9203
72 | 0.0021212 | 0.00053119 | -0.0021211 | -0.00053159 | 1.5335e-07 | -4.0123e-07 | 0.0032163 | 0.0032165 | 0.0032165 | 0.98133 | -0.35874 | 0.98125 | -0.36026 | 0.88366
73 | 0.015568 | 0.0039172 | -0.015549 | -0.003906 | 1.9194e-05 | 1.1126e-05 | 0.023612 | 0.023612 | 0.023612 | 0.98133 | -0.35874 | 0.98001 | -0.38458 | 6.4869
74 | -0.026518 | -0.0066568 | 0.026535 | 0.0066675 | 1.7282e-05 | 1.0705e-05 | 0.040343 | 0.040343 | 0.040343 | 0.97818 | -0.41895 | 0.97888 | -0.40529 | 11.0834
75 | 0.0052322 | 0.0013101 | -0.0052315 | -0.00131 | 7.4567e-07 | 8.3235e-08 | 0.0079588 | 0.007959 | 0.007959 | 0.97818 | -0.41895 | 0.97803 | -0.42194 | 2.1865
76 | -0.069206 | -0.017451 | 0.069304 | 0.017513 | 9.7978e-05 | 6.2408e-05 | 0.10522 | 0.10522 | 0.10522 | 0.97909 | -0.40153 | 0.9806 | -0.37199 | 28.906
77 | -0.07214 | -0.018224 | 0.072145 | 0.018227 | 4.8449e-06 | 3.0871e-06 | 0.10952 | 0.10952 | 0.10952 | 0.9806 | -0.37199 | 0.98067 | -0.37059 | 30.0882
78 | -0.075612 | -0.019096 | 0.075739 | 0.019177 | 0.00012726 | 8.1119e-05 | 0.11478 | 0.11478 | 0.11478 | 0.98067 | -0.37059 | 0.98248 | -0.33554 | 31.5333
79 | -0.078705 | -0.01992 | 0.07872 | 0.01993 | 1.5053e-05 | 9.5979e-06 | 0.11927 | 0.11927 | 0.11927 | 0.98248 | -0.33554 | 0.98268 | -0.33155 | 32.7675
80 | -0.081774 | -0.020695 | 0.081913 | 0.020784 | 0.00013889 | 8.8581e-05 | 0.1239 | 0.1239 | 0.1239 | 0.98268 | -0.33155 | 0.9845 | -0.29623 | 34.0378
81 | -0.083947 | -0.021294 | 0.084005 | 0.02133 | 5.7416e-05 | 3.6625e-05 | 0.12697 | 0.12697 | 0.12697 | 0.9845 | -0.29623 | 0.98524 | -0.28202 | 34.8825
82 | 0.015549 | 0.003906 | -0.015533 | -0.0038967 | 1.6072e-05 | 9.3188e-06 | 0.023612 | 0.023613 | 0.023613 | 0.98001 | -0.38458 | 0.9789 | -0.40626 | 6.487
83 | 0.0021116 | 0.00052813 | -0.0021113 | -0.00052913 | 3.8658e-07 | -1.0058e-06 | 0.0032124 | 0.0032128 | 0.0032128 | 0.97803 | -0.42194 | 0.97784 | -0.42579 | 0.88264
84 | -0.037445 | -0.0094016 | 0.037492 | 0.0094315 | 4.749e-05 | 2.9902e-05 | 0.056927 | 0.056926 | 0.056927 | 0.97888 | -0.40529 | 0.98023 | -0.37874 | 15.6392
85 | -0.037492 | -0.0094315 | 0.037536 | 0.0094593 | 4.4059e-05 | 2.774e-05 | 0.056926 | 0.056926 | 0.056926 | 0.98023 | -0.37874 | 0.98149 | -0.35418 | 15.6391
86 | 0.1408 | 0.035518 | -0.14061 | -0.035399 | 0.00018574 | 0.00011874 | 0.21354 | 0.21354 | 0.21354 | 0.98149 | -0.35418 | 0.98008 | -0.38177 | 58.6646
87 | -0.17833 | -0.044977 | 0.17874 | 0.045239 | 0.00041024 | 0.0002618 | 0.27047 | 0.27047 | 0.27047 | 0.98149 | -0.35418 | 0.98396 | -0.30624 | 37.1518
88 | -0.017671 | -0.0044304 | 0.017678 | 0.0044345 | 6.9284e-06 | 4.1147e-06 | 0.026916 | 0.026916 | 0.026916 | 0.97694 | -0.44334 | 0.97736 | -0.43511 | 7.3944
89 | 0.022871 | 0.0057403 | -0.022858 | -0.0057326 | 1.2668e-05 | 7.7584e-06 | 0.034824 | 0.034824 | 0.034824 | 0.97736 | -0.43511 | 0.97677 | -0.44673 | 9.567
90 | -0.049367 | -0.012385 | 0.049429 | 0.012424 | 6.1808e-05 | 3.9191e-05 | 0.075165 | 0.075165 | 0.075165 | 0.97736 | -0.43511 | 0.97869 | -0.40889 | 20.6497
91 | 0.073801 | 0.018586 | -0.073618 | -0.01847 | 0.00018263 | 0.00011639 | 0.11208 | 0.11208 | 0.11208 | 0.98008 | -0.38177 | 0.97743 | -0.43366 | 30.7915
92 | 0.066809 | 0.016813 | -0.066722 | -0.016758 | 8.6451e-05 | 5.5047e-05 | 0.10146 | 0.10146 | 0.10146 | 0.98008 | -0.38177 | 0.97869 | -0.40889 | 27.8732
93 | 0.069595 | 0.017461 | -0.069569 | -0.017445 | 2.6185e-05 | 1.668e-05 | 0.10596 | 0.10596 | 0.10596 | 0.97743 | -0.43366 | 0.97703 | -0.44156 | 29.109
94 | 0.019634 | 0.0049246 | -0.019629 | -0.0049216 | 4.9462e-06 | 2.9811e-06 | 0.029912 | 0.029912 | 0.029912 | 0.97677 | -0.44673 | 0.9765 | -0.45202 | 8.2176
95 | 0.02969 | 0.00745 | -0.029679 | -0.0074437 | 1.0125e-05 | 6.3145e-06 | 0.045221 | 0.045221 | 0.045221 | 0.97703 | -0.44156 | 0.97667 | -0.44871 | 12.4232
96 | 0.013946 | 0.0034973 | -0.01394 | -0.0034936 | 6.4965e-06 | 3.6782e-06 | 0.021252 | 0.021252 | 0.021252 | 0.9765 | -0.45202 | 0.976 | -0.4618 | 5.8386
97 | 0.024436 | 0.0061295 | -0.024423 | -0.0061216 | 1.2739e-05 | 7.8465e-06 | 0.037232 | 0.037232 | 0.037232 | 0.97667 | -0.44871 | 0.97611 | -0.45965 | 10.2285
98 | -0.0056307 | -0.0014088 | 0.0056312 | 0.0014089 | 5.2514e-07 | 9.7242e-08 | 0.0085721 | 0.008572 | 0.0085721 | 0.97733 | -0.43708 | 0.97743 | -0.43512 | 2.355
99 | 0.00509 | 0.0012733 | -0.0050878 | -0.0012731 | 2.1139e-06 | 1.7701e-07 | 0.0077487 | 0.0077492 | 0.0077492 | 0.97733 | -0.43708 | 0.97689 | -0.44581 | 2.1289
100 | -0.013995 | -0.003505 | 0.014004 | 0.0035104 | 9.5084e-06 | 5.3846e-06 | 0.021304 | 0.021304 | 0.021304 | 0.97743 | -0.43512 | 0.97816 | -0.42086 | 5.8528
101 | 0.0047616 | 0.0011914 | -0.0047612 | -0.0011914 | 3.8297e-07 | 2.0173e-09 | 0.0072522 | 0.0072523 | 0.0072523 | 0.97689 | -0.44581 | 0.97681 | -0.4475 | 1.9924
102 | -0.01435 | -0.0035971 | 0.01436 | 0.0036028 | 9.9879e-06 | 5.6902e-06 | 0.02183 | 0.02183 | 0.02183 | 0.97816 | -0.42086 | 0.9789 | -0.40626 | 5.9974
103 | 0.0047612 | 0.0011914 | -0.0047601 | -0.0011914 | 1.0415e-06 | 5.7315e-09 | 0.0072523 | 0.0072525 | 0.0072525 | 0.97681 | -0.4475 | 0.97657 | -0.4521 | 1.9924
104 | -0.014542 | -0.0036485 | 0.014542 | 0.0036485 | 5.3175e-10 | 2.836e-10 | 0.022107 | 0.022107 | 0.022107 | 0.9789 | -0.40626 | 0.9789 | -0.40626 | 6.0733
105 | 0.0047601 | 0.0011914 | -0.0047599 | -0.0011914 | 2.1958e-07 | 1.2542e-09 | 0.0072525 | 0.0072526 | 0.0072526 | 0.97657 | -0.4521 | 0.97652 | -0.45307 | 1.9925
106 | -0.00019474 | -4.8807e-05 | 0.00019475 | 4.8202e-05 | 1.5986e-09 | -6.0491e-07 | 0.00029676 | 0.00029655 | 0.00029676 | 0.97647 | -0.45413 | 0.97648 | -0.45395 | 0.081529
107 | -0.0040908 | -0.0010237 | 0.0040908 | 0.0010237 | 1.9061e-08 | -4.1663e-09 | 0.0062332 | 0.0062332 | 0.0062332 | 0.97648 | -0.45395 | 0.97648 | -0.45385 | 1.7124
108 | 0.003896 | 0.00097552 | -0.0038954 | -0.00097573 | 6.8545e-07 | -2.0993e-07 | 0.0059367 | 0.0059369 | 0.0059369 | 0.97648 | -0.45395 | 0.97629 | -0.45765 | 1.631
109 | 0.0043058 | 0.0010775 | -0.0043057 | -0.0010776 | 1.6141e-07 | -2.1801e-08 | 0.0065606 | 0.0065606 | 0.0065606 | 0.97652 | -0.45307 | 0.97648 | -0.45385 | 1.8024
110 | 0.0035128 | 0.00087985 | -0.0035122 | -0.00088016 | 5.8835e-07 | -3.0775e-07 | 0.0053538 | 0.0053541 | 0.0053541 | 0.97629 | -0.45765 | 0.97611 | -0.46116 | 1.4709
111 | 0.0035122 | 0.00088016 | -0.0035121 | -0.00088021 | 1.0421e-07 | -5.4477e-08 | 0.0053541 | 0.0053541 | 0.0053541 | 0.97611 | -0.46116 | 0.97608 | -0.46179 | 1.4709
112 | 0.014851 | 0.0037225 | -0.01485 | -0.0037222 | 5.0015e-07 | 2.8757e-07 | 0.022639 | 0.022639 | 0.022639 | 0.97611 | -0.45965 | 0.97607 | -0.46036 | 6.2195
113 | 0.013269 | 0.0033261 | -0.013266 | -0.0033242 | 3.3044e-06 | 1.8458e-06 | 0.020229 | 0.020229 | 0.020229 | 0.97607 | -0.46036 | 0.97581 | -0.46559 | 5.5575
114 | 0.0031369 | 0.00078564 | -0.0031364 | -0.00078605 | 5.0273e-07 | -4.1003e-07 | 0.0047833 | 0.0047836 | 0.0047836 | 0.97581 | -0.46559 | 0.97564 | -0.46896 | 1.3142
115 | 0.0016822 | 0.00042158 | -0.0016822 | -0.0004216 | 3.6218e-09 | -1.6005e-08 | 0.0025656 | 0.0025656 | 0.0025656 | 0.97564 | -0.46896 | 0.97564 | -0.469 | 0.70485

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46237 | 0.11839

## res_load
| p_mw | q_mvar
0 | 0.0024716 | 0.00061944
1 | 0.002864 | 0.00071779
2 | 0.005893 | 0.0014769
3 | 0.0020734 | 0.00051965
4 | 0.0097082 | 0.0024331
5 | 0.0055673 | 0.0013953
6 | 0.012199 | 0.0030575
7 | 0.011804 | 0.0029583
8 | 0.0058618 | 0.0014691
9 | 0.00087984 | 0.00022051
10 | 0.0017408 | 0.0004363
11 | 0.0020316 | 0.00050916
12 | 0.0041073 | 0.0010294
13 | 0.0066879 | 0.0016761
14 | 0.0028856 | 0.00072319
15 | 0.0020798 | 0.00052124
16 | 0.0040068 | 0.0010042
17 | 0.0030011 | 0.00075215
18 | 0.0038273 | 0.00095921
19 | 0.0071964 | 0.0018036
20 | 0.0018368 | 0.00046035
21 | 0.0021733 | 0.00054469
22 | 0.0031393 | 0.00078678
23 | 0.0025243 | 0.00063265
24 | 0.0036943 | 0.00092587
25 | 0.0028728 | 0.00072
26 | 0.001774 | 0.00044461
27 | 0.0043532 | 0.001091
28 | 0.0025721 | 0.00064462
29 | 0.0055407 | 0.0013886
30 | 0.0064082 | 0.001606
31 | 0.0014864 | 0.00037252
32 | 0.007763 | 0.0019456
33 | 0.007096 | 0.0017784
34 | 0.0079349 | 0.0019887
35 | 0.023041 | 0.0057747
36 | 0.006649 | 0.0016664
37 | 0.0036299 | 0.00090975
38 | 0.003168 | 0.00079398
39 | 0.0080134 | 0.0020083
40 | 0.0030704 | 0.00076951
41 | 0.0044595 | 0.0011177
42 | 0.0092208 | 0.0023109
43 | 0.0085319 | 0.0021383
44 | 0.0020912 | 0.00052409
45 | 0.0005826 | 0.00014601
46 | 0.0064825 | 0.0016247
47 | 0.0029153 | 0.00073065
48 | 0.0055693 | 0.0013958
49 | 0.0062199 | 0.0015589
50 | 0.0017746 | 0.00044476
51 | 0.0028359 | 0.00071073
52 | 0.0034668 | 0.00086887
53 | 0.0029662 | 0.00074341
54 | 0.0030536 | 0.0007653
55 | 0.0020345 | 0.00050989
56 | 0.0030773 | 0.00077125
57 | 0.0030868 | 0.00077363
58 | 0.011844 | 0.0029683
59 | 0.0021211 | 0.00053159
60 | 0.0031198 | 0.0007819
61 | 0.0021113 | 0.00052913
62 | 0.010909 | 0.0027341
63 | 0.0088184 | 0.0022101
64 | 0.010972 | 0.0027498
65 | 0.0040228 | 0.0010082
66 | 0.017294 | 0.0043342
67 | 0.0032241 | 0.00080803
68 | 0.039879 | 0.0099947
69 | 0.005683 | 0.0014243
70 | 0.0052436 | 0.0013142
71 | 0.01394 | 0.0034936
72 | 0.00054075 | 0.00013553
73 | 0.0083634 | 0.0020961
74 | 0.00032627 | 8.1772e-05
75 | 0.00034612 | 8.6746e-05
76 | 0.00018212 | 4.5644e-05
77 | 0.00099061 | 0.00024827
78 | 0.00019474 | 4.8807e-05
79 | 0.00045411 | 0.00011381
80 | 0.00021485 | 5.3847e-05
81 | 0.00038256 | 9.5879e-05
82 | 0.0035121 | 0.00088021
83 | 0.0095725 | 0.0023991
84 | 0.0015808 | 0.00039618
85 | 0.010129 | 0.0025386
86 | 0.0014542 | 0.00036447
87 | 0.0016822 | 0.0004216

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1