## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_158-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_158-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_158-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_158-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_158-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_158-1_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_158-1_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_158-1_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_158-1_0_4_node_115 | 0.4 | n |  | TRUE
9 | bus_LV_158-1_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_158-1_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_158-1_0_4_node_122 | 0.4 | n |  | TRUE
12 | bus_LV_158-1_0_4_node_125 | 0.4 | n |  | TRUE
13 | bus_LV_158-1_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_158-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_158-1_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_158-1_0_4_node_116 | 0.4 | n |  | TRUE
17 | bus_LV_158-1_0_4_node_123 | 0.4 | n |  | TRUE
18 | bus_LV_158-1_0_4_node_118 | 0.4 | n |  | TRUE
19 | bus_LV_158-1_0_4_node_128 | 0.4 | n |  | TRUE
20 | bus_LV_158-1_0_4_node_119 | 0.4 | n |  | TRUE
21 | bus_LV_158-1_0_4_node_127 | 0.4 | n |  | TRUE
22 | bus_LV_158-1_0_4_node_126 | 0.4 | n |  | TRUE
23 | bus_LV_158-1_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_158-1_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_158-1_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_158-1_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_158-1_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_158-1_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_158-1_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_158-1_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_158-1_0_4_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_158-1_0_4_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_158-1_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_158-1_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_158-1_0_4_node_130 | 0.4 | n |  | TRUE
36 | bus_LV_158-1_0_4_node_117 | 0.4 | n |  | TRUE
37 | bus_LV_158-1_0_4_node_138 | 0.4 | n |  | TRUE
38 | bus_LV_158-1_0_4_node_129 | 0.4 | n |  | TRUE
39 | bus_LV_158-1_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_158-1_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_158-1_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_158-1_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_158-1_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_158-1_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_158-1_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_158-1_0_4_node_120 | 0.4 | n |  | TRUE
47 | bus_LV_158-1_0_4_node_131 | 0.4 | n |  | TRUE
48 | bus_LV_158-1_0_4_node_121 | 0.4 | n |  | TRUE
49 | bus_LV_158-1_0_4_node_136 | 0.4 | n |  | TRUE
50 | bus_LV_158-1_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_158-1_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_158-1_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_158-1_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_158-1_0_4_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_158-1_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_158-1_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_158-1_0_4_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_158-1_0_4_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_158-1_0_4_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_158-1_0_4_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_158-1_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_158-1_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_158-1_0_4_node_91 | 0.4 | n |  | TRUE
64 | bus_LV_158-1_0_4_node_86 | 0.4 | n |  | TRUE
65 | bus_LV_158-1_0_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_158-1_0_4_node_92 | 0.4 | n |  | TRUE
67 | bus_LV_158-1_0_4_node_93 | 0.4 | n |  | TRUE
68 | bus_LV_158-1_0_4_node_84 | 0.4 | n |  | TRUE
69 | bus_LV_158-1_0_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_158-1_0_4_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_158-1_0_4_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_158-1_0_4_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_158-1_0_4_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_158-1_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_158-1_0_4_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_158-1_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_158-1_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_158-1_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_158-1_0_4_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_158-1_0_4_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_158-1_0_4_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_158-1_0_4_node_58 | 0.4 | n |  | TRUE
83 | bus_LV_158-1_0_4_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_158-1_0_4_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_158-1_0_4_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_158-1_0_4_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_158-1_0_4_node_64 | 0.4 | n |  | TRUE
88 | bus_LV_158-1_0_4_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_158-1_0_4_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_158-1_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_158-1_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_158-1_0_4_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_158-1_0_4_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_158-1_0_4_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_158-1_0_4_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_158-1_0_4_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_158-1_0_4_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_158-1_0_4_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_158-1_0_4_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_158-1_0_4_node_98 | 0.4 | n |  | TRUE
101 | bus_LV_158-1_0_4_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_158-1_0_4_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_158-1_0_4_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_158-1_0_4_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_158-1_0_4_node_80 | 0.4 | n |  | TRUE
106 | bus_LV_158-1_0_4_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_158-1_0_4_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_158-1_0_4_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_158-1_0_4_node_85 | 0.4 | n |  | TRUE
110 | bus_LV_158-1_0_4_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_158-1_0_4_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_158-1_0_4_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_158-1_0_4_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_158-1_0_4_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_158-1_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_158-1_0_4_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_158-1_0_4_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_158-1_0_4_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_158-1_0_4_node_146 | 0.4 | n |  | TRUE
120 | bus_LV_158-1_0_4_node_147 | 0.4 | n |  | TRUE
121 | bus_LV_158-1_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_158-1_0_4_node_104 | 0.4 | n |  | TRUE
123 | bus_LV_158-1_0_4_node_105 | 0.4 | n |  | TRUE
124 | bus_LV_158-1_0_4_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_158-1_0_4_node_107 | 0.4 | n |  | TRUE
126 | bus_LV_158-1_0_4_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_158-1_0_4_node_109 | 0.4 | n |  | TRUE
128 | bus_LV_158-1_0_4_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_158-1_0_4_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_158-1_0_4_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_158-1_0_4_node_113 | 0.4 | n |  | TRUE
132 | bus_LV_158-1_0_4_node_114 | 0.4 | n |  | TRUE
133 | bus_LV_158-1_0_4_node_152 | 0.4 | n |  | TRUE
134 | bus_LV_158-1_0_4_node_132 | 0.4 | n |  | TRUE
135 | bus_LV_158-1_0_4_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_158-1_0_4_node_124 | 0.4 | n |  | TRUE
137 | bus_LV_158-1_0_4_node_139 | 0.4 | n |  | TRUE
138 | bus_LV_158-1_0_4_node_134 | 0.4 | n |  | TRUE
139 | bus_LV_158-1_0_4_node_135 | 0.4 | n |  | TRUE
140 | bus_LV_158-1_0_4_node_143 | 0.4 | n |  | TRUE
141 | bus_LV_158-1_0_4_node_140 | 0.4 | n |  | TRUE
142 | bus_LV_158-1_0_4_node_144 | 0.4 | n |  | TRUE
143 | bus_LV_158-1_0_4_node_141 | 0.4 | n |  | TRUE
144 | bus_LV_158-1_0_4_node_142 | 0.4 | n |  | TRUE
145 | bus_LV_158-1_0_4_node_145 | 0.4 | n |  | TRUE
146 | bus_LV_158-1_0_4_node_148 | 0.4 | n |  | TRUE
147 | bus_LV_158-1_0_4_node_149 | 0.4 | n |  | TRUE
148 | bus_LV_158-1_0_4_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_158-1_0_4_node_151 | 0.4 | n |  | TRUE
150 | bus_MV_361_1_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_158-1_0_4_load_0 | 0 | 0.001123 | 0.00028145 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_158-1_0_4_load_1 | 1 | 0.0040789 | 0.0010223 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_158-1_0_4_load_9 | 6 | 0.011137 | 0.0027913 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_158-1_0_4_load_11 | 7 | 0.0038139 | 0.00095587 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_158-1_0_4_load_115 | 8 | 0.0047591 | 0.0011927 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_158-1_0_4_load_122 | 11 | 0.00030604 | 7.6702e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_158-1_0_4_load_125 | 12 | 0.00016806 | 4.2121e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_158-1_0_4_load_8 | 13 | 0.00096277 | 0.00024129 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_158-1_0_4_load_10 | 14 | 0.0098242 | 0.0024622 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_158-1_0_4_load_123 | 17 | 8.866e-05 | 2.222e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_158-1_0_4_load_127 | 21 | 0.0009618 | 0.00024105 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_158-1_0_4_load_126 | 22 | 3.971e-05 | 9.9524e-06 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_158-1_0_4_load_26 | 23 | 0.00055408 | 0.00013887 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_158-1_0_4_load_31 | 25 | 0.00022415 | 5.6177e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_158-1_0_4_load_27 | 26 | 0.0015866 | 0.00039763 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_158-1_0_4_load_19 | 30 | 0.0034617 | 0.00086759 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_158-1_0_4_load_13 | 31 | 0.010584 | 0.0026526 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_158-1_0_4_load_16 | 33 | 0.00092654 | 0.00023221 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_158-1_0_4_load_130 | 35 | 0.0015867 | 0.00039767 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_158-1_0_4_load_138 | 37 | 0.00035774 | 8.9658e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_158-1_0_4_load_129 | 38 | 0.00065478 | 0.0001641 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_158-1_0_4_load_20 | 40 | 0.0013213 | 0.00033115 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_158-1_0_4_load_22 | 41 | 0.0020872 | 0.00052309 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_158-1_0_4_load_25 | 42 | 0.0010567 | 0.00026484 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_158-1_0_4_load_28 | 43 | 0.0011031 | 0.00027646 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_158-1_0_4_load_29 | 44 | 0.0011486 | 0.00028786 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_158-1_0_4_load_32 | 45 | 0.00064177 | 0.00016084 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_158-1_0_4_load_131 | 47 | 0.00075179 | 0.00018842 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_158-1_0_4_load_136 | 49 | 0.0011347 | 0.00028439 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_158-1_0_4_load_34 | 52 | 0.014842 | 0.0037196 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_158-1_0_4_load_36 | 53 | 0.027581 | 0.0069124 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_158-1_0_4_load_90 | 54 | 0.0015708 | 0.00039367 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_158-1_0_4_load_37 | 56 | 0.0075049 | 0.0018809 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_158-1_0_4_load_38 | 57 | 0.004065 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_158-1_0_4_load_39 | 58 | 0.0034184 | 0.00085673 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_158-1_0_4_load_40 | 59 | 0.0050114 | 0.001256 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_158-1_0_4_load_41 | 60 | 0.0040844 | 0.0010236 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_158-1_0_4_load_42 | 61 | 0.0010097 | 0.00025305 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_158-1_0_4_load_49 | 62 | 0.0010025 | 0.00025124 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_158-1_0_4_load_86 | 64 | 0.0011071 | 0.00027746 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_158-1_0_4_load_92 | 66 | 0.00315 | 0.00078947 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_158-1_0_4_load_93 | 67 | 0.0061856 | 0.0015503 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_158-1_0_4_load_44 | 69 | 0.0028924 | 0.00072491 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_158-1_0_4_load_50 | 73 | 0.0057501 | 0.0014411 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_158-1_0_4_load_60 | 74 | 0.0071474 | 0.0017913 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_158-1_0_4_load_51 | 76 | 0.0025235 | 0.00063245 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_158-1_0_4_load_52 | 77 | 0.010398 | 0.0026059 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_158-1_0_4_load_53 | 78 | 0.0021095 | 0.00052869 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_158-1_0_4_load_55 | 80 | 0.0023605 | 0.00059158 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_158-1_0_4_load_57 | 81 | 0.012947 | 0.0032447 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_158-1_0_4_load_58 | 82 | 0.0074617 | 0.0018701 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_158-1_0_4_load_59 | 83 | 0.012897 | 0.0032322 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_158-1_0_4_load_61 | 84 | 0.0086972 | 0.0021797 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_158-1_0_4_load_62 | 85 | 0.0064045 | 0.0016051 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_158-1_0_4_load_65 | 88 | 0.0081844 | 0.0020512 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_158-1_0_4_load_67 | 89 | 0.0085474 | 0.0021422 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_158-1_0_4_load_68 | 90 | 0.0027074 | 0.00067853 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_158-1_0_4_load_72 | 91 | 0.0021277 | 0.00053325 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_158-1_0_4_load_70 | 92 | 0.0049874 | 0.00125 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_158-1_0_4_load_69 | 93 | 0.0044799 | 0.0011228 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_158-1_0_4_load_73 | 95 | 0.0031027 | 0.0007776 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_158-1_0_4_load_74 | 96 | 0.0021692 | 0.00054364 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_158-1_0_4_load_75 | 97 | 0.002502 | 0.00062707 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_158-1_0_4_load_77 | 98 | 0.0066125 | 0.0016573 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_158-1_0_4_load_76 | 99 | 0.0020017 | 0.00050167 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_158-1_0_4_load_78 | 101 | 0.0066145 | 0.0016578 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_158-1_0_4_load_99 | 102 | 0.0033406 | 0.00083722 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_158-1_0_4_load_97 | 103 | 0.001711 | 0.00042881 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_158-1_0_4_load_79 | 104 | 0.0050044 | 0.0012542 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_158-1_0_4_load_80 | 105 | 0.023141 | 0.0057996 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_158-1_0_4_load_81 | 106 | 0.0020484 | 0.00051339 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_158-1_0_4_load_82 | 107 | 0.0020338 | 0.00050973 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_158-1_0_4_load_83 | 108 | 0.0019081 | 0.00047822 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_158-1_0_4_load_85 | 109 | 0.0028503 | 0.00071436 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_158-1_0_4_load_87 | 110 | 0.022373 | 0.0056071 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_158-1_0_4_load_88 | 111 | 0.018914 | 0.0047404 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_158-1_0_4_load_89 | 112 | 0.014635 | 0.0036678 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_158-1_0_4_load_94 | 113 | 0.0041945 | 0.0010513 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_158-1_0_4_load_95 | 114 | 0.0033647 | 0.00084327 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_158-1_0_4_load_101 | 115 | 0.0034661 | 0.00086868 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_158-1_0_4_load_102 | 116 | 0.0053279 | 0.0013353 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_158-1_0_4_load_96 | 117 | 0.0026854 | 0.00067303 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_158-1_0_4_load_100 | 118 | 0.0025401 | 0.00063662 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_158-1_0_4_load_146 | 119 | 0.0042014 | 0.001053 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_158-1_0_4_load_147 | 120 | 0.0032209 | 0.00080724 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_158-1_0_4_load_103 | 121 | 0.0018457 | 0.00046257 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_158-1_0_4_load_104 | 122 | 0.0045019 | 0.0011283 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_158-1_0_4_load_105 | 123 | 0.004723 | 0.0011837 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_158-1_0_4_load_106 | 124 | 0.0028003 | 0.00070182 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_158-1_0_4_load_107 | 125 | 0.0012077 | 0.00030269 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_158-1_0_4_load_108 | 126 | 0.0031319 | 0.00078493 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_158-1_0_4_load_109 | 127 | 0.0053038 | 0.0013293 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_158-1_0_4_load_110 | 128 | 0.005214 | 0.0013067 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_158-1_0_4_load_111 | 129 | 0.0039868 | 0.00099918 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_158-1_0_4_load_112 | 130 | 0.0032164 | 0.0008061 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_158-1_0_4_load_114 | 132 | 0.0044023 | 0.0011033 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_158-1_0_4_load_152 | 133 | 0.008616 | 0.0021594 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_158-1_0_4_load_124 | 136 | 9.5009e-05 | 2.3812e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_158-1_0_4_load_139 | 137 | 0.00019508 | 4.8893e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_158-1_0_4_load_134 | 138 | 0.00024032 | 6.0229e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_158-1_0_4_load_135 | 139 | 0.00040979 | 0.0001027 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_158-1_0_4_load_143 | 140 | 0.0011941 | 0.00029928 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_158-1_0_4_load_140 | 141 | 0.00095395 | 0.00023908 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_158-1_0_4_load_144 | 142 | 0.00016368 | 4.1021e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_158-1_0_4_load_141 | 143 | 0.00040391 | 0.00010123 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_158-1_0_4_load_142 | 144 | 0.00040338 | 0.0001011 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_158-1_0_4_load_145 | 145 | 0.00063442 | 0.000159 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_158-1_0_4_load_148 | 146 | 0.0036212 | 0.00090756 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_158-1_0_4_load_149 | 147 | 0.0027004 | 0.00067678 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_158-1_0_4_load_150 | 148 | 0.0031076 | 0.00077884 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_158-1_0_4_load_151 | 149 | 0.001151 | 0.00028846 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_158-1_0_4_line_0 |  | 0 | 1 | 0.038702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_158-1_0_4_line_1 |  | 0 | 2 | 0.034765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_158-1_0_4_line_2 |  | 1 | 3 | 0.077064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_158-1_0_4_line_3 |  | 2 | 4 | 0.11327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_158-1_0_4_line_4 |  | 2 | 5 | 0.11875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_158-1_0_4_line_5 |  | 3 | 6 | 0.095924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_158-1_0_4_line_6 |  | 4 | 7 | 0.038532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_158-1_0_4_line_7 |  | 5 | 8 | 0.018166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_158-1_0_4_line_8 |  | 7 | 13 | 0.0022378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_158-1_0_4_line_9 |  | 8 | 16 | 0.071083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_158-1_0_4_line_10 |  | 9 | 10 | 0.095427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_158-1_0_4_line_11 |  | 9 | 11 | 0.1393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_158-1_0_4_line_12 |  | 10 | 12 | 0.056307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_158-1_0_4_line_13 |  | 11 | 17 | 0.0046837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_158-1_0_4_line_14 |  | 12 | 22 | 0.013532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_158-1_0_4_line_15 |  | 14 | 15 | 0.043958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_158-1_0_4_line_16 |  | 15 | 23 | 0.075147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_158-1_0_4_line_17 |  | 15 | 24 | 0.19431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_158-1_0_4_line_18 |  | 16 | 39 | 0.018249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_158-1_0_4_line_19 |  | 17 | 136 | 0.031908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_158-1_0_4_line_20 |  | 18 | 19 | 0.018593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_158-1_0_4_line_21 |  | 18 | 20 | 0.0617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_158-1_0_4_line_22 |  | 18 | 21 | 0.10173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_158-1_0_4_line_23 |  | 19 | 133 | 0.016688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_158-1_0_4_line_24 |  | 20 | 46 | 0.014488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_158-1_0_4_line_25 |  | 20 | 38 | 0.010127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_158-1_0_4_line_26 |  | 21 | 22 | 0.057898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_158-1_0_4_line_27 |  | 23 | 25 | 0.0019068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_158-1_0_4_line_28 |  | 24 | 26 | 0.074041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_158-1_0_4_line_29 |  | 25 | 45 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_158-1_0_4_line_30 |  | 26 | 28 | 0.082347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_158-1_0_4_line_31 |  | 27 | 28 | 0.032738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_158-1_0_4_line_32 |  | 27 | 29 | 0.03796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_158-1_0_4_line_33 |  | 27 | 30 | 0.024176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_158-1_0_4_line_34 |  | 29 | 33 | 0.0099308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_158-1_0_4_line_35 |  | 29 | 34 | 0.13192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_158-1_0_4_line_36 |  | 30 | 40 | 0.019113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_158-1_0_4_line_37 |  | 31 | 32 | 0.0056513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_158-1_0_4_line_38 |  | 32 | 33 | 0.0085195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_158-1_0_4_line_39 |  | 34 | 35 | 0.20355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_158-1_0_4_line_40 |  | 34 | 36 | 0.07259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_158-1_0_4_line_41 |  | 35 | 37 | 0.020633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_158-1_0_4_line_42 |  | 36 | 38 | 0.12249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_158-1_0_4_line_43 |  | 36 | 39 | 0.004667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_158-1_0_4_line_44 |  | 37 | 137 | 0.015974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_158-1_0_4_line_45 |  | 40 | 41 | 0.0060903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_158-1_0_4_line_46 |  | 41 | 42 | 0.0158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_158-1_0_4_line_47 |  | 42 | 43 | 0.0058285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_158-1_0_4_line_48 |  | 43 | 44 | 0.01085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_158-1_0_4_line_49 |  | 45 | 50 | 0.062637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_158-1_0_4_line_50 |  | 46 | 47 | 0.017153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_158-1_0_4_line_51 |  | 46 | 48 | 0.026719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_158-1_0_4_line_52 |  | 47 | 134 | 0.0037531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_158-1_0_4_line_53 |  | 48 | 49 | 0.1066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_158-1_0_4_line_54 |  | 50 | 51 | 0.020154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_158-1_0_4_line_55 |  | 51 | 53 | 0.069633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_158-1_0_4_line_56 |  | 51 | 54 | 0.078835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_158-1_0_4_line_57 |  | 52 | 53 | 0.014074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_158-1_0_4_line_58 |  | 54 | 55 | 0.032166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_158-1_0_4_line_59 |  | 55 | 63 | 0.002348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_158-1_0_4_line_60 |  | 55 | 64 | 0.032412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_158-1_0_4_line_61 |  | 55 | 60 | 0.057035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_158-1_0_4_line_62 |  | 56 | 57 | 0.0066941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_158-1_0_4_line_63 |  | 56 | 58 | 0.025384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_158-1_0_4_line_64 |  | 57 | 59 | 0.027825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_158-1_0_4_line_65 |  | 58 | 60 | 0.03601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_158-1_0_4_line_66 |  | 59 | 61 | 0.0088256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_158-1_0_4_line_67 |  | 61 | 62 | 0.01778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_158-1_0_4_line_68 |  | 62 | 65 | 0.018904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_158-1_0_4_line_69 |  | 63 | 66 | 0.074085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_158-1_0_4_line_70 |  | 63 | 67 | 0.022718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_158-1_0_4_line_71 |  | 64 | 68 | 0.019101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_158-1_0_4_line_72 |  | 65 | 72 | 0.12261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_158-1_0_4_line_73 |  | 65 | 69 | 0.028094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_158-1_0_4_line_74 |  | 67 | 115 | 0.010872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_158-1_0_4_line_75 |  | 68 | 109 | 0.032493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_158-1_0_4_line_76 |  | 68 | 108 | 0.0075813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_158-1_0_4_line_77 |  | 69 | 70 | 0.047404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_158-1_0_4_line_78 |  | 70 | 71 | 0.044116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_158-1_0_4_line_79 |  | 71 | 73 | 0.032404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_158-1_0_4_line_80 |  | 72 | 74 | 0.065021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_158-1_0_4_line_81 |  | 74 | 75 | 0.083987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_158-1_0_4_line_82 |  | 75 | 83 | 0.00739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_158-1_0_4_line_83 |  | 75 | 79 | 0.043034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_158-1_0_4_line_84 |  | 76 | 77 | 0.030308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_158-1_0_4_line_85 |  | 76 | 78 | 0.031991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_158-1_0_4_line_86 |  | 77 | 79 | 0.02144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_158-1_0_4_line_87 |  | 78 | 80 | 0.018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_158-1_0_4_line_88 |  | 79 | 81 | 0.025999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_158-1_0_4_line_89 |  | 80 | 82 | 0.0052355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_158-1_0_4_line_90 |  | 81 | 84 | 0.0061977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_158-1_0_4_line_91 |  | 83 | 85 | 0.036084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_158-1_0_4_line_92 |  | 85 | 86 | 0.030837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_158-1_0_4_line_93 |  | 86 | 87 | 0.052901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_158-1_0_4_line_94 |  | 87 | 88 | 0.069005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_158-1_0_4_line_95 |  | 88 | 89 | 0.023244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_158-1_0_4_line_96 |  | 89 | 90 | 0.0038919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_158-1_0_4_line_97 |  | 91 | 92 | 0.03047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_158-1_0_4_line_98 |  | 92 | 93 | 0.019843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_158-1_0_4_line_99 |  | 93 | 94 | 0.0067135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_158-1_0_4_line_100 |  | 94 | 95 | 0.030333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_158-1_0_4_line_101 |  | 94 | 96 | 0.0095197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_158-1_0_4_line_102 |  | 95 | 97 | 0.039797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_158-1_0_4_line_103 |  | 97 | 98 | 0.020898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_158-1_0_4_line_104 |  | 98 | 101 | 0.017752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_158-1_0_4_line_105 |  | 99 | 100 | 0.01747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_158-1_0_4_line_106 |  | 100 | 102 | 0.018353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_158-1_0_4_line_107 |  | 100 | 103 | 0.031223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_158-1_0_4_line_108 |  | 101 | 104 | 0.030735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_158-1_0_4_line_109 |  | 102 | 118 | 0.033206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_158-1_0_4_line_110 |  | 103 | 117 | 0.0016704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_158-1_0_4_line_111 |  | 104 | 105 | 0.020808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_158-1_0_4_line_112 |  | 105 | 106 | 0.0067487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_158-1_0_4_line_113 |  | 106 | 107 | 0.029375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_158-1_0_4_line_114 |  | 107 | 108 | 0.030247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_158-1_0_4_line_115 |  | 109 | 110 | 0.025818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
116 | LV_158-1_0_4_line_116 |  | 110 | 111 | 0.046889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_158-1_0_4_line_117 |  | 111 | 112 | 0.020935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_158-1_0_4_line_118 |  | 112 | 113 | 0.0038881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_158-1_0_4_line_119 |  | 113 | 114 | 0.021402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_158-1_0_4_line_120 |  | 114 | 117 | 0.020697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_158-1_0_4_line_121 |  | 115 | 116 | 0.022559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_158-1_0_4_line_122 |  | 116 | 121 | 0.0029395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_158-1_0_4_line_123 |  | 118 | 119 | 0.00014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_158-1_0_4_line_124 |  | 119 | 120 | 0.031774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_158-1_0_4_line_125 |  | 120 | 146 | 0.0046693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_158-1_0_4_line_126 |  | 121 | 122 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_158-1_0_4_line_127 |  | 122 | 123 | 0.0030887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_158-1_0_4_line_128 |  | 123 | 124 | 0.010269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_158-1_0_4_line_129 |  | 124 | 125 | 0.0041296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_158-1_0_4_line_130 |  | 125 | 126 | 0.013915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_158-1_0_4_line_131 |  | 126 | 127 | 0.00030692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_158-1_0_4_line_132 |  | 127 | 128 | 0.0086829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_158-1_0_4_line_133 |  | 128 | 129 | 0.00318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_158-1_0_4_line_134 |  | 129 | 130 | 0.016502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_158-1_0_4_line_135 |  | 130 | 131 | 0.0031086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_158-1_0_4_line_136 |  | 131 | 132 | 0.05691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_158-1_0_4_line_137 |  | 134 | 135 | 0.11568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_158-1_0_4_line_138 |  | 135 | 138 | 0.011773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_158-1_0_4_line_139 |  | 135 | 139 | 0.010599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_158-1_0_4_line_140 |  | 138 | 140 | 0.0017314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_158-1_0_4_line_141 |  | 139 | 141 | 0.01416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_158-1_0_4_line_142 |  | 140 | 142 | 0.017775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_158-1_0_4_line_143 |  | 141 | 143 | 0.0027889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_158-1_0_4_line_144 |  | 143 | 144 | 0.0086898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_158-1_0_4_line_145 |  | 144 | 145 | 0.023628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_158-1_0_4_line_146 |  | 146 | 147 | 0.020762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_158-1_0_4_line_147 |  | 147 | 148 | 0.014461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_158-1_0_4_line_148 |  | 148 | 149 | 0.0026141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_158-1_0_4_trafo_34 | 0.63 MVA 20/0.4 kV | 150 | 52 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2698328.4637 | 1233516.6929 | 2698331.1025 | 1233492.0161 | 2698334.718 | 1233478.6106
1 | 2698321.9829 | 1233550.7419 | 2698326.7037 | 1233533.1515 | 2698328.4637 | 1233516.6929
2 | 2698363.8893 | 1233407.4183 | 2698353.2551 | 1233433.6617 | 2698337.7902 | 1233467.2195 | 2698334.718 | 1233478.6106
3 | 2698229.2138 | 1233486.0937 | 2698241.8006 | 1233499.2337 | 2698298.7597 | 1233535.6578 | 2698321.9829 | 1233550.7419
4 | 2698301.5606 | 1233667.0011 | 2698305.2534 | 1233661.6471 | 2698307.335 | 1233653.4533 | 2698311.8115 | 1233628.6535 | 2698315.0138 | 1233607.6465 | 2698318.1159 | 1233587.2049 | 2698320.8261 | 1233561.6197 | 2698321.9829 | 1233550.7419
5 | 2698363.8893 | 1233407.4183 | 2698366.4577 | 1233400.4668 | 2698359.8388 | 1233359.3714 | 2698349.4725 | 1233313.6439
6 | 2698229.2138 | 1233486.0937 | 2698226.4047 | 1233458.6159 | 2698236.8827 | 1233455.5725
7 | 2698301.5606 | 1233667.0011 | 2698297.1349 | 1233671.3534 | 2698292.6831 | 1233676.8171 | 2698291.0264 | 1233681.44
8 | 2698236.8827 | 1233455.5725 | 2698239.0317 | 1233454.9483
9 | 2698303.7248 | 1233750.7988 | 2698301.2252 | 1233738.504 | 2698290.784 | 1233697.3231 | 2698290.0562 | 1233691.4289 | 2698290.1369 | 1233684.7253 | 2698290.6351 | 1233682.5319 | 2698291.0264 | 1233681.44
10 | 2698424.6543 | 1233534.04 | 2698429.5294 | 1233521.3224 | 2698434.9101 | 1233511.4486 | 2698443.3871 | 1233498.4127 | 2698456.434 | 1233481.483 | 2698466.5725 | 1233468.7193 | 2698475.4294 | 1233458.8143 | 2698478.3511 | 1233461.6203
11 | 2698478.3511 | 1233461.6203 | 2698480.8397 | 1233466.3428 | 2698486.716 | 1233487.3223 | 2698497.7353 | 1233514.1358 | 2698512.4482 | 1233557.9231 | 2698523.896 | 1233586.2783 | 2698525.0542 | 1233592.5884
12 | 2698424.6543 | 1233534.04 | 2698422.4431 | 1233542.732 | 2698420.6041 | 1233553.187 | 2698420.2255 | 1233564.1555 | 2698421.0537 | 1233574.9439 | 2698423.255 | 1233589.7077
13 | 2698525.0542 | 1233592.5884 | 2698525.8998 | 1233597.1951
14 | 2698423.255 | 1233589.7077 | 2698425.2505 | 1233603.092
15 | 2697999.3189 | 1233487.6334 | 2698010.6358 | 1233486.4525 | 2698014.3425 | 1233487.1252 | 2698043.143 | 1233487.9486
16 | 2697999.3189 | 1233487.6334 | 2697998.5 | 1233482.1937 | 2697985.6714 | 1233457.9754 | 2697968.8113 | 1233419.2467
17 | 2697895.0959 | 1233651.3478 | 2697947.6921 | 1233570.8216 | 2697995.4577 | 1233497.6994 | 2697998.3199 | 1233492.654 | 2697999.3189 | 1233487.6334
18 | 2698303.6511 | 1233768.9777 | 2698304.4188 | 1233762.8526 | 2698303.7248 | 1233750.7988
19 | 2698538.336 | 1233625.9581 | 2698533.4547 | 1233619.8727 | 2698527.9167 | 1233608.1833 | 2698525.8998 | 1233597.1951
20 | 2698457.1519 | 1233766.1386 | 2698451.8746 | 1233764.7613 | 2698439.0868 | 1233761.5249
21 | 2698426.5071 | 1233817.9138 | 2698426.736 | 1233816.4387 | 2698427.9919 | 1233813.3016 | 2698430.1545 | 1233810.7355 | 2698433.0232 | 1233808.9595 | 2698436.2997 | 1233808.1688 | 2698436.9085 | 1233797.015 | 2698438.4391 | 1233770.91 | 2698439.0868 | 1233761.5249
22 | 2698439.0868 | 1233761.5249 | 2698440.8037 | 1233705.9011 | 2698437.9125 | 1233688.0177 | 2698433.7884 | 1233660.3574
23 | 2698457.1519 | 1233766.1386 | 2698473.2992 | 1233770.3502
24 | 2698434.1376 | 1233828.9817 | 2698431.2371 | 1233827.6438 | 2698428.865 | 1233825.4918 | 2698427.2449 | 1233822.7407 | 2698426.5091 | 1233819.6262 | 2698426.5071 | 1233817.9138
25 | 2698426.5071 | 1233817.9138 | 2698419.3497 | 1233816.6832 | 2698416.5259 | 1233816.2028
26 | 2698433.7884 | 1233660.3574 | 2698425.2505 | 1233603.092
27 | 2697967.0137 | 1233418.6109 | 2697968.8113 | 1233419.2467
28 | 2697895.0959 | 1233651.3478 | 2697915.8715 | 1233650.5005 | 2697933.542 | 1233651.5368 | 2697967.3277 | 1233657.9317 | 2697968.4689 | 1233658.1493
29 | 2697947.9758 | 1233411.877 | 2697967.0137 | 1233418.6109
30 | 2698048.421 | 1233675.8153 | 2698042.3693 | 1233673.6361 | 2698040.6562 | 1233671.9177 | 2697968.4689 | 1233658.1493
31 | 2698079.8859 | 1233685.1747 | 2698048.421 | 1233675.8153
32 | 2698079.8859 | 1233685.1747 | 2698079.4127 | 1233690.4486 | 2698110.3676 | 1233700.8783
33 | 2698079.8859 | 1233685.1747 | 2698102.5864 | 1233693.4916
34 | 2698110.3676 | 1233700.8783 | 2698110.4522 | 1233710.8087
35 | 2698110.3676 | 1233700.8783 | 2698158.5572 | 1233718.5425 | 2698165.3155 | 1233721.0226 | 2698172.1424 | 1233723.4816 | 2698223.3851 | 1233743.7654 | 2698233.6459 | 1233747.8047
36 | 2698120.5328 | 1233700.0667 | 2698102.5864 | 1233693.4916
37 | 2698110.5247 | 1233719.3278 | 2698110.5708 | 1233724.9789
38 | 2698110.5247 | 1233719.3278 | 2698110.4522 | 1233710.8087
39 | 2698233.6459 | 1233747.8047 | 2698219.9065 | 1233895.042 | 2698225.2977 | 1233905.094 | 2698248.9198 | 1233918.8724 | 2698260.1809 | 1233931.5037
40 | 2698301.8234 | 1233773.2729 | 2698233.6459 | 1233747.8047
41 | 2698260.1809 | 1233931.5037 | 2698264.1733 | 1233935.9817 | 2698278.1758 | 1233940.2329
42 | 2698301.8234 | 1233773.2729 | 2698374.5136 | 1233800.0731 | 2698409.3782 | 1233813.9272 | 2698416.5259 | 1233816.2028
43 | 2698301.8234 | 1233773.2729 | 2698303.6511 | 1233768.9777
44 | 2698278.1758 | 1233940.2329 | 2698285.4781 | 1233942.4499 | 2698292.1739 | 1233947.4266
45 | 2698120.5328 | 1233700.0667 | 2698126.2513 | 1233702.1618
46 | 2698126.2513 | 1233702.1618 | 2698138.0479 | 1233706.4838 | 2698141.1117 | 1233707.5287
47 | 2698146.6282 | 1233709.4101 | 2698141.1117 | 1233707.5287
48 | 2698146.6282 | 1233709.4101 | 2698156.8974 | 1233712.9124
49 | 2697888.4682 | 1233402.4774 | 2697900.584 | 1233397.8513 | 2697911.3716 | 1233398.9298 | 2697947.9758 | 1233411.877
50 | 2698434.1376 | 1233828.9817 | 2698432.2284 | 1233835.4437 | 2698431.1444 | 1233841.4636 | 2698431.1661 | 1233845.7616
51 | 2698434.1376 | 1233828.9817 | 2698438.2577 | 1233829.3613 | 2698442.1922 | 1233828.1589 | 2698445.3851 | 1233825.5543 | 2698447.3455 | 1233821.9397 | 2698456.4993 | 1233826.5169
52 | 2698431.1851 | 1233849.5146 | 2698431.1661 | 1233845.7616
53 | 2698456.4993 | 1233826.5169 | 2698465.4028 | 1233831.1234 | 2698471.5574 | 1233833.9274 | 2698478.7992 | 1233836.9163 | 2698487.7949 | 1233839.6117 | 2698494.2206 | 1233841.1305 | 2698507.6101 | 1233844.5994 | 2698541.1766 | 1233852.2392 | 2698558.5914 | 1233855.545
54 | 2697869.3661 | 1233408.7786 | 2697876.3142 | 1233407.1251 | 2697888.4682 | 1233402.4774
55 | 2697869.3661 | 1233408.7786 | 2697858.6997 | 1233402.187 | 2697843.6423 | 1233399.6817 | 2697837.9518 | 1233389.803 | 2697838.9446 | 1233386.9951 | 2697857.044 | 1233376.7521 | 2697860.9483 | 1233371.3636
56 | 2697869.3661 | 1233408.7786 | 2697851.9156 | 1233418.2427 | 2697814.6349 | 1233412.0245 | 2697795.6408 | 1233412.2344 | 2697793.5196 | 1233412.7877
57 | 2697860.9483 | 1233371.3636 | 2697862.832 | 1233368.7637 | 2697872.5002 | 1233363.8094
58 | 2697765.9964 | 1233427.8693 | 2697779.6025 | 1233416.418 | 2697793.5196 | 1233412.7877
59 | 2697765.9964 | 1233427.8693 | 2697765.7157 | 1233430.1998
60 | 2697765.9964 | 1233427.8693 | 2697760.184 | 1233395.9832
61 | 2697765.9964 | 1233427.8693 | 2697761.0037 | 1233427.5759 | 2697760.9219 | 1233423.8051 | 2697712.6978 | 1233421.8852
62 | 2697681.3695 | 1233370.1257 | 2697678.6931 | 1233363.9899
63 | 2697681.3695 | 1233370.1257 | 2697690.2549 | 1233390.4965 | 2697691.9423 | 1233393.1674
64 | 2697678.6931 | 1233363.9899 | 2697667.5685 | 1233338.4854
65 | 2697691.9423 | 1233393.1674 | 2697706.4833 | 1233416.1822 | 2697711.4106 | 1233421.834 | 2697712.6978 | 1233421.8852
66 | 2697667.5685 | 1233338.4854 | 2697667.5685 | 1233338.4854 | 2697658.8669 | 1233337.0114
67 | 2697642.5942 | 1233329.9957 | 2697657.0272 | 1233336.6998 | 2697658.8669 | 1233337.0114
68 | 2697625.0597 | 1233323.2203 | 2697630.2747 | 1233324.2734 | 2697642.5942 | 1233329.9957
69 | 2697765.7157 | 1233430.1998 | 2697792.1556 | 1233433.5149 | 2697812.8173 | 1233436.4126 | 2697822.1734 | 1233440.2694 | 2697826.5081 | 1233446.0339 | 2697825.7856 | 1233455.4178
70 | 2697765.7157 | 1233430.1998 | 2697765.2783 | 1233433.773 | 2697760.7177 | 1233452.3389
71 | 2697761.7289 | 1233377.0728 | 2697759.6209 | 1233392.8943 | 2697760.184 | 1233395.9832
72 | 2697625.0597 | 1233323.2203 | 2697610.2217 | 1233289.3739 | 2697605.3223 | 1233281.5544 | 2697606.346 | 1233278.2354 | 2697599.7843 | 1233269.2767 | 2697598.2305 | 1233264.7589 | 2697599.9212 | 1233259.5607 | 2697609.6715 | 1233246.8225 | 2697622.2186 | 1233233.9302 | 2697627.2304 | 1233226.1623 | 2697632.1942 | 1233219.4723
73 | 2697625.0597 | 1233323.2203 | 2697629.5401 | 1233332.1116 | 2697632.7282 | 1233347.2973 | 2697632.6372 | 1233349.917
74 | 2697760.7177 | 1233452.3389 | 2697758.1241 | 1233462.8974
75 | 2697761.7289 | 1233377.0728 | 2697773.9059 | 1233374.2488 | 2697788.1429 | 1233360.2129
76 | 2697761.7289 | 1233377.0728 | 2697763.9797 | 1233370.0602 | 2697764.0772 | 1233369.8671
77 | 2697609.8907 | 1233389.2309 | 2697618.4123 | 1233381.6764 | 2697624.9141 | 1233373.9997 | 2697628.3376 | 1233369.7973 | 2697631.3144 | 1233361.9071 | 2697632.412 | 1233356.3988 | 2697632.6372 | 1233349.917
78 | 2697609.8907 | 1233389.2309 | 2697618.1043 | 1233410.0923 | 2697621.9574 | 1233414.759 | 2697636.7421 | 1233420.039
79 | 2697636.7421 | 1233420.039 | 2697642.3521 | 1233421.4767 | 2697646.868 | 1233422.674 | 2697648.9194 | 1233423.1747 | 2697653.8984 | 1233424.7577 | 2697660.3604 | 1233422.729 | 2697668.0025 | 1233424.4415
80 | 2697632.1942 | 1233219.4723 | 2697642.9841 | 1233219.5051 | 2697657.6969 | 1233221.3592 | 2697666.7805 | 1233221.0861 | 2697675.4812 | 1233219.6947 | 2697686.9279 | 1233217.092 | 2697695.8972 | 1233213.2332
81 | 2697767.3057 | 1233234.693 | 2697744.9179 | 1233219.3024 | 2697733.8179 | 1233207.2777 | 2697724.5229 | 1233203.3665 | 2697710.4777 | 1233206.9605 | 2697695.8972 | 1233213.2332
82 | 2697767.3057 | 1233234.693 | 2697773.7393 | 1233231.057
83 | 2697767.3057 | 1233234.693 | 2697728.8871 | 1233254.2979
84 | 2697686.5672 | 1233280.9219 | 2697687.252 | 1233276.5744 | 2697709.671 | 1233263.5908
85 | 2697706.0992 | 1233304.1742 | 2697705.1318 | 1233300.8639 | 2697703.6793 | 1233296.181 | 2697701.1013 | 1233292.7028 | 2697696.7767 | 1233289.9964 | 2697692.4437 | 1233287.8013 | 2697689.4288 | 1233286.0282 | 2697686.5672 | 1233280.9219 | 2697686.5672 | 1233280.9219
86 | 2697728.8871 | 1233254.2979 | 2697721.0814 | 1233256.9827 | 2697709.671 | 1233263.5908
87 | 2697707.1088 | 1233322.4568 | 2697706.5616 | 1233318.9007 | 2697707.4398 | 1233314.7677 | 2697707.4137 | 1233309.9081 | 2697706.3792 | 1233305.132 | 2697706.0992 | 1233304.1742
88 | 2697728.8871 | 1233254.2979 | 2697740.926 | 1233277.342
89 | 2697710.7036 | 1233326.2631 | 2697707.1088 | 1233322.4568 | 2697707.1088 | 1233322.4568
90 | 2697743.7958 | 1233282.8352 | 2697740.926 | 1233277.342
91 | 2697805.1532 | 1233213.3031 | 2697773.7393 | 1233231.057
92 | 2697831.9995 | 1233198.1305 | 2697805.1532 | 1233213.3031
93 | 2697878.7393 | 1233173.1038 | 2697831.9995 | 1233198.1305
94 | 2697878.7393 | 1233173.1038 | 2697890.4967 | 1233178.7682 | 2697895.5868 | 1233182.8106 | 2697899.582 | 1233186.2122 | 2697900.1019 | 1233188.667 | 2697898.4311 | 1233193.5542 | 2697897.1293 | 1233195.3563 | 2697878.5909 | 1233206.9262 | 2697876.5552 | 1233205.4694 | 2697874.3283 | 1233205.5105 | 2697871.2909 | 1233206.4835 | 2697870.1402 | 1233208.7662 | 2697870.1909 | 1233210.7463 | 2697870.1909 | 1233210.7463
95 | 2697870.1909 | 1233210.7463 | 2697876.8139 | 1233221.9414 | 2697877.5138 | 1233223.1204 | 2697882.0313 | 1233230.748
96 | 2697882.0313 | 1233230.748 | 2697884.0145 | 1233234.0967
97 | 2697951.0653 | 1233206.4753 | 2697970.5795 | 1233183.0746
98 | 2697937.4486 | 1233220.9094 | 2697951.0653 | 1233206.4753 | 2697951.0653 | 1233206.4753
99 | 2697932.6751 | 1233225.5863 | 2697933.5164 | 1233225.0776 | 2697937.4486 | 1233220.9094
100 | 2697932.6751 | 1233225.5863 | 2697906.6799 | 1233241.2184
101 | 2697932.6751 | 1233225.5863 | 2697940.623 | 1233230.8261
102 | 2697906.6799 | 1233241.2184 | 2697872.5746 | 1233261.7275
103 | 2697854.6649 | 1233272.4974 | 2697872.5746 | 1233261.7275
104 | 2697854.6649 | 1233272.4974 | 2697849.6709 | 1233275.5006 | 2697839.962 | 1233282.4234
105 | 2697939.3365 | 1233280.3698 | 2697942.7992 | 1233274.2668 | 2697950.9192 | 1233267.6846
106 | 2697939.3365 | 1233280.3698 | 2697955.2582 | 1233271.2407
107 | 2697939.3365 | 1233280.3698 | 2697937.8994 | 1233281.1911 | 2697910.234 | 1233291.6268
108 | 2697814.9374 | 1233300.2669 | 2697839.962 | 1233282.4234
109 | 2697984.0649 | 1233254.7237 | 2697955.2582 | 1233271.2407
110 | 2697910.234 | 1233291.6268 | 2697908.671 | 1233292.2163
111 | 2697814.9374 | 1233300.2669 | 2697809.8735 | 1233303.8776 | 2697799.6577 | 1233314.2918
112 | 2697794.9317 | 1233319.1095 | 2697799.6577 | 1233314.2918
113 | 2697794.9317 | 1233319.1095 | 2697790.5198 | 1233323.607 | 2697778.509 | 1233343.3101
114 | 2697778.509 | 1233343.3101 | 2697772.5817 | 1233353.0336 | 2697764.0772 | 1233369.8671
115 | 2697788.1429 | 1233360.2129 | 2697794.0182 | 1233354.4206 | 2697808.1509 | 1233343.9865
116 | 2697808.1509 | 1233343.9865 | 2697837.9789 | 1233321.9646 | 2697846.9199 | 1233317.9225
117 | 2697865.9959 | 1233309.2987 | 2697846.9199 | 1233317.9225
118 | 2697865.9959 | 1233309.2987 | 2697869.5389 | 1233307.697
119 | 2697869.5389 | 1233307.697 | 2697879.1525 | 1233303.3509 | 2697889.3055 | 1233299.5211
120 | 2697889.3055 | 1233299.5211 | 2697908.671 | 1233292.2163
121 | 2697752.7427 | 1233484.8051 | 2697758.1241 | 1233462.8974
122 | 2697752.0415 | 1233487.6597 | 2697752.7427 | 1233484.8051
123 | 2697984.0649 | 1233254.7237 | 2697984.1919 | 1233254.6508
124 | 2697984.1919 | 1233254.6508 | 2698011.7567 | 1233238.8459
125 | 2698015.8074 | 1233236.5233 | 2698011.7567 | 1233238.8459
126 | 2697752.0415 | 1233487.6597 | 2697749.5417 | 1233497.8362
127 | 2697748.8049 | 1233500.8358 | 2697749.5417 | 1233497.8362
128 | 2697748.8049 | 1233500.8358 | 2697746.3552 | 1233510.8082
129 | 2697746.3552 | 1233510.8082 | 2697745.3701 | 1233514.8187
130 | 2697742.0506 | 1233528.3324 | 2697745.3701 | 1233514.8187
131 | 2697741.9774 | 1233528.6305 | 2697742.0506 | 1233528.3324
132 | 2697741.9774 | 1233528.6305 | 2697740.9637 | 1233532.7572 | 2697738.7022 | 1233536.5705
133 | 2697737.0801 | 1233539.3057 | 2697738.7022 | 1233536.5705
134 | 2697737.0801 | 1233539.3057 | 2697734.8969 | 1233542.9872 | 2697726.2375 | 1233551.6118
135 | 2697724.035 | 1233553.8054 | 2697726.2375 | 1233551.6118
136 | 2697698.8461 | 1233514.9738 | 2697690.6005 | 1233523.7114 | 2697724.035 | 1233553.8054
137 | 2698460.1183 | 1233960.3425 | 2698453.0256 | 1233945.1693 | 2698443.3229 | 1233921.1909 | 2698437.5108 | 1233901.38 | 2698431.2743 | 1233867.4294 | 2698431.1851 | 1233849.5146
138 | 2698460.1183 | 1233960.3425 | 2698464.7668 | 1233971.1585
139 | 2698460.1183 | 1233960.3425 | 2698469.5722 | 1233955.5505
140 | 2698464.7668 | 1233971.1585 | 2698465.4504 | 1233972.7491
141 | 2698469.5722 | 1233955.5505 | 2698469.762 | 1233955.4542 | 2698483.5351 | 1233953.255
142 | 2698465.4504 | 1233972.7491 | 2698472.469 | 1233989.08
143 | 2698483.5351 | 1233953.255 | 2698486.2891 | 1233952.8153
144 | 2698494.8701 | 1233951.4451 | 2698486.2891 | 1233952.8153
145 | 2698518.3312 | 1233951.4331 | 2698503.3239 | 1233950.0953 | 2698494.8701 | 1233951.4451
146 | 2698015.8074 | 1233236.5233 | 2698033.8183 | 1233226.1963
147 | 2698046.3631 | 1233219.0034 | 2698033.8183 | 1233226.1963
148 | 2698048.6309 | 1233217.7032 | 2698046.3631 | 1233219.0034

## bus_geodata
| x | y | coords
0 | 2698328.4637 | 1233516.6929
1 | 2698334.718 | 1233478.6106
2 | 2698321.9829 | 1233550.7419
3 | 2698363.8893 | 1233407.4183
4 | 2698229.2138 | 1233486.0937
5 | 2698301.5606 | 1233667.0011
6 | 2698349.4725 | 1233313.6439
7 | 2698236.8827 | 1233455.5725
8 | 2698291.0264 | 1233681.44
9 | 2698478.3511 | 1233461.6203
10 | 2698424.6543 | 1233534.04
11 | 2698525.0542 | 1233592.5884
12 | 2698423.255 | 1233589.7077
13 | 2698239.0317 | 1233454.9483
14 | 2698043.143 | 1233487.9486
15 | 2697999.3189 | 1233487.6334
16 | 2698303.7248 | 1233750.7988
17 | 2698525.8998 | 1233597.1951
18 | 2698439.0868 | 1233761.5249
19 | 2698457.1519 | 1233766.1386
20 | 2698426.5071 | 1233817.9138
21 | 2698433.7884 | 1233660.3574
22 | 2698425.2505 | 1233603.092
23 | 2697968.8113 | 1233419.2467
24 | 2697895.0959 | 1233651.3478
25 | 2697967.0137 | 1233418.6109
26 | 2697968.4689 | 1233658.1493
27 | 2698079.8859 | 1233685.1747
28 | 2698048.421 | 1233675.8153
29 | 2698110.3676 | 1233700.8783
30 | 2698102.5864 | 1233693.4916
31 | 2698110.5708 | 1233724.9789
32 | 2698110.5247 | 1233719.3278
33 | 2698110.4522 | 1233710.8087
34 | 2698233.6459 | 1233747.8047
35 | 2698260.1809 | 1233931.5037
36 | 2698301.8234 | 1233773.2729
37 | 2698278.1758 | 1233940.2329
38 | 2698416.5259 | 1233816.2028
39 | 2698303.6511 | 1233768.9777
40 | 2698120.5328 | 1233700.0667
41 | 2698126.2513 | 1233702.1618
42 | 2698141.1117 | 1233707.5287
43 | 2698146.6282 | 1233709.4101
44 | 2698156.8974 | 1233712.9124
45 | 2697947.9758 | 1233411.877
46 | 2698434.1376 | 1233828.9817
47 | 2698431.1661 | 1233845.7616
48 | 2698456.4993 | 1233826.5169
49 | 2698558.5914 | 1233855.545
50 | 2697888.4682 | 1233402.4774
51 | 2697869.3661 | 1233408.7786
52 | 2697872.5002 | 1233363.8094
53 | 2697860.9483 | 1233371.3636
54 | 2697793.5196 | 1233412.7877
55 | 2697765.9964 | 1233427.8693
56 | 2697681.3695 | 1233370.1257
57 | 2697678.6931 | 1233363.9899
58 | 2697691.9423 | 1233393.1674
59 | 2697667.5685 | 1233338.4854
60 | 2697712.6978 | 1233421.8852
61 | 2697658.8669 | 1233337.0114
62 | 2697642.5942 | 1233329.9957
63 | 2697765.7157 | 1233430.1998
64 | 2697760.184 | 1233395.9832
65 | 2697625.0597 | 1233323.2203
66 | 2697825.7856 | 1233455.4178
67 | 2697760.7177 | 1233452.3389
68 | 2697761.7289 | 1233377.0728
69 | 2697632.6372 | 1233349.917
70 | 2697609.8907 | 1233389.2309
71 | 2697636.7421 | 1233420.039
72 | 2697632.1942 | 1233219.4723
73 | 2697668.0025 | 1233424.4415
74 | 2697695.8972 | 1233213.2332
75 | 2697767.3057 | 1233234.693
76 | 2697686.5672 | 1233280.9219
77 | 2697709.671 | 1233263.5908
78 | 2697706.0992 | 1233304.1742
79 | 2697728.8871 | 1233254.2979
80 | 2697707.1088 | 1233322.4568
81 | 2697740.926 | 1233277.342
82 | 2697710.7036 | 1233326.2631
83 | 2697773.7393 | 1233231.057
84 | 2697743.7958 | 1233282.8352
85 | 2697805.1532 | 1233213.3031
86 | 2697831.9995 | 1233198.1305
87 | 2697878.7393 | 1233173.1038
88 | 2697870.1909 | 1233210.7463
89 | 2697882.0313 | 1233230.748
90 | 2697884.0145 | 1233234.0967
91 | 2697970.5795 | 1233183.0746
92 | 2697951.0653 | 1233206.4753
93 | 2697937.4486 | 1233220.9094
94 | 2697932.6751 | 1233225.5863
95 | 2697906.6799 | 1233241.2184
96 | 2697940.623 | 1233230.8261
97 | 2697872.5746 | 1233261.7275
98 | 2697854.6649 | 1233272.4974
99 | 2697950.9192 | 1233267.6846
100 | 2697939.3365 | 1233280.3698
101 | 2697839.962 | 1233282.4234
102 | 2697955.2582 | 1233271.2407
103 | 2697910.234 | 1233291.6268
104 | 2697814.9374 | 1233300.2669
105 | 2697799.6577 | 1233314.2918
106 | 2697794.9317 | 1233319.1095
107 | 2697778.509 | 1233343.3101
108 | 2697764.0772 | 1233369.8671
109 | 2697788.1429 | 1233360.2129
110 | 2697808.1509 | 1233343.9865
111 | 2697846.9199 | 1233317.9225
112 | 2697865.9959 | 1233309.2987
113 | 2697869.5389 | 1233307.697
114 | 2697889.3055 | 1233299.5211
115 | 2697758.1241 | 1233462.8974
116 | 2697752.7427 | 1233484.8051
117 | 2697908.671 | 1233292.2163
118 | 2697984.0649 | 1233254.7237
119 | 2697984.1919 | 1233254.6508
120 | 2698011.7567 | 1233238.8459
121 | 2697752.0415 | 1233487.6597
122 | 2697749.5417 | 1233497.8362
123 | 2697748.8049 | 1233500.8358
124 | 2697746.3552 | 1233510.8082
125 | 2697745.3701 | 1233514.8187
126 | 2697742.0506 | 1233528.3324
127 | 2697741.9774 | 1233528.6305
128 | 2697738.7022 | 1233536.5705
129 | 2697737.0801 | 1233539.3057
130 | 2697726.2375 | 1233551.6118
131 | 2697724.035 | 1233553.8054
132 | 2697698.8461 | 1233514.9739
133 | 2698473.2992 | 1233770.3502
134 | 2698431.1851 | 1233849.5146
135 | 2698460.1183 | 1233960.3425
136 | 2698538.336 | 1233625.9581
137 | 2698292.1739 | 1233947.4266
138 | 2698464.7668 | 1233971.1585
139 | 2698469.5722 | 1233955.5505
140 | 2698465.4504 | 1233972.7491
141 | 2698483.5351 | 1233953.255
142 | 2698472.469 | 1233989.08
143 | 2698486.2891 | 1233952.8153
144 | 2698494.8701 | 1233951.4451
145 | 2698518.3312 | 1233951.4331
146 | 2698015.8074 | 1233236.5233
147 | 2698033.8183 | 1233226.1963
148 | 2698046.3631 | 1233219.0034
149 | 2698048.6309 | 1233217.7032
150 | 2697869.3661 | 1233408.7786

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97333 | -0.51396 | 0.001123 | 0.00028145
1 | 0.97278 | -0.5248 | 0.0040789 | 0.0010223
2 | 0.97386 | -0.50351 | 0 | 0
3 | 0.97198 | -0.54063 | 0 | 0
4 | 0.97336 | -0.51346 | 0 | 0
5 | 0.9762 | -0.4575 | 0 | 0
6 | 0.97098 | -0.56036 | 0.011137 | 0.0027913
7 | 0.97319 | -0.51685 | 0.0038139 | 0.00095587
8 | 0.97656 | -0.45048 | 0.0047591 | 0.0011927
9 | 0.97585 | -0.46472 | 0 | 0
10 | 0.9759 | -0.46385 | 0 | 0
11 | 0.97579 | -0.46598 | 0.00030604 | 7.6702e-05
12 | 0.97592 | -0.46334 | 0.00016806 | 4.2121e-05
13 | 0.97319 | -0.51689 | 0.00096277 | 0.00024129
14 | 0.98781 | -0.23166 | 0.0098242 | 0.0024622
15 | 0.98821 | -0.22395 | 0 | 0
16 | 0.97827 | -0.4169 | 0 | 0
17 | 0.97579 | -0.46599 | 8.866e-05 | 2.222e-05
18 | 0.97612 | -0.45931 | 0 | 0
19 | 0.97598 | -0.46224 | 0 | 0
20 | 0.97671 | -0.4477 | 0 | 0
21 | 0.97597 | -0.46242 | 0.0009618 | 0.00024105
22 | 0.97593 | -0.46317 | 3.971e-05 | 9.9524e-06
23 | 0.98957 | -0.19767 | 0.00055408 | 0.00013887
24 | 0.98512 | -0.28365 | 0 | 0
25 | 0.98961 | -0.197 | 0.00022415 | 5.6177e-05
26 | 0.98394 | -0.30649 | 0.0015866 | 0.00039763
27 | 0.98215 | -0.34127 | 0 | 0
28 | 0.98266 | -0.33136 | 0 | 0
29 | 0.98165 | -0.35102 | 0 | 0
30 | 0.98192 | -0.34572 | 0.0034617 | 0.00086759
31 | 0.98141 | -0.3558 | 0.010584 | 0.0026526
32 | 0.98146 | -0.35472 | 0 | 0
33 | 0.98154 | -0.35309 | 0.00092654 | 0.00023221
34 | 0.9798 | -0.38713 | 0 | 0
35 | 0.9794 | -0.39505 | 0.0015867 | 0.00039767
36 | 0.97883 | -0.4061 | 0 | 0
37 | 0.97939 | -0.39526 | 0.00035774 | 8.9658e-05
38 | 0.97687 | -0.44463 | 0.00065478 | 0.0001641
39 | 0.97872 | -0.4083 | 0 | 0
40 | 0.9818 | -0.34804 | 0.0013213 | 0.00033115
41 | 0.98177 | -0.34863 | 0.0020872 | 0.00052309
42 | 0.98173 | -0.34958 | 0.0010567 | 0.00026484
43 | 0.98171 | -0.34982 | 0.0011031 | 0.00027646
44 | 0.9817 | -0.35004 | 0.0011486 | 0.00028786
45 | 0.98998 | -0.18988 | 0.00064177 | 0.00016084
46 | 0.97663 | -0.44936 | 0 | 0
47 | 0.97655 | -0.45098 | 0.00075179 | 0.00018842
48 | 0.9766 | -0.44992 | 0 | 0
49 | 0.97649 | -0.45213 | 0.0011347 | 0.00028439
50 | 0.99114 | -0.16766 | 0 | 0
51 | 0.99151 | -0.16051 | 0 | 0
52 | 1 | 0 | -0.47042 | -0.12118
53 | 0.9985 | -0.028209 | 0.027581 | 0.0069124
54 | 0.98506 | -0.28423 | 0.0015708 | 0.00039367
55 | 0.98244 | -0.33495 | 0 | 0
56 | 0.97901 | -0.40168 | 0.0075049 | 0.0018809
57 | 0.97883 | -0.40509 | 0.004065 | 0.0010188
58 | 0.97971 | -0.38787 | 0.0034184 | 0.00085673
59 | 0.97813 | -0.41879 | 0.0050114 | 0.001256
60 | 0.98075 | -0.36777 | 0.0040844 | 0.0010236
61 | 0.97792 | -0.42293 | 0.0010097 | 0.00025305
62 | 0.97749 | -0.43121 | 0.0010025 | 0.00025124
63 | 0.98231 | -0.33743 | 0 | 0
64 | 0.9812 | -0.35905 | 0.0011071 | 0.00027746
65 | 0.97705 | -0.43993 | 0 | 0
66 | 0.9821 | -0.34165 | 0.00315 | 0.00078947
67 | 0.98115 | -0.36016 | 0.0061856 | 0.0015503
68 | 0.98047 | -0.37318 | 0 | 0
69 | 0.97682 | -0.44437 | 0.0028924 | 0.00072491
70 | 0.97657 | -0.44935 | 0 | 0
71 | 0.97633 | -0.45399 | 0 | 0
72 | 0.9744 | -0.49181 | 0 | 0
73 | 0.97616 | -0.4574 | 0.0057501 | 0.0014411
74 | 0.973 | -0.51944 | 0.0071474 | 0.0017913
75 | 0.97133 | -0.55246 | 0 | 0
76 | 0.97063 | -0.5662 | 0.0025235 | 0.00063245
77 | 0.97074 | -0.56418 | 0.010398 | 0.0026059
78 | 0.97046 | -0.56973 | 0.0021095 | 0.00052869
79 | 0.97086 | -0.56171 | 0 | 0
80 | 0.97028 | -0.57311 | 0.0023605 | 0.00059158
81 | 0.97033 | -0.57212 | 0.012947 | 0.0032447
82 | 0.97025 | -0.57383 | 0.0074617 | 0.0018701
83 | 0.97126 | -0.55379 | 0.012897 | 0.0032322
84 | 0.97028 | -0.57312 | 0.0086972 | 0.0021797
85 | 0.97104 | -0.5581 | 0.0064045 | 0.0016051
86 | 0.9709 | -0.56087 | 0 | 0
87 | 0.97066 | -0.56563 | 0 | 0
88 | 0.97035 | -0.57184 | 0.0081844 | 0.0020512
89 | 0.97023 | -0.57426 | 0.0085474 | 0.0021422
90 | 0.97022 | -0.57445 | 0.0027074 | 0.00067853
91 | 0.97233 | -0.53307 | 0.0021277 | 0.00053325
92 | 0.97239 | -0.53187 | 0.0049874 | 0.00125
93 | 0.97252 | -0.52927 | 0.0044799 | 0.0011228
94 | 0.9726 | -0.52783 | 0 | 0
95 | 0.97299 | -0.52014 | 0.0031027 | 0.0007776
96 | 0.97258 | -0.52821 | 0.0021692 | 0.00054364
97 | 0.97361 | -0.50779 | 0.002502 | 0.00062707
98 | 0.97399 | -0.50035 | 0.0066125 | 0.0016573
99 | 0.97382 | -0.50373 | 0.0020017 | 0.00050167
100 | 0.97385 | -0.50309 | 0 | 0
101 | 0.97442 | -0.49188 | 0.0066145 | 0.0016578
102 | 0.97344 | -0.51115 | 0.0033406 | 0.00083722
103 | 0.97461 | -0.48824 | 0.001711 | 0.00042881
104 | 0.97535 | -0.4735 | 0.0050044 | 0.0012542
105 | 0.97608 | -0.45917 | 0.023141 | 0.0057996
106 | 0.97646 | -0.45168 | 0.0020484 | 0.00051339
107 | 0.97818 | -0.41801 | 0.0020338 | 0.00050973
108 | 0.98 | -0.38236 | 0.0019081 | 0.00047822
109 | 0.97974 | -0.38742 | 0.0028503 | 0.00071436
110 | 0.97862 | -0.40943 | 0.022373 | 0.0056071
111 | 0.97706 | -0.43994 | 0.018914 | 0.0047404
112 | 0.97604 | -0.46002 | 0.014635 | 0.0036678
113 | 0.9759 | -0.46271 | 0.0041945 | 0.0010513
114 | 0.97523 | -0.4759 | 0.0033647 | 0.00084327
115 | 0.98065 | -0.36983 | 0.0034661 | 0.00086868
116 | 0.9797 | -0.38852 | 0.0053279 | 0.0013353
117 | 0.97465 | -0.4874 | 0.0026854 | 0.00067303
118 | 0.97281 | -0.52371 | 0.0025401 | 0.00063662
119 | 0.9728 | -0.52376 | 0.0042014 | 0.001053
120 | 0.9724 | -0.53184 | 0.0032209 | 0.00080724
121 | 0.97959 | -0.39068 | 0.0018457 | 0.00046257
122 | 0.97921 | -0.39801 | 0.0045019 | 0.0011283
123 | 0.97912 | -0.39991 | 0.004723 | 0.0011837
124 | 0.97884 | -0.40538 | 0.0028003 | 0.00070182
125 | 0.97874 | -0.40737 | 0.0012077 | 0.00030269
126 | 0.97841 | -0.41376 | 0.0031319 | 0.00078493
127 | 0.97841 | -0.41389 | 0.0053038 | 0.0013293
128 | 0.97827 | -0.41655 | 0.005214 | 0.0013067
129 | 0.97824 | -0.41722 | 0.0039868 | 0.00099918
130 | 0.97812 | -0.41951 | 0.0032164 | 0.0008061
131 | 0.97811 | -0.41976 | 0 | 0
132 | 0.97787 | -0.42433 | 0.0044023 | 0.0011033
133 | 0.97584 | -0.46487 | 0.008616 | 0.0021594
134 | 0.97653 | -0.45129 | 0 | 0
135 | 0.97606 | -0.46061 | 0 | 0
136 | 0.97579 | -0.46605 | 9.5009e-05 | 2.3812e-05
137 | 0.97938 | -0.39532 | 0.00019508 | 4.8893e-05
138 | 0.97604 | -0.46095 | 0.00024032 | 6.0229e-05
139 | 0.97603 | -0.46115 | 0.00040979 | 0.0001027
140 | 0.97604 | -0.461 | 0.0011941 | 0.00029928
141 | 0.976 | -0.46178 | 0.00095395 | 0.00023908
142 | 0.97604 | -0.46105 | 0.00016368 | 4.1021e-05
143 | 0.976 | -0.46185 | 0.00040391 | 0.00010123
144 | 0.97599 | -0.46201 | 0.00040338 | 0.0001011
145 | 0.97597 | -0.46229 | 0.00063442 | 0.000159
146 | 0.97235 | -0.53275 | 0.0036212 | 0.00090756
147 | 0.97222 | -0.53541 | 0.0027004 | 0.00067678
148 | 0.97216 | -0.53655 | 0.0031076 | 0.00077884
149 | 0.97215 | -0.5366 | 0.001151 | 0.00028846
150 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.015243 | 0.0038281 | -0.015235 | -0.0038235 | 7.8834e-06 | 4.5647e-06 | 0.023306 | 0.023307 | 0.023307 | 0.97333 | -0.51396 | 0.97278 | -0.5248 | 6.4029
1 | -0.016366 | -0.0041096 | 0.016374 | 0.0041143 | 8.1632e-06 | 4.7921e-06 | 0.025023 | 0.025023 | 0.025023 | 0.97333 | -0.51396 | 0.97386 | -0.50351 | 6.8745
2 | 0.011156 | 0.0028013 | -0.011148 | -0.0027968 | 8.4181e-06 | 4.4316e-06 | 0.017067 | 0.017068 | 0.017068 | 0.97278 | -0.5248 | 0.97198 | -0.54063 | 4.6889
3 | 0.0047798 | 0.0011972 | -0.0047775 | -0.0011971 | 2.2656e-06 | 4.1334e-08 | 0.007303 | 0.0073035 | 0.0073035 | 0.97386 | -0.50351 | 0.97336 | -0.51346 | 2.0065
4 | -0.021154 | -0.0053115 | 0.021201 | 0.0053398 | 4.6534e-05 | 2.83e-05 | 0.032326 | 0.032325 | 0.032326 | 0.97386 | -0.50351 | 0.9762 | -0.4575 | 8.8808
5 | 0.011148 | 0.0027968 | -0.011137 | -0.0027913 | 1.0479e-05 | 5.5187e-06 | 0.017068 | 0.017068 | 0.017068 | 0.97198 | -0.54063 | 0.97098 | -0.56036 | 4.689
6 | 0.0047775 | 0.0011971 | -0.0047767 | -0.0011971 | 7.7077e-07 | 1.4439e-08 | 0.0073035 | 0.0073037 | 0.0073037 | 0.97336 | -0.51346 | 0.97319 | -0.51685 | 2.0065
7 | -0.021201 | -0.0053398 | 0.021208 | 0.0053442 | 7.1182e-06 | 4.3285e-06 | 0.032325 | 0.032325 | 0.032325 | 0.9762 | -0.4575 | 0.97656 | -0.45048 | 8.8806
8 | 0.00096277 | 0.00024127 | -0.00096277 | -0.00024129 | 1.8185e-09 | -2.6641e-08 | 0.0014721 | 0.0014721 | 0.0014721 | 0.97319 | -0.51685 | 0.97319 | -0.51689 | 0.40442
9 | -0.025967 | -0.0065369 | 0.026009 | 0.0065627 | 4.1752e-05 | 2.583e-05 | 0.039577 | 0.039577 | 0.039577 | 0.97656 | -0.45048 | 0.97827 | -0.4169 | 10.8728
10 | -0.00048974 | -0.00012056 | 0.00048976 | 0.00011938 | 1.9904e-08 | -1.1795e-06 | 0.000746 | 0.00074558 | 0.000746 | 0.97585 | -0.46472 | 0.9759 | -0.46385 | 0.20494
11 | 0.00048974 | 0.00012056 | -0.00048971 | -0.00012228 | 2.9095e-08 | -1.7216e-06 | 0.000746 | 0.00074662 | 0.00074662 | 0.97585 | -0.46472 | 0.97579 | -0.46598 | 0.20511
12 | -0.00048976 | -0.00011938 | 0.00048978 | 0.00011868 | 1.1734e-08 | -6.9603e-07 | 0.00074558 | 0.00074533 | 0.00074558 | 0.9759 | -0.46385 | 0.97592 | -0.46334 | 0.20483
13 | 0.00018367 | 4.5575e-05 | -0.00018367 | -4.5633e-05 | 1.3762e-10 | -5.842e-08 | 0.00027992 | 0.00027994 | 0.00027994 | 0.97579 | -0.46598 | 0.97579 | -0.46599 | 0.076907
14 | -0.00065784 | -0.0001608 | 0.00065784 | 0.00016063 | 5.0904e-09 | -1.6583e-07 | 0.0010016 | 0.0010015 | 0.0010016 | 0.97592 | -0.46334 | 0.97593 | -0.46317 | 0.27516
15 | -0.0098242 | -0.0024622 | 0.0098278 | 0.0024639 | 3.6101e-06 | 1.7475e-06 | 0.014799 | 0.014799 | 0.014799 | 0.98781 | -0.23166 | 0.98821 | -0.22395 | 4.0656
16 | -0.079068 | -0.020046 | 0.079168 | 0.020106 | 9.9999e-05 | 6.0143e-05 | 0.11914 | 0.11914 | 0.11914 | 0.98821 | -0.22395 | 0.98957 | -0.19767 | 8.1827
17 | 0.06924 | 0.017582 | -0.069042 | -0.017465 | 0.00019833 | 0.000117 | 0.10434 | 0.10435 | 0.10435 | 0.98821 | -0.22395 | 0.98512 | -0.28365 | 7.1666
18 | -0.026009 | -0.0065627 | 0.026019 | 0.0065694 | 1.0719e-05 | 6.6308e-06 | 0.039577 | 0.039577 | 0.039577 | 0.97827 | -0.4169 | 0.97872 | -0.4083 | 10.8727
19 | 9.5009e-05 | 2.3413e-05 | -9.5009e-05 | -2.3812e-05 | 2.5092e-10 | -3.9842e-07 | 0.00014474 | 0.00014488 | 0.00014488 | 0.97579 | -0.46599 | 0.97579 | -0.46605 | 0.039803
20 | 0.0086183 | 0.0021604 | -0.0086171 | -0.0021599 | 1.2035e-06 | 5.3785e-07 | 0.013138 | 0.013138 | 0.013138 | 0.97612 | -0.45931 | 0.97598 | -0.46224 | 3.6094
21 | -0.010278 | -0.0025702 | 0.010284 | 0.0025731 | 5.6782e-06 | 2.8623e-06 | 0.015666 | 0.015665 | 0.015666 | 0.97612 | -0.45931 | 0.97671 | -0.4477 | 4.3038
22 | 0.0016596 | 0.00040981 | -0.0016594 | -0.00041093 | 2.438e-07 | -1.1154e-06 | 0.0025278 | 0.0025282 | 0.0025282 | 0.97612 | -0.45931 | 0.97597 | -0.46242 | 0.69456
23 | 0.0086171 | 0.0021599 | -0.008616 | -0.0021594 | 1.0802e-06 | 4.8279e-07 | 0.013138 | 0.013138 | 0.013138 | 0.97598 | -0.46224 | 0.97584 | -0.46487 | 3.6094
24 | 0.0062934 | 0.0015738 | -0.0062929 | -0.0015737 | 4.9932e-07 | 1.3826e-07 | 0.0095867 | 0.0095867 | 0.0095867 | 0.97671 | -0.4477 | 0.97663 | -0.44936 | 2.6337
25 | -0.016577 | -0.0041469 | 0.016579 | 0.0041483 | 2.4216e-06 | 1.423e-06 | 0.025252 | 0.025252 | 0.025252 | 0.97671 | -0.4477 | 0.97687 | -0.44463 | 6.9374
26 | 0.00069758 | 0.00016988 | -0.00069755 | -0.00017059 | 2.4485e-08 | -7.0782e-07 | 0.0010618 | 0.0010621 | 0.0010621 | 0.97597 | -0.46242 | 0.97593 | -0.46317 | 0.29178
27 | -0.079722 | -0.020245 | 0.079725 | 0.020247 | 2.573e-06 | 1.5487e-06 | 0.11997 | 0.11997 | 0.11997 | 0.98957 | -0.19767 | 0.98961 | -0.197 | 8.2399
28 | 0.069042 | 0.017465 | -0.068966 | -0.017421 | 7.5578e-05 | 4.4604e-05 | 0.10435 | 0.10435 | 0.10435 | 0.98512 | -0.28365 | 0.98394 | -0.30649 | 7.1667
29 | -0.079949 | -0.020303 | 0.079976 | 0.020319 | 2.7402e-05 | 1.6499e-05 | 0.12031 | 0.12031 | 0.12031 | 0.98961 | -0.197 | 0.98998 | -0.18988 | 8.263
30 | 0.06738 | 0.017023 | -0.0673 | -0.016976 | 8.0238e-05 | 4.7174e-05 | 0.10195 | 0.10195 | 0.10195 | 0.98394 | -0.30649 | 0.98266 | -0.33136 | 7.002
31 | -0.067268 | -0.016957 | 0.0673 | 0.016976 | 3.19e-05 | 1.8758e-05 | 0.10195 | 0.10195 | 0.10195 | 0.98215 | -0.34127 | 0.98266 | -0.33136 | 7.002
32 | 0.057086 | 0.014405 | -0.057059 | -0.01439 | 2.6642e-05 | 1.513e-05 | 0.086523 | 0.086524 | 0.086524 | 0.98215 | -0.34127 | 0.98165 | -0.35102 | 5.9426
33 | 0.010182 | 0.002552 | -0.01018 | -0.002551 | 2.1574e-06 | 1.0749e-06 | 0.015426 | 0.015426 | 0.015426 | 0.98215 | -0.34127 | 0.98192 | -0.34572 | 4.238
34 | 0.011513 | 0.0028861 | -0.011512 | -0.0028855 | 1.1342e-06 | 6.0037e-07 | 0.017452 | 0.017452 | 0.017452 | 0.98165 | -0.35102 | 0.98154 | -0.35309 | 4.7945
35 | 0.045546 | 0.011504 | -0.045468 | -0.011458 | 7.8675e-05 | 4.5358e-05 | 0.069072 | 0.069074 | 0.069074 | 0.98165 | -0.35102 | 0.9798 | -0.38713 | 6.3255
36 | 0.0067179 | 0.0016834 | -0.0067172 | -0.0016831 | 7.4282e-07 | 2.3367e-07 | 0.01018 | 0.01018 | 0.01018 | 0.98192 | -0.34572 | 0.9818 | -0.34804 | 2.7968
37 | -0.010584 | -0.0026526 | 0.010584 | 0.0026529 | 5.4574e-07 | 2.7786e-07 | 0.016047 | 0.016047 | 0.016047 | 0.98141 | -0.3558 | 0.98146 | -0.35472 | 4.4086
38 | -0.010584 | -0.0026529 | 0.010585 | 0.0026533 | 8.2272e-07 | 4.1887e-07 | 0.016047 | 0.016047 | 0.016047 | 0.98146 | -0.35472 | 0.98154 | -0.35309 | 4.4086
39 | 0.0021404 | 0.00053372 | -0.0021396 | -0.00053577 | 8.0629e-07 | -2.0466e-06 | 0.0032496 | 0.0032505 | 0.0032505 | 0.9798 | -0.38713 | 0.9794 | -0.39505 | 0.893
40 | 0.043327 | 0.010925 | -0.043288 | -0.010902 | 3.9316e-05 | 2.2422e-05 | 0.065824 | 0.065825 | 0.065825 | 0.9798 | -0.38713 | 0.97883 | -0.4061 | 6.028
41 | 0.00055283 | 0.00013809 | -0.00055282 | -0.00013835 | 5.457e-09 | -2.5615e-07 | 0.00083976 | 0.00083985 | 0.00083985 | 0.9794 | -0.39505 | 0.97939 | -0.39526 | 0.23073
42 | 0.017266 | 0.0043312 | -0.017234 | -0.0043124 | 3.1649e-05 | 1.8719e-05 | 0.026249 | 0.026249 | 0.026249 | 0.97883 | -0.4061 | 0.97687 | -0.44463 | 7.2114
43 | 0.026022 | 0.0065711 | -0.026019 | -0.0065694 | 2.7412e-06 | 1.6957e-06 | 0.039576 | 0.039577 | 0.039577 | 0.97883 | -0.4061 | 0.97872 | -0.4083 | 10.8727
44 | 0.00019509 | 4.8692e-05 | -0.00019508 | -4.8893e-05 | 5.2614e-10 | -2.0068e-07 | 0.00029633 | 0.0002964 | 0.0002964 | 0.97939 | -0.39526 | 0.97938 | -0.39532 | 0.081429
45 | 0.0053959 | 0.001352 | -0.0053957 | -0.001352 | 1.5274e-07 | 2.0736e-08 | 0.0081778 | 0.0081779 | 0.0081779 | 0.9818 | -0.34804 | 0.98177 | -0.34863 | 2.2467
46 | 0.0033086 | 0.00082887 | -0.0033084 | -0.00082898 | 1.4899e-07 | -1.0444e-07 | 0.0050145 | 0.0050146 | 0.0050146 | 0.98177 | -0.34863 | 0.98173 | -0.34958 | 1.3776
47 | 0.0022517 | 0.00056414 | -0.0022517 | -0.00056419 | 2.5459e-08 | -5.7403e-08 | 0.0034129 | 0.0034129 | 0.0034129 | 0.98173 | -0.34958 | 0.98171 | -0.34982 | 0.93761
48 | 0.0011486 | 0.00028774 | -0.0011486 | -0.00028786 | 1.2332e-08 | -1.2929e-07 | 0.0017409 | 0.001741 | 0.001741 | 0.98171 | -0.34982 | 0.9817 | -0.35004 | 0.47829
49 | -0.080618 | -0.02048 | 0.080704 | 0.020532 | 8.6363e-05 | 5.2047e-05 | 0.12127 | 0.12127 | 0.12127 | 0.98998 | -0.18988 | 0.99114 | -0.16766 | 8.3292
50 | 0.005158 | 0.0012909 | -0.0051576 | -0.0012908 | 3.972e-07 | 3.959e-08 | 0.0078581 | 0.0078582 | 0.0078582 | 0.97663 | -0.44936 | 0.97655 | -0.45098 | 2.1589
51 | 0.0011349 | 0.00028282 | -0.0011349 | -0.00028314 | 2.994e-08 | -3.1517e-07 | 0.0017286 | 0.0017287 | 0.0017287 | 0.97663 | -0.44936 | 0.9766 | -0.44992 | 0.47492
52 | 0.0044058 | 0.0011024 | -0.0044057 | -0.0011024 | 6.3418e-08 | -6.367e-09 | 0.0067127 | 0.0067127 | 0.0067127 | 0.97655 | -0.45098 | 0.97653 | -0.45129 | 1.8441
53 | 0.0011349 | 0.00028314 | -0.0011347 | -0.00028439 | 1.1949e-07 | -1.2572e-06 | 0.0017287 | 0.0017292 | 0.0017292 | 0.9766 | -0.44992 | 0.97649 | -0.45213 | 0.47505
54 | -0.080704 | -0.020532 | 0.080732 | 0.020549 | 2.7789e-05 | 1.6745e-05 | 0.12127 | 0.12127 | 0.12127 | 0.99114 | -0.16766 | 0.99151 | -0.16051 | 8.3292
55 | -0.43772 | -0.11205 | 0.44054 | 0.11385 | 0.0028242 | 0.0018039 | 0.65775 | 0.65774 | 0.65775 | 0.99151 | -0.16051 | 0.9985 | -0.028209 | 45.1748
56 | 0.35698 | 0.091498 | -0.35486 | -0.090141 | 0.0021271 | 0.0013573 | 0.53647 | 0.53647 | 0.53647 | 0.99151 | -0.16051 | 0.98506 | -0.28423 | 36.8458
57 | 0.46877 | 0.12118 | -0.46812 | -0.12076 | 0.0006444 | 0.00041168 | 0.69885 | 0.69885 | 0.69885 | 1 | 0 | 0.9985 | -0.028209 | 47.9976
58 | 0.35329 | 0.089747 | -0.35243 | -0.089198 | 0.00086025 | 0.00054892 | 0.5341 | 0.5341 | 0.5341 | 0.98506 | -0.28423 | 0.98244 | -0.33495 | 36.6829
59 | 0.058638 | 0.014761 | -0.058631 | -0.014756 | 6.9489e-06 | 4.4175e-06 | 0.088837 | 0.088837 | 0.088837 | 0.98244 | -0.33495 | 0.98231 | -0.33743 | 24.4057
60 | 0.16552 | 0.041884 | -0.16532 | -0.041763 | 0.00019119 | 0.00012072 | 0.25084 | 0.25084 | 0.25084 | 0.98244 | -0.33495 | 0.9812 | -0.35905 | 17.2279
61 | 0.12827 | 0.032554 | -0.12807 | -0.032427 | 0.00020213 | 0.00012648 | 0.19443 | 0.19443 | 0.19443 | 0.98244 | -0.33495 | 0.98075 | -0.36777 | 13.3537
62 | 0.11286 | 0.028541 | -0.11284 | -0.02853 | 1.8488e-05 | 1.1495e-05 | 0.17164 | 0.17164 | 0.17164 | 0.97901 | -0.40168 | 0.97883 | -0.40509 | 11.7882
63 | -0.12037 | -0.030422 | 0.12045 | 0.030472 | 7.9731e-05 | 4.975e-05 | 0.18304 | 0.18304 | 0.18304 | 0.97901 | -0.40168 | 0.97971 | -0.38787 | 12.5716
64 | 0.10878 | 0.027511 | -0.10871 | -0.027467 | 7.1412e-05 | 4.4306e-05 | 0.16546 | 0.16546 | 0.16546 | 0.97883 | -0.40509 | 0.97813 | -0.41879 | 11.3638
65 | -0.12387 | -0.031329 | 0.12399 | 0.031404 | 0.00011962 | 7.4738e-05 | 0.18823 | 0.18823 | 0.18823 | 0.97971 | -0.38787 | 0.98075 | -0.36777 | 12.9281
66 | 0.1037 | 0.026211 | -0.10368 | -0.026198 | 2.0611e-05 | 1.2748e-05 | 0.15783 | 0.15783 | 0.15783 | 0.97813 | -0.41879 | 0.97792 | -0.42293 | 10.8402
67 | 0.10267 | 0.025945 | -0.10263 | -0.02592 | 4.0719e-05 | 2.5168e-05 | 0.1563 | 0.1563 | 0.1563 | 0.97792 | -0.42293 | 0.97749 | -0.43121 | 10.7347
68 | 0.10162 | 0.025669 | -0.10158 | -0.025642 | 4.2452e-05 | 2.6222e-05 | 0.15477 | 0.15477 | 0.15477 | 0.97749 | -0.43121 | 0.97705 | -0.43993 | 10.6299
69 | 0.0031506 | 0.00078893 | -0.00315 | -0.00078947 | 6.3279e-07 | -5.3267e-07 | 0.0047724 | 0.0047727 | 0.0047727 | 0.98231 | -0.33743 | 0.9821 | -0.34165 | 1.3112
70 | 0.05548 | 0.013967 | -0.05542 | -0.013929 | 6.0203e-05 | 3.8243e-05 | 0.084064 | 0.084064 | 0.084064 | 0.98231 | -0.33743 | 0.98115 | -0.36016 | 23.0946
71 | 0.16422 | 0.041486 | -0.16411 | -0.041416 | 0.00011117 | 7.0184e-05 | 0.24916 | 0.24916 | 0.24916 | 0.9812 | -0.35905 | 0.98047 | -0.37318 | 17.1126
72 | 0.092933 | 0.023475 | -0.092703 | -0.023333 | 0.00023048 | 0.00014138 | 0.1416 | 0.1416 | 0.1416 | 0.97705 | -0.43993 | 0.9744 | -0.49181 | 9.7255
73 | 0.0086479 | 0.0021676 | -0.0086461 | -0.0021668 | 1.8275e-06 | 8.1785e-07 | 0.013171 | 0.013171 | 0.013171 | 0.97705 | -0.43993 | 0.97682 | -0.44437 | 3.6183
74 | 0.049234 | 0.012379 | -0.049211 | -0.012364 | 2.2741e-05 | 1.4417e-05 | 0.074683 | 0.074683 | 0.074683 | 0.98115 | -0.36016 | 0.98065 | -0.36983 | 20.5174
75 | 0.097023 | 0.02447 | -0.096957 | -0.024429 | 6.6096e-05 | 4.0663e-05 | 0.1473 | 0.1473 | 0.1473 | 0.98047 | -0.37318 | 0.97974 | -0.38742 | 10.1169
76 | 0.067084 | 0.016946 | -0.067054 | -0.016927 | 2.9496e-05 | 1.8782e-05 | 0.10186 | 0.10186 | 0.10186 | 0.98047 | -0.37318 | 0.98 | -0.38236 | 27.9828
77 | 0.0057537 | 0.0014418 | -0.0057523 | -0.0014416 | 1.3656e-06 | 2.8073e-07 | 0.0087646 | 0.0087648 | 0.0087648 | 0.97682 | -0.44437 | 0.97657 | -0.44935 | 2.4079
78 | 0.0057523 | 0.0014416 | -0.005751 | -0.0014413 | 1.2709e-06 | 2.6157e-07 | 0.0087648 | 0.008765 | 0.008765 | 0.97657 | -0.44935 | 0.97633 | -0.45399 | 2.408
79 | 0.005751 | 0.0014413 | -0.0057501 | -0.0014411 | 9.3356e-07 | 1.9232e-07 | 0.008765 | 0.0087652 | 0.0087652 | 0.97633 | -0.45399 | 0.97616 | -0.4574 | 2.408
80 | 0.092703 | 0.023333 | -0.09258 | -0.023258 | 0.00012223 | 7.4991e-05 | 0.1416 | 0.1416 | 0.1416 | 0.9744 | -0.49181 | 0.973 | -0.51944 | 9.7255
81 | 0.085433 | 0.021467 | -0.085298 | -0.021385 | 0.00013445 | 8.1883e-05 | 0.13067 | 0.13067 | 0.13067 | 0.973 | -0.51944 | 0.97133 | -0.55246 | 8.9749
82 | 0.038762 | 0.0097128 | -0.03876 | -0.0097116 | 2.4429e-06 | 1.1976e-06 | 0.05938 | 0.059381 | 0.059381 | 0.97133 | -0.55246 | 0.97126 | -0.55379 | 4.0783
83 | 0.046536 | 0.011672 | -0.046516 | -0.011661 | 2.0507e-05 | 1.0995e-05 | 0.071294 | 0.071295 | 0.071295 | 0.97133 | -0.55246 | 0.97086 | -0.56171 | 4.8966
84 | -0.014459 | -0.0036242 | 0.01446 | 0.0036236 | 1.3961e-06 | -6.0512e-07 | 0.022166 | 0.022166 | 0.022166 | 0.97063 | -0.5662 | 0.97074 | -0.56418 | 1.5224
85 | 0.011935 | 0.0029917 | -0.011933 | -0.0029912 | 2.0083e-06 | 4.9463e-07 | 0.018298 | 0.018298 | 0.018298 | 0.97063 | -0.5662 | 0.97046 | -0.56973 | 2.5135
86 | -0.024858 | -0.0062295 | 0.024861 | 0.0062303 | 2.9184e-06 | 8.0738e-07 | 0.038104 | 0.038104 | 0.038104 | 0.97074 | -0.56418 | 0.97086 | -0.56171 | 2.617
87 | 0.0098239 | 0.0024625 | -0.0098224 | -0.0024618 | 1.5799e-06 | 7.8177e-07 | 0.015063 | 0.015063 | 0.015063 | 0.97046 | -0.56973 | 0.97028 | -0.57311 | 4.1383
88 | 0.021655 | 0.0054312 | -0.021644 | -0.0054246 | 1.0741e-05 | 6.553e-06 | 0.033192 | 0.033192 | 0.033192 | 0.97086 | -0.56171 | 0.97033 | -0.57212 | 9.1186
89 | 0.0074619 | 0.0018702 | -0.0074617 | -0.0018701 | 2.571e-07 | 9.9884e-08 | 0.011443 | 0.011444 | 0.011444 | 0.97028 | -0.57311 | 0.97025 | -0.57383 | 3.1438
90 | 0.0086976 | 0.0021799 | -0.0086972 | -0.0021797 | 4.1346e-07 | 1.8806e-07 | 0.013338 | 0.013338 | 0.013338 | 0.97033 | -0.57212 | 0.97028 | -0.57312 | 3.6642
91 | 0.025863 | 0.0064794 | -0.025858 | -0.0064778 | 5.3109e-06 | 1.6131e-06 | 0.039622 | 0.039623 | 0.039623 | 0.97126 | -0.55379 | 0.97104 | -0.5581 | 2.7214
92 | 0.019453 | 0.0048727 | -0.019451 | -0.0048726 | 2.5689e-06 | 1.1843e-07 | 0.029809 | 0.029809 | 0.029809 | 0.97104 | -0.5581 | 0.9709 | -0.56087 | 2.0474
93 | 0.019451 | 0.0048726 | -0.019446 | -0.0048724 | 4.4071e-06 | 2.0433e-07 | 0.029809 | 0.02981 | 0.02981 | 0.9709 | -0.56087 | 0.97066 | -0.56563 | 2.0474
94 | 0.019446 | 0.0048724 | -0.01944 | -0.0048721 | 5.7492e-06 | 2.6874e-07 | 0.02981 | 0.029812 | 0.029812 | 0.97066 | -0.56563 | 0.97035 | -0.57184 | 2.0475
95 | 0.011256 | 0.0028209 | -0.011255 | -0.0028207 | 1.2985e-06 | 2.5686e-07 | 0.017261 | 0.017261 | 0.017261 | 0.97035 | -0.57184 | 0.97023 | -0.57426 | 2.371
96 | 0.0027074 | 0.0006785 | -0.0027074 | -0.00067853 | 2.5163e-08 | -3.1959e-08 | 0.0041523 | 0.0041523 | 0.0041523 | 0.97023 | -0.57426 | 0.97022 | -0.57445 | 1.1407
97 | -0.0021277 | -0.00053325 | 0.0021278 | 0.00053295 | 1.2114e-07 | -3.0042e-07 | 0.0032561 | 0.003256 | 0.0032561 | 0.97233 | -0.53307 | 0.97239 | -0.53187 | 0.89454
98 | -0.0071152 | -0.0017829 | 0.0071161 | 0.0017832 | 8.8215e-07 | 3.1839e-07 | 0.010888 | 0.010888 | 0.010888 | 0.97239 | -0.53187 | 0.97252 | -0.52927 | 2.9912
99 | -0.011596 | -0.002906 | 0.011597 | 0.0029064 | 7.9251e-07 | 4.239e-07 | 0.017742 | 0.017742 | 0.017742 | 0.97252 | -0.52927 | 0.9726 | -0.52783 | 4.8743
100 | -0.013766 | -0.00345 | 0.013771 | 0.0034528 | 5.0456e-06 | 2.8526e-06 | 0.021061 | 0.021061 | 0.021061 | 0.9726 | -0.52783 | 0.97299 | -0.52014 | 5.786
101 | 0.0021692 | 0.00054355 | -0.0021692 | -0.00054364 | 3.9319e-08 | -9.2974e-08 | 0.0033187 | 0.0033188 | 0.0033188 | 0.9726 | -0.52783 | 0.97258 | -0.52821 | 0.91175
102 | -0.016874 | -0.0042304 | 0.016884 | 0.0042363 | 9.9385e-06 | 5.866e-06 | 0.025806 | 0.025806 | 0.025806 | 0.97299 | -0.52014 | 0.97361 | -0.50779 | 7.0896
103 | -0.019386 | -0.0048634 | 0.019393 | 0.0048675 | 6.8802e-06 | 4.1434e-06 | 0.02963 | 0.02963 | 0.02963 | 0.97361 | -0.50779 | 0.97399 | -0.50035 | 8.1401
104 | -0.026005 | -0.0065248 | 0.026016 | 0.0065313 | 1.0509e-05 | 6.5046e-06 | 0.039732 | 0.039732 | 0.039732 | 0.97399 | -0.50035 | 0.97442 | -0.49188 | 10.9154
105 | -0.0020017 | -0.00050167 | 0.0020017 | 0.00050149 | 6.1284e-08 | -1.7813e-07 | 0.0030586 | 0.0030585 | 0.0030586 | 0.97382 | -0.50373 | 0.97385 | -0.50309 | 0.84027
106 | 0.023912 | 0.0060023 | -0.023902 | -0.0059967 | 9.1892e-06 | 5.6528e-06 | 0.03654 | 0.03654 | 0.03654 | 0.97385 | -0.50309 | 0.97344 | -0.51115 | 10.0384
107 | -0.025913 | -0.0065038 | 0.025932 | 0.0065152 | 1.836e-05 | 1.1361e-05 | 0.039598 | 0.039598 | 0.039598 | 0.97385 | -0.50309 | 0.97461 | -0.48824 | 10.8786
108 | -0.03263 | -0.008189 | 0.032659 | 0.008207 | 2.8621e-05 | 1.7935e-05 | 0.049833 | 0.049833 | 0.049833 | 0.97442 | -0.49188 | 0.97535 | -0.4735 | 13.6904
109 | 0.020562 | 0.0051595 | -0.02055 | -0.005152 | 1.2304e-05 | 7.4617e-06 | 0.031433 | 0.031434 | 0.031434 | 0.97344 | -0.51115 | 0.97281 | -0.52371 | 8.6356
110 | -0.027643 | -0.006944 | 0.027644 | 0.0069447 | 1.1161e-06 | 6.9349e-07 | 0.04221 | 0.04221 | 0.04221 | 0.97461 | -0.48824 | 0.97465 | -0.4874 | 11.5963
111 | -0.037663 | -0.0094612 | 0.037689 | 0.0094774 | 2.5769e-05 | 1.6232e-05 | 0.057468 | 0.057467 | 0.057468 | 0.97535 | -0.4735 | 0.97608 | -0.45917 | 15.7878
112 | -0.06083 | -0.015277 | 0.060851 | 0.015291 | 2.1769e-05 | 1.3848e-05 | 0.092745 | 0.092745 | 0.092745 | 0.97608 | -0.45917 | 0.97646 | -0.45168 | 25.4794
113 | -0.0629 | -0.015804 | 0.063001 | 0.015869 | 0.00010124 | 6.4425e-05 | 0.095867 | 0.095866 | 0.095867 | 0.97646 | -0.45168 | 0.97818 | -0.41801 | 26.337
114 | -0.065035 | -0.016378 | 0.065146 | 0.016449 | 0.00011108 | 7.0712e-05 | 0.09896 | 0.09896 | 0.09896 | 0.97818 | -0.41801 | 0.98 | -0.38236 | 27.1869
115 | 0.094107 | 0.023715 | -0.094008 | -0.023652 | 9.8953e-05 | 6.2681e-05 | 0.14297 | 0.14297 | 0.14297 | 0.97974 | -0.38742 | 0.97862 | -0.40943 | 19.6393
116 | 0.071635 | 0.018045 | -0.071531 | -0.017979 | 0.00010437 | 6.562e-05 | 0.10896 | 0.10896 | 0.10896 | 0.97862 | -0.40943 | 0.97706 | -0.43994 | 14.9665
117 | 0.052616 | 0.013239 | -0.052566 | -0.013207 | 5.0433e-05 | 3.2015e-05 | 0.080151 | 0.080151 | 0.080151 | 0.97706 | -0.43994 | 0.97604 | -0.46002 | 22.0194
118 | 0.037931 | 0.009539 | -0.037926 | -0.009536 | 4.8778e-06 | 3.0732e-06 | 0.05784 | 0.05784 | 0.05784 | 0.97604 | -0.46002 | 0.9759 | -0.46271 | 15.89
119 | 0.033732 | 0.0084847 | -0.033711 | -0.0084714 | 2.124e-05 | 1.3326e-05 | 0.051444 | 0.051444 | 0.051444 | 0.9759 | -0.46271 | 0.97523 | -0.4759 | 14.133
120 | 0.030346 | 0.0076281 | -0.030329 | -0.0076177 | 1.6646e-05 | 1.0395e-05 | 0.04631 | 0.04631 | 0.04631 | 0.97523 | -0.4759 | 0.97465 | -0.4874 | 12.7226
121 | 0.045745 | 0.011496 | -0.045705 | -0.01147 | 4.0773e-05 | 2.581e-05 | 0.069424 | 0.069424 | 0.069424 | 0.98065 | -0.36983 | 0.9797 | -0.38852 | 19.0725
122 | 0.040377 | 0.010134 | -0.040373 | -0.010132 | 4.1464e-06 | 2.6167e-06 | 0.061332 | 0.061332 | 0.061332 | 0.9797 | -0.38852 | 0.97959 | -0.39068 | 16.8494
123 | 0.018009 | 0.0045154 | -0.018009 | -0.0045153 | 4.1671e-08 | 2.4852e-08 | 0.027548 | 0.027548 | 0.027548 | 0.97281 | -0.52371 | 0.9728 | -0.52376 | 7.5682
124 | 0.013808 | 0.0034624 | -0.013803 | -0.0034594 | 5.3158e-06 | 3.0078e-06 | 0.021122 | 0.021122 | 0.021122 | 0.9728 | -0.52376 | 0.9724 | -0.53184 | 5.8027
125 | 0.010582 | 0.0026521 | -0.010581 | -0.0026519 | 4.5912e-07 | 2.3592e-07 | 0.016193 | 0.016193 | 0.016193 | 0.9724 | -0.53184 | 0.97235 | -0.53275 | 4.4486
126 | 0.038527 | 0.0096693 | -0.038513 | -0.0096608 | 1.3461e-05 | 8.4833e-06 | 0.058528 | 0.058528 | 0.058528 | 0.97959 | -0.39068 | 0.97921 | -0.39801 | 16.0792
127 | 0.034012 | 0.0085325 | -0.034008 | -0.0085306 | 3.0944e-06 | 1.9416e-06 | 0.051687 | 0.051687 | 0.051687 | 0.97921 | -0.39801 | 0.97912 | -0.39991 | 14.1997
128 | 0.029285 | 0.0073469 | -0.029278 | -0.0073421 | 7.6288e-06 | 4.7533e-06 | 0.044509 | 0.044509 | 0.044509 | 0.97912 | -0.39991 | 0.97884 | -0.40538 | 12.2278
129 | 0.026478 | 0.0066403 | -0.026475 | -0.0066387 | 2.5091e-06 | 1.554e-06 | 0.040252 | 0.040252 | 0.040252 | 0.97884 | -0.40538 | 0.97874 | -0.40737 | 11.0584
130 | 0.025267 | 0.006336 | -0.02526 | -0.0063313 | 7.7012e-06 | 4.754e-06 | 0.038416 | 0.038416 | 0.038416 | 0.97874 | -0.40737 | 0.97841 | -0.41376 | 10.5539
131 | 0.022128 | 0.0055464 | -0.022128 | -0.0055463 | 1.3035e-07 | 7.9569e-08 | 0.033653 | 0.033653 | 0.033653 | 0.97841 | -0.41376 | 0.97841 | -0.41389 | 9.2454
132 | 0.016824 | 0.004217 | -0.016822 | -0.0042158 | 2.1317e-06 | 1.2553e-06 | 0.025587 | 0.025587 | 0.025587 | 0.97841 | -0.41389 | 0.97827 | -0.41655 | 7.0294
133 | 0.011608 | 0.002909 | -0.011607 | -0.0029088 | 3.7174e-07 | 1.9799e-07 | 0.017656 | 0.017656 | 0.017656 | 0.97827 | -0.41655 | 0.97824 | -0.41722 | 4.8506
134 | 0.0076205 | 0.0019096 | -0.0076197 | -0.0019093 | 8.3149e-07 | 3.2501e-07 | 0.011592 | 0.011592 | 0.011592 | 0.97824 | -0.41722 | 0.97812 | -0.41951 | 3.1845
135 | 0.0044033 | 0.0011032 | -0.0044033 | -0.0011032 | 5.2309e-08 | -5.5392e-09 | 0.0066987 | 0.0066987 | 0.0066987 | 0.97812 | -0.41951 | 0.97811 | -0.41976 | 1.8403
136 | 0.0044033 | 0.0011032 | -0.0044023 | -0.0011033 | 9.5767e-07 | -1.012e-07 | 0.0066987 | 0.006699 | 0.006699 | 0.97811 | -0.41976 | 0.97787 | -0.42433 | 1.8404
137 | 0.0044057 | 0.0011024 | -0.0044038 | -0.0011026 | 1.9549e-06 | -1.9543e-07 | 0.0067127 | 0.0067132 | 0.0067132 | 0.97653 | -0.45129 | 0.97606 | -0.46061 | 1.8443
138 | 0.0015982 | 0.00040016 | -0.0015981 | -0.00040029 | 2.6204e-08 | -1.3037e-07 | 0.0024363 | 0.0024363 | 0.0024363 | 0.97606 | -0.46061 | 0.97604 | -0.46095 | 0.66932
139 | 0.0028056 | 0.00070247 | -0.0028055 | -0.00070255 | 7.2705e-08 | -8.5937e-08 | 0.0042769 | 0.004277 | 0.004277 | 0.97606 | -0.46061 | 0.97603 | -0.46115 | 1.175
140 | 0.0013578 | 0.00034006 | -0.0013578 | -0.00034008 | 2.7819e-09 | -1.9858e-08 | 0.0020699 | 0.00207 | 0.00207 | 0.97604 | -0.46095 | 0.97604 | -0.461 | 0.56867
141 | 0.0023957 | 0.00059985 | -0.0023957 | -0.00059998 | 7.0833e-08 | -1.3164e-07 | 0.0036522 | 0.0036523 | 0.0036523 | 0.97603 | -0.46115 | 0.976 | -0.46178 | 1.0034
142 | 0.00016368 | 4.0799e-05 | -0.00016368 | -4.1021e-05 | 4.1493e-10 | -2.2189e-07 | 0.00024945 | 0.00024953 | 0.00024953 | 0.97604 | -0.461 | 0.97604 | -0.46105 | 0.068553
143 | 0.0014417 | 0.0003609 | -0.0014417 | -0.00036093 | 5.0522e-09 | -3.1619e-08 | 0.0021979 | 0.0021979 | 0.0021979 | 0.976 | -0.46178 | 0.976 | -0.46185 | 0.60383
144 | 0.0010378 | 0.0002597 | -0.0010378 | -0.00025981 | 8.157e-09 | -1.0337e-07 | 0.0015821 | 0.0015822 | 0.0015822 | 0.976 | -0.46185 | 0.97599 | -0.46201 | 0.43466
145 | 0.00063443 | 0.00015871 | -0.00063442 | -0.000159 | 8.2889e-09 | -2.8996e-07 | 0.00096716 | 0.00096727 | 0.00096727 | 0.97599 | -0.46201 | 0.97597 | -0.46229 | 0.26573
146 | 0.0069601 | 0.0017443 | -0.0069592 | -0.001744 | 8.8327e-07 | 3.0781e-07 | 0.010651 | 0.010651 | 0.010651 | 0.97235 | -0.53275 | 0.97222 | -0.53541 | 2.9262
147 | 0.0042588 | 0.0010672 | -0.0042586 | -0.0010673 | 2.304e-07 | -3.1849e-08 | 0.0065183 | 0.0065183 | 0.0065183 | 0.97222 | -0.53541 | 0.97216 | -0.53655 | 1.7908
148 | 0.001151 | 0.00028843 | -0.001151 | -0.00028846 | 3.0425e-09 | -3.0464e-08 | 0.0017617 | 0.0017617 | 0.0017617 | 0.97216 | -0.53655 | 0.97215 | -0.5366 | 0.48399

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48526 | 0.12489

## res_load
| p_mw | q_mvar
0 | 0.001123 | 0.00028145
1 | 0.0040789 | 0.0010223
2 | 0.011137 | 0.0027913
3 | 0.0038139 | 0.00095587
4 | 0.0047591 | 0.0011927
5 | 0.00030604 | 7.6702e-05
6 | 0.00016806 | 4.2121e-05
7 | 0.00096277 | 0.00024129
8 | 0.0098242 | 0.0024622
9 | 8.866e-05 | 2.222e-05
10 | 0.0009618 | 0.00024105
11 | 3.971e-05 | 9.9524e-06
12 | 0.00055408 | 0.00013887
13 | 0.00022415 | 5.6177e-05
14 | 0.0015866 | 0.00039763
15 | 0.0034617 | 0.00086759
16 | 0.010584 | 0.0026526
17 | 0.00092654 | 0.00023221
18 | 0.0015867 | 0.00039767
19 | 0.00035774 | 8.9658e-05
20 | 0.00065478 | 0.0001641
21 | 0.0013213 | 0.00033115
22 | 0.0020872 | 0.00052309
23 | 0.0010567 | 0.00026484
24 | 0.0011031 | 0.00027646
25 | 0.0011486 | 0.00028786
26 | 0.00064177 | 0.00016084
27 | 0.00075179 | 0.00018842
28 | 0.0011347 | 0.00028439
29 | 0.014842 | 0.0037196
30 | 0.027581 | 0.0069124
31 | 0.0015708 | 0.00039367
32 | 0.0075049 | 0.0018809
33 | 0.004065 | 0.0010188
34 | 0.0034184 | 0.00085673
35 | 0.0050114 | 0.001256
36 | 0.0040844 | 0.0010236
37 | 0.0010097 | 0.00025305
38 | 0.0010025 | 0.00025124
39 | 0.0011071 | 0.00027746
40 | 0.00315 | 0.00078947
41 | 0.0061856 | 0.0015503
42 | 0.0028924 | 0.00072491
43 | 0.0057501 | 0.0014411
44 | 0.0071474 | 0.0017913
45 | 0.0025235 | 0.00063245
46 | 0.010398 | 0.0026059
47 | 0.0021095 | 0.00052869
48 | 0.0023605 | 0.00059158
49 | 0.012947 | 0.0032447
50 | 0.0074617 | 0.0018701
51 | 0.012897 | 0.0032322
52 | 0.0086972 | 0.0021797
53 | 0.0064045 | 0.0016051
54 | 0.0081844 | 0.0020512
55 | 0.0085474 | 0.0021422
56 | 0.0027074 | 0.00067853
57 | 0.0021277 | 0.00053325
58 | 0.0049874 | 0.00125
59 | 0.0044799 | 0.0011228
60 | 0.0031027 | 0.0007776
61 | 0.0021692 | 0.00054364
62 | 0.002502 | 0.00062707
63 | 0.0066125 | 0.0016573
64 | 0.0020017 | 0.00050167
65 | 0.0066145 | 0.0016578
66 | 0.0033406 | 0.00083722
67 | 0.001711 | 0.00042881
68 | 0.0050044 | 0.0012542
69 | 0.023141 | 0.0057996
70 | 0.0020484 | 0.00051339
71 | 0.0020338 | 0.00050973
72 | 0.0019081 | 0.00047822
73 | 0.0028503 | 0.00071436
74 | 0.022373 | 0.0056071
75 | 0.018914 | 0.0047404
76 | 0.014635 | 0.0036678
77 | 0.0041945 | 0.0010513
78 | 0.0033647 | 0.00084327
79 | 0.0034661 | 0.00086868
80 | 0.0053279 | 0.0013353
81 | 0.0026854 | 0.00067303
82 | 0.0025401 | 0.00063662
83 | 0.0042014 | 0.001053
84 | 0.0032209 | 0.00080724
85 | 0.0018457 | 0.00046257
86 | 0.0045019 | 0.0011283
87 | 0.004723 | 0.0011837
88 | 0.0028003 | 0.00070182
89 | 0.0012077 | 0.00030269
90 | 0.0031319 | 0.00078493
91 | 0.0053038 | 0.0013293
92 | 0.005214 | 0.0013067
93 | 0.0039868 | 0.00099918
94 | 0.0032164 | 0.0008061
95 | 0.0044023 | 0.0011033
96 | 0.008616 | 0.0021594
97 | 9.5009e-05 | 2.3812e-05
98 | 0.00019508 | 4.8893e-05
99 | 0.00024032 | 6.0229e-05
100 | 0.00040979 | 0.0001027
101 | 0.0011941 | 0.00029928
102 | 0.00095395 | 0.00023908
103 | 0.00016368 | 4.1021e-05
104 | 0.00040391 | 0.00010123
105 | 0.00040338 | 0.0001011
106 | 0.00063442 | 0.000159
107 | 0.0036212 | 0.00090756
108 | 0.0027004 | 0.00067678
109 | 0.0031076 | 0.00077884
110 | 0.001151 | 0.00028846

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1