## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_158-24_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_158-24_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_158-24_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_158-24_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_158-24_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_158-24_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_158-24_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_158-24_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_158-24_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_158-24_0_4_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_158-24_0_4_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_158-24_0_4_node_108 | 0.4 | n |  | TRUE
12 | bus_LV_158-24_0_4_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_158-24_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_158-24_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_158-24_0_4_node_153 | 0.4 | n |  | TRUE
16 | bus_LV_158-24_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_158-24_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_158-24_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_158-24_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_158-24_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_158-24_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_158-24_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_158-24_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_158-24_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_158-24_0_4_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_158-24_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_158-24_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_158-24_0_4_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_158-24_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_158-24_0_4_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_158-24_0_4_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_158-24_0_4_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_158-24_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_158-24_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_158-24_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_158-24_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_158-24_0_4_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_158-24_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_158-24_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_158-24_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_158-24_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_158-24_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_158-24_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_158-24_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_158-24_0_4_node_150 | 0.4 | n |  | TRUE
46 | bus_LV_158-24_0_4_node_61 | 0.4 | n |  | TRUE
47 | bus_LV_158-24_0_4_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_158-24_0_4_node_151 | 0.4 | n |  | TRUE
49 | bus_LV_158-24_0_4_node_136 | 0.4 | n |  | TRUE
50 | bus_LV_158-24_0_4_node_134 | 0.4 | n |  | TRUE
51 | bus_LV_158-24_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_158-24_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_158-24_0_4_node_161 | 0.4 | n |  | TRUE
54 | bus_LV_158-24_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_158-24_0_4_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_158-24_0_4_node_87 | 0.4 | n |  | TRUE
57 | bus_LV_158-24_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_158-24_0_4_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_158-24_0_4_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_158-24_0_4_node_65 | 0.4 | n |  | TRUE
61 | bus_LV_158-24_0_4_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_158-24_0_4_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_158-24_0_4_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_158-24_0_4_node_86 | 0.4 | n |  | TRUE
65 | bus_LV_158-24_0_4_node_135 | 0.4 | n |  | TRUE
66 | bus_LV_158-24_0_4_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_158-24_0_4_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_158-24_0_4_node_154 | 0.4 | n |  | TRUE
69 | bus_LV_158-24_0_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_158-24_0_4_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_158-24_0_4_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_158-24_0_4_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_158-24_0_4_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_158-24_0_4_node_96 | 0.4 | n |  | TRUE
75 | bus_LV_158-24_0_4_node_147 | 0.4 | n |  | TRUE
76 | bus_LV_158-24_0_4_node_152 | 0.4 | n |  | TRUE
77 | bus_LV_158-24_0_4_node_99 | 0.4 | n |  | TRUE
78 | bus_LV_158-24_0_4_node_94 | 0.4 | n |  | TRUE
79 | bus_LV_158-24_0_4_node_148 | 0.4 | n |  | TRUE
80 | bus_LV_158-24_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_158-24_0_4_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_158-24_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_158-24_0_4_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_158-24_0_4_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_158-24_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_158-24_0_4_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_158-24_0_4_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_158-24_0_4_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_158-24_0_4_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_158-24_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_158-24_0_4_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_158-24_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_158-24_0_4_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_158-24_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_158-24_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_158-24_0_4_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_158-24_0_4_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_158-24_0_4_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_158-24_0_4_node_145 | 0.4 | n |  | TRUE
100 | bus_LV_158-24_0_4_node_144 | 0.4 | n |  | TRUE
101 | bus_LV_158-24_0_4_node_146 | 0.4 | n |  | TRUE
102 | bus_LV_158-24_0_4_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_158-24_0_4_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_158-24_0_4_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_158-24_0_4_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_158-24_0_4_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_158-24_0_4_node_137 | 0.4 | n |  | TRUE
108 | bus_LV_158-24_0_4_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_158-24_0_4_node_155 | 0.4 | n |  | TRUE
110 | bus_LV_158-24_0_4_node_133 | 0.4 | n |  | TRUE
111 | bus_LV_158-24_0_4_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_158-24_0_4_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_158-24_0_4_node_139 | 0.4 | n |  | TRUE
114 | bus_LV_158-24_0_4_node_156 | 0.4 | n |  | TRUE
115 | bus_LV_158-24_0_4_node_124 | 0.4 | n |  | TRUE
116 | bus_LV_158-24_0_4_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_158-24_0_4_node_126 | 0.4 | n |  | TRUE
118 | bus_LV_158-24_0_4_node_123 | 0.4 | n |  | TRUE
119 | bus_LV_158-24_0_4_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_158-24_0_4_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_158-24_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_158-24_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_158-24_0_4_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_158-24_0_4_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_158-24_0_4_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_158-24_0_4_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_158-24_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_158-24_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_158-24_0_4_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_158-24_0_4_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_158-24_0_4_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_158-24_0_4_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_158-24_0_4_node_160 | 0.4 | n |  | TRUE
134 | bus_LV_158-24_0_4_node_158 | 0.4 | n |  | TRUE
135 | bus_LV_158-24_0_4_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_158-24_0_4_node_157 | 0.4 | n |  | TRUE
137 | bus_LV_158-24_0_4_node_121 | 0.4 | n |  | TRUE
138 | bus_LV_158-24_0_4_node_122 | 0.4 | n |  | TRUE
139 | bus_LV_158-24_0_4_node_127 | 0.4 | n |  | TRUE
140 | bus_LV_158-24_0_4_node_125 | 0.4 | n |  | TRUE
141 | bus_LV_158-24_0_4_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_158-24_0_4_node_129 | 0.4 | n |  | TRUE
143 | bus_LV_158-24_0_4_node_130 | 0.4 | n |  | TRUE
144 | bus_LV_158-24_0_4_node_131 | 0.4 | n |  | TRUE
145 | bus_LV_158-24_0_4_node_132 | 0.4 | n |  | TRUE
146 | bus_LV_158-24_0_4_node_140 | 0.4 | n |  | TRUE
147 | bus_LV_158-24_0_4_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_158-24_0_4_node_138 | 0.4 | n |  | TRUE
149 | bus_LV_158-24_0_4_node_141 | 0.4 | n |  | TRUE
150 | bus_LV_158-24_0_4_node_143 | 0.4 | n |  | TRUE
151 | bus_LV_158-24_0_4_node_149 | 0.4 | n |  | TRUE
152 | bus_LV_158-24_0_4_node_159 | 0.4 | n |  | TRUE
153 | bus_MV_361_1_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_158-24_0_4_load_0 | 0 | 0.0029643 | 0.00074294 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_158-24_0_4_load_3 | 3 | 0.0081349 | 0.0020388 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_158-24_0_4_load_4 | 4 | 0.0085379 | 0.0021398 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_158-24_0_4_load_5 | 5 | 0.0024647 | 0.00061772 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_158-24_0_4_load_9 | 7 | 0.0024661 | 0.00061806 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_158-24_0_4_load_108 | 11 | 0.0034074 | 0.00085396 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_158-24_0_4_load_21 | 13 | 0.0056158 | 0.0014074 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_158-24_0_4_load_153 | 15 | 0.0074196 | 0.0018595 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_158-24_0_4_load_10 | 16 | 0.0060531 | 0.001517 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_158-24_0_4_load_11 | 17 | 0.00091119 | 0.00022837 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_158-24_0_4_load_12 | 18 | 0.00070384 | 0.0001764 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_158-24_0_4_load_13 | 19 | 0.0024863 | 0.00062313 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_158-24_0_4_load_17 | 20 | 0.0027692 | 0.00069403 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_158-24_0_4_load_16 | 21 | 0.0027783 | 0.00069631 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_158-24_0_4_load_25 | 26 | 0.0056446 | 0.0014147 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_158-24_0_4_load_23 | 27 | 0.0045783 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_158-24_0_4_load_54 | 28 | 0.0039434 | 0.00098832 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_158-24_0_4_load_56 | 30 | 0.013169 | 0.0033005 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_158-24_0_4_load_55 | 31 | 0.0065752 | 0.0016479 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_158-24_0_4_load_41 | 32 | 0.0081927 | 0.0020533 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_158-24_0_4_load_31 | 34 | 0.0019921 | 0.00049926 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_158-24_0_4_load_28 | 38 | 0.005059 | 0.0012679 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_158-24_0_4_load_29 | 39 | 0.0048594 | 0.0012179 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_158-24_0_4_load_35 | 40 | 0.0053417 | 0.0013388 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_158-24_0_4_load_36 | 44 | 0.006439 | 0.0016138 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_158-24_0_4_load_150 | 45 | 0.0092588 | 0.0023205 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_158-24_0_4_load_61 | 46 | 0.0089201 | 0.0022356 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_158-24_0_4_load_151 | 48 | 0.0081553 | 0.0020439 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_158-24_0_4_load_136 | 49 | 0.0062675 | 0.0015708 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_158-24_0_4_load_134 | 50 | 0.0024028 | 0.0006022 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_158-24_0_4_load_42 | 52 | 0.0073106 | 0.0018322 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_158-24_0_4_load_161 | 53 | 0.0040439 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_158-24_0_4_load_88 | 55 | 0.002857 | 0.00071603 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_158-24_0_4_load_87 | 56 | 0.0027346 | 0.00068536 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_158-24_0_4_load_37 | 57 | 0.0046857 | 0.0011743 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_158-24_0_4_load_59 | 58 | 0.0086369 | 0.0021646 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_158-24_0_4_load_66 | 61 | 0.00088688 | 0.00022227 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_158-24_0_4_load_85 | 63 | 0.0032238 | 0.00080796 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_158-24_0_4_load_86 | 64 | 0.0028735 | 0.00072017 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_158-24_0_4_load_40 | 66 | 0.0032409 | 0.00081226 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_158-24_0_4_load_38 | 67 | 0.0033079 | 0.00082904 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_158-24_0_4_load_154 | 68 | 0.011113 | 0.0027852 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_158-24_0_4_load_44 | 69 | 0.0093634 | 0.0023467 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_158-24_0_4_load_45 | 70 | 0.0023339 | 0.00058494 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_158-24_0_4_load_47 | 71 | 0.001941 | 0.00048645 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_158-24_0_4_load_51 | 72 | 0.0030652 | 0.0007682 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_158-24_0_4_load_53 | 73 | 0.005958 | 0.0014932 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_158-24_0_4_load_152 | 76 | 0.0081859 | 0.0020516 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_158-24_0_4_load_94 | 78 | 0.0033825 | 0.00084773 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_158-24_0_4_load_148 | 79 | 0.010661 | 0.0026719 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_158-24_0_4_load_58 | 80 | 0.0082812 | 0.0020755 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_158-24_0_4_load_60 | 81 | 0.0068036 | 0.0017052 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_158-24_0_4_load_64 | 82 | 0.0022447 | 0.00056257 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_158-24_0_4_load_68 | 83 | 0.0058457 | 0.0014651 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_158-24_0_4_load_77 | 84 | 0.0019149 | 0.00047992 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_158-24_0_4_load_73 | 85 | 0.00075047 | 0.00018808 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_158-24_0_4_load_69 | 86 | 0.0011842 | 0.00029678 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_158-24_0_4_load_71 | 87 | 0.00096319 | 0.0002414 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_158-24_0_4_load_90 | 88 | 0.0012901 | 0.00032332 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_158-24_0_4_load_70 | 89 | 0.002223 | 0.00055714 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_158-24_0_4_load_75 | 92 | 0.001704 | 0.00042707 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_158-24_0_4_load_78 | 93 | 0.00061439 | 0.00015398 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_158-24_0_4_load_83 | 95 | 0.0004659 | 0.00011677 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_158-24_0_4_load_80 | 97 | 0.0011762 | 0.00029477 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_158-24_0_4_load_145 | 99 | 0.00090607 | 0.00022708 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_158-24_0_4_load_144 | 100 | 0.00055812 | 0.00013988 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_158-24_0_4_load_146 | 101 | 0.0048891 | 0.0012253 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_158-24_0_4_load_91 | 102 | 0.004749 | 0.0011902 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_158-24_0_4_load_92 | 103 | 0.0054028 | 0.0013541 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_158-24_0_4_load_93 | 104 | 0.0017136 | 0.00042946 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_158-24_0_4_load_155 | 109 | 0.0052993 | 0.0013281 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_158-24_0_4_load_133 | 110 | 0.0097919 | 0.0024541 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_158-24_0_4_load_100 | 111 | 0.0025327 | 0.00063475 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_158-24_0_4_load_101 | 112 | 0.0031558 | 0.00079091 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_158-24_0_4_load_139 | 113 | 0.010092 | 0.0025294 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_158-24_0_4_load_106 | 116 | 0.0018696 | 0.00046856 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_158-24_0_4_load_126 | 117 | 0.00086905 | 0.0002178 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_158-24_0_4_load_123 | 118 | 0.0035022 | 0.00087773 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_158-24_0_4_load_104 | 119 | 0.0015497 | 0.00038838 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_158-24_0_4_load_102 | 120 | 0.0031927 | 0.00080016 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_158-24_0_4_load_103 | 121 | 0.0031565 | 0.0007911 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_158-24_0_4_load_105 | 122 | 0.0023929 | 0.00059971 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_158-24_0_4_load_110 | 123 | 0.0013092 | 0.00032813 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_158-24_0_4_load_111 | 124 | 0.0026756 | 0.00067058 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_158-24_0_4_load_113 | 126 | 0.0024761 | 0.00062056 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_158-24_0_4_load_114 | 127 | 0.0010957 | 0.0002746 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_158-24_0_4_load_116 | 129 | 0.00092421 | 0.00023163 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_158-24_0_4_load_117 | 130 | 0.0024152 | 0.0006053 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_158-24_0_4_load_118 | 131 | 0.0025402 | 0.00063663 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_158-24_0_4_load_119 | 132 | 0.00091391 | 0.00022905 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_158-24_0_4_load_160 | 133 | 0.0024136 | 0.0006049 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_158-24_0_4_load_158 | 134 | 0.0024727 | 0.00061972 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_158-24_0_4_load_120 | 135 | 0.0011234 | 0.00028154 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_158-24_0_4_load_157 | 136 | 0.002621 | 0.00065689 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_158-24_0_4_load_121 | 137 | 0.001121 | 0.00028095 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_158-24_0_4_load_122 | 138 | 0.002444 | 0.00061252 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_158-24_0_4_load_127 | 139 | 0.00086781 | 0.00021749 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_158-24_0_4_load_125 | 140 | 0.0067516 | 0.0016921 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_158-24_0_4_load_128 | 141 | 0.011086 | 0.0027783 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_158-24_0_4_load_130 | 143 | 0.0052554 | 0.0013171 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_158-24_0_4_load_131 | 144 | 0.0056301 | 0.001411 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_158-24_0_4_load_132 | 145 | 0.0039187 | 0.00098213 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_158-24_0_4_load_142 | 147 | 0.0094801 | 0.0023759 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_158-24_0_4_load_138 | 148 | 0.0030931 | 0.00077521 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_158-24_0_4_load_141 | 149 | 0.003646 | 0.00091379 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_158-24_0_4_load_143 | 150 | 0.0061142 | 0.0015324 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_158-24_0_4_load_149 | 151 | 0.0074784 | 0.0018743 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_158-24_0_4_load_159 | 152 | 0.011401 | 0.0028574 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_158-24_0_4_line_0 |  | 0 | 1 | 0.0021027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_158-24_0_4_line_1 |  | 0 | 2 | 0.025195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_158-24_0_4_line_2 |  | 1 | 3 | 0.017784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_158-24_0_4_line_3 |  | 1 | 4 | 0.017168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_158-24_0_4_line_4 |  | 2 | 5 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_158-24_0_4_line_5 |  | 4 | 6 | 0.012931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_158-24_0_4_line_6 |  | 5 | 7 | 0.008853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_158-24_0_4_line_7 |  | 6 | 8 | 0.003711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_158-24_0_4_line_8 |  | 6 | 9 | 0.021978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_158-24_0_4_line_9 |  | 8 | 13 | 0.023617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_158-24_0_4_line_10 |  | 8 | 14 | 0.004683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_158-24_0_4_line_11 |  | 9 | 15 | 0.03133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_158-24_0_4_line_12 |  | 10 | 11 | 0.003178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_158-24_0_4_line_13 |  | 10 | 12 | 0.010478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_158-24_0_4_line_14 |  | 12 | 73 | 0.015233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_158-24_0_4_line_15 |  | 13 | 25 | 0.020389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_158-24_0_4_line_16 |  | 14 | 20 | 0.032663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_158-24_0_4_line_17 |  | 14 | 19 | 0.039698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_158-24_0_4_line_18 |  | 15 | 76 | 0.0003637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_158-24_0_4_line_19 |  | 16 | 17 | 0.0049959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_158-24_0_4_line_20 |  | 16 | 18 | 0.016342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_158-24_0_4_line_21 |  | 17 | 19 | 0.0006303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_158-24_0_4_line_22 |  | 21 | 22 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_158-24_0_4_line_23 |  | 22 | 23 | 0.013358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_158-24_0_4_line_24 |  | 23 | 24 | 0.042088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_158-24_0_4_line_25 |  | 24 | 26 | 0.006315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_158-24_0_4_line_26 |  | 25 | 32 | 0.0099583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_158-24_0_4_line_27 |  | 26 | 36 | 0.012649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_158-24_0_4_line_28 |  | 27 | 28 | 0.001792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_158-24_0_4_line_29 |  | 28 | 31 | 0.016227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_158-24_0_4_line_30 |  | 29 | 30 | 0.048087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_158-24_0_4_line_31 |  | 29 | 31 | 0.011344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_158-24_0_4_line_32 |  | 30 | 37 | 0.014235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_158-24_0_4_line_33 |  | 32 | 66 | 0.033273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_158-24_0_4_line_34 |  | 33 | 34 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_158-24_0_4_line_35 |  | 33 | 35 | 0.045707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_158-24_0_4_line_36 |  | 34 | 44 | 0.015637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_158-24_0_4_line_37 |  | 35 | 45 | 0.014566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_158-24_0_4_line_38 |  | 35 | 46 | 0.0050022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_158-24_0_4_line_39 |  | 36 | 38 | 0.01248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_158-24_0_4_line_40 |  | 36 | 39 | 0.032821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_158-24_0_4_line_41 |  | 37 | 80 | 0.016431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_158-24_0_4_line_42 |  | 37 | 58 | 0.022149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_158-24_0_4_line_43 |  | 39 | 40 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_158-24_0_4_line_44 |  | 40 | 51 | 0.046646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_158-24_0_4_line_45 |  | 41 | 42 | 0.023514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_158-24_0_4_line_46 |  | 41 | 43 | 0.041592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_158-24_0_4_line_47 |  | 42 | 49 | 0.028671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_158-24_0_4_line_48 |  | 42 | 50 | 0.015038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_158-24_0_4_line_49 |  | 43 | 47 | 0.0097037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_158-24_0_4_line_50 |  | 43 | 48 | 0.018481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_158-24_0_4_line_51 |  | 44 | 57 | 0.0020156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_158-24_0_4_line_52 |  | 45 | 48 | 0.01085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_158-24_0_4_line_53 |  | 46 | 58 | 0.038103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_158-24_0_4_line_54 |  | 47 | 63 | 0.019621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_158-24_0_4_line_55 |  | 47 | 64 | 0.050366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_158-24_0_4_line_56 |  | 50 | 65 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_158-24_0_4_line_57 |  | 51 | 66 | 0.00055455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_158-24_0_4_line_58 |  | 51 | 67 | 0.019485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_158-24_0_4_line_59 |  | 52 | 53 | 0.014621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_158-24_0_4_line_60 |  | 53 | 68 | 0.014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_158-24_0_4_line_61 |  | 54 | 55 | 0.04353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_158-24_0_4_line_62 |  | 54 | 56 | 0.040104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_158-24_0_4_line_63 |  | 55 | 64 | 0.060178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_158-24_0_4_line_64 |  | 57 | 67 | 0.01376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_158-24_0_4_line_65 |  | 59 | 60 | 0.004641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_158-24_0_4_line_66 |  | 59 | 61 | 0.063686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_158-24_0_4_line_67 |  | 59 | 62 | 0.018162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_158-24_0_4_line_68 |  | 60 | 84 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_158-24_0_4_line_69 |  | 61 | 85 | 0.019801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_158-24_0_4_line_70 |  | 62 | 82 | 0.028007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_158-24_0_4_line_71 |  | 62 | 81 | 0.01917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_158-24_0_4_line_72 |  | 63 | 88 | 0.0084232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_158-24_0_4_line_73 |  | 65 | 148 | 0.016938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_158-24_0_4_line_74 |  | 68 | 106 | 0.0036898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_158-24_0_4_line_75 |  | 69 | 70 | 0.010171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_158-24_0_4_line_76 |  | 70 | 71 | 0.020019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_158-24_0_4_line_77 |  | 71 | 72 | 0.0045664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_158-24_0_4_line_78 |  | 72 | 74 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_158-24_0_4_line_79 |  | 73 | 75 | 0.00027698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_158-24_0_4_line_80 |  | 74 | 77 | 0.002963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_158-24_0_4_line_81 |  | 74 | 78 | 0.019289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_158-24_0_4_line_82 |  | 75 | 79 | 0.022091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_158-24_0_4_line_83 |  | 76 | 151 | 0.020998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_158-24_0_4_line_84 |  | 77 | 111 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_158-24_0_4_line_85 |  | 77 | 112 | 0.027489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_158-24_0_4_line_86 |  | 78 | 103 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_158-24_0_4_line_87 |  | 79 | 151 | 0.0044604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_158-24_0_4_line_88 |  | 80 | 81 | 0.0011467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_158-24_0_4_line_89 |  | 82 | 83 | 0.0059542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_158-24_0_4_line_90 |  | 83 | 86 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_158-24_0_4_line_91 |  | 85 | 87 | 0.025795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_158-24_0_4_line_92 |  | 87 | 89 | 0.037649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_158-24_0_4_line_93 |  | 88 | 101 | 0.0047426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_158-24_0_4_line_94 |  | 89 | 90 | 0.015849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_158-24_0_4_line_95 |  | 90 | 91 | 0.004059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_158-24_0_4_line_96 |  | 91 | 92 | 0.025147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_158-24_0_4_line_97 |  | 92 | 93 | 0.049111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_158-24_0_4_line_98 |  | 93 | 94 | 0.020545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_158-24_0_4_line_99 |  | 94 | 97 | 0.03842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_158-24_0_4_line_100 |  | 94 | 96 | 0.008546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_158-24_0_4_line_101 |  | 95 | 96 | 0.031865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_158-24_0_4_line_102 |  | 96 | 98 | 0.00762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_158-24_0_4_line_103 |  | 98 | 99 | 0.024039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_158-24_0_4_line_104 |  | 98 | 100 | 0.021068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_158-24_0_4_line_105 |  | 102 | 103 | 0.015525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_158-24_0_4_line_106 |  | 102 | 104 | 0.012843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_158-24_0_4_line_107 |  | 104 | 105 | 0.0061959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_158-24_0_4_line_108 |  | 105 | 106 | 0.023969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_158-24_0_4_line_109 |  | 106 | 107 | 0.022532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_158-24_0_4_line_110 |  | 107 | 113 | 0.001961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_158-24_0_4_line_111 |  | 108 | 109 | 0.015348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_158-24_0_4_line_112 |  | 108 | 110 | 0.012409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_158-24_0_4_line_113 |  | 109 | 114 | 0.0098155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_158-24_0_4_line_114 |  | 111 | 115 | 0.0218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_158-24_0_4_line_115 |  | 112 | 116 | 0.0065587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_158-24_0_4_line_116 |  | 113 | 114 | 0.0092088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_158-24_0_4_line_117 |  | 114 | 146 | 0.008093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_158-24_0_4_line_118 |  | 115 | 117 | 0.008865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_158-24_0_4_line_119 |  | 115 | 118 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_158-24_0_4_line_120 |  | 116 | 119 | 0.0060631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_158-24_0_4_line_121 |  | 117 | 139 | 0.0044976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_158-24_0_4_line_122 |  | 118 | 140 | 0.020732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_158-24_0_4_line_123 |  | 119 | 120 | 0.013234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_158-24_0_4_line_124 |  | 120 | 121 | 0.015992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_158-24_0_4_line_125 |  | 121 | 122 | 0.0056518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_158-24_0_4_line_126 |  | 123 | 124 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_158-24_0_4_line_127 |  | 123 | 125 | 0.0094862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_158-24_0_4_line_128 |  | 124 | 126 | 0.00050593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_158-24_0_4_line_129 |  | 125 | 127 | 0.0059012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_158-24_0_4_line_130 |  | 126 | 128 | 0.0079325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_158-24_0_4_line_131 |  | 127 | 129 | 5.6588e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_158-24_0_4_line_132 |  | 128 | 130 | 0.014742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_158-24_0_4_line_133 |  | 128 | 131 | 0.012801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_158-24_0_4_line_134 |  | 129 | 132 | 6.2091e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_158-24_0_4_line_135 |  | 130 | 133 | 0.0057733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_158-24_0_4_line_136 |  | 131 | 134 | 0.0059705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_158-24_0_4_line_137 |  | 132 | 135 | 0.011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_158-24_0_4_line_138 |  | 134 | 136 | 0.0060926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_158-24_0_4_line_139 |  | 135 | 137 | 0.0052949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_158-24_0_4_line_140 |  | 136 | 152 | 0.004429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_158-24_0_4_line_141 |  | 137 | 138 | 0.0051144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_158-24_0_4_line_142 |  | 138 | 139 | 0.0012536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_158-24_0_4_line_143 |  | 141 | 142 | 0.016806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_158-24_0_4_line_144 |  | 142 | 143 | 0.016483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_158-24_0_4_line_145 |  | 142 | 144 | 0.00033792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_158-24_0_4_line_146 |  | 143 | 145 | 0.014037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_158-24_0_4_line_147 |  | 145 | 146 | 0.018647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_158-24_0_4_line_148 |  | 145 | 147 | 0.011685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_158-24_0_4_line_149 |  | 146 | 148 | 0.011052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
150 | LV_158-24_0_4_line_150 |  | 147 | 149 | 0.012906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_158-24_0_4_line_151 |  | 149 | 150 | 0.0030262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_158-24_0_4_trafo_37 | 0.63 MVA 20/0.4 kV | 153 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2698301.9346 | 1232773.2258 | 2698299.8465 | 1232773.4733
1 | 2698275.249 | 1232778.6441 | 2698290.4923 | 1232774.582 | 2698299.8465 | 1232773.4733
2 | 2698301.9346 | 1232773.2258 | 2698301.8304 | 1232755.4416
3 | 2698301.9346 | 1232773.2258 | 2698306.0626 | 1232773.6388 | 2698318.3609 | 1232777.9122
4 | 2698275.249 | 1232778.6441 | 2698271.1258 | 1232779.3209 | 2698257.3813 | 1232779.2733
5 | 2698330.468 | 1232782.4489 | 2698322.1909 | 1232779.243 | 2698318.3609 | 1232777.9122
6 | 2698248.7905 | 1232781.0845 | 2698254.9738 | 1232779.265 | 2698257.3813 | 1232779.2733
7 | 2698330.468 | 1232782.4489 | 2698332.7673 | 1232785.3669
8 | 2698349.7947 | 1232771.8831 | 2698330.468 | 1232782.4489
9 | 2698332.7673 | 1232785.3669 | 2698351.2625 | 1232775.6212 | 2698353.7873 | 1232774.6342
10 | 2698328.6703 | 1232787.6564 | 2698332.7673 | 1232785.3669
11 | 2698349.7947 | 1232771.8831 | 2698349.5009 | 1232765.3845 | 2698349.1304 | 1232757.1168 | 2698349.8513 | 1232740.5838
12 | 2698355.8573 | 1232667.3397 | 2698355.5337 | 1232664.1782
13 | 2698353.3831 | 1232677.2728 | 2698354.0443 | 1232670.2674 | 2698355.8573 | 1232667.3397
14 | 2698353.3831 | 1232677.2728 | 2698351.9642 | 1232692.44
15 | 2698373.7385 | 1232771.9793 | 2698365.6477 | 1232771.7008 | 2698358.6027 | 1232772.7517 | 2698353.7873 | 1232774.6342
16 | 2698328.6703 | 1232787.6564 | 2698329.3346 | 1232792.3597 | 2698329.5444 | 1232793.8643 | 2698331.6104 | 1232808.5871 | 2698333.104 | 1232820.0168
17 | 2698328.6703 | 1232787.6564 | 2698298.9592 | 1232803.3877 | 2698293.5519 | 1232806.165
18 | 2698349.8671 | 1232740.2205 | 2698349.8513 | 1232740.5838
19 | 2698288.5473 | 1232808.7355 | 2698292.9912 | 1232806.453
20 | 2698288.5473 | 1232808.7355 | 2698275.5113 | 1232815.4311 | 2698273.9841 | 1232816.1489
21 | 2698292.9912 | 1232806.453 | 2698293.5519 | 1232806.165
22 | 2698339.0499 | 1232871.0784 | 2698323.8649 | 1232866.5912
23 | 2698339.0499 | 1232871.0784 | 2698349.1042 | 1232879.9068
24 | 2698387.2807 | 1232862.3923 | 2698376.4499 | 1232866.6162 | 2698351.6109 | 1232877.6133 | 2698349.1042 | 1232879.9068
25 | 2698387.2807 | 1232862.3923 | 2698386.1752 | 1232856.9033 | 2698385.467 | 1232857.0071
26 | 2698373.7385 | 1232771.9793 | 2698380.323 | 1232773.1336 | 2698383.4384 | 1232774.1381
27 | 2698372.9513 | 1232858.8414 | 2698385.467 | 1232857.0071
28 | 2698389.4392 | 1232906.3018 | 2698390.9616 | 1232907.2472
29 | 2698390.9616 | 1232907.2472 | 2698398.8082 | 1232912.1197 | 2698403.7348 | 1232916.4267 | 2698403.9973 | 1232916.7882
30 | 2698407.9292 | 1232926.9928 | 2698415.1852 | 1232928.7364 | 2698421.4394 | 1232931.5309 | 2698429.7165 | 1232936.0936 | 2698437.2615 | 1232939.1319 | 2698445.1731 | 1232941.9872 | 2698452.7446 | 1232943.7699
31 | 2698407.9292 | 1232926.9928 | 2698407.4367 | 1232921.5251 | 2698403.9973 | 1232916.7882
32 | 2698466.8227 | 1232945.6818 | 2698460.2043 | 1232945.2163 | 2698454.3683 | 1232944.1522 | 2698452.7446 | 1232943.7699
33 | 2698409.8105 | 1232793.7985 | 2698401.3757 | 1232785.4689 | 2698396.0285 | 1232780.9437 | 2698390.8565 | 1232777.2665 | 2698386.1758 | 1232775.0207 | 2698383.4384 | 1232774.1381
34 | 2698446.7812 | 1232844.4975 | 2698440.2466 | 1232835.2423
35 | 2698459.7679 | 1232884.7423 | 2698459.7203 | 1232875.7348 | 2698458.6006 | 1232870.6459 | 2698455.1227 | 1232862.082 | 2698455.5714 | 1232861.0553 | 2698456.0342 | 1232859.1727 | 2698455.5029 | 1232857.4181 | 2698456.0887 | 1232852.691 | 2698453.3148 | 1232851.4553 | 2698450.5047 | 1232848.7512 | 2698446.7812 | 1232844.4975
36 | 2698431.2248 | 1232822.4702 | 2698435.5567 | 1232828.5999 | 2698440.2466 | 1232835.2423
37 | 2698459.7679 | 1232884.7423 | 2698474.3333 | 1232884.8066
38 | 2698459.7679 | 1232884.7423 | 2698459.797 | 1232889.7444
39 | 2698372.9513 | 1232858.8414 | 2698366.2981 | 1232861.8446 | 2698361.1231 | 1232862.4706
40 | 2698372.9513 | 1232858.8414 | 2698370.1379 | 1232847.1863 | 2698365.4721 | 1232832.1535 | 2698365.3477 | 1232827.0638
41 | 2698466.8227 | 1232945.6818 | 2698483.2349 | 1232946.471
42 | 2698466.8227 | 1232945.6818 | 2698467.1479 | 1232923.5352
43 | 2698368.543 | 1232813.1681 | 2698365.2554 | 1232823.2879 | 2698365.3477 | 1232827.0638
44 | 2698410.2051 | 1232794.1881 | 2698384.1918 | 1232810.6808 | 2698368.543 | 1232813.1681 | 2698368.543 | 1232813.1681
45 | 2698529.7084 | 1232842.3587 | 2698506.3597 | 1232845.6631
46 | 2698503.6638 | 1232884.9363 | 2698503.515 | 1232861.0273 | 2698504.167 | 1232857.7913 | 2698505.6439 | 1232854.58 | 2698508.9064 | 1232851.4651 | 2698506.3597 | 1232845.6631
47 | 2698529.7084 | 1232842.3587 | 2698558.2989 | 1232840.2163
48 | 2698529.7084 | 1232842.3587 | 2698528.5995 | 1232827.3618
49 | 2698503.6638 | 1232884.9363 | 2698504.0421 | 1232890.8914 | 2698507.7458 | 1232890.3968
50 | 2698503.6638 | 1232884.9363 | 2698485.1834 | 1232884.8546
51 | 2698431.2248 | 1232822.4702 | 2698430.0615 | 1232820.8242
52 | 2698474.3333 | 1232884.8066 | 2698485.1834 | 1232884.8546
53 | 2698467.1479 | 1232923.5352 | 2698467.3517 | 1232909.6529 | 2698466.8021 | 1232906.7194 | 2698461.2293 | 1232904.3921 | 2698459.8743 | 1232902.9908 | 2698459.797 | 1232889.7444
54 | 2698507.7458 | 1232890.3968 | 2698526.9589 | 1232886.4169
55 | 2698507.7458 | 1232890.3968 | 2698507.469 | 1232869.6436 | 2698507.7652 | 1232861.3758 | 2698509.2328 | 1232857.3527 | 2698511.7521 | 1232854.7592 | 2698515.3177 | 1232853.0059 | 2698518.8707 | 1232852.0085 | 2698524.6349 | 1232851.6454
56 | 2698527.6734 | 1232814.838 | 2698528.5995 | 1232827.3618
57 | 2698410.2051 | 1232794.1881 | 2698409.8105 | 1232793.7985
58 | 2698410.2051 | 1232794.1881 | 2698417.0066 | 1232802.3512 | 2698422.12 | 1232809.5867
59 | 2698490.4719 | 1232807.7593 | 2698496.1242 | 1232821.244
60 | 2698490.4719 | 1232807.7593 | 2698490.2097 | 1232807.1338 | 2698484.9212 | 1232794.5035
61 | 2698628.1288 | 1232848.0284 | 2698617.0822 | 1232846.9888 | 2698608.7965 | 1232846.5955 | 2698602.4329 | 1232846.7456 | 2698584.6939 | 1232847.8628
62 | 2698628.1288 | 1232848.0284 | 2698624.1217 | 1232876.3717 | 2698623.9996 | 1232887.8498
63 | 2698584.6939 | 1232847.8628 | 2698552.4078 | 1232849.8961 | 2698524.6349 | 1232851.6454
64 | 2698422.12 | 1232809.5867 | 2698430.0615 | 1232820.8242
65 | 2698522.8534 | 1232936.9704 | 2698519.4314 | 1232940.1161
66 | 2698519.4314 | 1232940.1161 | 2698528.3303 | 1232949.1813 | 2698536.8651 | 1232956.0056 | 2698567.9821 | 1232981.2274
67 | 2698503.5284 | 1232947.4468 | 2698507.8982 | 1232947.4192 | 2698511.2389 | 1232946.4405 | 2698513.2471 | 1232944.9838 | 2698519.4314 | 1232940.1161
68 | 2698522.8534 | 1232936.9704 | 2698525.8498 | 1232940.7674 | 2698532.1683 | 1232946.5686
69 | 2698567.9821 | 1232981.2274 | 2698571.4014 | 1232983.9989 | 2698576.6146 | 1232988.8222 | 2698579.7108 | 1232993.4436 | 2698580.5424 | 1232996.0488
70 | 2698503.5284 | 1232947.4468 | 2698503.7144 | 1232975.4529
71 | 2698503.5284 | 1232947.4468 | 2698484.3803 | 1232946.5261
72 | 2698535.207 | 1232884.7083 | 2698526.9589 | 1232886.4169
73 | 2698527.6734 | 1232814.838 | 2698524.8759 | 1232806.808 | 2698524.6781 | 1232802.7573 | 2698524.4648 | 1232798.3831
74 | 2698484.1328 | 1232790.8989 | 2698484.9212 | 1232794.5035
75 | 2698416.5669 | 1232727.7301 | 2698408.4361 | 1232733.8409
76 | 2698416.5669 | 1232727.7301 | 2698432.57 | 1232715.7028
77 | 2698436.2204 | 1232712.9593 | 2698432.57 | 1232715.7028
78 | 2698448.2937 | 1232703.8856 | 2698436.2204 | 1232712.9593
79 | 2698351.9642 | 1232692.44 | 2698351.9384 | 1232692.7158
80 | 2698448.2937 | 1232703.8856 | 2698450.6485 | 1232702.0788
81 | 2698448.2937 | 1232703.8856 | 2698457.8258 | 1232720.655
82 | 2698351.9384 | 1232692.7158 | 2698350.9761 | 1232714.7859
83 | 2698349.8671 | 1232740.2205 | 2698350.7818 | 1232719.2421
84 | 2698450.6485 | 1232702.0788 | 2698461.2844 | 1232694.1046 | 2698463.1609 | 1232693.1748
85 | 2698450.6485 | 1232702.0788 | 2698431.4248 | 1232682.429
86 | 2698457.8258 | 1232720.655 | 2698466.3512 | 1232735.6533
87 | 2698350.9761 | 1232714.7859 | 2698350.7818 | 1232719.2421
88 | 2698484.3803 | 1232946.5261 | 2698483.2349 | 1232946.471
89 | 2698503.7144 | 1232975.4529 | 2698503.754 | 1232981.407
90 | 2698503.8554 | 1232996.6774 | 2698503.754 | 1232981.407
91 | 2698575.9945 | 1233020.1957 | 2698578.7621 | 1233016.3893 | 2698580.5625 | 1233012.394 | 2698581.7615 | 1233008.1329 | 2698582.1175 | 1233004.0247 | 2698581.3664 | 1232998.6305 | 2698580.5424 | 1232996.0488
92 | 2698546.5576 | 1233043.1978 | 2698561.1653 | 1233034.0772 | 2698568.6511 | 1233028.3526 | 2698572.2209 | 1233024.9649 | 2698575.3911 | 1233021.0257 | 2698575.9945 | 1233020.1957
93 | 2698539.851 | 1232883.7463 | 2698535.207 | 1232884.7083
94 | 2698533.1137 | 1233051.5917 | 2698546.5576 | 1233043.1978
95 | 2698535.3443 | 1233054.9868 | 2698533.1137 | 1233051.5917
96 | 2698535.3443 | 1233054.9868 | 2698537.9376 | 1233058.8882 | 2698539.3715 | 1233060.0906 | 2698541.2533 | 1233060.7779 | 2698543.6326 | 1233061.1398 | 2698546.007 | 1233060.8901 | 2698553.1676 | 1233056.0497 | 2698555.9263 | 1233054.5279
97 | 2698602.4011 | 1233038.8499 | 2698565.7255 | 1233050.4093 | 2698558.823 | 1233052.93 | 2698555.9263 | 1233054.5279
98 | 2698621.9962 | 1233032.674 | 2698602.4011 | 1233038.8499
99 | 2698621.9962 | 1233032.674 | 2698621.4735 | 1233037.7023 | 2698611.1022 | 1233052.5635 | 2698603.3468 | 1233065.6848
100 | 2698630.2792 | 1233030.4764 | 2698621.9962 | 1233032.674
101 | 2698630.2792 | 1233030.4764 | 2698627.7198 | 1233027.7319 | 2698608.7971 | 1233013.5186 | 2698605.2428 | 1233010.8466
102 | 2698637.7285 | 1233028.7766 | 2698630.2792 | 1233030.4764
103 | 2698637.7285 | 1233028.7766 | 2698650.441 | 1233027.5199 | 2698661.6969 | 1233027.0849
104 | 2698637.7285 | 1233028.7766 | 2698636.2945 | 1233021.6475 | 2698636.3033 | 1233015.1873 | 2698637.8342 | 1233008.0128
105 | 2698473.8696 | 1232749.236 | 2698468.0289 | 1232738.6047 | 2698466.3512 | 1232735.6533
106 | 2698473.8696 | 1232749.236 | 2698475.1741 | 1232751.6104 | 2698477.5486 | 1232761.4621
107 | 2698479.0003 | 1232767.4855 | 2698477.5486 | 1232761.4621
108 | 2698479.0003 | 1232767.4855 | 2698484.1328 | 1232790.8989
109 | 2698506.7193 | 1232790.1837 | 2698484.1328 | 1232790.8989
110 | 2698506.7193 | 1232790.1837 | 2698506.6231 | 1232788.2251
111 | 2698514.2044 | 1232762.5985 | 2698515.1883 | 1232777.9151
112 | 2698514.2044 | 1232762.5985 | 2698513.7711 | 1232758.1325 | 2698521.6686 | 1232757.5142
113 | 2698515.8175 | 1232787.7104 | 2698515.1883 | 1232777.9151
114 | 2698482.6949 | 1232683.4959 | 2698463.1609 | 1232693.1748
115 | 2698426.8382 | 1232677.7407 | 2698431.4248 | 1232682.429
116 | 2698515.8175 | 1232787.7104 | 2698506.6231 | 1232788.2251
117 | 2698523.9265 | 1232787.3446 | 2698515.8175 | 1232787.7104
118 | 2698482.6949 | 1232683.4959 | 2698491.2492 | 1232681.1694
119 | 2698482.6949 | 1232683.4959 | 2698481.4559 | 1232670.6647
120 | 2698426.8382 | 1232677.7407 | 2698422.5981 | 1232673.4067
121 | 2698491.2492 | 1232681.1694 | 2698495.5891 | 1232679.9891
122 | 2698479.4632 | 1232650.0288 | 2698481.4559 | 1232670.6647
123 | 2698413.3437 | 1232663.9472 | 2698422.5981 | 1232673.4067
124 | 2698413.3437 | 1232663.9472 | 2698402.1603 | 1232652.5158
125 | 2698398.2079 | 1232648.4758 | 2698402.1603 | 1232652.5158
126 | 2698525.5516 | 1232682.9723 | 2698525.5516 | 1232682.9723 | 2698528.7393 | 1232682.5471 | 2698533.8874 | 1232707.148
127 | 2698523.9801 | 1232673.6172 | 2698525.5516 | 1232682.9723
128 | 2698533.991 | 1232707.6432 | 2698533.8874 | 1232707.148
129 | 2698523.9801 | 1232673.6172 | 2698518.2162 | 1232674.8828
130 | 2698535.6158 | 1232715.4075 | 2698533.991 | 1232707.6432
131 | 2698518.2162 | 1232674.8828 | 2698518.161 | 1232674.895
132 | 2698535.6158 | 1232715.4075 | 2698546.4037 | 1232713.7962 | 2698550.0564 | 1232712.6291
133 | 2698535.6158 | 1232715.4075 | 2698525.7037 | 1232718.0896 | 2698523.1824 | 1232718.3291
134 | 2698518.161 | 1232674.895 | 2698518.1003 | 1232674.9083
135 | 2698550.0564 | 1232712.6291 | 2698555.5558 | 1232710.8719
136 | 2698517.2387 | 1232718.8935 | 2698523.1824 | 1232718.3291
137 | 2698518.1003 | 1232674.9083 | 2698513.8104 | 1232675.8503 | 2698506.9566 | 1232677.3852
138 | 2698511.1734 | 1232719.4695 | 2698517.2387 | 1232718.8935
139 | 2698501.7896 | 1232678.5424 | 2698506.9566 | 1232677.3852
140 | 2698506.7642 | 1232719.8882 | 2698511.1734 | 1232719.4695
141 | 2698501.7896 | 1232678.5424 | 2698496.7988 | 1232679.6601 | 2698496.7988 | 1232679.6601
142 | 2698495.5891 | 1232679.9891 | 2698496.7988 | 1232679.6601
143 | 2698541.0766 | 1232755.9946 | 2698557.8312 | 1232754.6793
144 | 2698541.0766 | 1232755.9946 | 2698541.9037 | 1232772.4564
145 | 2698540.7397 | 1232756.021 | 2698541.0766 | 1232755.9946
146 | 2698542.6081 | 1232786.4758 | 2698541.9037 | 1232772.4564
147 | 2698542.6081 | 1232786.4758 | 2698523.9265 | 1232787.3446
148 | 2698542.6081 | 1232786.4758 | 2698554.268 | 1232785.7095
149 | 2698523.9265 | 1232787.3446 | 2698524.4648 | 1232798.3831
150 | 2698554.268 | 1232785.7095 | 2698567.1458 | 1232784.8631
151 | 2698570.1655 | 1232784.6647 | 2698567.1458 | 1232784.8631

## bus_geodata
| x | y | coords
0 | 2698299.8465 | 1232773.4733
1 | 2698301.9346 | 1232773.2258
2 | 2698275.249 | 1232778.6441
3 | 2698301.8304 | 1232755.4416
4 | 2698318.3609 | 1232777.9122
5 | 2698257.3813 | 1232779.2733
6 | 2698330.468 | 1232782.4489
7 | 2698248.7905 | 1232781.0845
8 | 2698332.7673 | 1232785.3669
9 | 2698349.7947 | 1232771.8831
10 | 2698355.8573 | 1232667.3397
11 | 2698355.5337 | 1232664.1782
12 | 2698353.3831 | 1232677.2728
13 | 2698353.7873 | 1232774.6342
14 | 2698328.6703 | 1232787.6564
15 | 2698349.8513 | 1232740.5838
16 | 2698288.5473 | 1232808.7355
17 | 2698292.9912 | 1232806.453
18 | 2698273.9841 | 1232816.1489
19 | 2698293.5519 | 1232806.165
20 | 2698333.104 | 1232820.0168
21 | 2698323.8649 | 1232866.5912
22 | 2698339.0499 | 1232871.0784
23 | 2698349.1042 | 1232879.9068
24 | 2698387.2807 | 1232862.3923
25 | 2698373.7385 | 1232771.9793
26 | 2698385.467 | 1232857.0071
27 | 2698389.4392 | 1232906.3018
28 | 2698390.9616 | 1232907.2472
29 | 2698407.9292 | 1232926.9928
30 | 2698452.7446 | 1232943.7699
31 | 2698403.9973 | 1232916.7882
32 | 2698383.4384 | 1232774.1381
33 | 2698446.7812 | 1232844.4975
34 | 2698440.2466 | 1232835.2423
35 | 2698459.7679 | 1232884.7423
36 | 2698372.9513 | 1232858.8414
37 | 2698466.8227 | 1232945.6818
38 | 2698361.1231 | 1232862.4706
39 | 2698365.3477 | 1232827.0638
40 | 2698368.543 | 1232813.1681
41 | 2698506.3597 | 1232845.6631
42 | 2698529.7084 | 1232842.3587
43 | 2698503.6638 | 1232884.9363
44 | 2698431.2248 | 1232822.4702
45 | 2698474.3333 | 1232884.8066
46 | 2698459.797 | 1232889.7444
47 | 2698507.7458 | 1232890.3968
48 | 2698485.1834 | 1232884.8546
49 | 2698558.2989 | 1232840.2163
50 | 2698528.5995 | 1232827.3618
51 | 2698410.2051 | 1232794.1881
52 | 2698496.1242 | 1232821.244
53 | 2698490.4719 | 1232807.7593
54 | 2698628.1288 | 1232848.0284
55 | 2698584.6939 | 1232847.8628
56 | 2698623.9996 | 1232887.8498
57 | 2698430.0615 | 1232820.8242
58 | 2698467.1479 | 1232923.5352
59 | 2698519.4314 | 1232940.1161
60 | 2698522.8534 | 1232936.9705
61 | 2698567.9821 | 1232981.2274
62 | 2698503.5284 | 1232947.4468
63 | 2698526.9589 | 1232886.4169
64 | 2698524.6349 | 1232851.6454
65 | 2698527.6734 | 1232814.838
66 | 2698409.8105 | 1232793.7985
67 | 2698422.12 | 1232809.5867
68 | 2698484.9212 | 1232794.5035
69 | 2698408.4361 | 1232733.8409
70 | 2698416.5669 | 1232727.7301
71 | 2698432.57 | 1232715.7028
72 | 2698436.2204 | 1232712.9593
73 | 2698351.9642 | 1232692.44
74 | 2698448.2937 | 1232703.8856
75 | 2698351.9384 | 1232692.7158
76 | 2698349.8671 | 1232740.2205
77 | 2698450.6485 | 1232702.0788
78 | 2698457.8258 | 1232720.655
79 | 2698350.9761 | 1232714.7859
80 | 2698483.2349 | 1232946.471
81 | 2698484.3803 | 1232946.5261
82 | 2698503.7144 | 1232975.4529
83 | 2698503.754 | 1232981.407
84 | 2698532.1683 | 1232946.5686
85 | 2698580.5424 | 1232996.0488
86 | 2698503.8554 | 1232996.6774
87 | 2698575.9945 | 1233020.1957
88 | 2698535.207 | 1232884.7083
89 | 2698546.5576 | 1233043.1978
90 | 2698533.1137 | 1233051.5917
91 | 2698535.3443 | 1233054.9868
92 | 2698555.9263 | 1233054.5279
93 | 2698602.4011 | 1233038.8499
94 | 2698621.9961 | 1233032.674
95 | 2698605.2428 | 1233010.8467
96 | 2698630.2792 | 1233030.4764
97 | 2698603.3468 | 1233065.6848
98 | 2698637.7285 | 1233028.7766
99 | 2698661.6969 | 1233027.0849
100 | 2698637.8342 | 1233008.0128
101 | 2698539.851 | 1232883.7463
102 | 2698473.8696 | 1232749.236
103 | 2698466.3512 | 1232735.6533
104 | 2698477.5486 | 1232761.4621
105 | 2698479.0003 | 1232767.4855
106 | 2698484.1328 | 1232790.8989
107 | 2698506.7193 | 1232790.1837
108 | 2698514.2044 | 1232762.5985
109 | 2698515.1883 | 1232777.9151
110 | 2698521.6686 | 1232757.5142
111 | 2698463.1609 | 1232693.1748
112 | 2698431.4248 | 1232682.429
113 | 2698506.6231 | 1232788.2251
114 | 2698515.8175 | 1232787.7104
115 | 2698482.6949 | 1232683.4959
116 | 2698426.8382 | 1232677.7407
117 | 2698491.2492 | 1232681.1694
118 | 2698481.4559 | 1232670.6647
119 | 2698422.5981 | 1232673.4067
120 | 2698413.3437 | 1232663.9472
121 | 2698402.1603 | 1232652.5158
122 | 2698398.2079 | 1232648.4758
123 | 2698525.5516 | 1232682.9723
124 | 2698533.8874 | 1232707.148
125 | 2698523.9801 | 1232673.6172
126 | 2698533.991 | 1232707.6432
127 | 2698518.2162 | 1232674.8828
128 | 2698535.6158 | 1232715.4075
129 | 2698518.161 | 1232674.895
130 | 2698550.0564 | 1232712.6291
131 | 2698523.1824 | 1232718.3291
132 | 2698518.1003 | 1232674.9083
133 | 2698555.5558 | 1232710.8719
134 | 2698517.2387 | 1232718.8935
135 | 2698506.9566 | 1232677.3852
136 | 2698511.1734 | 1232719.4695
137 | 2698501.7896 | 1232678.5424
138 | 2698496.7988 | 1232679.6601
139 | 2698495.5891 | 1232679.9891
140 | 2698479.4632 | 1232650.0288
141 | 2698557.8312 | 1232754.6793
142 | 2698541.0766 | 1232755.9946
143 | 2698541.9037 | 1232772.4564
144 | 2698540.7397 | 1232756.021
145 | 2698542.6081 | 1232786.4758
146 | 2698523.9265 | 1232787.3446
147 | 2698554.268 | 1232785.7095
148 | 2698524.4648 | 1232798.3831
149 | 2698567.1458 | 1232784.8631
150 | 2698570.1655 | 1232784.6647
151 | 2698350.7818 | 1232719.2421
152 | 2698506.7642 | 1232719.8882
153 | 2698446.7812 | 1232844.4975

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98839 | -0.2232 | 0.0029643 | 0.00074294
1 | 0.9884 | -0.22291 | 0 | 0
2 | 0.98827 | -0.22542 | 0 | 0
3 | 0.98827 | -0.22549 | 0.0081349 | 0.0020388
4 | 0.98865 | -0.218 | 0.0085379 | 0.0021398
5 | 0.98819 | -0.227 | 0.0024647 | 0.00061772
6 | 0.98894 | -0.21233 | 0 | 0
7 | 0.98817 | -0.22739 | 0.0024661 | 0.00061806
8 | 0.98918 | -0.20786 | 0 | 0
9 | 0.98807 | -0.22923 | 0 | 0
10 | 0.98593 | -0.27088 | 0 | 0
11 | 0.98592 | -0.27108 | 0.0034074 | 0.00085396
12 | 0.98597 | -0.27024 | 0 | 0
13 | 0.99092 | -0.174 | 0.0056158 | 0.0014074
14 | 0.98912 | -0.20894 | 0 | 0
15 | 0.98683 | -0.25338 | 0.0074196 | 0.0018595
16 | 0.98871 | -0.21681 | 0.0060531 | 0.001517
17 | 0.98875 | -0.21621 | 0.00091119 | 0.00022837
18 | 0.9887 | -0.21701 | 0.00070384 | 0.0001764
19 | 0.98875 | -0.21612 | 0.0024863 | 0.00062313
20 | 0.98904 | -0.21055 | 0.0027692 | 0.00069403
21 | 0.99432 | -0.10893 | 0.0027783 | 0.00069631
22 | 0.99436 | -0.10816 | 0 | 0
23 | 0.99439 | -0.1075 | 0 | 0
24 | 0.9945 | -0.10544 | 0 | 0
25 | 0.99254 | -0.14285 | 0 | 0
26 | 0.99451 | -0.10513 | 0.0056446 | 0.0014147
27 | 0.98698 | -0.24944 | 0.0045783 | 0.0011474
28 | 0.98699 | -0.24929 | 0.0039434 | 0.00098832
29 | 0.98727 | -0.24375 | 0 | 0
30 | 0.98794 | -0.23078 | 0.013169 | 0.0033005
31 | 0.98711 | -0.24682 | 0.0065752 | 0.0016479
32 | 0.99333 | -0.12767 | 0.0081927 | 0.0020533
33 | 0.99711 | -0.054655 | 0 | 0
34 | 0.99823 | -0.033362 | 0.0019921 | 0.00049926
35 | 0.99257 | -0.14105 | 0 | 0
36 | 0.99461 | -0.10325 | 0 | 0
37 | 0.98831 | -0.2236 | 0 | 0
38 | 0.99455 | -0.10437 | 0.005059 | 0.0012679
39 | 0.99501 | -0.095459 | 0.0048594 | 0.0012179
40 | 0.99525 | -0.090804 | 0.0053417 | 0.0013388
41 | 0.98682 | -0.25134 | 0 | 0
42 | 0.98533 | -0.28004 | 0 | 0
43 | 0.98945 | -0.20077 | 0 | 0
44 | 0.99979 | -0.0038701 | 0.006439 | 0.0016138
45 | 0.99149 | -0.16165 | 0.0092588 | 0.0023205
46 | 0.99219 | -0.14834 | 0.0089201 | 0.0022356
47 | 0.98929 | -0.20386 | 0 | 0
48 | 0.99072 | -0.17643 | 0.0081553 | 0.0020439
49 | 0.98517 | -0.28327 | 0.0062675 | 0.0015708
50 | 0.98441 | -0.29788 | 0.0024028 | 0.0006022
51 | 0.99626 | -0.07138 | 0 | 0
52 | 0.97997 | -0.38438 | 0.0073106 | 0.0018322
53 | 0.98007 | -0.38244 | 0.0040439 | 0.0010135
54 | 0.98848 | -0.21959 | 0 | 0
55 | 0.98859 | -0.21746 | 0.002857 | 0.00071603
56 | 0.98838 | -0.22155 | 0.0027346 | 0.00068536
57 | 1 | 0 | -0.46336 | -0.11829
58 | 0.98962 | -0.19802 | 0.0086369 | 0.0021646
59 | 0.98714 | -0.2462 | 0 | 0
60 | 0.98714 | -0.24636 | 0 | 0
61 | 0.98654 | -0.25789 | 0.00088688 | 0.00022227
62 | 0.98735 | -0.24224 | 0 | 0
63 | 0.98912 | -0.20715 | 0.0032238 | 0.00080796
64 | 0.9889 | -0.21146 | 0.0028735 | 0.00072017
65 | 0.98365 | -0.31262 | 0 | 0
66 | 0.99621 | -0.072331 | 0.0032409 | 0.00081226
67 | 0.99843 | -0.029946 | 0.0033079 | 0.00082904
68 | 0.98022 | -0.37948 | 0.011113 | 0.0027852
69 | 0.97476 | -0.48627 | 0.0093634 | 0.0023467
70 | 0.97485 | -0.48452 | 0.0023339 | 0.00058494
71 | 0.97507 | -0.48023 | 0.001941 | 0.00048645
72 | 0.97513 | -0.47909 | 0.0030652 | 0.0007682
73 | 0.98601 | -0.26931 | 0.005958 | 0.0014932
74 | 0.97536 | -0.47446 | 0 | 0
75 | 0.98602 | -0.26926 | 0 | 0
76 | 0.98682 | -0.25361 | 0.0081859 | 0.0020516
77 | 0.97517 | -0.47814 | 0 | 0
78 | 0.97688 | -0.44465 | 0.0033825 | 0.00084773
79 | 0.98621 | -0.26556 | 0.010661 | 0.0026719
80 | 0.98775 | -0.23432 | 0.0082812 | 0.0020755
81 | 0.98772 | -0.23489 | 0.0068036 | 0.0017052
82 | 0.98711 | -0.24689 | 0.0022447 | 0.00056257
83 | 0.98707 | -0.24764 | 0.0058457 | 0.0014651
84 | 0.98711 | -0.24682 | 0.0019149 | 0.00047992
85 | 0.98637 | -0.26122 | 0.00075047 | 0.00018808
86 | 0.98705 | -0.24796 | 0.0011842 | 0.00029678
87 | 0.98617 | -0.2652 | 0.00096319 | 0.0002414
88 | 0.98907 | -0.20807 | 0.0012901 | 0.00032332
89 | 0.9859 | -0.27037 | 0.002223 | 0.00055714
90 | 0.98583 | -0.27191 | 0 | 0
91 | 0.98581 | -0.27231 | 0 | 0
92 | 0.98568 | -0.27476 | 0.001704 | 0.00042707
93 | 0.98551 | -0.27804 | 0.00061439 | 0.00015398
94 | 0.98545 | -0.27919 | 0 | 0
95 | 0.98542 | -0.27975 | 0.0004659 | 0.00011677
96 | 0.98544 | -0.27949 | 0 | 0
97 | 0.98541 | -0.28 | 0.0011762 | 0.00029477
98 | 0.98543 | -0.27969 | 0 | 0
99 | 0.98541 | -0.28008 | 0.00090607 | 0.00022708
100 | 0.98542 | -0.2799 | 0.00055812 | 0.00013988
101 | 0.98905 | -0.20849 | 0.0048891 | 0.0012253
102 | 0.97897 | -0.40382 | 0.004749 | 0.0011902
103 | 0.97829 | -0.41699 | 0.0054028 | 0.0013541
104 | 0.97936 | -0.39619 | 0.0017136 | 0.00042946
105 | 0.97955 | -0.39244 | 0 | 0
106 | 0.98029 | -0.37798 | 0 | 0
107 | 0.98115 | -0.36134 | 0 | 0
108 | 0.98132 | -0.35794 | 0 | 0
109 | 0.98146 | -0.35522 | 0.0052993 | 0.0013281
110 | 0.98121 | -0.36014 | 0.0097919 | 0.0024541
111 | 0.97442 | -0.49295 | 0.0025327 | 0.00063475
112 | 0.97478 | -0.48586 | 0.0031558 | 0.00079091
113 | 0.98122 | -0.35989 | 0.010092 | 0.0025294
114 | 0.9816 | -0.35254 | 0 | 0
115 | 0.9734 | -0.51296 | 0 | 0
116 | 0.97471 | -0.48733 | 0.0018696 | 0.00046856
117 | 0.97307 | -0.51944 | 0.00086905 | 0.0002178
118 | 0.97328 | -0.51539 | 0.0035022 | 0.00087773
119 | 0.97465 | -0.48847 | 0.0015497 | 0.00038838
120 | 0.97454 | -0.4906 | 0.0031927 | 0.00080016
121 | 0.97446 | -0.49222 | 0.0031565 | 0.0007911
122 | 0.97445 | -0.49247 | 0.0023929 | 0.00059971
123 | 0.97173 | -0.5459 | 0.0013092 | 0.00032813
124 | 0.97097 | -0.5611 | 0.0026756 | 0.00067058
125 | 0.972 | -0.5406 | 0 | 0
126 | 0.97095 | -0.56135 | 0.0024761 | 0.00062056
127 | 0.97217 | -0.5373 | 0.0010957 | 0.0002746
128 | 0.97078 | -0.56485 | 0 | 0
129 | 0.97217 | -0.53726 | 0.00092421 | 0.00023163
130 | 0.97071 | -0.56617 | 0.0024152 | 0.0006053
131 | 0.97055 | -0.56936 | 0.0025402 | 0.00063663
132 | 0.97217 | -0.53723 | 0.00091391 | 0.00022905
133 | 0.9707 | -0.56642 | 0.0024136 | 0.0006049
134 | 0.97046 | -0.57118 | 0.0024727 | 0.00061972
135 | 0.97253 | -0.53023 | 0.0011234 | 0.00028154
136 | 0.97038 | -0.57276 | 0.002621 | 0.00065689
137 | 0.9727 | -0.52687 | 0.001121 | 0.00028095
138 | 0.97287 | -0.52353 | 0.002444 | 0.00061252
139 | 0.97291 | -0.52265 | 0.00086781 | 0.00021749
140 | 0.97315 | -0.51797 | 0.0067516 | 0.0016921
141 | 0.98048 | -0.37453 | 0.011086 | 0.0027783
142 | 0.98065 | -0.37116 | 0 | 0
143 | 0.98091 | -0.36616 | 0.0052554 | 0.0013171
144 | 0.98065 | -0.37119 | 0.0056301 | 0.001411
145 | 0.98119 | -0.36058 | 0.0039187 | 0.00098213
146 | 0.98197 | -0.34535 | 0 | 0
147 | 0.98098 | -0.36465 | 0.0094801 | 0.0023759
148 | 0.98263 | -0.33254 | 0.0030931 | 0.00077521
149 | 0.98087 | -0.36693 | 0.003646 | 0.00091379
150 | 0.98085 | -0.36727 | 0.0061142 | 0.0015324
151 | 0.98629 | -0.26395 | 0.0074784 | 0.0018743
152 | 0.97033 | -0.57369 | 0.011401 | 0.0028574
153 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0078961 | -0.0019787 | 0.0078962 | 0.0019787 | 1.1143e-07 | 4.4364e-08 | 0.011888 | 0.011888 | 0.011888 | 0.98839 | -0.2232 | 0.9884 | -0.22291 | 3.2658
1 | 0.0049318 | 0.0012357 | -0.0049312 | -0.0012357 | 5.2084e-07 | 1.0471e-08 | 0.0074247 | 0.0074248 | 0.0074248 | 0.98839 | -0.2232 | 0.98827 | -0.22542 | 2.0398
2 | 0.0081359 | 0.0020392 | -0.0081349 | -0.0020388 | 1.0005e-06 | 4.1244e-07 | 0.012248 | 0.012249 | 0.012249 | 0.9884 | -0.22291 | 0.98827 | -0.22549 | 3.365
3 | -0.016032 | -0.0040179 | 0.016036 | 0.0040201 | 3.7504e-06 | 2.1802e-06 | 0.024136 | 0.024136 | 0.024136 | 0.9884 | -0.22291 | 0.98865 | -0.218 | 6.6308
4 | 0.0049312 | 0.0012357 | -0.0049309 | -0.0012357 | 3.7052e-07 | 7.5004e-09 | 0.0074248 | 0.0074249 | 0.0074249 | 0.98827 | -0.22542 | 0.98819 | -0.227 | 2.0398
5 | -0.024574 | -0.0061599 | 0.02458 | 0.006164 | 6.6335e-06 | 4.0795e-06 | 0.036986 | 0.036986 | 0.036986 | 0.98865 | -0.218 | 0.98894 | -0.21233 | 10.1611
6 | 0.0024661 | 0.00061798 | -0.0024661 | -0.00061806 | 4.5781e-08 | -8.4115e-08 | 0.0037135 | 0.0037135 | 0.0037135 | 0.98819 | -0.227 | 0.98817 | -0.22739 | 1.0202
7 | -0.067792 | -0.017032 | 0.067807 | 0.017041 | 1.4484e-05 | 9.222e-06 | 0.10202 | 0.10202 | 0.10202 | 0.98894 | -0.21233 | 0.98918 | -0.20786 | 28.0271
8 | 0.043212 | 0.010868 | -0.043177 | -0.010846 | 3.4856e-05 | 2.2026e-05 | 0.065033 | 0.065033 | 0.065033 | 0.98894 | -0.21233 | 0.98807 | -0.22923 | 17.8661
9 | -0.080735 | -0.020282 | 0.080866 | 0.020365 | 0.00013067 | 8.3323e-05 | 0.12147 | 0.12147 | 0.12147 | 0.98918 | -0.20786 | 0.99092 | -0.174 | 33.37
10 | 0.012928 | 0.0032406 | -0.012928 | -0.0032403 | 6.6422e-07 | 3.6499e-07 | 0.019448 | 0.019448 | 0.019448 | 0.98918 | -0.20786 | 0.98912 | -0.20894 | 5.3429
11 | 0.043177 | 0.010846 | -0.043128 | -0.010815 | 4.9688e-05 | 3.14e-05 | 0.065033 | 0.065033 | 0.065033 | 0.98807 | -0.22923 | 0.98683 | -0.25338 | 17.8662
12 | 0.0034074 | 0.00085394 | -0.0034074 | -0.00085396 | 3.1517e-08 | -2.0357e-08 | 0.0051426 | 0.0051426 | 0.0051426 | 0.98593 | -0.27088 | 0.98592 | -0.27108 | 1.4128
13 | -0.0034074 | -0.00085394 | 0.0034075 | 0.00085388 | 1.0391e-07 | -6.7125e-08 | 0.0051426 | 0.0051425 | 0.0051426 | 0.98593 | -0.27088 | 0.98597 | -0.27024 | 1.4128
14 | -0.0034075 | -0.00085388 | 0.0034076 | 0.00085378 | 1.5107e-07 | -9.7607e-08 | 0.0051425 | 0.0051425 | 0.0051425 | 0.98597 | -0.27024 | 0.98601 | -0.26931 | 1.4128
15 | -0.086482 | -0.021773 | 0.086611 | 0.021855 | 0.00012902 | 8.2307e-05 | 0.1299 | 0.1299 | 0.1299 | 0.99092 | -0.174 | 0.99254 | -0.14285 | 35.6867
16 | 0.0027694 | 0.00069374 | -0.0027692 | -0.00069403 | 2.126e-07 | -2.8314e-07 | 0.0041661 | 0.0041663 | 0.0041663 | 0.98912 | -0.20894 | 0.98904 | -0.21055 | 1.1446
17 | 0.010158 | 0.0025465 | -0.010155 | -0.0025448 | 3.4767e-06 | 1.7157e-06 | 0.015282 | 0.015282 | 0.015282 | 0.98912 | -0.20894 | 0.98875 | -0.21612 | 4.1984
18 | 0.035708 | 0.0089551 | -0.035708 | -0.0089548 | 3.9542e-07 | 2.4842e-07 | 0.053845 | 0.053845 | 0.053845 | 0.98683 | -0.25338 | 0.98682 | -0.25361 | 14.7926
19 | -0.0067569 | -0.0016932 | 0.0067571 | 0.0016933 | 1.9374e-07 | 5.9917e-08 | 0.010169 | 0.010169 | 0.010169 | 0.98871 | -0.21681 | 0.98875 | -0.21621 | 2.7937
20 | 0.00070385 | 0.00017619 | -0.00070384 | -0.0001764 | 6.8762e-09 | -2.0519e-07 | 0.0010592 | 0.0010593 | 0.0010593 | 0.98871 | -0.21681 | 0.9887 | -0.21701 | 0.29101
21 | -0.0076683 | -0.0019217 | 0.0076684 | 0.0019217 | 3.1479e-08 | 1.2063e-08 | 0.01154 | 0.01154 | 0.01154 | 0.98875 | -0.21621 | 0.98875 | -0.21612 | 3.1704
22 | -0.0027783 | -0.00069631 | 0.0027784 | 0.00069617 | 1.0265e-07 | -1.3969e-07 | 0.0041578 | 0.0041578 | 0.0041578 | 0.99432 | -0.10893 | 0.99436 | -0.10816 | 1.1423
23 | -0.0027784 | -0.00069617 | 0.0027785 | 0.00069606 | 8.6593e-08 | -1.1786e-07 | 0.0041578 | 0.0041577 | 0.0041578 | 0.99436 | -0.10816 | 0.99439 | -0.1075 | 1.1422
24 | -0.0027785 | -0.00069606 | 0.0027788 | 0.00069568 | 2.7282e-07 | -3.7144e-07 | 0.0041577 | 0.0041575 | 0.0041577 | 0.99439 | -0.1075 | 0.9945 | -0.10544 | 1.1422
25 | -0.0027788 | -0.00069568 | 0.0027788 | 0.00069563 | 4.0932e-08 | -5.5743e-08 | 0.0041575 | 0.0041575 | 0.0041575 | 0.9945 | -0.10544 | 0.99451 | -0.10513 | 1.1422
26 | -0.086611 | -0.021855 | 0.086674 | 0.021895 | 6.3013e-05 | 4.02e-05 | 0.1299 | 0.1299 | 0.1299 | 0.99254 | -0.14285 | 0.99333 | -0.12767 | 35.6867
27 | -0.0084234 | -0.0021103 | 0.0084241 | 0.0021106 | 7.5344e-07 | 3.1805e-07 | 0.012603 | 0.012603 | 0.012603 | 0.99451 | -0.10513 | 0.99461 | -0.10325 | 3.4624
28 | -0.0045783 | -0.0011474 | 0.0045784 | 0.0011474 | 3.2017e-08 | -2.4105e-09 | 0.0069025 | 0.0069025 | 0.0069025 | 0.98698 | -0.24944 | 0.98699 | -0.24929 | 1.8963
29 | -0.0085218 | -0.0021358 | 0.0085228 | 0.0021362 | 1.0044e-06 | 4.3543e-07 | 0.012848 | 0.012848 | 0.012848 | 0.98699 | -0.24929 | 0.98711 | -0.24682 | 3.5296
30 | -0.0151 | -0.0037853 | 0.015109 | 0.0037907 | 9.3407e-06 | 5.3627e-06 | 0.022759 | 0.022759 | 0.022759 | 0.98727 | -0.24375 | 0.98794 | -0.23078 | 6.2526
31 | 0.0151 | 0.0037853 | -0.015098 | -0.0037841 | 2.2035e-06 | 1.2652e-06 | 0.022759 | 0.022759 | 0.022759 | 0.98727 | -0.24375 | 0.98711 | -0.24682 | 6.2526
32 | -0.028278 | -0.0070912 | 0.028288 | 0.0070972 | 9.6847e-06 | 6.0159e-06 | 0.042594 | 0.042594 | 0.042594 | 0.98794 | -0.23078 | 0.98831 | -0.2236 | 11.7017
33 | -0.094866 | -0.023948 | 0.095119 | 0.024109 | 0.00025221 | 0.00016098 | 0.14217 | 0.14217 | 0.14217 | 0.99333 | -0.12767 | 0.99621 | -0.072331 | 39.0584
34 | -0.32659 | -0.083644 | 0.32693 | 0.083859 | 0.00033729 | 0.00021542 | 0.48802 | 0.48802 | 0.48802 | 0.99711 | -0.054655 | 0.99823 | -0.033362 | 44.6906
35 | 0.32659 | 0.083644 | -0.32523 | -0.082775 | 0.0013607 | 0.00086908 | 0.48802 | 0.48802 | 0.48802 | 0.99711 | -0.054655 | 0.99257 | -0.14105 | 44.6906
36 | -0.32892 | -0.084359 | 0.32939 | 0.08466 | 0.00047121 | 0.00030096 | 0.49099 | 0.49099 | 0.49099 | 0.99823 | -0.033362 | 0.99979 | -0.0038701 | 44.9625
37 | 0.24254 | 0.061922 | -0.24229 | -0.061768 | 0.00024124 | 0.00015383 | 0.364 | 0.364 | 0.364 | 0.99257 | -0.14105 | 0.99149 | -0.16165 | 33.3337
38 | 0.082695 | 0.020853 | -0.082666 | -0.020834 | 2.8851e-05 | 1.84e-05 | 0.12402 | 0.12402 | 0.12402 | 0.99257 | -0.14105 | 0.99219 | -0.14834 | 34.0708
39 | 0.0050592 | 0.0012679 | -0.005059 | -0.0012679 | 2.6812e-07 | 9.6381e-09 | 0.007569 | 0.0075691 | 0.0075691 | 0.99461 | -0.10325 | 0.99455 | -0.10437 | 2.0794
40 | -0.013483 | -0.0033785 | 0.013488 | 0.0033813 | 5.0082e-06 | 2.7791e-06 | 0.020172 | 0.020172 | 0.020172 | 0.99461 | -0.10325 | 0.99501 | -0.095459 | 5.5418
41 | 0.036567 | 0.0091752 | -0.036548 | -0.0091635 | 1.868e-05 | 1.1745e-05 | 0.05506 | 0.05506 | 0.05506 | 0.98831 | -0.2236 | 0.98775 | -0.23432 | 15.1263
42 | -0.064855 | -0.016272 | 0.064934 | 0.016323 | 7.9207e-05 | 5.0408e-05 | 0.097654 | 0.097654 | 0.097654 | 0.98831 | -0.2236 | 0.98962 | -0.19802 | 26.828
43 | -0.018348 | -0.0045992 | 0.018352 | 0.0046016 | 4.0706e-06 | 2.4179e-06 | 0.027439 | 0.027439 | 0.027439 | 0.99501 | -0.095459 | 0.99525 | -0.090804 | 7.5382
44 | -0.023694 | -0.0059404 | 0.023716 | 0.0059538 | 2.1952e-05 | 1.3442e-05 | 0.035425 | 0.035425 | 0.035425 | 0.99525 | -0.090804 | 0.99626 | -0.07138 | 9.7322
45 | 0.20607 | 0.052328 | -0.20579 | -0.052147 | 0.00028424 | 0.00018101 | 0.31097 | 0.31098 | 0.31098 | 0.98682 | -0.25134 | 0.98533 | -0.28004 | 28.4776
46 | -0.20607 | -0.052328 | 0.20657 | 0.052648 | 0.00050277 | 0.00032018 | 0.31097 | 0.31097 | 0.31097 | 0.98682 | -0.25134 | 0.98945 | -0.20077 | 28.4776
47 | 0.0062685 | 0.001571 | -0.0062675 | -0.0015708 | 9.635e-07 | 2.5151e-07 | 0.0094665 | 0.0094666 | 0.0094666 | 0.98533 | -0.28004 | 0.98517 | -0.28327 | 2.6007
48 | 0.19952 | 0.050576 | -0.19935 | -0.050467 | 0.00017088 | 0.00010879 | 0.30151 | 0.30151 | 0.30151 | 0.98533 | -0.28004 | 0.98441 | -0.29788 | 27.6107
49 | 0.017878 | 0.0044813 | -0.017875 | -0.0044798 | 2.6305e-06 | 1.5589e-06 | 0.026886 | 0.026886 | 0.026886 | 0.98945 | -0.20077 | 0.98929 | -0.20386 | 7.3864
50 | -0.22445 | -0.05713 | 0.22471 | 0.057298 | 0.00026369 | 0.00016805 | 0.33786 | 0.33786 | 0.33786 | 0.98945 | -0.20077 | 0.99072 | -0.17643 | 30.9396
51 | -0.33583 | -0.086273 | 0.33589 | 0.086314 | 6.3132e-05 | 4.0325e-05 | 0.50057 | 0.50057 | 0.50057 | 0.99979 | -0.0038701 | 1 | 0 | 45.84
52 | 0.23304 | 0.059448 | -0.23287 | -0.059342 | 0.00016625 | 0.00010598 | 0.35011 | 0.35011 | 0.35011 | 0.99149 | -0.16165 | 0.99072 | -0.17643 | 32.0613
53 | 0.073746 | 0.018599 | -0.073571 | -0.018487 | 0.00017491 | 0.00011145 | 0.11064 | 0.11064 | 0.11064 | 0.99219 | -0.14834 | 0.98962 | -0.19802 | 30.3957
54 | 0.0094048 | 0.0023574 | -0.0094033 | -0.0023567 | 1.4724e-06 | 6.9045e-07 | 0.014146 | 0.014146 | 0.014146 | 0.98929 | -0.20386 | 0.98912 | -0.20715 | 3.8863
55 | 0.0084703 | 0.0021224 | -0.0084673 | -0.0021211 | 3.0657e-06 | 1.3156e-06 | 0.01274 | 0.01274 | 0.01274 | 0.98929 | -0.20386 | 0.9889 | -0.21146 | 3.5001
56 | 0.19694 | 0.049865 | -0.1968 | -0.049776 | 0.00013928 | 8.8663e-05 | 0.29788 | 0.29788 | 0.29788 | 0.98441 | -0.29788 | 0.98365 | -0.31262 | 27.2781
57 | 0.098364 | 0.024925 | -0.09836 | -0.024922 | 4.4946e-06 | 2.8693e-06 | 0.14701 | 0.14701 | 0.14701 | 0.99626 | -0.07138 | 0.99621 | -0.072331 | 40.3882
58 | -0.12208 | -0.030878 | 0.12232 | 0.031034 | 0.0002432 | 0.0001554 | 0.18244 | 0.18244 | 0.18244 | 0.99626 | -0.07138 | 0.99843 | -0.029946 | 50.1204
59 | -0.0073106 | -0.0018322 | 0.0073112 | 0.0018324 | 6.7564e-07 | 2.4817e-07 | 0.011101 | 0.011101 | 0.011101 | 0.97997 | -0.38438 | 0.98007 | -0.38244 | 3.0496
60 | -0.011355 | -0.0028459 | 0.011357 | 0.0028468 | 1.6018e-06 | 8.4403e-07 | 0.01724 | 0.01724 | 0.01724 | 0.98007 | -0.38244 | 0.98022 | -0.37948 | 4.7364
61 | -0.0027349 | -0.00068501 | 0.0027352 | 0.00068463 | 2.7664e-07 | -3.8101e-07 | 0.0041168 | 0.0041166 | 0.0041168 | 0.98848 | -0.21959 | 0.98859 | -0.21746 | 1.131
62 | 0.0027349 | 0.00068501 | -0.0027346 | -0.00068536 | 2.5489e-07 | -3.509e-07 | 0.0041168 | 0.004117 | 0.004117 | 0.98848 | -0.21959 | 0.98838 | -0.22155 | 1.131
63 | -0.0055921 | -0.0014007 | 0.0055937 | 0.0014009 | 1.5987e-06 | 2.5133e-07 | 0.0084169 | 0.0084166 | 0.0084169 | 0.98859 | -0.21746 | 0.9889 | -0.21146 | 2.3123
64 | 0.12581 | 0.031979 | -0.12563 | -0.031863 | 0.00018116 | 0.00011576 | 0.18737 | 0.18737 | 0.18737 | 1 | 0 | 0.99843 | -0.029946 | 51.4748
65 | 0.001915 | 0.00047973 | -0.001915 | -0.00047978 | 1.4501e-08 | -5.005e-08 | 0.0028865 | 0.0028866 | 0.0028866 | 0.98714 | -0.2462 | 0.98714 | -0.24636 | 0.79301
66 | 0.010261 | 0.0025716 | -0.010255 | -0.0025687 | 5.7136e-06 | 2.843e-06 | 0.015467 | 0.015468 | 0.015468 | 0.98714 | -0.2462 | 0.98654 | -0.25789 | 4.2493
67 | -0.012176 | -0.0030513 | 0.012178 | 0.0030525 | 2.2943e-06 | 1.2361e-06 | 0.018354 | 0.018354 | 0.018354 | 0.98714 | -0.2462 | 0.98735 | -0.24224 | 5.0423
68 | 0.001915 | 0.00047978 | -0.0019149 | -0.00047992 | 4.1916e-08 | -1.4466e-07 | 0.0028866 | 0.0028866 | 0.0028866 | 0.98714 | -0.24636 | 0.98711 | -0.24682 | 0.79303
69 | 0.0093684 | 0.0023465 | -0.0093669 | -0.0023458 | 1.4825e-06 | 6.9602e-07 | 0.01413 | 0.01413 | 0.01413 | 0.98654 | -0.25789 | 0.98637 | -0.26122 | 3.8819
70 | 0.0092768 | 0.0023253 | -0.0092748 | -0.0023243 | 2.053e-06 | 9.5579e-07 | 0.013981 | 0.013981 | 0.013981 | 0.98735 | -0.24224 | 0.98711 | -0.24689 | 3.841
71 | -0.021455 | -0.0053778 | 0.021463 | 0.0053824 | 7.5162e-06 | 4.5651e-06 | 0.032335 | 0.032335 | 0.032335 | 0.98735 | -0.24224 | 0.98772 | -0.23489 | 8.8832
72 | 0.0061796 | 0.0015487 | -0.0061793 | -0.0015487 | 2.7299e-07 | 6.66e-08 | 0.0092964 | 0.0092964 | 0.0092964 | 0.98912 | -0.20715 | 0.98907 | -0.20807 | 2.554
73 | 0.1968 | 0.049776 | -0.19662 | -0.049657 | 0.00018787 | 0.00011959 | 0.29788 | 0.29788 | 0.29788 | 0.98365 | -0.31262 | 0.98263 | -0.33254 | 27.2782
74 | -0.02247 | -0.005632 | 0.022472 | 0.005633 | 1.61e-06 | 9.8386e-07 | 0.034111 | 0.034111 | 0.034111 | 0.98022 | -0.37948 | 0.98029 | -0.37798 | 9.3711
75 | -0.0093634 | -0.0023467 | 0.0093642 | 0.0023471 | 7.7926e-07 | 3.7193e-07 | 0.014294 | 0.014294 | 0.014294 | 0.97476 | -0.48627 | 0.97485 | -0.48452 | 3.9268
76 | -0.011698 | -0.002932 | 0.011701 | 0.0029333 | 2.3936e-06 | 1.2822e-06 | 0.017856 | 0.017856 | 0.017856 | 0.97485 | -0.48452 | 0.97507 | -0.48023 | 4.9055
77 | -0.013641 | -0.0034197 | 0.013642 | 0.0034202 | 7.4214e-07 | 4.1801e-07 | 0.020818 | 0.020818 | 0.020818 | 0.97507 | -0.48023 | 0.97513 | -0.47909 | 5.7193
78 | -0.016707 | -0.0041884 | 0.016711 | 0.0041905 | 3.6814e-06 | 2.1677e-06 | 0.025495 | 0.025495 | 0.025495 | 0.97513 | -0.47909 | 0.97536 | -0.47446 | 7.0042
79 | -0.0093656 | -0.002347 | 0.0093656 | 0.002347 | 2.0749e-08 | 9.7467e-09 | 0.014134 | 0.014134 | 0.014134 | 0.98601 | -0.26931 | 0.98602 | -0.26926 | 3.8829
80 | 0.067982 | 0.01711 | -0.06797 | -0.017103 | 1.1958e-05 | 7.6161e-06 | 0.10374 | 0.10374 | 0.10374 | 0.97536 | -0.47446 | 0.97517 | -0.47814 | 28.5
81 | -0.084693 | -0.021301 | 0.084814 | 0.021378 | 0.00012081 | 7.7078e-05 | 0.12924 | 0.12924 | 0.12924 | 0.97536 | -0.47446 | 0.97688 | -0.44465 | 35.5043
82 | -0.0093656 | -0.002347 | 0.0093673 | 0.0023478 | 1.6549e-06 | 7.7728e-07 | 0.014134 | 0.014134 | 0.014134 | 0.98602 | -0.26926 | 0.98621 | -0.26556 | 3.8829
83 | 0.027522 | 0.0069033 | -0.027508 | -0.0068948 | 1.3563e-05 | 8.4121e-06 | 0.041502 | 0.041502 | 0.041502 | 0.98682 | -0.25361 | 0.98629 | -0.26395 | 11.4016
84 | 0.052645 | 0.013259 | -0.052608 | -0.013236 | 3.7258e-05 | 2.3653e-05 | 0.080354 | 0.080354 | 0.080354 | 0.97517 | -0.47814 | 0.97442 | -0.49295 | 22.0754
85 | 0.015325 | 0.0038433 | -0.01532 | -0.00384 | 5.6378e-06 | 3.2654e-06 | 0.023386 | 0.023386 | 0.023386 | 0.97517 | -0.47814 | 0.97478 | -0.48586 | 6.4247
86 | -0.088197 | -0.022226 | 0.088313 | 0.0223 | 0.00011684 | 7.4561e-05 | 0.13439 | 0.13439 | 0.13439 | 0.97688 | -0.44465 | 0.97829 | -0.41699 | 36.9197
87 | -0.020028 | -0.0050197 | 0.02003 | 0.0050206 | 1.5275e-06 | 9.2066e-07 | 0.030219 | 0.030219 | 0.030219 | 0.98621 | -0.26556 | 0.98629 | -0.26395 | 8.302
88 | 0.028267 | 0.007088 | -0.028266 | -0.0070875 | 7.7979e-07 | 4.8439e-07 | 0.042585 | 0.042585 | 0.042585 | 0.98775 | -0.23432 | 0.98772 | -0.23489 | 11.699
89 | 0.0070301 | 0.0017617 | -0.0070298 | -0.0017617 | 2.5076e-07 | 8.4377e-08 | 0.010597 | 0.010597 | 0.010597 | 0.98711 | -0.24689 | 0.98707 | -0.24764 | 2.9114
90 | 0.0011842 | 0.0002966 | -0.0011842 | -0.00029678 | 1.8249e-08 | -1.8351e-07 | 0.0017851 | 0.0017852 | 0.0017852 | 0.98707 | -0.24764 | 0.98705 | -0.24796 | 0.49043
91 | 0.0086164 | 0.0021577 | -0.0086148 | -0.002157 | 1.6342e-06 | 7.1672e-07 | 0.012998 | 0.012998 | 0.012998 | 0.98637 | -0.26122 | 0.98617 | -0.2652 | 3.5709
92 | 0.0076516 | 0.0019156 | -0.0076497 | -0.0019148 | 1.8817e-06 | 7.2405e-07 | 0.011545 | 0.011545 | 0.011545 | 0.98617 | -0.2652 | 0.9859 | -0.27037 | 3.1716
93 | 0.0048892 | 0.0012253 | -0.0048891 | -0.0012253 | 9.6223e-08 | 7.1727e-10 | 0.0073556 | 0.0073556 | 0.0073556 | 0.98907 | -0.20807 | 0.98905 | -0.20849 | 2.0208
94 | 0.0054267 | 0.0013577 | -0.0054263 | -0.0013576 | 3.9863e-07 | 5.3027e-08 | 0.0081896 | 0.0081897 | 0.0081897 | 0.9859 | -0.27037 | 0.98583 | -0.27191 | 2.2499
95 | 0.0054263 | 0.0013576 | -0.0054262 | -0.0013576 | 1.0209e-07 | 1.3586e-08 | 0.0081897 | 0.0081897 | 0.0081897 | 0.98583 | -0.27191 | 0.98581 | -0.27231 | 2.2499
96 | 0.0054262 | 0.0013576 | -0.0054255 | -0.0013575 | 6.325e-07 | 8.4227e-08 | 0.0081897 | 0.0081898 | 0.0081898 | 0.98581 | -0.27231 | 0.98568 | -0.27476 | 2.2499
97 | 0.0037215 | 0.00093047 | -0.0037209 | -0.00093073 | 5.8115e-07 | -2.5394e-07 | 0.0056173 | 0.0056176 | 0.0056176 | 0.98568 | -0.27476 | 0.98551 | -0.27804 | 1.5433
98 | 0.0031065 | 0.00077675 | -0.0031064 | -0.0007769 | 1.6946e-07 | -1.5331e-07 | 0.0046899 | 0.00469 | 0.00469 | 0.98551 | -0.27804 | 0.98545 | -0.27919 | 1.2885
99 | 0.0011762 | 0.00029431 | -0.0011762 | -0.00029477 | 4.5442e-08 | -4.6038e-07 | 0.0017759 | 0.0017761 | 0.0017761 | 0.98545 | -0.27919 | 0.98541 | -0.28 | 0.48793
100 | 0.0019302 | 0.00048259 | -0.0019301 | -0.00048268 | 2.7215e-08 | -9.146e-08 | 0.0029141 | 0.0029141 | 0.0029141 | 0.98545 | -0.27919 | 0.98544 | -0.27949 | 0.80059
101 | -0.0004659 | -0.00011677 | 0.00046591 | 0.00011636 | 5.9132e-09 | -4.0217e-07 | 0.00070352 | 0.00070338 | 0.00070352 | 0.98542 | -0.27975 | 0.98544 | -0.27949 | 0.19328
102 | 0.0014642 | 0.00036631 | -0.0014642 | -0.0003664 | 1.3966e-08 | -8.8139e-08 | 0.0022108 | 0.0022108 | 0.0022108 | 0.98544 | -0.27949 | 0.98543 | -0.27969 | 0.60736
103 | 0.00090609 | 0.00022679 | -0.00090607 | -0.00022708 | 1.6874e-08 | -2.9544e-07 | 0.0013681 | 0.0013682 | 0.0013682 | 0.98543 | -0.27969 | 0.98541 | -0.28008 | 0.37588
104 | 0.00055812 | 0.00013961 | -0.00055812 | -0.00013988 | 5.6109e-09 | -2.6481e-07 | 0.00084268 | 0.00084278 | 0.00084278 | 0.98543 | -0.27969 | 0.98542 | -0.2799 | 0.23153
105 | 0.093775 | 0.023692 | -0.093716 | -0.023654 | 5.9197e-05 | 3.7496e-05 | 0.14261 | 0.14261 | 0.14261 | 0.97897 | -0.40382 | 0.97829 | -0.41699 | 19.5887
106 | -0.098524 | -0.024882 | 0.09856 | 0.024905 | 3.6036e-05 | 2.2578e-05 | 0.14982 | 0.14982 | 0.14982 | 0.97897 | -0.40382 | 0.97936 | -0.39619 | 13.7201
107 | -0.10027 | -0.025334 | 0.10029 | 0.025345 | 1.7994e-05 | 1.1282e-05 | 0.15243 | 0.15243 | 0.15243 | 0.97936 | -0.39619 | 0.97955 | -0.39244 | 13.9585
108 | -0.10029 | -0.025345 | 0.10036 | 0.025389 | 6.9612e-05 | 4.3646e-05 | 0.15243 | 0.15243 | 0.15243 | 0.97955 | -0.39244 | 0.98029 | -0.37798 | 13.9585
109 | -0.12283 | -0.031022 | 0.12293 | 0.031084 | 9.8003e-05 | 6.1869e-05 | 0.18654 | 0.18654 | 0.18654 | 0.98029 | -0.37798 | 0.98115 | -0.36134 | 17.0822
110 | -0.12293 | -0.031084 | 0.12294 | 0.031089 | 8.5292e-06 | 5.3844e-06 | 0.18654 | 0.18654 | 0.18654 | 0.98115 | -0.36134 | 0.98122 | -0.35989 | 17.0821
111 | -0.0097929 | -0.0024546 | 0.0097942 | 0.0024552 | 1.2691e-06 | 6.1831e-07 | 0.014849 | 0.014849 | 0.014849 | 0.98132 | -0.35794 | 0.98146 | -0.35522 | 4.0795
112 | 0.0097929 | 0.0024546 | -0.0097919 | -0.0024541 | 1.0261e-06 | 4.9993e-07 | 0.014849 | 0.014849 | 0.014849 | 0.98132 | -0.35794 | 0.98121 | -0.36014 | 4.0795
113 | -0.015094 | -0.0037833 | 0.015095 | 0.0037844 | 1.9275e-06 | 1.1096e-06 | 0.022884 | 0.022884 | 0.022884 | 0.98146 | -0.35522 | 0.9816 | -0.35254 | 6.2868
114 | 0.050075 | 0.012601 | -0.050027 | -0.012571 | 4.7826e-05 | 3.0338e-05 | 0.076487 | 0.076487 | 0.076487 | 0.97442 | -0.49295 | 0.9734 | -0.51296 | 21.0128
115 | 0.012164 | 0.0030491 | -0.012163 | -0.0030486 | 8.4804e-07 | 4.6099e-07 | 0.018569 | 0.018569 | 0.018569 | 0.97478 | -0.48586 | 0.97471 | -0.48733 | 5.1013
116 | -0.13303 | -0.033619 | 0.13308 | 0.033648 | 4.6896e-05 | 2.9664e-05 | 0.20184 | 0.20184 | 0.20184 | 0.98122 | -0.35989 | 0.9816 | -0.35254 | 18.4837
117 | -0.14817 | -0.037433 | 0.14823 | 0.037465 | 5.1088e-05 | 3.239e-05 | 0.22473 | 0.22473 | 0.22473 | 0.9816 | -0.35254 | 0.98197 | -0.34535 | 20.5792
118 | 0.039771 | 0.01 | -0.039759 | -0.0099922 | 1.2293e-05 | 7.7572e-06 | 0.060809 | 0.060809 | 0.060809 | 0.9734 | -0.51296 | 0.97307 | -0.51944 | 16.7057
119 | 0.010256 | 0.0025707 | -0.010255 | -0.0025701 | 1.1882e-06 | 6.0023e-07 | 0.015678 | 0.015678 | 0.015678 | 0.9734 | -0.51296 | 0.97328 | -0.51539 | 4.3071
120 | 0.010294 | 0.0025801 | -0.010293 | -0.0025798 | 5.6148e-07 | 2.8378e-07 | 0.015715 | 0.015715 | 0.015715 | 0.97471 | -0.48733 | 0.97465 | -0.48847 | 4.3172
121 | 0.03889 | 0.0097744 | -0.038884 | -0.0097706 | 5.9669e-06 | 3.763e-06 | 0.05948 | 0.05948 | 0.05948 | 0.97307 | -0.51944 | 0.97291 | -0.52265 | 16.3407
122 | 0.0067524 | 0.0016924 | -0.0067516 | -0.0016921 | 8.2857e-07 | 2.7268e-07 | 0.010324 | 0.010324 | 0.010324 | 0.97328 | -0.51539 | 0.97315 | -0.51797 | 2.8362
123 | 0.0087434 | 0.0021914 | -0.0087425 | -0.002191 | 8.8428e-07 | 4.0103e-07 | 0.013349 | 0.013349 | 0.013349 | 0.97465 | -0.48847 | 0.97454 | -0.4906 | 3.6673
124 | 0.0055498 | 0.0013908 | -0.0055494 | -0.0013908 | 4.3064e-07 | 7.6368e-08 | 0.008474 | 0.008474 | 0.008474 | 0.97454 | -0.4906 | 0.97446 | -0.49222 | 2.328
125 | 0.0023929 | 0.00059966 | -0.0023929 | -0.00059971 | 2.8298e-08 | -5.2297e-08 | 0.003654 | 0.003654 | 0.003654 | 0.97446 | -0.49222 | 0.97445 | -0.49247 | 1.0038
126 | 0.029048 | 0.0072919 | -0.029027 | -0.0072788 | 2.1039e-05 | 1.3114e-05 | 0.044486 | 0.044486 | 0.044486 | 0.97173 | -0.5459 | 0.97097 | -0.5611 | 12.2214
127 | -0.030358 | -0.00762 | 0.030365 | 0.0076248 | 7.6888e-06 | 4.8033e-06 | 0.046491 | 0.046491 | 0.046491 | 0.97173 | -0.5459 | 0.972 | -0.5406 | 12.7722
128 | 0.026352 | 0.0066082 | -0.026351 | -0.006608 | 3.0944e-07 | 1.9178e-07 | 0.040386 | 0.040386 | 0.040386 | 0.97097 | -0.5611 | 0.97095 | -0.56135 | 11.0949
129 | -0.030365 | -0.0076248 | 0.03037 | 0.0076278 | 4.783e-06 | 2.988e-06 | 0.046491 | 0.046491 | 0.046491 | 0.972 | -0.5406 | 0.97217 | -0.5373 | 12.7722
130 | 0.023875 | 0.0059874 | -0.023871 | -0.005985 | 3.9828e-06 | 2.4509e-06 | 0.036591 | 0.036591 | 0.036591 | 0.97095 | -0.56135 | 0.97078 | -0.56485 | 10.0524
131 | -0.031466 | -0.0079024 | 0.031466 | 0.0079024 | 4.9234e-08 | 3.0808e-08 | 0.048168 | 0.048168 | 0.048168 | 0.97217 | -0.5373 | 0.97217 | -0.53726 | 13.2329
132 | 0.0048291 | 0.0012102 | -0.0048288 | -0.0012101 | 3.029e-07 | 1.1599e-08 | 0.007402 | 0.0074021 | 0.0074021 | 0.97078 | -0.56485 | 0.97071 | -0.56617 | 2.0335
133 | 0.019042 | 0.0047748 | -0.019038 | -0.0047723 | 4.0899e-06 | 2.4593e-06 | 0.029189 | 0.029189 | 0.029189 | 0.97078 | -0.56485 | 0.97055 | -0.56936 | 8.0189
134 | -0.03239 | -0.008134 | 0.03239 | 0.0081341 | 5.7242e-08 | 3.5866e-08 | 0.049582 | 0.049582 | 0.049582 | 0.97217 | -0.53726 | 0.97217 | -0.53723 | 13.6215
135 | 0.0024136 | 0.00060485 | -0.0024136 | -0.0006049 | 2.9636e-08 | -5.2402e-08 | 0.0036998 | 0.0036999 | 0.0036999 | 0.97071 | -0.56617 | 0.9707 | -0.56642 | 1.0164
136 | 0.016498 | 0.0041357 | -0.016496 | -0.0041349 | 1.4325e-06 | 8.4301e-07 | 0.025294 | 0.025294 | 0.025294 | 0.97055 | -0.56936 | 0.97046 | -0.57118 | 6.949
137 | -0.033304 | -0.0083631 | 0.033315 | 0.0083701 | 1.1126e-05 | 6.9793e-06 | 0.050981 | 0.050981 | 0.050981 | 0.97217 | -0.53723 | 0.97253 | -0.53023 | 14.0058
138 | 0.014024 | 0.0035151 | -0.014023 | -0.0035145 | 1.0564e-06 | 6.0083e-07 | 0.021503 | 0.021503 | 0.021503 | 0.97046 | -0.57118 | 0.97038 | -0.57276 | 5.9074
139 | -0.034438 | -0.0086516 | 0.034444 | 0.0086551 | 5.5146e-06 | 3.4636e-06 | 0.0527 | 0.0527 | 0.0527 | 0.97253 | -0.53023 | 0.9727 | -0.52687 | 14.478
140 | 0.011402 | 0.0028577 | -0.011401 | -0.0028574 | 5.077e-07 | 2.7022e-07 | 0.017484 | 0.017484 | 0.017484 | 0.97038 | -0.57276 | 0.97033 | -0.57369 | 4.8032
141 | -0.035565 | -0.0089361 | 0.035571 | 0.0089396 | 5.6788e-06 | 3.5709e-06 | 0.054415 | 0.054415 | 0.054415 | 0.9727 | -0.52687 | 0.97287 | -0.52353 | 14.9491
142 | -0.038015 | -0.0095521 | 0.038016 | 0.0095531 | 1.5898e-06 | 1.0019e-06 | 0.058153 | 0.058153 | 0.058153 | 0.97287 | -0.52353 | 0.97291 | -0.52265 | 15.976
143 | -0.011086 | -0.0027783 | 0.011087 | 0.0027792 | 1.7838e-06 | 9.2965e-07 | 0.016824 | 0.016824 | 0.016824 | 0.98048 | -0.37453 | 0.98065 | -0.37116 | 4.622
144 | -0.016717 | -0.0041903 | 0.016721 | 0.0041926 | 3.9773e-06 | 2.3375e-06 | 0.025367 | 0.025367 | 0.025367 | 0.98065 | -0.37116 | 0.98091 | -0.36616 | 6.9689
145 | 0.0056301 | 0.001411 | -0.0056301 | -0.001411 | 9.2485e-09 | 1.6557e-09 | 0.008543 | 0.008543 | 0.008543 | 0.98065 | -0.37116 | 0.98065 | -0.37119 | 2.347
146 | -0.021977 | -0.0055097 | 0.021983 | 0.0055133 | 5.8508e-06 | 3.5672e-06 | 0.033339 | 0.033339 | 0.033339 | 0.98091 | -0.36616 | 0.98119 | -0.36058 | 9.1591
147 | -0.045147 | -0.01132 | 0.045179 | 0.011341 | 3.2781e-05 | 2.0744e-05 | 0.068469 | 0.068469 | 0.068469 | 0.98119 | -0.36058 | 0.98197 | -0.34535 | 18.8101
148 | 0.019245 | 0.0048249 | -0.019242 | -0.0048226 | 3.7328e-06 | 2.2414e-06 | 0.029187 | 0.029187 | 0.029187 | 0.98119 | -0.36058 | 0.98098 | -0.36465 | 8.0184
149 | -0.1934 | -0.048806 | 0.19352 | 0.048882 | 0.00011875 | 7.5582e-05 | 0.29319 | 0.29319 | 0.29319 | 0.98197 | -0.34535 | 0.98263 | -0.33254 | 26.8492
150 | 0.0097614 | 0.0024467 | -0.0097603 | -0.0024462 | 1.061e-06 | 5.1615e-07 | 0.014807 | 0.014807 | 0.014807 | 0.98098 | -0.36465 | 0.98087 | -0.36693 | 4.0678
151 | 0.0061143 | 0.0015324 | -0.0061142 | -0.0015324 | 9.7636e-08 | 2.4292e-08 | 0.0092757 | 0.0092757 | 0.0092757 | 0.98087 | -0.36693 | 0.98085 | -0.36727 | 2.5483

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46804 | 0.11947

## res_load
| p_mw | q_mvar
0 | 0.0029643 | 0.00074294
1 | 0.0081349 | 0.0020388
2 | 0.0085379 | 0.0021398
3 | 0.0024647 | 0.00061772
4 | 0.0024661 | 0.00061806
5 | 0.0034074 | 0.00085396
6 | 0.0056158 | 0.0014074
7 | 0.0074196 | 0.0018595
8 | 0.0060531 | 0.001517
9 | 0.00091119 | 0.00022837
10 | 0.00070384 | 0.0001764
11 | 0.0024863 | 0.00062313
12 | 0.0027692 | 0.00069403
13 | 0.0027783 | 0.00069631
14 | 0.0056446 | 0.0014147
15 | 0.0045783 | 0.0011474
16 | 0.0039434 | 0.00098832
17 | 0.013169 | 0.0033005
18 | 0.0065752 | 0.0016479
19 | 0.0081927 | 0.0020533
20 | 0.0019921 | 0.00049926
21 | 0.005059 | 0.0012679
22 | 0.0048594 | 0.0012179
23 | 0.0053417 | 0.0013388
24 | 0.006439 | 0.0016138
25 | 0.0092588 | 0.0023205
26 | 0.0089201 | 0.0022356
27 | 0.0081553 | 0.0020439
28 | 0.0062675 | 0.0015708
29 | 0.0024028 | 0.0006022
30 | 0.0073106 | 0.0018322
31 | 0.0040439 | 0.0010135
32 | 0.002857 | 0.00071603
33 | 0.0027346 | 0.00068536
34 | 0.0046857 | 0.0011743
35 | 0.0086369 | 0.0021646
36 | 0.00088688 | 0.00022227
37 | 0.0032238 | 0.00080796
38 | 0.0028735 | 0.00072017
39 | 0.0032409 | 0.00081226
40 | 0.0033079 | 0.00082904
41 | 0.011113 | 0.0027852
42 | 0.0093634 | 0.0023467
43 | 0.0023339 | 0.00058494
44 | 0.001941 | 0.00048645
45 | 0.0030652 | 0.0007682
46 | 0.005958 | 0.0014932
47 | 0.0081859 | 0.0020516
48 | 0.0033825 | 0.00084773
49 | 0.010661 | 0.0026719
50 | 0.0082812 | 0.0020755
51 | 0.0068036 | 0.0017052
52 | 0.0022447 | 0.00056257
53 | 0.0058457 | 0.0014651
54 | 0.0019149 | 0.00047992
55 | 0.00075047 | 0.00018808
56 | 0.0011842 | 0.00029678
57 | 0.00096319 | 0.0002414
58 | 0.0012901 | 0.00032332
59 | 0.002223 | 0.00055714
60 | 0.001704 | 0.00042707
61 | 0.00061439 | 0.00015398
62 | 0.0004659 | 0.00011677
63 | 0.0011762 | 0.00029477
64 | 0.00090607 | 0.00022708
65 | 0.00055812 | 0.00013988
66 | 0.0048891 | 0.0012253
67 | 0.004749 | 0.0011902
68 | 0.0054028 | 0.0013541
69 | 0.0017136 | 0.00042946
70 | 0.0052993 | 0.0013281
71 | 0.0097919 | 0.0024541
72 | 0.0025327 | 0.00063475
73 | 0.0031558 | 0.00079091
74 | 0.010092 | 0.0025294
75 | 0.0018696 | 0.00046856
76 | 0.00086905 | 0.0002178
77 | 0.0035022 | 0.00087773
78 | 0.0015497 | 0.00038838
79 | 0.0031927 | 0.00080016
80 | 0.0031565 | 0.0007911
81 | 0.0023929 | 0.00059971
82 | 0.0013092 | 0.00032813
83 | 0.0026756 | 0.00067058
84 | 0.0024761 | 0.00062056
85 | 0.0010957 | 0.0002746
86 | 0.00092421 | 0.00023163
87 | 0.0024152 | 0.0006053
88 | 0.0025402 | 0.00063663
89 | 0.00091391 | 0.00022905
90 | 0.0024136 | 0.0006049
91 | 0.0024727 | 0.00061972
92 | 0.0011234 | 0.00028154
93 | 0.002621 | 0.00065689
94 | 0.001121 | 0.00028095
95 | 0.002444 | 0.00061252
96 | 0.00086781 | 0.00021749
97 | 0.0067516 | 0.0016921
98 | 0.011086 | 0.0027783
99 | 0.0052554 | 0.0013171
100 | 0.0056301 | 0.001411
101 | 0.0039187 | 0.00098213
102 | 0.0094801 | 0.0023759
103 | 0.0030931 | 0.00077521
104 | 0.003646 | 0.00091379
105 | 0.0061142 | 0.0015324
106 | 0.0074784 | 0.0018743
107 | 0.011401 | 0.0028574

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1