## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_159-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_159-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_159-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_159-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_159-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_159-4_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_159-4_0_3_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_159-4_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_159-4_0_3_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_159-4_0_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_159-4_0_3_node_43 | 0.4 | n |  | TRUE
11 | bus_LV_159-4_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_159-4_0_3_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_159-4_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_159-4_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_159-4_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_159-4_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_159-4_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_159-4_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_159-4_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_159-4_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_159-4_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_159-4_0_3_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_159-4_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_159-4_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_159-4_0_3_node_80 | 0.4 | n |  | TRUE
26 | bus_LV_159-4_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_159-4_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_159-4_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_159-4_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_159-4_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_159-4_0_3_node_81 | 0.4 | n |  | TRUE
32 | bus_LV_159-4_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_159-4_0_3_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_159-4_0_3_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_159-4_0_3_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_159-4_0_3_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_159-4_0_3_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_159-4_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_159-4_0_3_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_159-4_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_159-4_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_159-4_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_159-4_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_159-4_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_159-4_0_3_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_159-4_0_3_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_159-4_0_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_159-4_0_3_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_159-4_0_3_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_159-4_0_3_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_159-4_0_3_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_159-4_0_3_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_159-4_0_3_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_159-4_0_3_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_159-4_0_3_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_159-4_0_3_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_159-4_0_3_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_159-4_0_3_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_159-4_0_3_node_60 | 0.4 | n |  | TRUE
60 | bus_LV_159-4_0_3_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_159-4_0_3_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_159-4_0_3_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_159-4_0_3_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_159-4_0_3_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_159-4_0_3_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_159-4_0_3_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_159-4_0_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_159-4_0_3_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_159-4_0_3_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_159-4_0_3_node_82 | 0.4 | n |  | TRUE
71 | bus_LV_159-4_0_3_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_159-4_0_3_node_77 | 0.4 | n |  | TRUE
73 | bus_LV_159-4_0_3_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_159-4_0_3_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_159-4_0_3_node_78 | 0.4 | n |  | TRUE
76 | bus_LV_159-4_0_3_node_79 | 0.4 | n |  | TRUE
77 | bus_MV_495_0_node_89 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_159-4_0_3_load_0 | 0 | 0.01335 | 0.0033458 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_159-4_0_3_load_1 | 1 | 0.004766 | 0.0011945 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_159-4_0_3_load_3 | 3 | 0.004814 | 0.0012065 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_159-4_0_3_load_4 | 4 | 0.014562 | 0.0036495 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_159-4_0_3_load_6 | 7 | 0.022924 | 0.0057452 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_159-4_0_3_load_26 | 8 | 0.0034732 | 0.00087047 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_159-4_0_3_load_25 | 9 | 0.0022019 | 0.00055184 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_159-4_0_3_load_7 | 11 | 0.011141 | 0.0027923 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_159-4_0_3_load_40 | 12 | 0.0065369 | 0.0016383 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_159-4_0_3_load_8 | 14 | 0.0092262 | 0.0023123 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_159-4_0_3_load_14 | 16 | 0.010945 | 0.0027431 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_159-4_0_3_load_9 | 17 | 0.0052056 | 0.0013046 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_159-4_0_3_load_11 | 19 | 0.0022221 | 0.00055691 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_159-4_0_3_load_12 | 20 | 0.0037935 | 0.00095075 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_159-4_0_3_load_28 | 22 | 0.0024637 | 0.00061746 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_159-4_0_3_load_80 | 25 | 0.0012442 | 0.00031183 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_159-4_0_3_load_19 | 26 | 0.0014212 | 0.0003562 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_159-4_0_3_load_18 | 27 | 0.0066331 | 0.0016624 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_159-4_0_3_load_27 | 30 | 0.0055162 | 0.0013825 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_159-4_0_3_load_81 | 31 | 0.001293 | 0.00032405 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_159-4_0_3_load_39 | 33 | 0.0034062 | 0.00085367 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_159-4_0_3_load_38 | 34 | 0.0016855 | 0.00042243 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_159-4_0_3_load_44 | 35 | 0.0037648 | 0.00094355 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_159-4_0_3_load_36 | 36 | 0.0014971 | 0.0003752 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_159-4_0_3_load_29 | 37 | 0.0026135 | 0.00065499 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_159-4_0_3_load_30 | 38 | 0.0022695 | 0.0005688 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_159-4_0_3_load_31 | 39 | 0.0022683 | 0.00056848 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_159-4_0_3_load_32 | 40 | 0.001397 | 0.00035012 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_159-4_0_3_load_33 | 41 | 0.0059961 | 0.0015028 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_159-4_0_3_load_35 | 43 | 0.0020101 | 0.00050378 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_159-4_0_3_load_37 | 44 | 0.001427 | 0.00035764 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_159-4_0_3_load_56 | 45 | 0.0027045 | 0.0006778 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_159-4_0_3_load_57 | 46 | 0.0017798 | 0.00044606 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_159-4_0_3_load_45 | 47 | 0.0035476 | 0.00088912 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_159-4_0_3_load_46 | 48 | 0.0012951 | 0.00032459 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_159-4_0_3_load_48 | 49 | 0.0043553 | 0.0010915 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_159-4_0_3_load_49 | 50 | 0.0022997 | 0.00057636 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_159-4_0_3_load_50 | 51 | 0.0083822 | 0.0021008 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_159-4_0_3_load_52 | 53 | 0.0010243 | 0.00025672 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_159-4_0_3_load_53 | 54 | 0.0049152 | 0.0012319 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_159-4_0_3_load_54 | 55 | 0.00089897 | 0.0002253 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_159-4_0_3_load_55 | 56 | 0.0016872 | 0.00042284 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_159-4_0_3_load_58 | 57 | 0.003052 | 0.00076491 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_159-4_0_3_load_59 | 58 | 0.0046404 | 0.001163 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_159-4_0_3_load_60 | 59 | 0.0013843 | 0.00034693 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_159-4_0_3_load_63 | 60 | 0.0013941 | 0.0003494 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_159-4_0_3_load_64 | 61 | 0.00055538 | 0.00013919 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_159-4_0_3_load_65 | 62 | 0.0021524 | 0.00053944 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_159-4_0_3_load_66 | 63 | 0.00087441 | 0.00021915 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_159-4_0_3_load_71 | 64 | 0.0059356 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_159-4_0_3_load_72 | 65 | 0.0062947 | 0.0015776 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_159-4_0_3_load_67 | 66 | 0.00080029 | 0.00020057 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_159-4_0_3_load_69 | 68 | 0.0024409 | 0.00061175 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_159-4_0_3_load_82 | 70 | 0.0042541 | 0.0010662 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_159-4_0_3_load_77 | 72 | 0.0011662 | 0.00029228 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_159-4_0_3_load_73 | 73 | 0.0026259 | 0.0006581 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_159-4_0_3_load_74 | 74 | 0.0010532 | 0.00026395 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_159-4_0_3_line_0 |  | 0 | 1 | 0.012865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_159-4_0_3_line_1 |  | 0 | 2 | 0.012651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_159-4_0_3_line_2 |  | 1 | 3 | 0.029367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_159-4_0_3_line_3 |  | 2 | 4 | 0.011188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_159-4_0_3_line_4 |  | 2 | 5 | 0.042688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_159-4_0_3_line_5 |  | 3 | 6 | 0.021407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_159-4_0_3_line_6 |  | 4 | 7 | 0.03338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_159-4_0_3_line_7 |  | 5 | 8 | 0.0097791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_159-4_0_3_line_8 |  | 5 | 9 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_159-4_0_3_line_9 |  | 6 | 10 | 0.053031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_159-4_0_3_line_10 |  | 7 | 11 | 0.017375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_159-4_0_3_line_11 |  | 8 | 12 | 0.032401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_159-4_0_3_line_12 |  | 9 | 13 | 0.027732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_159-4_0_3_line_13 |  | 10 | 45 | 0.034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_159-4_0_3_line_14 |  | 11 | 14 | 0.0075747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_159-4_0_3_line_15 |  | 13 | 30 | 0.0067761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_159-4_0_3_line_16 |  | 13 | 32 | 0.004125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_159-4_0_3_line_17 |  | 14 | 15 | 0.0091983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_159-4_0_3_line_18 |  | 15 | 16 | 0.011272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_159-4_0_3_line_19 |  | 16 | 23 | 0.051187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_159-4_0_3_line_20 |  | 17 | 18 | 0.025109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_159-4_0_3_line_21 |  | 18 | 19 | 0.02426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_159-4_0_3_line_22 |  | 18 | 20 | 0.021351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_159-4_0_3_line_23 |  | 20 | 21 | 0.0007573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_159-4_0_3_line_24 |  | 21 | 22 | 0.010132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_159-4_0_3_line_25 |  | 22 | 35 | 0.010715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_159-4_0_3_line_26 |  | 23 | 24 | 0.067962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_159-4_0_3_line_27 |  | 24 | 25 | 0.087872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_159-4_0_3_line_28 |  | 25 | 31 | 0.002592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_159-4_0_3_line_29 |  | 26 | 27 | 0.0046785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_159-4_0_3_line_30 |  | 27 | 32 | 0.02434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_159-4_0_3_line_31 |  | 28 | 29 | 0.004164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_159-4_0_3_line_32 |  | 28 | 30 | 0.015753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_159-4_0_3_line_33 |  | 29 | 33 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_159-4_0_3_line_34 |  | 31 | 76 | 0.077209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_159-4_0_3_line_35 |  | 33 | 34 | 0.018886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_159-4_0_3_line_36 |  | 34 | 44 | 0.011149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_159-4_0_3_line_37 |  | 35 | 36 | 0.0075943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_159-4_0_3_line_38 |  | 36 | 42 | 0.0096012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_159-4_0_3_line_39 |  | 37 | 38 | 0.032314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_159-4_0_3_line_40 |  | 37 | 39 | 0.0070413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_159-4_0_3_line_41 |  | 38 | 40 | 0.0032186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_159-4_0_3_line_42 |  | 39 | 41 | 0.01739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_159-4_0_3_line_43 |  | 40 | 42 | 0.005244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_159-4_0_3_line_44 |  | 42 | 43 | 0.029068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_159-4_0_3_line_45 |  | 43 | 44 | 0.0072554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_159-4_0_3_line_46 |  | 45 | 46 | 0.0012734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_159-4_0_3_line_47 |  | 46 | 56 | 3.8109e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_159-4_0_3_line_48 |  | 47 | 48 | 0.00051221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_159-4_0_3_line_49 |  | 48 | 49 | 0.024925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_159-4_0_3_line_50 |  | 49 | 50 | 0.037057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_159-4_0_3_line_51 |  | 50 | 51 | 0.018582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_159-4_0_3_line_52 |  | 51 | 52 | 0.018775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_159-4_0_3_line_53 |  | 52 | 53 | 0.01147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_159-4_0_3_line_54 |  | 53 | 54 | 0.002592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_159-4_0_3_line_55 |  | 54 | 55 | 0.0028168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_159-4_0_3_line_56 |  | 55 | 56 | 0.018701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_159-4_0_3_line_57 |  | 57 | 58 | 0.026019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_159-4_0_3_line_58 |  | 58 | 59 | 0.0040951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_159-4_0_3_line_59 |  | 59 | 60 | 0.0083396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_159-4_0_3_line_60 |  | 60 | 61 | 0.029076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_159-4_0_3_line_61 |  | 61 | 64 | 0.0018524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_159-4_0_3_line_62 |  | 62 | 63 | 0.032678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_159-4_0_3_line_63 |  | 63 | 66 | 0.033719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_159-4_0_3_line_64 |  | 64 | 65 | 0.029982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_159-4_0_3_line_65 |  | 65 | 68 | 0.02011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_159-4_0_3_line_66 |  | 66 | 67 | 0.055131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_159-4_0_3_line_67 |  | 67 | 68 | 0.040837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_159-4_0_3_line_68 |  | 67 | 69 | 0.10274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_159-4_0_3_line_69 |  | 69 | 70 | 0.10103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_159-4_0_3_line_70 |  | 69 | 71 | 0.15258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_159-4_0_3_line_71 |  | 71 | 72 | 0.13001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_159-4_0_3_line_72 |  | 71 | 73 | 0.076844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_159-4_0_3_line_73 |  | 72 | 75 | 0.0096572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_159-4_0_3_line_74 |  | 73 | 74 | 0.019532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_159-4_0_3_line_75 |  | 75 | 76 | 0.030608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_159-4_0_3_trafo_42 | 0.63 MVA 20/0.4 kV | 77 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2693579.7224 | 1236139.2562 | 2693570.2612 | 1236147.9743
1 | 2693589.0261 | 1236130.6833 | 2693579.7224 | 1236139.2562
2 | 2693570.2612 | 1236147.9743 | 2693568.7741 | 1236149.3446 | 2693551.6205 | 1236170.6402
3 | 2693589.0261 | 1236130.6833 | 2693600.2011 | 1236131.2137
4 | 2693551.7963 | 1236109.6038 | 2693589.0261 | 1236130.6833
5 | 2693543.2316 | 1236190.1279 | 2693548.9893 | 1236173.9066 | 2693551.6205 | 1236170.6402
6 | 2693631.9968 | 1236123.2155 | 2693624.7115 | 1236127.2986 | 2693607.2674 | 1236131.5491 | 2693600.2011 | 1236131.2137
7 | 2693551.7963 | 1236109.6038 | 2693546.15 | 1236117.5882
8 | 2693551.7963 | 1236109.6038 | 2693555.8921 | 1236097.9931 | 2693556.2832 | 1236091.9724
9 | 2693543.2316 | 1236190.1279 | 2693540.8793 | 1236196.7623 | 2693532.426 | 1236203.9345 | 2693509.2027 | 1236214.2654 | 2693502.3612 | 1236220.9738
10 | 2693631.9968 | 1236123.2155 | 2693647.1534 | 1236114.7208
11 | 2693546.15 | 1236117.5882 | 2693541.6247 | 1236123.9875 | 2693530.9402 | 1236134.4269 | 2693522.5851 | 1236139.2068
12 | 2693555.1052 | 1236064.3561 | 2693556.9313 | 1236081.9977 | 2693556.2832 | 1236091.9724
13 | 2693502.3612 | 1236220.9738 | 2693499.0202 | 1236231.2843 | 2693500.3696 | 1236246.5167 | 2693502.4686 | 1236254.6684
14 | 2693647.1534 | 1236114.7208 | 2693647.1534 | 1236114.7208 | 2693651.493 | 1236108.5124
15 | 2693555.1052 | 1236064.3561 | 2693553.3074 | 1236057.8229
16 | 2693555.1052 | 1236064.3561 | 2693559.0021 | 1236062.972
17 | 2693656.7627 | 1236100.9733 | 2693651.493 | 1236108.5124
18 | 2693656.7627 | 1236100.9733 | 2693666.6504 | 1236095.5611
19 | 2693703.329 | 1236063.7136 | 2693697.8931 | 1236070.0547 | 2693693.2188 | 1236082.3345 | 2693677.8106 | 1236089.4523 | 2693666.6504 | 1236095.5611
20 | 2693425.1371 | 1236037.08 | 2693401.0359 | 1236044.1209
21 | 2693425.1371 | 1236037.08 | 2693423.9103 | 1236031.8346 | 2693419.6145 | 1236013.4564
22 | 2693425.1371 | 1236037.08 | 2693431.5876 | 1236035.5025 | 2693446.2826 | 1236036.1673
23 | 2693446.2826 | 1236036.1673 | 2693447.0391 | 1236036.2015
24 | 2693447.0391 | 1236036.2015 | 2693446.1612 | 1236046.2951
25 | 2693448.4236 | 1236056.7681 | 2693446.1612 | 1236046.2951 | 2693446.1612 | 1236046.2951
26 | 2693768.5862 | 1236050.6669 | 2693764.9516 | 1236051.2544 | 2693755.9865 | 1236052.9475 | 2693745.6863 | 1236050.0384 | 2693723.4399 | 1236055.4692 | 2693703.329 | 1236063.7136
27 | 2693768.5862 | 1236050.6669 | 2693768.8347 | 1236057.4536 | 2693770.8858 | 1236070.8736 | 2693787.813 | 1236094.5692 | 2693789.2293 | 1236103.1312 | 2693799.7343 | 1236130.9174
28 | 2693799.7343 | 1236130.9174 | 2693799.4143 | 1236133.4895
29 | 2693581.9313 | 1236054.8059 | 2693586.3386 | 1236053.2362
30 | 2693559.0021 | 1236062.972 | 2693581.9313 | 1236054.8059
31 | 2693549.1278 | 1236042.6349 | 2693545.2802 | 1236044.2533
32 | 2693549.1278 | 1236042.6349 | 2693553.3074 | 1236057.8229
33 | 2693545.2802 | 1236044.2533 | 2693541.6536 | 1236045.7751 | 2693536.4468 | 1236048.6397 | 2693530.4379 | 1236051.4916 | 2693521.9909 | 1236053.7873
34 | 2693797.4259 | 1236210.4392 | 2693795.4532 | 1236171.9465 | 2693797.6016 | 1236148.0629 | 2693799.4143 | 1236133.4895
35 | 2693503.7625 | 1236058.7249 | 2693503.9863 | 1236058.6806 | 2693521.9909 | 1236053.7873
36 | 2693503.7625 | 1236058.7249 | 2693492.8265 | 1236060.8928
37 | 2693448.4236 | 1236056.7681 | 2693450.0271 | 1236064.1912
38 | 2693457.7015 | 1236069.9606 | 2693450.0271 | 1236064.1912
39 | 2693466.3171 | 1236109.3709 | 2693465.4162 | 1236105.8638 | 2693460.1226 | 1236093.0934 | 2693457.9888 | 1236081.518 | 2693457.9118 | 1236078.4205
40 | 2693466.3171 | 1236109.3709 | 2693468.0691 | 1236116.1908
41 | 2693457.8318 | 1236075.2029 | 2693457.9118 | 1236078.4205
42 | 2693468.0691 | 1236116.1908 | 2693468.0691 | 1236116.1908 | 2693473.7907 | 1236132.6125
43 | 2693457.7015 | 1236069.9606 | 2693457.8318 | 1236075.2029
44 | 2693457.7015 | 1236069.9606 | 2693476.9657 | 1236064.0371 | 2693485.7096 | 1236062.3037
45 | 2693485.7096 | 1236062.3037 | 2693492.8265 | 1236060.8928
46 | 2693502.4686 | 1236254.6684 | 2693502.7862 | 1236255.9015
47 | 2693502.7957 | 1236255.9384 | 2693502.7862 | 1236255.9015
48 | 2693408.5413 | 1236292.5473 | 2693409.0252 | 1236292.3794
49 | 2693432.5738 | 1236284.2104 | 2693409.0252 | 1236292.3794
50 | 2693432.5738 | 1236284.2104 | 2693442.8435 | 1236280.6478 | 2693451.6366 | 1236281.6868 | 2693461.2252 | 1236296.126 | 2693461.2252 | 1236296.126
51 | 2693461.2252 | 1236296.126 | 2693479.3787 | 1236292.1569
52 | 2693497.6311 | 1236287.7705 | 2693486.6055 | 1236290.5768 | 2693479.3787 | 1236292.1569
53 | 2693497.6311 | 1236287.7705 | 2693504.3095 | 1236278.4458
54 | 2693505.8187 | 1236276.3385 | 2693504.3095 | 1236278.4458
55 | 2693505.8187 | 1236276.3385 | 2693507.4588 | 1236274.0484 | 2693507.4588 | 1236274.0484
56 | 2693507.4588 | 1236274.0484 | 2693502.7957 | 1236255.9384
57 | 2693550.5083 | 1236545.374 | 2693574.594 | 1236535.5327
58 | 2693578.3848 | 1236533.9838 | 2693574.594 | 1236535.5327
59 | 2693578.3848 | 1236533.9838 | 2693586.1049 | 1236530.8294
60 | 2693613.0206 | 1236519.8318 | 2693586.1049 | 1236530.8294
61 | 2693613.0206 | 1236519.8318 | 2693614.7354 | 1236519.1312
62 | 2693580.214 | 1236602.9571 | 2693610.176 | 1236589.913
63 | 2693610.176 | 1236589.913 | 2693611.9113 | 1236589.1576 | 2693637.8125 | 1236570.6629
64 | 2693614.7354 | 1236519.1312 | 2693642.4897 | 1236507.7909 | 2693642.4897 | 1236507.7909
65 | 2693642.4897 | 1236507.7909 | 2693651.7483 | 1236508.0815 | 2693662.1751 | 1236511.0703
66 | 2693685.7 | 1236543.4427 | 2693644.1347 | 1236566.1485 | 2693637.8125 | 1236570.6629
67 | 2693685.7 | 1236543.4427 | 2693671.0835 | 1236517.2486 | 2693662.1751 | 1236511.0703 | 2693662.1751 | 1236511.0703
68 | 2693685.7 | 1236543.4427 | 2693708.0652 | 1236531.798 | 2693731.0297 | 1236516.2378 | 2693749.1846 | 1236505.7276 | 2693763.2891 | 1236500.5909 | 2693776.5121 | 1236496.6411
69 | 2693776.5121 | 1236496.6411 | 2693775.1769 | 1236482.9545 | 2693773.6554 | 1236472.4338 | 2693769.4778 | 1236459.5029 | 2693764.8596 | 1236452.4248 | 2693751.9107 | 1236450.0298 | 2693713.1516 | 1236465.1071
70 | 2693757.1898 | 1236357.2784 | 2693762.1986 | 1236362.628 | 2693758.4707 | 1236366.7389 | 2693759.5502 | 1236371.2259 | 2693768.0887 | 1236394.6 | 2693772.1569 | 1236406.3172 | 2693780.4056 | 1236439.8832 | 2693783.3532 | 1236496.1821 | 2693776.5121 | 1236496.6411
71 | 2693757.1898 | 1236357.2784 | 2693761.2507 | 1236353.1617 | 2693755.8733 | 1236348.1509 | 2693754.2322 | 1236341.3645 | 2693746.8254 | 1236331.6294 | 2693763.5745 | 1236318.1616 | 2693772.2645 | 1236309.4257 | 2693773.5248 | 1236290.9654 | 2693783.9733 | 1236261.9423 | 2693790.5141 | 1236249.0058
72 | 2693757.1898 | 1236357.2784 | 2693749.6387 | 1236349.4869 | 2693741.9525 | 1236344.5064 | 2693730.8745 | 1236340.562 | 2693718.4558 | 1236340.0435 | 2693709.6938 | 1236342.3181 | 2693702.477 | 1236345.9514 | 2693696.0223 | 1236350.6864 | 2693691.1597 | 1236356.4087
73 | 2693794.8715 | 1236240.3875 | 2693790.5141 | 1236249.0058
74 | 2693691.1597 | 1236356.4087 | 2693688.0411 | 1236360.0785 | 2693681.6582 | 1236366.0267 | 2693676.6462 | 1236369.3089
75 | 2693797.4259 | 1236210.4392 | 2693797.6292 | 1236234.9381 | 2693794.8715 | 1236240.3875

## bus_geodata
| x | y | coords
0 | 2693579.7224 | 1236139.2562
1 | 2693570.2612 | 1236147.9743
2 | 2693589.0261 | 1236130.6833
3 | 2693551.6205 | 1236170.6402
4 | 2693600.2011 | 1236131.2137
5 | 2693551.7963 | 1236109.6038
6 | 2693543.2316 | 1236190.1279
7 | 2693631.9968 | 1236123.2155
8 | 2693546.15 | 1236117.5882
9 | 2693556.2832 | 1236091.9724
10 | 2693502.3612 | 1236220.9738
11 | 2693647.1534 | 1236114.7208
12 | 2693522.5851 | 1236139.2068
13 | 2693555.1052 | 1236064.3561
14 | 2693651.493 | 1236108.5124
15 | 2693656.7627 | 1236100.9733
16 | 2693666.6504 | 1236095.5611
17 | 2693401.0359 | 1236044.1209
18 | 2693425.1371 | 1236037.08
19 | 2693419.6145 | 1236013.4564
20 | 2693446.2826 | 1236036.1673
21 | 2693447.0391 | 1236036.2015
22 | 2693446.1612 | 1236046.2951
23 | 2693703.329 | 1236063.7136
24 | 2693768.5862 | 1236050.6669
25 | 2693799.7343 | 1236130.9174
26 | 2693586.3386 | 1236053.2362
27 | 2693581.9313 | 1236054.8059
28 | 2693549.1278 | 1236042.6349
29 | 2693545.2802 | 1236044.2533
30 | 2693553.3074 | 1236057.8229
31 | 2693799.4143 | 1236133.4895
32 | 2693559.0021 | 1236062.972
33 | 2693521.9909 | 1236053.7873
34 | 2693503.7625 | 1236058.7249
35 | 2693448.4236 | 1236056.7681
36 | 2693450.0271 | 1236064.1912
37 | 2693466.3171 | 1236109.3709
38 | 2693457.9118 | 1236078.4205
39 | 2693468.0691 | 1236116.1908
40 | 2693457.8318 | 1236075.2029
41 | 2693473.7907 | 1236132.6125
42 | 2693457.7015 | 1236069.9606
43 | 2693485.7096 | 1236062.3037
44 | 2693492.8266 | 1236060.8928
45 | 2693502.4686 | 1236254.6684
46 | 2693502.7862 | 1236255.9015
47 | 2693408.5413 | 1236292.5473
48 | 2693409.0252 | 1236292.3794
49 | 2693432.5738 | 1236284.2104
50 | 2693461.2252 | 1236296.126
51 | 2693479.3787 | 1236292.1569
52 | 2693497.6311 | 1236287.7705
53 | 2693504.3095 | 1236278.4458
54 | 2693505.8187 | 1236276.3385
55 | 2693507.4588 | 1236274.0484
56 | 2693502.7957 | 1236255.9384
57 | 2693550.5083 | 1236545.374
58 | 2693574.594 | 1236535.5327
59 | 2693578.3848 | 1236533.9838
60 | 2693586.1049 | 1236530.8294
61 | 2693613.0206 | 1236519.8318
62 | 2693580.214 | 1236602.9571
63 | 2693610.176 | 1236589.913
64 | 2693614.7354 | 1236519.1312
65 | 2693642.4897 | 1236507.7909
66 | 2693637.8125 | 1236570.6629
67 | 2693685.7 | 1236543.4427
68 | 2693662.1751 | 1236511.0703
69 | 2693776.5121 | 1236496.6411
70 | 2693713.1516 | 1236465.1071
71 | 2693757.1898 | 1236357.2784
72 | 2693790.5141 | 1236249.0058
73 | 2693691.1597 | 1236356.4087
74 | 2693676.6462 | 1236369.3089
75 | 2693794.8715 | 1236240.3875
76 | 2693797.4259 | 1236210.4392
77 | 2693502.3612 | 1236220.9738

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99424 | -0.10967 | 0.01335 | 0.0033458
1 | 0.99538 | -0.088012 | 0.004766 | 0.0011945
2 | 0.99321 | -0.12953 | 0 | 0
3 | 0.99802 | -0.037529 | 0.004814 | 0.0012065
4 | 0.99264 | -0.14041 | 0.014562 | 0.0036495
5 | 0.99055 | -0.18081 | 0 | 0
6 | 1 | 0 | -0.23788 | -0.060205
7 | 0.99117 | -0.16863 | 0.022924 | 0.0057452
8 | 0.99046 | -0.18255 | 0.0034732 | 0.00087047
9 | 0.98957 | -0.19967 | 0.0022019 | 0.00055184
10 | 0.99841 | -0.030454 | 0 | 0
11 | 0.99059 | -0.17981 | 0.011141 | 0.0027923
12 | 0.99026 | -0.18632 | 0.0065369 | 0.0016383
13 | 0.98815 | -0.22715 | 0 | 0
14 | 0.99038 | -0.18395 | 0.0092262 | 0.0023123
15 | 0.99015 | -0.18821 | 0 | 0
16 | 0.98988 | -0.19344 | 0.010945 | 0.0027431
17 | 0.98311 | -0.32524 | 0.0052056 | 0.0013046
18 | 0.98323 | -0.32288 | 0 | 0
19 | 0.98318 | -0.32385 | 0.0022221 | 0.00055691
20 | 0.98338 | -0.32002 | 0.0037935 | 0.00095075
21 | 0.98339 | -0.31987 | 0 | 0
22 | 0.98349 | -0.31782 | 0.0024637 | 0.00061746
23 | 0.9889 | -0.21222 | 0 | 0
24 | 0.9876 | -0.23721 | 0 | 0
25 | 0.98591 | -0.26961 | 0.0012442 | 0.00031183
26 | 0.98793 | -0.23137 | 0.0014212 | 0.0003562
27 | 0.98794 | -0.23125 | 0.0066331 | 0.0016624
28 | 0.98724 | -0.24474 | 0 | 0
29 | 0.98708 | -0.24787 | 0 | 0
30 | 0.98785 | -0.23291 | 0.0055162 | 0.0013825
31 | 0.98586 | -0.27054 | 0.001293 | 0.00032405
32 | 0.98812 | -0.22775 | 0 | 0
33 | 0.9861 | -0.26689 | 0.0034062 | 0.00085367
34 | 0.98543 | -0.27998 | 0.0016855 | 0.00042243
35 | 0.98363 | -0.31518 | 0.0037648 | 0.00094355
36 | 0.98375 | -0.31279 | 0.0014971 | 0.0003752
37 | 0.98348 | -0.31798 | 0.0026135 | 0.00065499
38 | 0.98381 | -0.31165 | 0.0022695 | 0.0005688
39 | 0.98343 | -0.31903 | 0.0022683 | 0.00056848
40 | 0.98384 | -0.31089 | 0.001397 | 0.00035012
41 | 0.98333 | -0.32091 | 0.0059961 | 0.0015028
42 | 0.98392 | -0.30951 | 0 | 0
43 | 0.98481 | -0.292 | 0.0020101 | 0.00050378
44 | 0.98505 | -0.28737 | 0.001427 | 0.00035764
45 | 0.99738 | -0.050346 | 0.0027045 | 0.0006778
46 | 0.99734 | -0.051019 | 0.0017798 | 0.00044606
47 | 0.99561 | -0.08448 | 0.0035476 | 0.00088912
48 | 0.99561 | -0.084448 | 0.0012951 | 0.00032459
49 | 0.99572 | -0.082325 | 0.0043553 | 0.0010915
50 | 0.99603 | -0.076334 | 0.0022997 | 0.00057636
51 | 0.99623 | -0.07258 | 0.0083822 | 0.0021008
52 | 0.99656 | -0.066027 | 0 | 0
53 | 0.99677 | -0.062025 | 0.0010243 | 0.00025672
54 | 0.99682 | -0.061075 | 0.0049152 | 0.0012319
55 | 0.99689 | -0.059799 | 0.00089897 | 0.0002253
56 | 0.99734 | -0.051038 | 0.0016872 | 0.00042284
57 | 0.97148 | -0.55145 | 0.003052 | 0.00076491
58 | 0.97155 | -0.54999 | 0.0046404 | 0.001163
59 | 0.97158 | -0.54941 | 0.0013843 | 0.00034693
60 | 0.97165 | -0.54801 | 0.0013941 | 0.0003494
61 | 0.97194 | -0.54239 | 0.00055538 | 0.00013919
62 | 0.97349 | -0.51176 | 0.0021524 | 0.00053944
63 | 0.97355 | -0.51046 | 0.00087441 | 0.00021915
64 | 0.97196 | -0.54201 | 0.0059356 | 0.0014876
65 | 0.97243 | -0.53263 | 0.0062947 | 0.0015776
66 | 0.97365 | -0.50859 | 0.00080029 | 0.00020057
67 | 0.97385 | -0.50471 | 0 | 0
68 | 0.97287 | -0.52401 | 0.0024409 | 0.00061175
69 | 0.97667 | -0.4491 | 0 | 0
70 | 0.97628 | -0.45696 | 0.0042541 | 0.0010662
71 | 0.98148 | -0.35534 | 0 | 0
72 | 0.98375 | -0.31135 | 0.0011662 | 0.00029228
73 | 0.98122 | -0.36046 | 0.0026259 | 0.0006581
74 | 0.9812 | -0.36083 | 0.0010532 | 0.00026395
75 | 0.98392 | -0.30799 | 0 | 0
76 | 0.98447 | -0.29734 | 0 | 0
77 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.19261 | -0.048824 | 0.19281 | 0.048952 | 0.00020072 | 0.00012812 | 0.28845 | 0.28845 | 0.28845 | 0.99424 | -0.10967 | 0.99538 | -0.088012 | 39.6229
1 | 0.17926 | 0.045478 | -0.17908 | -0.045369 | 0.00017098 | 0.0001091 | 0.26848 | 0.26848 | 0.26848 | 0.99424 | -0.10967 | 0.99321 | -0.12953 | 36.8785
2 | -0.19757 | -0.050146 | 0.19805 | 0.050453 | 0.00048107 | 0.00030712 | 0.29558 | 0.29558 | 0.29558 | 0.99538 | -0.088012 | 0.99802 | -0.037529 | 40.6016
3 | 0.11082 | 0.028083 | -0.11076 | -0.028046 | 5.7896e-05 | 3.6764e-05 | 0.16613 | 0.16613 | 0.16613 | 0.99321 | -0.12953 | 0.99264 | -0.14041 | 22.8204
4 | 0.068269 | 0.017286 | -0.068102 | -0.017179 | 0.00016767 | 0.00010676 | 0.10234 | 0.10234 | 0.10234 | 0.99321 | -0.12953 | 0.99055 | -0.18081 | 28.1162
5 | -0.20287 | -0.05166 | 0.20323 | 0.051895 | 0.00036792 | 0.00023491 | 0.30276 | 0.30276 | 0.30276 | 0.99802 | -0.037529 | 1 | 0 | 41.5875
6 | 0.096195 | 0.024397 | -0.096065 | -0.024314 | 0.00013033 | 8.255e-05 | 0.1443 | 0.1443 | 0.1443 | 0.99264 | -0.14041 | 0.99117 | -0.16863 | 19.822
7 | 0.010012 | 0.0025095 | -0.010011 | -0.0025091 | 8.2958e-07 | 4.0506e-07 | 0.015041 | 0.015041 | 0.015041 | 0.99055 | -0.18081 | 0.99046 | -0.18255 | 4.132
8 | 0.05809 | 0.01467 | -0.058037 | -0.014636 | 5.2434e-05 | 3.3322e-05 | 0.087303 | 0.087303 | 0.087303 | 0.99055 | -0.18081 | 0.98957 | -0.19967 | 23.9843
9 | 0.032999 | 0.0083099 | -0.032951 | -0.0082799 | 4.7976e-05 | 3.001e-05 | 0.049117 | 0.049117 | 0.049117 | 1 | 0 | 0.99841 | -0.030454 | 13.4937
10 | 0.073141 | 0.018569 | -0.073102 | -0.018544 | 3.934e-05 | 2.473e-05 | 0.10989 | 0.10989 | 0.10989 | 0.99117 | -0.16863 | 0.99059 | -0.17981 | 15.0947
11 | 0.0065381 | 0.0016386 | -0.0065369 | -0.0016383 | 1.1723e-06 | 3.3336e-07 | 0.0098225 | 0.0098227 | 0.0098227 | 0.99046 | -0.18255 | 0.99026 | -0.18632 | 2.6985
12 | 0.055835 | 0.014084 | -0.055762 | -0.014038 | 7.3364e-05 | 4.6597e-05 | 0.083992 | 0.083992 | 0.083992 | 0.98957 | -0.19967 | 0.98815 | -0.22715 | 23.0747
13 | 0.032951 | 0.0082799 | -0.03292 | -0.0082603 | 3.1255e-05 | 1.9552e-05 | 0.049117 | 0.049117 | 0.049117 | 0.99841 | -0.030454 | 0.99738 | -0.050346 | 13.4938
14 | 0.061961 | 0.015752 | -0.061948 | -0.015744 | 1.2324e-05 | 7.6927e-06 | 0.093154 | 0.093154 | 0.093154 | 0.99059 | -0.17981 | 0.99038 | -0.18395 | 12.7959
15 | 0.047706 | 0.012019 | -0.047693 | -0.01201 | 1.3122e-05 | 8.3112e-06 | 0.071861 | 0.071861 | 0.071861 | 0.98815 | -0.22715 | 0.98785 | -0.23291 | 19.742
16 | 0.0080559 | 0.0020192 | -0.0080557 | -0.0020191 | 2.2764e-07 | 9.2852e-08 | 0.012131 | 0.012131 | 0.012131 | 0.98815 | -0.22715 | 0.98812 | -0.22775 | 3.3327
17 | 0.052722 | 0.013432 | -0.052711 | -0.013425 | 1.0843e-05 | 6.7031e-06 | 0.079292 | 0.079292 | 0.079292 | 0.99038 | -0.18395 | 0.99015 | -0.18821 | 10.8917
18 | 0.052711 | 0.013425 | -0.052698 | -0.013417 | 1.3288e-05 | 8.2145e-06 | 0.079292 | 0.079292 | 0.079292 | 0.99015 | -0.18821 | 0.98988 | -0.19344 | 10.8917
19 | 0.041753 | 0.010674 | -0.041715 | -0.010651 | 3.7898e-05 | 2.294e-05 | 0.062839 | 0.062839 | 0.062839 | 0.98988 | -0.19344 | 0.9889 | -0.21222 | 8.6318
20 | -0.0052056 | -0.0013046 | 0.0052062 | 0.0013047 | 5.8452e-07 | 5.5679e-08 | 0.0078791 | 0.007879 | 0.0078791 | 0.98311 | -0.32524 | 0.98323 | -0.32288 | 2.1646
21 | 0.0022222 | 0.00055667 | -0.0022221 | -0.00055691 | 1.0289e-07 | -2.4183e-07 | 0.003363 | 0.0033631 | 0.0033631 | 0.98323 | -0.32288 | 0.98318 | -0.32385 | 0.92392
22 | -0.0074284 | -0.0018614 | 0.0074294 | 0.0018617 | 1.0119e-06 | 3.7676e-07 | 0.011242 | 0.011242 | 0.011242 | 0.98323 | -0.32288 | 0.98338 | -0.32002 | 3.0884
23 | -0.011223 | -0.0028125 | 0.011223 | 0.0028125 | 8.19e-08 | 4.2808e-08 | 0.016982 | 0.016982 | 0.016982 | 0.98338 | -0.32002 | 0.98339 | -0.31987 | 4.6654
24 | -0.011223 | -0.0028125 | 0.011224 | 0.0028131 | 1.0957e-06 | 5.727e-07 | 0.016982 | 0.016982 | 0.016982 | 0.98339 | -0.31987 | 0.98349 | -0.31782 | 4.6654
25 | -0.013688 | -0.0034306 | 0.01369 | 0.0034315 | 1.7233e-06 | 9.669e-07 | 0.02071 | 0.02071 | 0.02071 | 0.98349 | -0.31782 | 0.98363 | -0.31518 | 5.6895
26 | 0.041715 | 0.010651 | -0.041664 | -0.01062 | 5.0319e-05 | 3.0463e-05 | 0.062839 | 0.06284 | 0.06284 | 0.9889 | -0.21222 | 0.9876 | -0.23721 | 8.6319
27 | 0.041664 | 0.01062 | -0.041599 | -0.010581 | 6.5062e-05 | 3.9395e-05 | 0.06284 | 0.062841 | 0.062841 | 0.9876 | -0.23721 | 0.98591 | -0.26961 | 8.632
28 | 0.040355 | 0.010269 | -0.040353 | -0.010268 | 1.8062e-06 | 1.0899e-06 | 0.060963 | 0.060963 | 0.060963 | 0.98591 | -0.26961 | 0.98586 | -0.27054 | 8.374
29 | -0.0014212 | -0.0003562 | 0.0014212 | 0.00035614 | 8.0395e-09 | -5.4761e-08 | 0.0021407 | 0.0021406 | 0.0021407 | 0.98793 | -0.23137 | 0.98794 | -0.23125 | 0.58809
30 | -0.0080543 | -0.0020185 | 0.0080557 | 0.0020191 | 1.3433e-06 | 5.4796e-07 | 0.012131 | 0.012131 | 0.012131 | 0.98794 | -0.23125 | 0.98812 | -0.22775 | 3.3328
31 | 0.042153 | 0.010613 | -0.042146 | -0.010609 | 6.3066e-06 | 3.983e-06 | 0.063552 | 0.063552 | 0.063552 | 0.98724 | -0.24474 | 0.98708 | -0.24787 | 17.4593
32 | -0.042153 | -0.010613 | 0.042177 | 0.010628 | 2.3858e-05 | 1.5068e-05 | 0.063552 | 0.063552 | 0.063552 | 0.98724 | -0.24474 | 0.98785 | -0.23291 | 17.4593
33 | 0.042146 | 0.010609 | -0.042108 | -0.010585 | 3.8289e-05 | 2.4182e-05 | 0.063552 | 0.063552 | 0.063552 | 0.98708 | -0.24787 | 0.9861 | -0.26689 | 17.4593
34 | 0.03906 | 0.009944 | -0.03901 | -0.0099137 | 5.0413e-05 | 3.0298e-05 | 0.059011 | 0.059012 | 0.059012 | 0.98586 | -0.27054 | 0.98447 | -0.29734 | 8.106
35 | 0.038702 | 0.0097309 | -0.038678 | -0.0097157 | 2.4164e-05 | 1.5224e-05 | 0.058412 | 0.058412 | 0.058412 | 0.9861 | -0.26689 | 0.98543 | -0.27998 | 16.0473
36 | 0.036992 | 0.0092933 | -0.036979 | -0.0092851 | 1.3049e-05 | 8.2092e-06 | 0.055867 | 0.055867 | 0.055867 | 0.98543 | -0.27998 | 0.98505 | -0.28737 | 15.3481
37 | -0.017454 | -0.0043751 | 0.017456 | 0.0043763 | 1.9856e-06 | 1.1744e-06 | 0.026405 | 0.026405 | 0.026405 | 0.98363 | -0.31518 | 0.98375 | -0.31279 | 7.2541
38 | -0.018953 | -0.0047515 | 0.018956 | 0.0047532 | 2.9593e-06 | 1.772e-06 | 0.028669 | 0.028669 | 0.028669 | 0.98375 | -0.31279 | 0.98392 | -0.30951 | 7.8762
39 | -0.010879 | -0.0027265 | 0.010882 | 0.0027282 | 3.2829e-06 | 1.6909e-06 | 0.01646 | 0.016459 | 0.01646 | 0.98348 | -0.31798 | 0.98381 | -0.31165 | 4.5219
40 | 0.0082653 | 0.0020715 | -0.0082649 | -0.0020714 | 4.1294e-07 | 1.7493e-07 | 0.012505 | 0.012505 | 0.012505 | 0.98348 | -0.31798 | 0.98343 | -0.31903 | 3.4356
41 | -0.013152 | -0.003297 | 0.013152 | 0.0032973 | 4.7759e-07 | 2.6479e-07 | 0.019892 | 0.019892 | 0.019892 | 0.98381 | -0.31165 | 0.98384 | -0.31089 | 5.4649
42 | 0.0059966 | 0.0015029 | -0.0059961 | -0.0015028 | 5.3687e-07 | 1.2298e-07 | 0.0090734 | 0.0090735 | 0.0090735 | 0.98343 | -0.31903 | 0.98333 | -0.32091 | 2.4927
43 | -0.014549 | -0.0036474 | 0.01455 | 0.0036479 | 9.5221e-07 | 5.4282e-07 | 0.022005 | 0.022005 | 0.022005 | 0.98384 | -0.31089 | 0.98392 | -0.30951 | 6.0453
44 | -0.033506 | -0.0084012 | 0.033534 | 0.0084187 | 2.7991e-05 | 1.7545e-05 | 0.050674 | 0.050674 | 0.050674 | 0.98392 | -0.30951 | 0.98481 | -0.292 | 13.9215
45 | -0.035544 | -0.0089225 | 0.035552 | 0.0089274 | 7.8492e-06 | 4.9312e-06 | 0.053711 | 0.053711 | 0.053711 | 0.98481 | -0.292 | 0.98505 | -0.28737 | 14.7559
46 | 0.030215 | 0.0075825 | -0.030214 | -0.0075819 | 9.7053e-07 | 6.0452e-07 | 0.045082 | 0.045082 | 0.045082 | 0.99738 | -0.050346 | 0.99734 | -0.051019 | 12.3853
47 | 0.028434 | 0.0071358 | -0.028434 | -0.0071358 | 2.5727e-08 | 1.5968e-08 | 0.042427 | 0.042427 | 0.042427 | 0.99734 | -0.051019 | 0.99734 | -0.051038 | 11.6558
48 | -0.0035476 | -0.00088912 | 0.0035477 | 0.00088912 | 5.4002e-09 | -3.2051e-09 | 0.0053022 | 0.0053022 | 0.0053022 | 0.99561 | -0.08448 | 0.99561 | -0.084448 | 1.4567
49 | -0.0048428 | -0.0012137 | 0.0048433 | 0.0012137 | 4.8965e-07 | -1.0795e-08 | 0.0072379 | 0.0072378 | 0.0072379 | 0.99561 | -0.084448 | 0.99572 | -0.082325 | 1.9884
50 | -0.0091986 | -0.0023052 | 0.0092012 | 0.0023064 | 2.6259e-06 | 1.1984e-06 | 0.013746 | 0.013746 | 0.013746 | 0.99572 | -0.082325 | 0.99603 | -0.076334 | 3.7765
51 | -0.011501 | -0.0028828 | 0.011503 | 0.0028839 | 2.0572e-06 | 1.0747e-06 | 0.017182 | 0.017182 | 0.017182 | 0.99603 | -0.076334 | 0.99623 | -0.07258 | 4.7203
52 | -0.019885 | -0.0049846 | 0.019891 | 0.0049884 | 6.2111e-06 | 3.7306e-06 | 0.029702 | 0.029702 | 0.029702 | 0.99623 | -0.07258 | 0.99656 | -0.066027 | 8.1598
53 | -0.019891 | -0.0049884 | 0.019895 | 0.0049907 | 3.7944e-06 | 2.2789e-06 | 0.029702 | 0.029702 | 0.029702 | 0.99656 | -0.066027 | 0.99677 | -0.062025 | 8.1598
54 | -0.020919 | -0.0052474 | 0.02092 | 0.0052479 | 9.4806e-07 | 5.7297e-07 | 0.031231 | 0.031231 | 0.031231 | 0.99677 | -0.062025 | 0.99682 | -0.061075 | 8.5799
55 | -0.025836 | -0.0064798 | 0.025837 | 0.0064808 | 1.5712e-06 | 9.6887e-07 | 0.038568 | 0.038568 | 0.038568 | 0.99682 | -0.061075 | 0.99689 | -0.059799 | 10.5956
56 | -0.026736 | -0.0067061 | 0.026747 | 0.006713 | 1.117e-05 | 6.9048e-06 | 0.03991 | 0.03991 | 0.03991 | 0.99689 | -0.059799 | 0.99734 | -0.051038 | 10.9642
57 | -0.003052 | -0.00076491 | 0.0030522 | 0.00076472 | 2.1322e-07 | -1.8571e-07 | 0.0046748 | 0.0046747 | 0.0046748 | 0.97148 | -0.55145 | 0.97155 | -0.54999 | 1.2843
58 | -0.0076927 | -0.0019277 | 0.0076929 | 0.0019278 | 2.1317e-07 | 8.5715e-08 | 0.011782 | 0.011782 | 0.011782 | 0.97155 | -0.54999 | 0.97158 | -0.54941 | 3.2368
59 | -0.0090771 | -0.0022747 | 0.0090778 | 0.002275 | 6.044e-07 | 2.8353e-07 | 0.013902 | 0.013902 | 0.013902 | 0.97158 | -0.54941 | 0.97165 | -0.54801 | 3.8192
60 | -0.010472 | -0.0026244 | 0.010475 | 0.0026259 | 2.8042e-06 | 1.4344e-06 | 0.016037 | 0.016037 | 0.016037 | 0.97165 | -0.54801 | 0.97194 | -0.54239 | 4.4057
61 | -0.01103 | -0.0027651 | 0.01103 | 0.0027652 | 1.981e-07 | 1.0382e-07 | 0.016887 | 0.016887 | 0.016887 | 0.97194 | -0.54239 | 0.97196 | -0.54201 | 4.6393
62 | -0.0021524 | -0.00053944 | 0.0021525 | 0.00053912 | 1.3264e-07 | -3.2142e-07 | 0.00329 | 0.0032899 | 0.00329 | 0.97349 | -0.51176 | 0.97355 | -0.51046 | 0.90386
63 | -0.003027 | -0.00075827 | 0.0030272 | 0.00075802 | 2.7063e-07 | -2.4612e-07 | 0.0046264 | 0.0046262 | 0.0046264 | 0.97355 | -0.51046 | 0.97365 | -0.50859 | 1.271
64 | -0.016966 | -0.0042528 | 0.016973 | 0.0042572 | 7.5852e-06 | 4.4828e-06 | 0.025974 | 0.025974 | 0.025974 | 0.97196 | -0.54201 | 0.97243 | -0.53263 | 7.1358
65 | -0.023268 | -0.0058348 | 0.023278 | 0.0058407 | 9.5607e-06 | 5.8693e-06 | 0.035606 | 0.035606 | 0.035606 | 0.97243 | -0.53263 | 0.97287 | -0.52401 | 9.7819
66 | -0.0038275 | -0.0009586 | 0.0038282 | 0.00095836 | 7.0732e-07 | -2.3312e-07 | 0.0058493 | 0.0058491 | 0.0058493 | 0.97365 | -0.50859 | 0.97385 | -0.50471 | 1.607
67 | 0.025742 | 0.0064671 | -0.025719 | -0.0064525 | 2.37e-05 | 1.466e-05 | 0.039339 | 0.03934 | 0.03934 | 0.97385 | -0.50471 | 0.97287 | -0.52401 | 10.8076
68 | -0.029571 | -0.0074255 | 0.029649 | 0.0074746 | 7.8675e-05 | 4.907e-05 | 0.045188 | 0.045188 | 0.045188 | 0.97385 | -0.50471 | 0.97667 | -0.4491 | 12.4144
69 | 0.0042557 | 0.0010659 | -0.0042541 | -0.0010662 | 1.5927e-06 | -2.4449e-07 | 0.0064835 | 0.006484 | 0.006484 | 0.97667 | -0.4491 | 0.97628 | -0.45696 | 1.7813
70 | -0.033905 | -0.0085405 | 0.034058 | 0.0086363 | 0.00015276 | 9.585e-05 | 0.051671 | 0.051671 | 0.051671 | 0.97667 | -0.4491 | 0.98148 | -0.35534 | 14.1955
71 | -0.037738 | -0.0095578 | 0.037818 | 0.0096056 | 7.9892e-05 | 4.7838e-05 | 0.05725 | 0.057248 | 0.05725 | 0.98148 | -0.35534 | 0.98375 | -0.31135 | 7.864
72 | 0.00368 | 0.00092142 | -0.0036791 | -0.00092182 | 8.9693e-07 | -3.9685e-07 | 0.0055788 | 0.0055792 | 0.0055792 | 0.98148 | -0.35534 | 0.98122 | -0.36046 | 1.5327
73 | -0.038984 | -0.0098979 | 0.03899 | 0.0099017 | 6.3058e-06 | 3.7904e-06 | 0.059012 | 0.059012 | 0.059012 | 0.98375 | -0.31135 | 0.98392 | -0.30799 | 8.1061
74 | 0.0010532 | 0.00026372 | -0.0010532 | -0.00026395 | 1.8683e-08 | -2.3475e-07 | 0.0015971 | 0.0015972 | 0.0015972 | 0.98122 | -0.36046 | 0.9812 | -0.36083 | 0.43878
75 | -0.03899 | -0.0099017 | 0.03901 | 0.0099137 | 1.9986e-05 | 1.2013e-05 | 0.059012 | 0.059012 | 0.059012 | 0.98392 | -0.30799 | 0.98447 | -0.29734 | 8.1061

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23788 | 0.060205

## res_load
| p_mw | q_mvar
0 | 0.01335 | 0.0033458
1 | 0.004766 | 0.0011945
2 | 0.004814 | 0.0012065
3 | 0.014562 | 0.0036495
4 | 0.022924 | 0.0057452
5 | 0.0034732 | 0.00087047
6 | 0.0022019 | 0.00055184
7 | 0.011141 | 0.0027923
8 | 0.0065369 | 0.0016383
9 | 0.0092262 | 0.0023123
10 | 0.010945 | 0.0027431
11 | 0.0052056 | 0.0013046
12 | 0.0022221 | 0.00055691
13 | 0.0037935 | 0.00095075
14 | 0.0024637 | 0.00061746
15 | 0.0012442 | 0.00031183
16 | 0.0014212 | 0.0003562
17 | 0.0066331 | 0.0016624
18 | 0.0055162 | 0.0013825
19 | 0.001293 | 0.00032405
20 | 0.0034062 | 0.00085367
21 | 0.0016855 | 0.00042243
22 | 0.0037648 | 0.00094355
23 | 0.0014971 | 0.0003752
24 | 0.0026135 | 0.00065499
25 | 0.0022695 | 0.0005688
26 | 0.0022683 | 0.00056848
27 | 0.001397 | 0.00035012
28 | 0.0059961 | 0.0015028
29 | 0.0020101 | 0.00050378
30 | 0.001427 | 0.00035764
31 | 0.0027045 | 0.0006778
32 | 0.0017798 | 0.00044606
33 | 0.0035476 | 0.00088912
34 | 0.0012951 | 0.00032459
35 | 0.0043553 | 0.0010915
36 | 0.0022997 | 0.00057636
37 | 0.0083822 | 0.0021008
38 | 0.0010243 | 0.00025672
39 | 0.0049152 | 0.0012319
40 | 0.00089897 | 0.0002253
41 | 0.0016872 | 0.00042284
42 | 0.003052 | 0.00076491
43 | 0.0046404 | 0.001163
44 | 0.0013843 | 0.00034693
45 | 0.0013941 | 0.0003494
46 | 0.00055538 | 0.00013919
47 | 0.0021524 | 0.00053944
48 | 0.00087441 | 0.00021915
49 | 0.0059356 | 0.0014876
50 | 0.0062947 | 0.0015776
51 | 0.00080029 | 0.00020057
52 | 0.0024409 | 0.00061175
53 | 0.0042541 | 0.0010662
54 | 0.0011662 | 0.00029228
55 | 0.0026259 | 0.0006581
56 | 0.0010532 | 0.00026395

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1