## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_159-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_159-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_159-9_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_159-9_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_159-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_159-9_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_159-9_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_159-9_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_159-9_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_159-9_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_159-9_0_4_node_104 | 0.4 | n |  | TRUE
11 | bus_LV_159-9_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_159-9_0_4_node_95 | 0.4 | n |  | TRUE
13 | bus_LV_159-9_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_159-9_0_4_node_83 | 0.4 | n |  | TRUE
15 | bus_LV_159-9_0_4_node_100 | 0.4 | n |  | TRUE
16 | bus_LV_159-9_0_4_node_117 | 0.4 | n |  | TRUE
17 | bus_LV_159-9_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_159-9_0_4_node_116 | 0.4 | n |  | TRUE
19 | bus_LV_159-9_0_4_node_115 | 0.4 | n |  | TRUE
20 | bus_LV_159-9_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_159-9_0_4_node_103 | 0.4 | n |  | TRUE
22 | bus_LV_159-9_0_4_node_101 | 0.4 | n |  | TRUE
23 | bus_LV_159-9_0_4_node_97 | 0.4 | n |  | TRUE
24 | bus_LV_159-9_0_4_node_80 | 0.4 | n |  | TRUE
25 | bus_LV_159-9_0_4_node_96 | 0.4 | n |  | TRUE
26 | bus_LV_159-9_0_4_node_120 | 0.4 | n |  | TRUE
27 | bus_LV_159-9_0_4_node_119 | 0.4 | n |  | TRUE
28 | bus_LV_159-9_0_4_node_102 | 0.4 | n |  | TRUE
29 | bus_LV_159-9_0_4_node_79 | 0.4 | n |  | TRUE
30 | bus_LV_159-9_0_4_node_99 | 0.4 | n |  | TRUE
31 | bus_LV_159-9_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_159-9_0_4_node_91 | 0.4 | n |  | TRUE
33 | bus_LV_159-9_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_159-9_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_159-9_0_4_node_94 | 0.4 | n |  | TRUE
36 | bus_LV_159-9_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_159-9_0_4_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_159-9_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_159-9_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_159-9_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_159-9_0_4_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_159-9_0_4_node_110 | 0.4 | n |  | TRUE
43 | bus_LV_159-9_0_4_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_159-9_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_159-9_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_159-9_0_4_node_93 | 0.4 | n |  | TRUE
47 | bus_LV_159-9_0_4_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_159-9_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_159-9_0_4_node_108 | 0.4 | n |  | TRUE
50 | bus_LV_159-9_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_159-9_0_4_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_159-9_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_159-9_0_4_node_109 | 0.4 | n |  | TRUE
54 | bus_LV_159-9_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_159-9_0_4_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_159-9_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_159-9_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_159-9_0_4_node_87 | 0.4 | n |  | TRUE
59 | bus_LV_159-9_0_4_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_159-9_0_4_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_159-9_0_4_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_159-9_0_4_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_159-9_0_4_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_159-9_0_4_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_159-9_0_4_node_35 | 0.4 | n |  | TRUE
66 | bus_LV_159-9_0_4_node_36 | 0.4 | n |  | TRUE
67 | bus_LV_159-9_0_4_node_85 | 0.4 | n |  | TRUE
68 | bus_LV_159-9_0_4_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_159-9_0_4_node_113 | 0.4 | n |  | TRUE
70 | bus_LV_159-9_0_4_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_159-9_0_4_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_159-9_0_4_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_159-9_0_4_node_82 | 0.4 | n |  | TRUE
74 | bus_LV_159-9_0_4_node_114 | 0.4 | n |  | TRUE
75 | bus_LV_159-9_0_4_node_121 | 0.4 | n |  | TRUE
76 | bus_LV_159-9_0_4_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_159-9_0_4_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_159-9_0_4_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_159-9_0_4_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_159-9_0_4_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_159-9_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_159-9_0_4_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_159-9_0_4_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_159-9_0_4_node_107 | 0.4 | n |  | TRUE
85 | bus_LV_159-9_0_4_node_123 | 0.4 | n |  | TRUE
86 | bus_LV_159-9_0_4_node_125 | 0.4 | n |  | TRUE
87 | bus_LV_159-9_0_4_node_55 | 0.4 | n |  | TRUE
88 | bus_LV_159-9_0_4_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_159-9_0_4_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_159-9_0_4_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_159-9_0_4_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_159-9_0_4_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_159-9_0_4_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_159-9_0_4_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_159-9_0_4_node_124 | 0.4 | n |  | TRUE
96 | bus_LV_159-9_0_4_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_159-9_0_4_node_61 | 0.4 | n |  | TRUE
98 | bus_LV_159-9_0_4_node_106 | 0.4 | n |  | TRUE
99 | bus_LV_159-9_0_4_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_159-9_0_4_node_66 | 0.4 | n |  | TRUE
101 | bus_LV_159-9_0_4_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_159-9_0_4_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_159-9_0_4_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_159-9_0_4_node_64 | 0.4 | n |  | TRUE
105 | bus_LV_159-9_0_4_node_118 | 0.4 | n |  | TRUE
106 | bus_LV_159-9_0_4_node_74 | 0.4 | n |  | TRUE
107 | bus_LV_159-9_0_4_node_75 | 0.4 | n |  | TRUE
108 | bus_LV_159-9_0_4_node_76 | 0.4 | n |  | TRUE
109 | bus_LV_159-9_0_4_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_159-9_0_4_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_159-9_0_4_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_159-9_0_4_node_127 | 0.4 | n |  | TRUE
113 | bus_LV_159-9_0_4_node_126 | 0.4 | n |  | TRUE
114 | bus_LV_159-9_0_4_node_90 | 0.4 | n |  | TRUE
115 | bus_LV_159-9_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_159-9_0_4_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_159-9_0_4_node_105 | 0.4 | n |  | TRUE
118 | bus_MV_495_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_159-9_0_4_load_0 | 0 | 0.0059107 | 0.0014814 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_159-9_0_4_load_1 | 1 | 0.0026413 | 0.00066197 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_159-9_0_4_load_3 | 2 | 0.0057861 | 0.0014501 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_159-9_0_4_load_6 | 3 | 0.0037561 | 0.00094137 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_159-9_0_4_load_8 | 7 | 0.0022044 | 0.00055247 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_159-9_0_4_load_104 | 10 | 0.0042151 | 0.0010564 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_159-9_0_4_load_83 | 14 | 0.0012988 | 0.0003255 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_159-9_0_4_load_100 | 15 | 0.0018689 | 0.00046839 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_159-9_0_4_load_117 | 16 | 0.00078193 | 0.00019597 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_159-9_0_4_load_116 | 18 | 0.0065703 | 0.0016467 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_159-9_0_4_load_115 | 19 | 0.0046536 | 0.0011663 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_159-9_0_4_load_23 | 20 | 0.001355 | 0.00033959 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_159-9_0_4_load_103 | 21 | 0.0035216 | 0.00088259 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_159-9_0_4_load_80 | 24 | 0.00087491 | 0.00021927 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_159-9_0_4_load_120 | 26 | 0.0013828 | 0.00034657 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_159-9_0_4_load_119 | 27 | 0.0017839 | 0.00044708 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_159-9_0_4_load_102 | 28 | 0.0029563 | 0.00074091 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_159-9_0_4_load_99 | 30 | 0.0019915 | 0.00049911 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_159-9_0_4_load_94 | 35 | 0.0035863 | 0.00089881 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_159-9_0_4_load_21 | 36 | 0.00098255 | 0.00024625 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_159-9_0_4_load_18 | 37 | 0.004121 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_159-9_0_4_load_22 | 40 | 0.0039527 | 0.00099063 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_159-9_0_4_load_48 | 41 | 0.0019844 | 0.00049735 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_159-9_0_4_load_110 | 42 | 0.0029576 | 0.00074124 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_159-9_0_4_load_47 | 43 | 0.0024159 | 0.00060549 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_159-9_0_4_load_93 | 46 | 0.0018652 | 0.00046747 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_159-9_0_4_load_89 | 47 | 0.0013837 | 0.00034678 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_159-9_0_4_load_108 | 49 | 0.0077377 | 0.0019392 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_159-9_0_4_load_112 | 51 | 0.0088014 | 0.0022058 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_159-9_0_4_load_109 | 53 | 0.0054495 | 0.0013658 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_159-9_0_4_load_37 | 56 | 0.0027929 | 0.00069995 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_159-9_0_4_load_87 | 58 | 0.0011744 | 0.00029434 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_159-9_0_4_load_29 | 59 | 0.0016062 | 0.00040255 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_159-9_0_4_load_88 | 60 | 0.0049229 | 0.0012338 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_159-9_0_4_load_30 | 61 | 0.0063274 | 0.0015858 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_159-9_0_4_load_32 | 62 | 0.00169 | 0.00042354 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_159-9_0_4_load_33 | 63 | 0.0056379 | 0.001413 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_159-9_0_4_load_35 | 65 | 0.0085327 | 0.0021385 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_159-9_0_4_load_36 | 66 | 0.0052763 | 0.0013224 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_159-9_0_4_load_85 | 67 | 0.0017661 | 0.00044262 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_159-9_0_4_load_113 | 69 | 0.0019299 | 0.00048367 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_159-9_0_4_load_70 | 70 | 0.0071392 | 0.0017892 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_159-9_0_4_load_114 | 74 | 0.098268 | 0.024628 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_159-9_0_4_load_121 | 75 | 0.0015446 | 0.0003871 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_159-9_0_4_load_49 | 77 | 0.007209 | 0.0018067 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_159-9_0_4_load_51 | 79 | 0.002709 | 0.00067895 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_159-9_0_4_load_52 | 80 | 0.0021507 | 0.000539 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_159-9_0_4_load_107 | 84 | 0.0071645 | 0.0017956 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_159-9_0_4_load_125 | 86 | 0.001572 | 0.00039398 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_159-9_0_4_load_67 | 91 | 0.0023298 | 0.0005839 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_159-9_0_4_load_69 | 92 | 0.00060557 | 0.00015177 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_159-9_0_4_load_73 | 93 | 0.001702 | 0.00042657 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_159-9_0_4_load_124 | 95 | 0.00073328 | 0.00018378 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_159-9_0_4_load_65 | 96 | 0.0030675 | 0.00076879 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_159-9_0_4_load_61 | 97 | 0.0073117 | 0.0018325 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_159-9_0_4_load_106 | 98 | 0.018045 | 0.0045225 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_159-9_0_4_load_122 | 99 | 0.002514 | 0.00063006 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_159-9_0_4_load_66 | 100 | 0.0024411 | 0.00061179 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_159-9_0_4_load_68 | 101 | 0.0026781 | 0.0006712 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_159-9_0_4_load_72 | 102 | 0.010355 | 0.0025952 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_159-9_0_4_load_62 | 103 | 0.0068462 | 0.0017158 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_159-9_0_4_load_118 | 105 | 0.0013694 | 0.00034321 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_159-9_0_4_load_74 | 106 | 0.0011359 | 0.00028468 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_159-9_0_4_load_75 | 107 | 0.011016 | 0.0027609 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_159-9_0_4_load_76 | 108 | 0.005795 | 0.0014524 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_159-9_0_4_load_77 | 109 | 0.00071197 | 0.00017844 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_159-9_0_4_load_84 | 111 | 0.00026632 | 6.6747e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_159-9_0_4_load_127 | 112 | 0.049469 | 0.012398 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_159-9_0_4_load_90 | 114 | 0.0017512 | 0.0004389 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_159-9_0_4_load_92 | 115 | 0.0062368 | 0.0015631 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_159-9_0_4_load_111 | 116 | 0.001872 | 0.00046918 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_159-9_0_4_load_105 | 117 | 0.0052792 | 0.0013231 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_159-9_0_4_line_0 |  | 0 | 1 | 0.023453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_159-9_0_4_line_1 |  | 1 | 2 | 0.012284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_159-9_0_4_line_2 |  | 2 | 3 | 0.0026277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_159-9_0_4_line_3 |  | 3 | 4 | 0.023417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_159-9_0_4_line_4 |  | 4 | 5 | 0.010871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_159-9_0_4_line_5 |  | 5 | 6 | 0.005148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_159-9_0_4_line_6 |  | 5 | 7 | 0.031021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_159-9_0_4_line_7 |  | 6 | 20 | 0.032324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_159-9_0_4_line_8 |  | 8 | 9 | 0.02328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_159-9_0_4_line_9 |  | 8 | 10 | 0.010153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_159-9_0_4_line_10 |  | 9 | 16 | 0.016198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_159-9_0_4_line_11 |  | 10 | 21 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_159-9_0_4_line_12 |  | 11 | 12 | 0.15623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_159-9_0_4_line_13 |  | 11 | 13 | 0.069334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_159-9_0_4_line_14 |  | 11 | 14 | 0.097717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_159-9_0_4_line_15 |  | 12 | 24 | 0.029546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_159-9_0_4_line_16 |  | 13 | 15 | 0.036303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_159-9_0_4_line_17 |  | 14 | 29 | 0.092337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_159-9_0_4_line_18 |  | 15 | 30 | 0.042052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_159-9_0_4_line_19 |  | 16 | 31 | 0.035368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_159-9_0_4_line_20 |  | 17 | 18 | 0.01273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_159-9_0_4_line_21 |  | 17 | 19 | 0.032567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_159-9_0_4_line_22 |  | 18 | 22 | 0.016893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_159-9_0_4_line_23 |  | 20 | 36 | 0.008996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_159-9_0_4_line_24 |  | 21 | 28 | 0.021109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_159-9_0_4_line_25 |  | 22 | 23 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_159-9_0_4_line_26 |  | 23 | 28 | 0.013739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_159-9_0_4_line_27 |  | 25 | 26 | 0.042499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_159-9_0_4_line_28 |  | 25 | 27 | 0.023898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_159-9_0_4_line_29 |  | 26 | 111 | 0.0087016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_159-9_0_4_line_30 |  | 29 | 111 | 0.042785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_159-9_0_4_line_31 |  | 29 | 109 | 0.019311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_159-9_0_4_line_32 |  | 31 | 32 | 0.063573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_159-9_0_4_line_33 |  | 32 | 46 | 0.023321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_159-9_0_4_line_34 |  | 32 | 47 | 0.0025107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_159-9_0_4_line_35 |  | 33 | 34 | 0.010571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_159-9_0_4_line_36 |  | 33 | 35 | 0.021096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_159-9_0_4_line_37 |  | 34 | 45 | 0.004591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_159-9_0_4_line_38 |  | 34 | 40 | 0.04592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_159-9_0_4_line_39 |  | 35 | 46 | 0.001295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_159-9_0_4_line_40 |  | 36 | 38 | 0.047284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_159-9_0_4_line_41 |  | 37 | 38 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_159-9_0_4_line_42 |  | 38 | 39 | 0.063041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_159-9_0_4_line_43 |  | 38 | 40 | 0.013606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_159-9_0_4_line_44 |  | 39 | 41 | 0.048151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_159-9_0_4_line_45 |  | 39 | 42 | 0.035656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_159-9_0_4_line_46 |  | 41 | 43 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_159-9_0_4_line_47 |  | 42 | 44 | 0.057145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_159-9_0_4_line_48 |  | 44 | 48 | 0.010449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_159-9_0_4_line_49 |  | 44 | 50 | 0.070281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_159-9_0_4_line_50 |  | 45 | 57 | 0.034363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_159-9_0_4_line_51 |  | 45 | 58 | 0.064132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_159-9_0_4_line_52 |  | 47 | 114 | 0.013886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_159-9_0_4_line_53 |  | 48 | 49 | 0.027849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_159-9_0_4_line_54 |  | 49 | 52 | 0.011143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_159-9_0_4_line_55 |  | 50 | 51 | 0.025156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_159-9_0_4_line_56 |  | 51 | 69 | 0.024012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_159-9_0_4_line_57 |  | 52 | 53 | 0.01473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_159-9_0_4_line_58 |  | 53 | 66 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_159-9_0_4_line_59 |  | 54 | 55 | 0.0099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_159-9_0_4_line_60 |  | 54 | 56 | 0.015245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_159-9_0_4_line_61 |  | 55 | 69 | 0.003151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_159-9_0_4_line_62 |  | 57 | 59 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_159-9_0_4_line_63 |  | 58 | 60 | 0.025156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_159-9_0_4_line_64 |  | 59 | 61 | 0.032995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_159-9_0_4_line_65 |  | 62 | 63 | 0.025256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_159-9_0_4_line_66 |  | 63 | 64 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_159-9_0_4_line_67 |  | 64 | 65 | 0.02085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_159-9_0_4_line_68 |  | 64 | 66 | 0.039172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_159-9_0_4_line_69 |  | 65 | 67 | 0.0088739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_159-9_0_4_line_70 |  | 67 | 68 | 0.032043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_159-9_0_4_line_71 |  | 68 | 72 | 0.011624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_159-9_0_4_line_72 |  | 70 | 71 | 0.0077899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_159-9_0_4_line_73 |  | 71 | 76 | 0.004909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_159-9_0_4_line_74 |  | 71 | 90 | 0.018209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_159-9_0_4_line_75 |  | 72 | 112 | 0.024656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_159-9_0_4_line_76 |  | 72 | 73 | 0.03712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_159-9_0_4_line_77 |  | 72 | 110 | 0.061786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_159-9_0_4_line_78 |  | 73 | 74 | 0.027177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_159-9_0_4_line_79 |  | 74 | 87 | 0.030072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_159-9_0_4_line_80 |  | 75 | 76 | 0.016404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_159-9_0_4_line_81 |  | 76 | 87 | 0.04879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_159-9_0_4_line_82 |  | 77 | 78 | 0.015549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_159-9_0_4_line_83 |  | 78 | 79 | 0.021764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_159-9_0_4_line_84 |  | 78 | 80 | 0.028023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_159-9_0_4_line_85 |  | 79 | 81 | 0.011184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_159-9_0_4_line_86 |  | 81 | 96 | 0.028783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_159-9_0_4_line_87 |  | 81 | 97 | 0.039572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_159-9_0_4_line_88 |  | 82 | 83 | 0.024648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_159-9_0_4_line_89 |  | 82 | 84 | 0.042119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_159-9_0_4_line_90 |  | 82 | 85 | 0.010504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_159-9_0_4_line_91 |  | 83 | 86 | 0.019849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_159-9_0_4_line_92 |  | 84 | 98 | 0.0099223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_159-9_0_4_line_93 |  | 85 | 95 | 0.032266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_159-9_0_4_line_94 |  | 85 | 99 | 0.025522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_159-9_0_4_line_95 |  | 87 | 88 | 0.035361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_159-9_0_4_line_96 |  | 88 | 94 | 0.01791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_159-9_0_4_line_97 |  | 89 | 90 | 0.011796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_159-9_0_4_line_98 |  | 89 | 91 | 0.010404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_159-9_0_4_line_99 |  | 89 | 92 | 0.0041783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_159-9_0_4_line_100 |  | 90 | 93 | 0.024157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_159-9_0_4_line_101 |  | 91 | 100 | 0.021694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_159-9_0_4_line_102 |  | 92 | 101 | 0.01294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_159-9_0_4_line_103 |  | 93 | 102 | 0.011204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_159-9_0_4_line_104 |  | 94 | 95 | 0.039969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_159-9_0_4_line_105 |  | 96 | 100 | 0.023812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_159-9_0_4_line_106 |  | 97 | 103 | 0.0022973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_159-9_0_4_line_107 |  | 98 | 117 | 0.14775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_159-9_0_4_line_108 |  | 102 | 106 | 0.028863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_159-9_0_4_line_109 |  | 103 | 104 | 0.035406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_159-9_0_4_line_110 |  | 104 | 105 | 0.003109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_159-9_0_4_line_111 |  | 106 | 107 | 0.11242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_159-9_0_4_line_112 |  | 108 | 109 | 0.0849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_159-9_0_4_line_113 |  | 108 | 110 | 0.053995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_159-9_0_4_line_114 |  | 112 | 113 | 0.0031237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_159-9_0_4_line_115 |  | 113 | 116 | 0.020822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_159-9_0_4_line_116 |  | 114 | 115 | 0.030008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_159-9_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 118 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2693951.741 | 1235285.049 | 2693948.3592 | 1235285.8803 | 2693929.2684 | 1235291.7411
1 | 2693917.5254 | 1235295.3461 | 2693929.2684 | 1235291.7411
2 | 2693917.5254 | 1235295.3461 | 2693915.0134 | 1235296.1173
3 | 2693892.6271 | 1235302.9897 | 2693915.0134 | 1235296.1173
4 | 2693892.6271 | 1235302.9897 | 2693890.8516 | 1235299.4257 | 2693889.687 | 1235296.0048 | 2693888.9883 | 1235292.8026
5 | 2693889.7725 | 1235287.7224 | 2693889.2393 | 1235290.327 | 2693888.9883 | 1235292.8026
6 | 2693888.9883 | 1235292.8026 | 2693884.0554 | 1235294.0811 | 2693880.3514 | 1235295.2012 | 2693875.9716 | 1235297.8895 | 2693862.7779 | 1235308.4763
7 | 2693889.7725 | 1235287.7224 | 2693889.9147 | 1235278.251 | 2693886.7269 | 1235262.5225 | 2693885.5252 | 1235255.8262
8 | 2693768.7773 | 1235335.9471 | 2693786.5466 | 1235320.8498
9 | 2693768.7773 | 1235335.9471 | 2693766.3068 | 1235326.0996
10 | 2693786.5466 | 1235320.8498 | 2693793.3047 | 1235315.1857 | 2693797.1469 | 1235308.8847
11 | 2693762.9659 | 1235312.7833 | 2693766.3068 | 1235326.0996
12 | 2693387.2017 | 1235179.1459 | 2693400.1413 | 1235199.642 | 2693408.1175 | 1235212.2877 | 2693415.4855 | 1235223.6562 | 2693430.2878 | 1235246.5056 | 2693453.4724 | 1235290.3244 | 2693463.733 | 1235315.0816
13 | 2693463.733 | 1235315.0816 | 2693468.7174 | 1235326.8686 | 2693471.5122 | 1235333.9733 | 2693473.5828 | 1235338.9984 | 2693475.5801 | 1235342.9105 | 2693477.5028 | 1235345.7873 | 2693481.6793 | 1235350.7121 | 2693483.4 | 1235352.9631 | 2693488.1532 | 1235350.5806 | 2693492.5899 | 1235348.5934 | 2693497.1054 | 1235346.8854 | 2693507.9719 | 1235343.7207
14 | 2693463.733 | 1235315.0816 | 2693536.9162 | 1235276.9942 | 2693550.2715 | 1235269.7042
15 | 2693387.2017 | 1235179.1459 | 2693413.6676 | 1235166.0117
16 | 2693507.9719 | 1235343.7207 | 2693543.1655 | 1235334.8126
17 | 2693547.4449 | 1235183.8142 | 2693547.6256 | 1235185.7963 | 2693547.597 | 1235187.6082 | 2693547.5638 | 1235189.7204 | 2693547.7132 | 1235191.7687 | 2693548.1269 | 1235193.8545 | 2693551.833 | 1235209.9023 | 2693555.5143 | 1235227.5176 | 2693557.5923 | 1235237.8356 | 2693560.6207 | 1235250.7705 | 2693561.0038 | 1235252.8781 | 2693561.2326 | 1235254.6941 | 2693561.3107 | 1235256.9414 | 2693560.9802 | 1235259.1823 | 2693560.1655 | 1235261.4044 | 2693558.8857 | 1235263.3635 | 2693557.1075 | 1235265.248 | 2693555.1829 | 1235266.8077 | 2693552.4385 | 1235268.5213 | 2693550.2715 | 1235269.7042
18 | 2693584.0536 | 1235325.2475 | 2693582.6097 | 1235325.2489 | 2693579.2798 | 1235325.6857 | 2693548.4175 | 1235333.4832 | 2693543.1655 | 1235334.8126
19 | 2693815.5602 | 1235278.6881 | 2693797.1469 | 1235308.8847
20 | 2693722.0695 | 1235288.2754 | 2693717.9455 | 1235290.1117 | 2693714.431 | 1235292.1689 | 2693711.4928 | 1235295.1247
21 | 2693711.4928 | 1235295.1247 | 2693710.2554 | 1235300.1533 | 2693709.9729 | 1235307.0205 | 2693710.4251 | 1235312.8986 | 2693711.7805 | 1235318.6242 | 2693714.4275 | 1235326.9494
22 | 2693722.0695 | 1235288.2754 | 2693738.0973 | 1235282.802
23 | 2693885.5252 | 1235255.8262 | 2693883.9362 | 1235246.9716
24 | 2693757.8579 | 1235292.3013 | 2693761.9267 | 1235308.6412 | 2693762.9659 | 1235312.7833
25 | 2693754.5381 | 1235278.9697 | 2693738.0973 | 1235282.802
26 | 2693754.5381 | 1235278.9697 | 2693757.8579 | 1235292.3013
27 | 2693640.6907 | 1235172.0743 | 2693610.083 | 1235176.1505 | 2693598.5656 | 1235177.6987
28 | 2693640.6907 | 1235172.0743 | 2693664.3316 | 1235168.5806
29 | 2693589.9415 | 1235178.858 | 2693598.5656 | 1235177.6987
30 | 2693547.4449 | 1235183.8142 | 2693588.168 | 1235179.0964 | 2693589.9415 | 1235178.858
31 | 2693547.4449 | 1235183.8142 | 2693543.4086 | 1235164.9294
32 | 2693774.9519 | 1235232.0686 | 2693779.5254 | 1235237.2446 | 2693793.4959 | 1235248.9292 | 2693808.033 | 1235260.2002 | 2693809.5128 | 1235261.8803 | 2693810.5301 | 1235263.6088 | 2693815.5602 | 1235278.6881
33 | 2693774.9519 | 1235232.0686 | 2693797.9098 | 1235227.9667
34 | 2693774.9519 | 1235232.0686 | 2693772.5325 | 1235231.3975
35 | 2693816.0416 | 1235214.2041 | 2693819.9512 | 1235224.0286
36 | 2693819.9512 | 1235224.0286 | 2693799.1846 | 1235227.739
37 | 2693816.0416 | 1235214.2041 | 2693814.132 | 1235210.0265
38 | 2693816.0416 | 1235214.2041 | 2693844.7548 | 1235207.3859 | 2693860.816 | 1235204.0293
39 | 2693799.1846 | 1235227.739 | 2693797.9098 | 1235227.9667
40 | 2693873.9647 | 1235200.7535 | 2693879.2726 | 1235224.5881 | 2693883.4851 | 1235244.4581 | 2693883.9362 | 1235246.9716
41 | 2693873.9647 | 1235200.7535 | 2693877.0985 | 1235201.7148 | 2693887.1305 | 1235200.2583
42 | 2693873.9647 | 1235200.7535 | 2693875.0099 | 1235199.2801 | 2693875.5551 | 1235197.8321 | 2693875.7872 | 1235195.6008 | 2693875.7613 | 1235193.888 | 2693875.4089 | 1235191.7586 | 2693874.5644 | 1235188.6764 | 2693869.9011 | 1235172.9023 | 2693861.5326 | 1235144.4271 | 2693860.0895 | 1235140.4236
43 | 2693873.9647 | 1235200.7535 | 2693872.7048 | 1235201.4452 | 2693871.2678 | 1235201.845 | 2693860.816 | 1235204.0293
44 | 2693860.0895 | 1235140.4236 | 2693855.0787 | 1235127.4683 | 2693854.5014 | 1235125.202 | 2693854.2678 | 1235122.741 | 2693854.4189 | 1235120.3638 | 2693854.9215 | 1235118.2591 | 2693855.6937 | 1235116.3366 | 2693857.2019 | 1235113.8252 | 2693859.2026 | 1235111.2883 | 2693861.3963 | 1235108.9879 | 2693863.8912 | 1235106.7924 | 2693866.8239 | 1235104.6705 | 2693869.672 | 1235103.1144 | 2693872.6571 | 1235101.6974
45 | 2693860.0895 | 1235140.4236 | 2693854.5832 | 1235135.8333 | 2693850.5255 | 1235132.022 | 2693847.8575 | 1235129.3668 | 2693845.6125 | 1235126.7739 | 2693843.2551 | 1235123.1451 | 2693842.1035 | 1235120.8141 | 2693841.0432 | 1235117.4949 | 2693839.4811 | 1235112.4153
46 | 2693895.6667 | 1235094.3007 | 2693882.1199 | 1235098.1185 | 2693877.4395 | 1235099.7013 | 2693872.9364 | 1235101.5648 | 2693872.6571 | 1235101.6974
47 | 2693836.8676 | 1235056.9515 | 2693834.8319 | 1235063.1461 | 2693833.568 | 1235067.9185 | 2693832.5654 | 1235072.9285 | 2693831.9583 | 1235076.8551 | 2693831.7659 | 1235080.4102 | 2693831.8113 | 1235082.8016 | 2693832.0853 | 1235085.5857 | 2693832.5767 | 1235088.4956 | 2693833.2201 | 1235091.3746 | 2693835.6436 | 1235099.9191 | 2693837.1193 | 1235104.7348 | 2693839.4811 | 1235112.4153
48 | 2693836.8676 | 1235056.9515 | 2693829.9365 | 1235049.1141
49 | 2693836.8676 | 1235056.9515 | 2693838.5456 | 1235051.8409 | 2693839.3384 | 1235050.0521 | 2693840.1686 | 1235048.7754 | 2693841.127 | 1235047.5229 | 2693842.3952 | 1235046.3088 | 2693844.4157 | 1235044.9174 | 2693845.7455 | 1235044.1156 | 2693847.2435 | 1235043.2053 | 2693850.0961 | 1235041.8493 | 2693854.6269 | 1235040.153 | 2693858.3234 | 1235039.0439 | 2693861.8634 | 1235038.2548 | 2693861.6254 | 1235037.0279 | 2693859.5107 | 1235026.6647 | 2693858.6126 | 1235022.1806 | 2693856.3729 | 1235018.2868 | 2693851.1777 | 1235021.307 | 2693849.2047 | 1235011.5576
50 | 2693794.4359 | 1235182.2286 | 2693799.8499 | 1235187.3956 | 2693802.4332 | 1235190.1384 | 2693804.2684 | 1235192.3245 | 2693806.0893 | 1235194.9329 | 2693808.639 | 1235199.3208 | 2693814.132 | 1235210.0265
51 | 2693814.132 | 1235210.0265 | 2693764.6259 | 1235169.2581
52 | 2693772.5325 | 1235231.3975 | 2693759.1523 | 1235227.6859
53 | 2693829.9365 | 1235049.1141 | 2693804.4309 | 1235060.2957
54 | 2693796.437 | 1235059.8597 | 2693797.5482 | 1235063.3131 | 2693804.4309 | 1235060.2957
55 | 2693849.2047 | 1235011.5576 | 2693847.2663 | 1235008.2357 | 2693865.8264 | 1234997.7641
56 | 2693886.7393 | 1234985.9651 | 2693865.8264 | 1234997.7641
57 | 2693796.437 | 1235059.8597 | 2693793.9171 | 1235060.7651 | 2693791.1347 | 1235061.5106 | 2693788.5754 | 1235062.0372 | 2693782.0893 | 1235063.0094
58 | 2693782.0893 | 1235063.0094 | 2693765.839 | 1235065.4452
59 | 2693890.924 | 1234998.0289 | 2693890.5867 | 1234993.0311 | 2693888.2245 | 1234988.7462
60 | 2693890.924 | 1234998.0289 | 2693891.255 | 1235002.9489 | 2693895.825 | 1235012.1954
61 | 2693888.2245 | 1234988.7462 | 2693886.7393 | 1234985.9651
62 | 2693794.4359 | 1235182.2286 | 2693808.2965 | 1235168.1704
63 | 2693743.5118 | 1235160.3869 | 2693751.6326 | 1235158.5581 | 2693764.6259 | 1235169.2581
64 | 2693831.4619 | 1235144.6746 | 2693808.2965 | 1235168.1704
65 | 2693732.3955 | 1235085.9828 | 2693738.6878 | 1235103.4581 | 2693738.5666 | 1235104.9017 | 2693740.7321 | 1235109.1834 | 2693740.9104 | 1235109.5811
66 | 2693727.0997 | 1235071.2518 | 2693730.0509 | 1235079.471 | 2693732.3955 | 1235085.9828
67 | 2693727.0997 | 1235071.2518 | 2693717.6178 | 1235072.5032 | 2693709.444 | 1235073.8419 | 2693706.4943 | 1235074.4085
68 | 2693727.0997 | 1235071.2518 | 2693765.839 | 1235065.4452
69 | 2693706.4943 | 1235074.4085 | 2693703.5065 | 1235074.9825 | 2693698.5156 | 1235076.0935 | 2693697.8182 | 1235076.2656
70 | 2693666.3001 | 1235081.7675 | 2693671.3408 | 1235081.3355 | 2693675.4667 | 1235080.8335 | 2693680.2624 | 1235080.0975 | 2693684.8778 | 1235079.2697 | 2693689.9208 | 1235078.2151 | 2693697.8182 | 1235076.2656
71 | 2693666.3001 | 1235081.7675 | 2693660.6351 | 1235083.3905 | 2693655.0205 | 1235084.6919
72 | 2693722.7585 | 1235022.0919 | 2693725.8422 | 1235029.2454
73 | 2693718.2461 | 1235024.0555 | 2693722.7585 | 1235022.0919
74 | 2693726.7784 | 1235006.7219 | 2693722.0102 | 1235010.505 | 2693720.6543 | 1235016.7993 | 2693722.7585 | 1235022.0919
75 | 2693655.0205 | 1235084.6919 | 2693657.6021 | 1235091.8711 | 2693659.5068 | 1235096.3711 | 2693662.4205 | 1235102.6549 | 2693665.1576 | 1235107.0927
76 | 2693655.0205 | 1235084.6919 | 2693652.2567 | 1235085.2265 | 2693651.4296 | 1235081.5107 | 2693658.6802 | 1235079.6681 | 2693662.2395 | 1235078.6123 | 2693667.4454 | 1235076.8264 | 2693680.3386 | 1235071.9038
77 | 2693594.9985 | 1235099.2012 | 2693605.8599 | 1235095.9144 | 2693617.5708 | 1235092.9967 | 2693631.0526 | 1235089.6289 | 2693642.052 | 1235087.1893 | 2693652.2567 | 1235085.2265 | 2693655.0205 | 1235084.6919
78 | 2693680.3386 | 1235071.9038 | 2693680.042 | 1235071.0318 | 2693676.7382 | 1235061.1726 | 2693674.2667 | 1235053.2501 | 2693676.4989 | 1235050.4276 | 2693680.279 | 1235049.2451
79 | 2693673.1525 | 1235023.1105 | 2693675.4409 | 1235030.641 | 2693679.4543 | 1235041.59 | 2693680.4751 | 1235044.0634 | 2693681.4958 | 1235046.0588 | 2693682.9956 | 1235048.3952 | 2693680.279 | 1235049.2451
80 | 2693718.2461 | 1235024.0555 | 2693724.6953 | 1235039.139
81 | 2693718.2461 | 1235024.0555 | 2693714.0386 | 1235025.8905 | 2693710.3923 | 1235021.4297 | 2693703.028 | 1235018 | 2693694.9943 | 1235018.129 | 2693673.1525 | 1235023.1105
82 | 2693829.2071 | 1234946.7612 | 2693842.686 | 1234939.0093
83 | 2693829.2071 | 1234946.7612 | 2693823.5081 | 1234950.0402 | 2693810.3864 | 1234957.6906
84 | 2693829.2071 | 1234946.7612 | 2693815.7834 | 1234922.943 | 2693815.2929 | 1234922.4679
85 | 2693800.7248 | 1234963.3236 | 2693810.3864 | 1234957.6906
86 | 2693800.7248 | 1234963.3236 | 2693780.8879 | 1234974.1073 | 2693775.1357 | 1234976.4316
87 | 2693800.7248 | 1234963.3236 | 2693793.4916 | 1234946.7974 | 2693781.1695 | 1234929.1391
88 | 2693556.58 | 1235039.764 | 2693567.9342 | 1235035.9511 | 2693580.1482 | 1235032.3408
89 | 2693556.58 | 1235039.764 | 2693516.7552 | 1235053.4744
90 | 2693556.58 | 1235039.764 | 2693554.946 | 1235034.8903 | 2693560.1025 | 1235033.3592
91 | 2693580.1482 | 1235032.3408 | 2693586.0949 | 1235051.2779
92 | 2693507.3885 | 1235056.746 | 2693508.6152 | 1235056.2767 | 2693516.7552 | 1235053.4744
93 | 2693560.1025 | 1235033.3592 | 2693591.0264 | 1235024.1506
94 | 2693560.1025 | 1235033.3592 | 2693552.5345 | 1235008.9847
95 | 2693648.0516 | 1235013.9526 | 2693649.5244 | 1235020.4028 | 2693661.0832 | 1235018.5058 | 2693671.2179 | 1235016.6642 | 2693673.1525 | 1235023.1105
96 | 2693630.3786 | 1235017.1543 | 2693648.0516 | 1235013.9526
97 | 2693722.6531 | 1234995.671 | 2693724.8321 | 1235001.4985 | 2693726.7784 | 1235006.7219
98 | 2693722.6531 | 1234995.671 | 2693732.4703 | 1234992.2247
99 | 2693722.6531 | 1234995.671 | 2693718.6563 | 1234996.889
100 | 2693726.7784 | 1235006.7219 | 2693749.3698 | 1234998.1679
101 | 2693752.9395 | 1234985.039 | 2693732.4703 | 1234992.2247
102 | 2693706.2779 | 1235000.6612 | 2693718.6563 | 1234996.889
103 | 2693759.8474 | 1234994.2006 | 2693749.3698 | 1234998.1679
104 | 2693630.3786 | 1235017.1543 | 2693591.0264 | 1235024.1506
105 | 2693775.1357 | 1234976.4316 | 2693759.7542 | 1234982.6467 | 2693752.9395 | 1234985.039
106 | 2693781.1695 | 1234929.1391 | 2693779.8548 | 1234927.2552
107 | 2693384.6053 | 1235138.0269 | 2693387.293 | 1235136.2827 | 2693394.8755 | 1235131.1315 | 2693402.0711 | 1235126.0409 | 2693443.6345 | 1235095.3608 | 2693461.311 | 1235082.2959 | 2693472.2359 | 1235074.4843 | 2693478.2941 | 1235070.4878 | 2693483.9186 | 1235067.1071 | 2693489.9473 | 1235064.0219 | 2693497.403 | 1235060.6924 | 2693502.9491 | 1235058.4447 | 2693507.3885 | 1235056.746
108 | 2693759.8474 | 1234994.2006 | 2693760.4383 | 1234993.9769 | 2693780.9473 | 1234985.6833 | 2693786.4829 | 1234983.1005
109 | 2693756.4621 | 1234912.1211 | 2693766.9026 | 1234907.2267 | 2693771.4769 | 1234915.2492 | 2693779.8548 | 1234927.2552
110 | 2693757.8793 | 1234914.8899 | 2693756.4621 | 1234912.1211
111 | 2693884.3286 | 1234927.8099 | 2693825.3801 | 1234961.8784 | 2693796.2529 | 1234978.5419 | 2693786.4829 | 1234983.1005
112 | 2693546.132 | 1235120.6827 | 2693520.1545 | 1235129.6229 | 2693517.6537 | 1235130.7621 | 2693515.6465 | 1235132.2872 | 2693513.9896 | 1235134.1514 | 2693513.0764 | 1235135.905 | 2693512.5608 | 1235137.3979 | 2693512.2952 | 1235138.8837 | 2693512.2246 | 1235140.4838 | 2693512.3757 | 1235141.9428 | 2693512.7437 | 1235143.572 | 2693513.3978 | 1235145.2946 | 2693514.3274 | 1235146.8326 | 2693515.4938 | 1235148.2298 | 2693517.2558 | 1235149.7808 | 2693519.2771 | 1235151.2137 | 2693521.9042 | 1235152.6227 | 2693524.3881 | 1235153.518 | 2693527.4874 | 1235154.2674 | 2693532.61 | 1235155.3599 | 2693535.0976 | 1235156.0218 | 2693537.1976 | 1235156.7776 | 2693539.4935 | 1235158.0702 | 2693540.7765 | 1235159.2802 | 2693541.853 | 1235160.6203 | 2693542.682 | 1235162.2902 | 2693543.229 | 1235164.089 | 2693543.4086 | 1235164.9294
113 | 2693594.9985 | 1235099.2012 | 2693591.8201 | 1235102.5091 | 2693589.7195 | 1235104.1884 | 2693586.507 | 1235106.2949 | 2693584.0133 | 1235107.4676 | 2693575.2815 | 1235110.599 | 2693557.6613 | 1235116.715 | 2693546.132 | 1235120.6827
114 | 2693666.7974 | 1235109.7513 | 2693665.1576 | 1235107.0927
115 | 2693666.7974 | 1235109.7513 | 2693672.3037 | 1235118.6668 | 2693678.1379 | 1235127.2071
116 | 2693729.4973 | 1235224.0709 | 2693733.6749 | 1235223.9337 | 2693752.2971 | 1235225.7843 | 2693759.1523 | 1235227.6859

## bus_geodata
| x | y | coords
0 | 2693951.741 | 1235285.049
1 | 2693929.2684 | 1235291.7411
2 | 2693917.5254 | 1235295.3461
3 | 2693915.0134 | 1235296.1173
4 | 2693892.6271 | 1235302.9897
5 | 2693888.9883 | 1235292.8026
6 | 2693889.7725 | 1235287.7224
7 | 2693862.7779 | 1235308.4763
8 | 2693768.7773 | 1235335.9471
9 | 2693786.5466 | 1235320.8498
10 | 2693766.3068 | 1235326.0996
11 | 2693463.733 | 1235315.0816
12 | 2693387.2017 | 1235179.1459
13 | 2693507.9719 | 1235343.7207
14 | 2693550.2715 | 1235269.7042
15 | 2693543.1655 | 1235334.8126
16 | 2693797.1469 | 1235308.8847
17 | 2693711.4928 | 1235295.1247
18 | 2693722.0695 | 1235288.2754
19 | 2693714.4275 | 1235326.9494
20 | 2693885.5252 | 1235255.8262
21 | 2693762.9659 | 1235312.7833
22 | 2693738.0973 | 1235282.802
23 | 2693754.5381 | 1235278.9697
24 | 2693413.6676 | 1235166.0117
25 | 2693640.6907 | 1235172.0743
26 | 2693598.5656 | 1235177.6987
27 | 2693664.3316 | 1235168.5806
28 | 2693757.8579 | 1235292.3013
29 | 2693547.4449 | 1235183.8142
30 | 2693584.0536 | 1235325.2475
31 | 2693815.5602 | 1235278.6881
32 | 2693774.9519 | 1235232.0686
33 | 2693819.9512 | 1235224.0286
34 | 2693816.0416 | 1235214.2041
35 | 2693799.1846 | 1235227.739
36 | 2693883.9362 | 1235246.9716
37 | 2693887.1305 | 1235200.2583
38 | 2693873.9647 | 1235200.7535
39 | 2693860.0895 | 1235140.4236
40 | 2693860.816 | 1235204.0293
41 | 2693872.6571 | 1235101.6974
42 | 2693839.4811 | 1235112.4153
43 | 2693895.6667 | 1235094.3007
44 | 2693836.8676 | 1235056.9515
45 | 2693814.132 | 1235210.0265
46 | 2693797.9098 | 1235227.9667
47 | 2693772.5325 | 1235231.3975
48 | 2693829.9365 | 1235049.1141
49 | 2693804.4309 | 1235060.2957
50 | 2693849.2047 | 1235011.5576
51 | 2693865.8264 | 1234997.7641
52 | 2693796.437 | 1235059.8597
53 | 2693782.0893 | 1235063.0094
54 | 2693890.924 | 1234998.0289
55 | 2693888.2245 | 1234988.7462
56 | 2693895.825 | 1235012.1954
57 | 2693794.4359 | 1235182.2286
58 | 2693764.6259 | 1235169.2581
59 | 2693808.2965 | 1235168.1704
60 | 2693743.5118 | 1235160.3869
61 | 2693831.4619 | 1235144.6746
62 | 2693740.9104 | 1235109.5811
63 | 2693732.3955 | 1235085.9828
64 | 2693727.0997 | 1235071.2518
65 | 2693706.4943 | 1235074.4085
66 | 2693765.839 | 1235065.4452
67 | 2693697.8182 | 1235076.2656
68 | 2693666.3001 | 1235081.7675
69 | 2693886.7393 | 1234985.9651
70 | 2693725.8422 | 1235029.2454
71 | 2693722.7585 | 1235022.0919
72 | 2693655.0205 | 1235084.6919
73 | 2693680.3386 | 1235071.9038
74 | 2693680.279 | 1235049.2451
75 | 2693724.6953 | 1235039.139
76 | 2693718.2461 | 1235024.0555
77 | 2693842.686 | 1234939.0093
78 | 2693829.2071 | 1234946.7612
79 | 2693810.3864 | 1234957.6906
80 | 2693815.2929 | 1234922.4679
81 | 2693800.7248 | 1234963.3236
82 | 2693556.58 | 1235039.764
83 | 2693580.1482 | 1235032.3408
84 | 2693516.7552 | 1235053.4744
85 | 2693560.1025 | 1235033.3592
86 | 2693586.0949 | 1235051.2779
87 | 2693673.1525 | 1235023.1105
88 | 2693648.0516 | 1235013.9526
89 | 2693722.6531 | 1234995.671
90 | 2693726.7784 | 1235006.7219
91 | 2693732.4703 | 1234992.2247
92 | 2693718.6563 | 1234996.889
93 | 2693749.3698 | 1234998.1679
94 | 2693630.3786 | 1235017.1543
95 | 2693591.0264 | 1235024.1506
96 | 2693775.1357 | 1234976.4316
97 | 2693781.1695 | 1234929.1391
98 | 2693507.3885 | 1235056.746
99 | 2693552.5345 | 1235008.9847
100 | 2693752.9395 | 1234985.039
101 | 2693706.2779 | 1235000.6612
102 | 2693759.8474 | 1234994.2006
103 | 2693779.8548 | 1234927.2552
104 | 2693756.4621 | 1234912.1211
105 | 2693757.8793 | 1234914.8899
106 | 2693786.4829 | 1234983.1005
107 | 2693884.3286 | 1234927.8099
108 | 2693546.132 | 1235120.6827
109 | 2693543.4086 | 1235164.9294
110 | 2693594.9985 | 1235099.2012
111 | 2693589.9415 | 1235178.858
112 | 2693665.1576 | 1235107.0927
113 | 2693666.7974 | 1235109.7513
114 | 2693759.1523 | 1235227.6859
115 | 2693729.4973 | 1235224.0709
116 | 2693678.1379 | 1235127.2071
117 | 2693384.6053 | 1235138.0269
118 | 2693727.0997 | 1235071.2518

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9776 | -0.43035 | 0.0059107 | 0.0014814
1 | 0.97773 | -0.42782 | 0.0026413 | 0.00066197
2 | 0.97783 | -0.42591 | 0.0057861 | 0.0014501
3 | 0.97787 | -0.42522 | 0.0037561 | 0.00094137
4 | 0.97826 | -0.4175 | 0 | 0
5 | 0.97844 | -0.41392 | 0 | 0
6 | 0.97854 | -0.41201 | 0 | 0
7 | 0.97838 | -0.41516 | 0.0022044 | 0.00055247
8 | 0.97266 | -0.52728 | 0 | 0
9 | 0.97314 | -0.51789 | 0 | 0
10 | 0.97246 | -0.53138 | 0.0042151 | 0.0010564
11 | 0.98824 | -0.22541 | 0 | 0
12 | 0.98812 | -0.22786 | 0 | 0
13 | 0.988 | -0.23019 | 0 | 0
14 | 0.98867 | -0.21713 | 0.0012988 | 0.0003255
15 | 0.98787 | -0.23269 | 0.0018689 | 0.00046839
16 | 0.97347 | -0.51135 | 0.00078193 | 0.00019597
17 | 0.9714 | -0.55232 | 0 | 0
18 | 0.97145 | -0.55122 | 0.0065703 | 0.0016467
19 | 0.97126 | -0.55512 | 0.0046536 | 0.0011663
20 | 0.97915 | -0.40008 | 0.001355 | 0.00033959
21 | 0.97223 | -0.53587 | 0.0035216 | 0.00088259
22 | 0.97163 | -0.54772 | 0 | 0
23 | 0.97181 | -0.54423 | 0 | 0
24 | 0.98809 | -0.22832 | 0.00087491 | 0.00021927
25 | 0.98895 | -0.21164 | 0 | 0
26 | 0.98902 | -0.21029 | 0.0013828 | 0.00034657
27 | 0.98891 | -0.2124 | 0.0017839 | 0.00044708
28 | 0.97195 | -0.54139 | 0.0029563 | 0.00074091
29 | 0.98918 | -0.20718 | 0 | 0
30 | 0.98779 | -0.23419 | 0.0019915 | 0.00049911
31 | 0.97422 | -0.49659 | 0 | 0
32 | 0.97557 | -0.47012 | 0 | 0
33 | 0.97704 | -0.44116 | 0 | 0
34 | 0.97741 | -0.43392 | 0 | 0
35 | 0.97631 | -0.45563 | 0.0035863 | 0.00089881
36 | 0.97933 | -0.39653 | 0.00098255 | 0.00024625
37 | 0.98027 | -0.3781 | 0.004121 | 0.0010328
38 | 0.98032 | -0.3771 | 0 | 0
39 | 0.98514 | -0.28347 | 0 | 0
40 | 0.97962 | -0.39081 | 0.0039527 | 0.00099063
41 | 0.98495 | -0.28728 | 0.0019844 | 0.00049735
42 | 0.98801 | -0.22812 | 0.0029576 | 0.00074124
43 | 0.98489 | -0.28833 | 0.0024159 | 0.00060549
44 | 0.99277 | -0.13708 | 0 | 0
45 | 0.97735 | -0.43509 | 0 | 0
46 | 0.97626 | -0.45643 | 0.0018652 | 0.00046747
47 | 0.97555 | -0.47055 | 0.0013837 | 0.00034678
48 | 0.99377 | -0.11804 | 0 | 0
49 | 0.99511 | -0.092714 | 0.0077377 | 0.0019392
50 | 0.9919 | -0.15391 | 0 | 0
51 | 0.99159 | -0.15994 | 0.0088014 | 0.0022058
52 | 0.99549 | -0.085465 | 0 | 0
53 | 0.99599 | -0.075891 | 0.0054495 | 0.0013658
54 | 0.99146 | -0.1626 | 0 | 0
55 | 0.99148 | -0.16211 | 0 | 0
56 | 0.99142 | -0.16336 | 0.0027929 | 0.00069995
57 | 0.9771 | -0.44007 | 0 | 0
58 | 0.97699 | -0.44223 | 0.0011744 | 0.00029434
59 | 0.97695 | -0.44293 | 0.0016062 | 0.00040255
60 | 0.97688 | -0.4445 | 0.0049229 | 0.0012338
61 | 0.97676 | -0.44674 | 0.0063274 | 0.0015858
62 | 0.99996 | -0.00074414 | 0.00169 | 0.00042354
63 | 1 | 0 | -0.41394 | -0.10569
64 | 0.99805 | -0.036863 | 0 | 0
65 | 0.99624 | -0.071326 | 0.0085327 | 0.0021385
66 | 0.99658 | -0.064699 | 0.0052763 | 0.0013224
67 | 0.99549 | -0.085587 | 0.0017661 | 0.00044262
68 | 0.99281 | -0.13693 | 0 | 0
69 | 0.99149 | -0.16195 | 0.0019299 | 0.00048367
70 | 0.98032 | -0.37859 | 0.0071392 | 0.0017892
71 | 0.98037 | -0.37758 | 0 | 0
72 | 0.99183 | -0.15562 | 0 | 0
73 | 0.98949 | -0.20072 | 0 | 0
74 | 0.98691 | -0.25049 | 0.098268 | 0.024628
75 | 0.98066 | -0.3718 | 0.0015446 | 0.0003871
76 | 0.98069 | -0.37134 | 0 | 0
77 | 0.97604 | -0.46256 | 0.007209 | 0.0018067
78 | 0.97614 | -0.46051 | 0 | 0
79 | 0.97633 | -0.45679 | 0.002709 | 0.00067895
80 | 0.97608 | -0.46161 | 0.0021507 | 0.000539
81 | 0.97645 | -0.45432 | 0 | 0
82 | 0.97953 | -0.39405 | 0 | 0
83 | 0.97949 | -0.39475 | 0 | 0
84 | 0.97834 | -0.41741 | 0.0071645 | 0.0017956
85 | 0.97984 | -0.38793 | 0 | 0
86 | 0.97947 | -0.39532 | 0.001572 | 0.00039398
87 | 0.98393 | -0.30822 | 0 | 0
88 | 0.98277 | -0.33073 | 0 | 0
89 | 0.97888 | -0.40669 | 0 | 0
90 | 0.9793 | -0.39839 | 0 | 0
91 | 0.97854 | -0.4134 | 0.0023298 | 0.0005839
92 | 0.97887 | -0.40694 | 0.00060557 | 0.00015177
93 | 0.97876 | -0.40902 | 0.001702 | 0.00042657
94 | 0.98219 | -0.34215 | 0 | 0
95 | 0.98088 | -0.36769 | 0.00073328 | 0.00018378
96 | 0.97719 | -0.43981 | 0.0030675 | 0.00076879
97 | 0.97588 | -0.46556 | 0.0073117 | 0.0018325
98 | 0.97813 | -0.42162 | 0.018045 | 0.0045225
99 | 0.97978 | -0.38909 | 0.002514 | 0.00063006
100 | 0.97787 | -0.42649 | 0.0024411 | 0.00061179
101 | 0.97884 | -0.40757 | 0.0026781 | 0.0006712
102 | 0.97853 | -0.41361 | 0.010355 | 0.0025952
103 | 0.97587 | -0.4659 | 0.0068462 | 0.0017158
104 | 0.97582 | -0.46679 | 0 | 0
105 | 0.97582 | -0.46687 | 0.0013694 | 0.00034321
106 | 0.9782 | -0.42 | 0.0011359 | 0.00028468
107 | 0.97705 | -0.44259 | 0.011016 | 0.0027609
108 | 0.99014 | -0.1885 | 0.005795 | 0.0014524
109 | 0.98935 | -0.20391 | 0.00071197 | 0.00017844
110 | 0.99093 | -0.17316 | 0 | 0
111 | 0.98904 | -0.2098 | 0.00026632 | 6.6747e-05
112 | 0.99068 | -0.17808 | 0.049469 | 0.012398
113 | 0.99067 | -0.17818 | 0 | 0
114 | 0.97544 | -0.47259 | 0.0017512 | 0.0004389
115 | 0.97527 | -0.47601 | 0.0062368 | 0.0015631
116 | 0.99063 | -0.17887 | 0.001872 | 0.00046918
117 | 0.9774 | -0.43585 | 0.0052792 | 0.0013231
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0059107 | -0.0014814 | 0.0059114 | 0.0014815 | 7.1184e-07 | 1.6149e-07 | 0.0089967 | 0.0089966 | 0.0089967 | 0.9776 | -0.43035 | 0.97773 | -0.42782 | 2.4716
1 | -0.0085527 | -0.0021435 | 0.0085535 | 0.0021438 | 7.8045e-07 | 3.4542e-07 | 0.013016 | 0.013016 | 0.013016 | 0.97773 | -0.42782 | 0.97783 | -0.42591 | 3.5759
2 | -0.01434 | -0.003594 | 0.01434 | 0.0035942 | 4.6921e-07 | 2.6733e-07 | 0.021821 | 0.021821 | 0.021821 | 0.97783 | -0.42591 | 0.97787 | -0.42522 | 5.9949
3 | -0.018096 | -0.0045356 | 0.018103 | 0.0045396 | 6.6589e-06 | 3.9678e-06 | 0.027537 | 0.027537 | 0.027537 | 0.97787 | -0.42522 | 0.97826 | -0.4175 | 7.5651
4 | -0.018103 | -0.0045396 | 0.018106 | 0.0045414 | 3.0912e-06 | 1.8419e-06 | 0.027537 | 0.027537 | 0.027537 | 0.97826 | -0.4175 | 0.97844 | -0.41392 | 7.5651
5 | -0.02031 | -0.0050936 | 0.020312 | 0.0050947 | 1.842e-06 | 1.1142e-06 | 0.030889 | 0.030889 | 0.030889 | 0.97844 | -0.41392 | 0.97854 | -0.41201 | 8.4861
6 | 0.0022045 | 0.00055216 | -0.0022044 | -0.00055247 | 1.3075e-07 | -3.0591e-07 | 0.0033525 | 0.0033526 | 0.0033526 | 0.97844 | -0.41392 | 0.97838 | -0.41516 | 0.92105
7 | -0.020312 | -0.0050947 | 0.020324 | 0.0051017 | 1.1566e-05 | 6.9957e-06 | 0.030889 | 0.030889 | 0.030889 | 0.97854 | -0.41201 | 0.97915 | -0.40008 | 8.4861
8 | -0.021935 | -0.0055026 | 0.021945 | 0.0055086 | 9.8314e-06 | 6.003e-06 | 0.033558 | 0.033558 | 0.033558 | 0.97266 | -0.52728 | 0.97314 | -0.51789 | 9.2193
9 | 0.021935 | 0.0055026 | -0.02193 | -0.0055 | 4.2876e-06 | 2.6181e-06 | 0.033558 | 0.033558 | 0.033558 | 0.97266 | -0.52728 | 0.97246 | -0.53138 | 9.2194
10 | -0.021945 | -0.0055086 | 0.021951 | 0.0055128 | 6.8405e-06 | 4.1766e-06 | 0.033558 | 0.033558 | 0.033558 | 0.97314 | -0.51789 | 0.97347 | -0.51135 | 9.2193
11 | 0.017715 | 0.0044436 | -0.017712 | -0.0044414 | 3.7835e-06 | 2.2511e-06 | 0.027109 | 0.027109 | 0.027109 | 0.97246 | -0.53138 | 0.97223 | -0.53587 | 7.4475
12 | 0.00087503 | 0.00021697 | -0.00087493 | -0.00021891 | 1.0163e-07 | -1.9365e-06 | 0.0013167 | 0.0013174 | 0.0013174 | 0.98824 | -0.22541 | 0.98812 | -0.22786 | 0.36193
13 | 0.0038618 | 0.00096655 | -0.0038609 | -0.00096687 | 8.7903e-07 | -3.2555e-07 | 0.0058143 | 0.0058147 | 0.0058147 | 0.98824 | -0.22541 | 0.988 | -0.23019 | 1.5974
14 | -0.0047368 | -0.0011835 | 0.0047387 | 0.0011835 | 1.8633e-06 | -6.0037e-08 | 0.0071311 | 0.0071306 | 0.0071311 | 0.98824 | -0.22541 | 0.98867 | -0.21713 | 1.9591
15 | 0.00087493 | 0.00021891 | -0.00087491 | -0.00021927 | 1.9232e-08 | -3.6614e-07 | 0.0013174 | 0.0013176 | 0.0013176 | 0.98812 | -0.22786 | 0.98809 | -0.22832 | 0.36197
16 | 0.0038609 | 0.00096687 | -0.0038605 | -0.00096704 | 4.603e-07 | -1.7026e-07 | 0.0058147 | 0.0058148 | 0.0058148 | 0.988 | -0.23019 | 0.98787 | -0.23269 | 1.5975
17 | -0.0060375 | -0.001509 | 0.0060403 | 0.0015096 | 2.8581e-06 | 6.4445e-07 | 0.0090854 | 0.009085 | 0.0090854 | 0.98867 | -0.21713 | 0.98918 | -0.20718 | 2.496
18 | 0.0019916 | 0.00049866 | -0.0019915 | -0.00049911 | 1.4191e-07 | -4.4752e-07 | 0.0029997 | 0.0029999 | 0.0029999 | 0.98787 | -0.23269 | 0.98779 | -0.23419 | 0.82416
19 | -0.022733 | -0.0057088 | 0.022749 | 0.0057186 | 1.6019e-05 | 9.8121e-06 | 0.034753 | 0.034753 | 0.034753 | 0.97347 | -0.51135 | 0.97422 | -0.49659 | 9.5477
20 | -0.0046542 | -0.0011663 | 0.0046544 | 0.0011663 | 2.4264e-07 | -2.3142e-09 | 0.0071293 | 0.0071293 | 0.0071293 | 0.9714 | -0.55232 | 0.97145 | -0.55122 | 1.9586
21 | 0.0046542 | 0.0011663 | -0.0046536 | -0.0011663 | 6.2075e-07 | -5.8273e-09 | 0.0071293 | 0.0071295 | 0.0071295 | 0.9714 | -0.55232 | 0.97126 | -0.55512 | 1.9586
22 | -0.011225 | -0.002813 | 0.011227 | 0.0028139 | 1.8726e-06 | 9.893e-07 | 0.017193 | 0.017193 | 0.017193 | 0.97145 | -0.55122 | 0.97163 | -0.54772 | 4.7234
23 | -0.021679 | -0.0054413 | 0.021682 | 0.0054435 | 3.6622e-06 | 2.2307e-06 | 0.032948 | 0.032948 | 0.032948 | 0.97915 | -0.40008 | 0.97933 | -0.39653 | 9.0517
24 | 0.01419 | 0.0035588 | -0.014186 | -0.0035566 | 3.7341e-06 | 2.1281e-06 | 0.021719 | 0.021719 | 0.021719 | 0.97223 | -0.53587 | 0.97195 | -0.54139 | 5.9668
25 | -0.011227 | -0.0028139 | 0.011228 | 0.0028149 | 1.8662e-06 | 9.8581e-07 | 0.017193 | 0.017193 | 0.017193 | 0.97163 | -0.54772 | 0.97181 | -0.54423 | 4.7234
26 | -0.011228 | -0.0028149 | 0.01123 | 0.0028157 | 1.523e-06 | 8.0444e-07 | 0.017193 | 0.017193 | 0.017193 | 0.97181 | -0.54423 | 0.97195 | -0.54139 | 4.7234
27 | -0.0017839 | -0.00044681 | 0.0017841 | 0.00044634 | 1.1481e-07 | -4.7186e-07 | 0.0026841 | 0.0026839 | 0.0026841 | 0.98895 | -0.21164 | 0.98902 | -0.21029 | 0.73739
28 | 0.0017839 | 0.00044681 | -0.0017839 | -0.00044708 | 6.4565e-08 | -2.653e-07 | 0.0026841 | 0.0026842 | 0.0026842 | 0.98895 | -0.21164 | 0.98891 | -0.2124 | 0.73742
29 | -0.0031669 | -0.00079291 | 0.0031669 | 0.00079285 | 7.407e-08 | -6.4264e-08 | 0.0047644 | 0.0047644 | 0.0047644 | 0.98902 | -0.21029 | 0.98904 | -0.2098 | 1.3089
30 | 0.0034337 | 0.00085932 | -0.0034333 | -0.00085959 | 4.2801e-07 | -2.7523e-07 | 0.0051648 | 0.005165 | 0.005165 | 0.98918 | -0.20718 | 0.98904 | -0.2098 | 1.419
31 | -0.009474 | -0.0023689 | 0.0094755 | 0.0023696 | 1.4705e-06 | 6.9316e-07 | 0.01425 | 0.01425 | 0.01425 | 0.98918 | -0.20718 | 0.98935 | -0.20391 | 3.9148
32 | -0.022749 | -0.0057186 | 0.022778 | 0.0057362 | 2.8793e-05 | 1.7635e-05 | 0.034753 | 0.034753 | 0.034753 | 0.97422 | -0.49659 | 0.97557 | -0.47012 | 9.5476
33 | -0.032152 | -0.0080857 | 0.032173 | 0.0080989 | 2.1041e-05 | 1.3175e-05 | 0.04905 | 0.04905 | 0.04905 | 0.97557 | -0.47012 | 0.97626 | -0.45643 | 13.4754
34 | 0.0093736 | 0.0023494 | -0.0093734 | -0.0023494 | 1.9246e-07 | 9.1828e-08 | 0.014297 | 0.014297 | 0.014297 | 0.97557 | -0.47012 | 0.97555 | -0.47055 | 3.9279
35 | -0.037652 | -0.0094823 | 0.037665 | 0.0094906 | 1.3042e-05 | 8.2146e-06 | 0.057359 | 0.057359 | 0.057359 | 0.97704 | -0.44116 | 0.97741 | -0.43392 | 15.758
36 | 0.037652 | 0.0094823 | -0.037626 | -0.0094659 | 2.6027e-05 | 1.6393e-05 | 0.057359 | 0.057359 | 0.057359 | 0.97704 | -0.44116 | 0.97631 | -0.45563 | 15.758
37 | 0.014038 | 0.003519 | -0.014038 | -0.0035186 | 7.8641e-07 | 4.4576e-07 | 0.021372 | 0.021372 | 0.021372 | 0.97741 | -0.43392 | 0.97735 | -0.43509 | 5.8716
38 | -0.051703 | -0.01301 | 0.05181 | 0.013077 | 0.00010674 | 6.7737e-05 | 0.078732 | 0.078731 | 0.078732 | 0.97741 | -0.43392 | 0.97962 | -0.39081 | 21.6295
39 | 0.034039 | 0.0085671 | -0.034038 | -0.0085663 | 1.3077e-06 | 8.2076e-07 | 0.051893 | 0.051893 | 0.051893 | 0.97631 | -0.45563 | 0.97626 | -0.45643 | 14.2564
40 | -0.022665 | -0.0056898 | 0.022686 | 0.0057026 | 2.1033e-05 | 1.2865e-05 | 0.034441 | 0.034441 | 0.034441 | 0.97933 | -0.39653 | 0.98032 | -0.3771 | 9.4619
41 | -0.004121 | -0.0010328 | 0.0041212 | 0.0010328 | 1.9686e-07 | -4.3138e-08 | 0.0062556 | 0.0062555 | 0.0062556 | 0.98027 | -0.3781 | 0.98032 | -0.3771 | 1.7186
42 | -0.082606 | -0.020827 | 0.082978 | 0.021064 | 0.00037194 | 0.00023724 | 0.12543 | 0.12543 | 0.12543 | 0.98032 | -0.3771 | 0.98514 | -0.28347 | 34.4593
43 | 0.055799 | 0.014091 | -0.055763 | -0.014068 | 3.6636e-05 | 2.3275e-05 | 0.084735 | 0.084735 | 0.084735 | 0.98032 | -0.3771 | 0.97962 | -0.39081 | 23.279
44 | 0.0044013 | 0.0011025 | -0.0044005 | -0.0011026 | 7.9801e-07 | -1.0222e-07 | 0.0066478 | 0.006648 | 0.006648 | 0.98514 | -0.28347 | 0.98495 | -0.28728 | 1.8264
45 | -0.08738 | -0.022166 | 0.087613 | 0.022315 | 0.00023325 | 0.00014883 | 0.13208 | 0.13208 | 0.13208 | 0.98514 | -0.28347 | 0.98801 | -0.22812 | 36.2855
46 | 0.0024161 | 0.00060526 | -0.0024159 | -0.00060549 | 1.2089e-07 | -2.3058e-07 | 0.00365 | 0.0036501 | 0.0036501 | 0.98495 | -0.28728 | 0.98489 | -0.28833 | 1.0028
47 | -0.090571 | -0.023056 | 0.09097 | 0.023311 | 0.00039947 | 0.00025492 | 0.13653 | 0.13653 | 0.13653 | 0.98801 | -0.22812 | 0.99277 | -0.13708 | 37.5092
48 | -0.10451 | -0.026709 | 0.10461 | 0.02677 | 9.6372e-05 | 6.1543e-05 | 0.15683 | 0.15683 | 0.15683 | 0.99277 | -0.13708 | 0.99377 | -0.11804 | 43.0846
49 | 0.013539 | 0.0033974 | -0.013529 | -0.0033914 | 1.0856e-05 | 6.0397e-06 | 0.020295 | 0.020295 | 0.020295 | 0.99277 | -0.13708 | 0.9919 | -0.15391 | 5.5757
50 | 0.0079377 | 0.0019899 | -0.0079358 | -0.0019891 | 1.8821e-06 | 7.7403e-07 | 0.012085 | 0.012086 | 0.012086 | 0.97735 | -0.43509 | 0.9771 | -0.44007 | 3.3202
51 | 0.0060999 | 0.0015287 | -0.0060979 | -0.0015282 | 2.0743e-06 | 5.2419e-07 | 0.0092871 | 0.0092874 | 0.0092874 | 0.97735 | -0.43509 | 0.97699 | -0.44223 | 2.5515
52 | 0.0079898 | 0.0020026 | -0.007989 | -0.0020023 | 7.7337e-07 | 3.2161e-07 | 0.012187 | 0.012187 | 0.012187 | 0.97555 | -0.47055 | 0.97544 | -0.47259 | 3.3481
53 | -0.10461 | -0.02677 | 0.10473 | 0.026852 | 0.00012843 | 8.1471e-05 | 0.15683 | 0.15683 | 0.15683 | 0.99377 | -0.11804 | 0.99511 | -0.092714 | 21.5423
54 | -0.11247 | -0.028791 | 0.11251 | 0.028816 | 3.9498e-05 | 2.4845e-05 | 0.1684 | 0.1684 | 0.1684 | 0.99511 | -0.092714 | 0.99549 | -0.085465 | 15.4211
55 | 0.013529 | 0.0033914 | -0.013525 | -0.0033892 | 3.8858e-06 | 2.1623e-06 | 0.020295 | 0.020296 | 0.020296 | 0.9919 | -0.15391 | 0.99159 | -0.15994 | 5.5757
56 | 0.0047234 | 0.0011834 | -0.0047229 | -0.0011834 | 4.5237e-07 | -2.0193e-08 | 0.0070879 | 0.007088 | 0.007088 | 0.99159 | -0.15994 | 0.99149 | -0.16195 | 1.9472
57 | -0.11251 | -0.028816 | 0.11256 | 0.028849 | 5.2212e-05 | 3.2841e-05 | 0.1684 | 0.1684 | 0.1684 | 0.99549 | -0.085465 | 0.99599 | -0.075891 | 15.421
58 | -0.11801 | -0.030214 | 0.11808 | 0.030255 | 6.4014e-05 | 4.0327e-05 | 0.17654 | 0.17654 | 0.17654 | 0.99599 | -0.075891 | 0.99658 | -0.064699 | 16.1666
59 | -0.002793 | -0.00069982 | 0.002793 | 0.00069974 | 6.523e-08 | -8.5927e-08 | 0.0041917 | 0.0041917 | 0.0041917 | 0.99146 | -0.1626 | 0.99148 | -0.16211 | 1.1516
60 | 0.002793 | 0.00069982 | -0.0027929 | -0.00069995 | 1.0045e-07 | -1.3231e-07 | 0.0041917 | 0.0041918 | 0.0041918 | 0.99146 | -0.1626 | 0.99142 | -0.16336 | 1.1516
61 | -0.002793 | -0.00069974 | 0.002793 | 0.00069971 | 2.0761e-08 | -2.7351e-08 | 0.0041917 | 0.0041917 | 0.0041917 | 0.99148 | -0.16211 | 0.99149 | -0.16195 | 1.1516
62 | 0.0079358 | 0.0019891 | -0.0079348 | -0.0019887 | 1.0813e-06 | 4.4481e-07 | 0.012086 | 0.012086 | 0.012086 | 0.9771 | -0.44007 | 0.97695 | -0.44293 | 3.3202
63 | 0.0049234 | 0.0012338 | -0.0049229 | -0.0012338 | 5.3046e-07 | 2.4512e-08 | 0.0074987 | 0.0074988 | 0.0074988 | 0.97699 | -0.44223 | 0.97688 | -0.4445 | 2.0601
64 | 0.0063286 | 0.0015861 | -0.0063274 | -0.0015858 | 1.1497e-06 | 3.2272e-07 | 0.0096392 | 0.0096393 | 0.0096393 | 0.97695 | -0.44293 | 0.97676 | -0.44674 | 2.6482
65 | -0.00169 | -0.00042354 | 0.00169 | 0.00042325 | 5.9894e-08 | -2.93e-07 | 0.0025148 | 0.0025147 | 0.0025148 | 0.99996 | -0.00074414 | 1 | 0 | 0.69088
66 | 0.4106 | 0.10527 | -0.40987 | -0.1048 | 0.00073246 | 0.00046816 | 0.61182 | 0.61182 | 0.61182 | 1 | 0 | 0.99805 | -0.036863 | 56.0274
67 | 0.28635 | 0.073118 | -0.28587 | -0.072814 | 0.0004761 | 0.00030389 | 0.4274 | 0.4274 | 0.4274 | 0.99805 | -0.036863 | 0.99624 | -0.071326 | 39.1395
68 | 0.12352 | 0.031682 | -0.12335 | -0.031577 | 0.00016653 | 0.00010504 | 0.18442 | 0.18442 | 0.18442 | 0.99805 | -0.036863 | 0.99658 | -0.064699 | 16.888
69 | 0.27734 | 0.070676 | -0.27715 | -0.070554 | 0.00019072 | 0.00012172 | 0.41466 | 0.41466 | 0.41466 | 0.99624 | -0.071326 | 0.99549 | -0.085587 | 37.9724
70 | 0.27538 | 0.070112 | -0.2747 | -0.069678 | 0.00067995 | 0.00043392 | 0.41202 | 0.41202 | 0.41202 | 0.99549 | -0.085587 | 0.99281 | -0.13693 | 37.7307
71 | 0.2747 | 0.069678 | -0.27446 | -0.06952 | 0.00024666 | 0.00015741 | 0.41202 | 0.41202 | 0.41202 | 0.99281 | -0.13693 | 0.99183 | -0.15562 | 37.7307
72 | -0.0071392 | -0.0017892 | 0.0071395 | 0.0017894 | 3.4303e-07 | 1.2132e-07 | 0.010836 | 0.010836 | 0.010836 | 0.98032 | -0.37859 | 0.98037 | -0.37758 | 2.9771
73 | -0.07026 | -0.017679 | 0.070281 | 0.017692 | 2.0945e-05 | 1.3343e-05 | 0.10667 | 0.10667 | 0.10667 | 0.98037 | -0.37758 | 0.98069 | -0.37134 | 29.3042
74 | 0.063121 | 0.015889 | -0.063058 | -0.015849 | 6.2709e-05 | 3.9904e-05 | 0.095831 | 0.095831 | 0.095831 | 0.98037 | -0.37758 | 0.9793 | -0.39839 | 26.3272
75 | 0.051396 | 0.012902 | -0.051341 | -0.012867 | 5.4985e-05 | 3.4872e-05 | 0.077115 | 0.077116 | 0.077116 | 0.99183 | -0.15562 | 0.99068 | -0.17808 | 21.1856
76 | 0.20705 | 0.0526 | -0.2066 | -0.052314 | 0.00044843 | 0.00028556 | 0.31088 | 0.31088 | 0.31088 | 0.99183 | -0.15562 | 0.98949 | -0.20072 | 28.4685
77 | 0.016015 | 0.0040187 | -0.016002 | -0.0040109 | 1.3378e-05 | 7.7651e-06 | 0.024029 | 0.024029 | 0.024029 | 0.99183 | -0.15562 | 0.99093 | -0.17316 | 6.6013
78 | 0.2066 | 0.052314 | -0.2061 | -0.052 | 0.00049248 | 0.00031449 | 0.31088 | 0.31088 | 0.31088 | 0.98949 | -0.20072 | 0.98691 | -0.25049 | 42.7028
79 | 0.10784 | 0.027371 | -0.10754 | -0.027181 | 0.00029856 | 0.0001907 | 0.16271 | 0.16271 | 0.16271 | 0.98691 | -0.25049 | 0.98393 | -0.30822 | 44.7015
80 | -0.0015446 | -0.0003871 | 0.0015446 | 0.00038692 | 3.3788e-08 | -1.8535e-07 | 0.0023437 | 0.0023436 | 0.0023437 | 0.98066 | -0.3718 | 0.98069 | -0.37134 | 0.64386
81 | -0.071826 | -0.018079 | 0.072043 | 0.018218 | 0.00021742 | 0.00013853 | 0.10901 | 0.10901 | 0.10901 | 0.98069 | -0.37134 | 0.98393 | -0.30822 | 29.948
82 | -0.007209 | -0.0018067 | 0.0072097 | 0.001807 | 7.0431e-07 | 2.5641e-07 | 0.01099 | 0.01099 | 0.01099 | 0.97604 | -0.46256 | 0.97614 | -0.46051 | 3.0194
83 | -0.0093605 | -0.0023457 | 0.0093621 | 0.0023465 | 1.6617e-06 | 7.9136e-07 | 0.014269 | 0.014269 | 0.014269 | 0.97614 | -0.46051 | 0.97633 | -0.45679 | 3.92
84 | 0.0021508 | 0.00053873 | -0.0021507 | -0.000539 | 1.1296e-07 | -2.78e-07 | 0.0032785 | 0.0032786 | 0.0032786 | 0.97614 | -0.46051 | 0.97608 | -0.46161 | 0.90072
85 | -0.012071 | -0.0030255 | 0.012073 | 0.0030262 | 1.4195e-06 | 7.6862e-07 | 0.018398 | 0.018398 | 0.018398 | 0.97633 | -0.45679 | 0.97645 | -0.45432 | 5.0543
86 | -0.027608 | -0.0069222 | 0.027628 | 0.0069341 | 1.9106e-05 | 1.1868e-05 | 0.042073 | 0.042073 | 0.042073 | 0.97645 | -0.45432 | 0.97719 | -0.43981 | 11.5586
87 | 0.015536 | 0.003896 | -0.015528 | -0.0038911 | 8.3184e-06 | 4.829e-06 | 0.023676 | 0.023676 | 0.023676 | 0.97645 | -0.45432 | 0.97588 | -0.46556 | 6.5044
88 | 0.0015721 | 0.00039348 | -0.001572 | -0.00039376 | 5.2711e-08 | -2.7652e-07 | 0.002388 | 0.0023881 | 0.0023881 | 0.97953 | -0.39405 | 0.97949 | -0.39475 | 0.65608
89 | 0.030531 | 0.0076658 | -0.030497 | -0.0076445 | 3.3983e-05 | 2.122e-05 | 0.046385 | 0.046385 | 0.046385 | 0.97953 | -0.39405 | 0.97834 | -0.41741 | 12.7432
90 | -0.032103 | -0.0080592 | 0.032113 | 0.0080651 | 9.3701e-06 | 5.8646e-06 | 0.048773 | 0.048773 | 0.048773 | 0.97953 | -0.39405 | 0.97984 | -0.38793 | 13.3992
91 | 0.001572 | 0.00039376 | -0.001572 | -0.00039398 | 4.2452e-08 | -2.2266e-07 | 0.0023881 | 0.0023882 | 0.0023882 | 0.97949 | -0.39475 | 0.97947 | -0.39532 | 0.6561
92 | 0.023333 | 0.0058489 | -0.023328 | -0.0058461 | 4.6861e-06 | 2.8746e-06 | 0.035488 | 0.035488 | 0.035488 | 0.97834 | -0.41741 | 0.97813 | -0.42162 | 9.7496
93 | -0.034627 | -0.0086949 | 0.03466 | 0.0087159 | 3.3465e-05 | 2.1011e-05 | 0.052591 | 0.052591 | 0.052591 | 0.97984 | -0.38793 | 0.98088 | -0.36769 | 14.4481
94 | 0.0025141 | 0.00062983 | -0.002514 | -0.00063006 | 1.3951e-07 | -2.3216e-07 | 0.0038179 | 0.003818 | 0.003818 | 0.97984 | -0.38793 | 0.97978 | -0.38909 | 1.0489
95 | 0.035494 | 0.0089631 | -0.035456 | -0.008939 | 3.8242e-05 | 2.4027e-05 | 0.053703 | 0.053703 | 0.053703 | 0.98393 | -0.30822 | 0.98277 | -0.33073 | 14.7536
96 | 0.035456 | 0.008939 | -0.035437 | -0.0089269 | 1.937e-05 | 1.217e-05 | 0.053703 | 0.053703 | 0.053703 | 0.98277 | -0.33073 | 0.98219 | -0.34215 | 14.7536
97 | -0.038801 | -0.0097537 | 0.038817 | 0.0097634 | 1.5394e-05 | 9.704e-06 | 0.058993 | 0.058993 | 0.058993 | 0.97888 | -0.40669 | 0.9793 | -0.39839 | 16.2069
98 | 0.035518 | 0.0089309 | -0.035506 | -0.0089237 | 1.1378e-05 | 7.1511e-06 | 0.054001 | 0.054001 | 0.054001 | 0.97888 | -0.40669 | 0.97854 | -0.4134 | 14.8356
99 | 0.0032838 | 0.00082283 | -0.0032838 | -0.00082286 | 3.9042e-08 | -2.7538e-08 | 0.0049917 | 0.0049917 | 0.0049917 | 0.97888 | -0.40669 | 0.97887 | -0.40694 | 1.3714
100 | 0.024241 | 0.006086 | -0.024229 | -0.0060785 | 1.2293e-05 | 7.5637e-06 | 0.036838 | 0.036838 | 0.036838 | 0.9793 | -0.39839 | 0.97876 | -0.40902 | 10.1203
101 | 0.033176 | 0.0083398 | -0.033156 | -0.0083268 | 2.0713e-05 | 1.2984e-05 | 0.050459 | 0.050459 | 0.050459 | 0.97854 | -0.4134 | 0.97787 | -0.42649 | 13.8623
102 | 0.0026782 | 0.00067109 | -0.0026781 | -0.0006712 | 8.0432e-08 | -1.1119e-07 | 0.0040712 | 0.0040712 | 0.0040712 | 0.97887 | -0.40694 | 0.97884 | -0.40757 | 1.1185
103 | 0.022527 | 0.0056519 | -0.022522 | -0.0056489 | 4.9285e-06 | 3.0135e-06 | 0.03425 | 0.03425 | 0.03425 | 0.97876 | -0.40902 | 0.97853 | -0.41361 | 9.4094
104 | 0.035437 | 0.0089269 | -0.035393 | -0.0088997 | 4.3227e-05 | 2.716e-05 | 0.053703 | 0.053703 | 0.053703 | 0.98219 | -0.34215 | 0.98088 | -0.36769 | 14.7536
105 | -0.030695 | -0.0077029 | 0.030715 | 0.007715 | 1.9511e-05 | 1.2189e-05 | 0.046744 | 0.046744 | 0.046744 | 0.97719 | -0.43981 | 0.97787 | -0.42649 | 12.8419
106 | 0.0082158 | 0.0020587 | -0.0082157 | -0.0020586 | 1.352e-07 | 5.7823e-08 | 0.012527 | 0.012527 | 0.012527 | 0.97588 | -0.46556 | 0.97587 | -0.4659 | 3.4416
107 | 0.0052828 | 0.0013235 | -0.0052792 | -0.0013231 | 3.5788e-06 | 4.3729e-07 | 0.0080366 | 0.0080372 | 0.0080372 | 0.97813 | -0.42162 | 0.9774 | -0.43585 | 2.208
108 | 0.012167 | 0.0030537 | -0.012164 | -0.0030517 | 3.706e-06 | 2.0094e-06 | 0.018504 | 0.018504 | 0.018504 | 0.97853 | -0.41361 | 0.9782 | -0.42 | 5.0836
109 | 0.0013695 | 0.00034277 | -0.0013694 | -0.00034318 | 5.7893e-08 | -4.0528e-07 | 0.0020881 | 0.0020882 | 0.0020882 | 0.97587 | -0.4659 | 0.97582 | -0.46679 | 0.57369
110 | 0.0013694 | 0.00034318 | -0.0013694 | -0.00034321 | 5.084e-09 | -3.5585e-08 | 0.0020882 | 0.0020882 | 0.0020882 | 0.97582 | -0.46679 | 0.97582 | -0.46687 | 0.57369
111 | 0.011028 | 0.002767 | -0.011016 | -0.0027609 | 1.1866e-05 | 6.1844e-06 | 0.016776 | 0.016777 | 0.016777 | 0.9782 | -0.42 | 0.97705 | -0.44259 | 4.609
112 | 0.010195 | 0.0025517 | -0.010187 | -0.0025481 | 7.4727e-06 | 3.6914e-06 | 0.01532 | 0.015321 | 0.015321 | 0.99014 | -0.1885 | 0.98935 | -0.20391 | 4.2089
113 | -0.01599 | -0.0040041 | 0.016002 | 0.0040109 | 1.1691e-05 | 6.7873e-06 | 0.024029 | 0.024029 | 0.024029 | 0.99014 | -0.1885 | 0.99093 | -0.17316 | 6.6014
114 | 0.0018721 | 0.00046892 | -0.0018721 | -0.00046895 | 9.2616e-09 | -3.4292e-08 | 0.0028119 | 0.0028119 | 0.0028119 | 0.99068 | -0.17808 | 0.99067 | -0.17818 | 0.77249
115 | 0.0018721 | 0.00046895 | -0.001872 | -0.00046918 | 6.1738e-08 | -2.2857e-07 | 0.0028119 | 0.002812 | 0.002812 | 0.99067 | -0.17818 | 0.99063 | -0.17887 | 0.77252
116 | 0.0062378 | 0.0015634 | -0.0062368 | -0.0015631 | 1.0189e-06 | 2.776e-07 | 0.0095156 | 0.0095157 | 0.0095157 | 0.97544 | -0.47259 | 0.97527 | -0.47601 | 2.6142

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41958 | 0.10711

## res_load
| p_mw | q_mvar
0 | 0.0059107 | 0.0014814
1 | 0.0026413 | 0.00066197
2 | 0.0057861 | 0.0014501
3 | 0.0037561 | 0.00094137
4 | 0.0022044 | 0.00055247
5 | 0.0042151 | 0.0010564
6 | 0.0012988 | 0.0003255
7 | 0.0018689 | 0.00046839
8 | 0.00078193 | 0.00019597
9 | 0.0065703 | 0.0016467
10 | 0.0046536 | 0.0011663
11 | 0.001355 | 0.00033959
12 | 0.0035216 | 0.00088259
13 | 0.00087491 | 0.00021927
14 | 0.0013828 | 0.00034657
15 | 0.0017839 | 0.00044708
16 | 0.0029563 | 0.00074091
17 | 0.0019915 | 0.00049911
18 | 0.0035863 | 0.00089881
19 | 0.00098255 | 0.00024625
20 | 0.004121 | 0.0010328
21 | 0.0039527 | 0.00099063
22 | 0.0019844 | 0.00049735
23 | 0.0029576 | 0.00074124
24 | 0.0024159 | 0.00060549
25 | 0.0018652 | 0.00046747
26 | 0.0013837 | 0.00034678
27 | 0.0077377 | 0.0019392
28 | 0.0088014 | 0.0022058
29 | 0.0054495 | 0.0013658
30 | 0.0027929 | 0.00069995
31 | 0.0011744 | 0.00029434
32 | 0.0016062 | 0.00040255
33 | 0.0049229 | 0.0012338
34 | 0.0063274 | 0.0015858
35 | 0.00169 | 0.00042354
36 | 0.0056379 | 0.001413
37 | 0.0085327 | 0.0021385
38 | 0.0052763 | 0.0013224
39 | 0.0017661 | 0.00044262
40 | 0.0019299 | 0.00048367
41 | 0.0071392 | 0.0017892
42 | 0.098268 | 0.024628
43 | 0.0015446 | 0.0003871
44 | 0.007209 | 0.0018067
45 | 0.002709 | 0.00067895
46 | 0.0021507 | 0.000539
47 | 0.0071645 | 0.0017956
48 | 0.001572 | 0.00039398
49 | 0.0023298 | 0.0005839
50 | 0.00060557 | 0.00015177
51 | 0.001702 | 0.00042657
52 | 0.00073328 | 0.00018378
53 | 0.0030675 | 0.00076879
54 | 0.0073117 | 0.0018325
55 | 0.018045 | 0.0045225
56 | 0.002514 | 0.00063006
57 | 0.0024411 | 0.00061179
58 | 0.0026781 | 0.0006712
59 | 0.010355 | 0.0025952
60 | 0.0068462 | 0.0017158
61 | 0.0013694 | 0.00034321
62 | 0.0011359 | 0.00028468
63 | 0.011016 | 0.0027609
64 | 0.005795 | 0.0014524
65 | 0.00071197 | 0.00017844
66 | 0.00026632 | 6.6747e-05
67 | 0.049469 | 0.012398
68 | 0.0017512 | 0.0004389
69 | 0.0062368 | 0.0015631
70 | 0.001872 | 0.00046918
71 | 0.0052792 | 0.0013231

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1