## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_160-11_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_160-11_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_160-11_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_160-11_0_6_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_160-11_0_6_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_160-11_0_6_node_132 | 0.4 | n |  | TRUE
6 | bus_LV_160-11_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_160-11_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_160-11_0_6_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_160-11_0_6_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_160-11_0_6_node_79 | 0.4 | n |  | TRUE
11 | bus_LV_160-11_0_6_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_160-11_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_160-11_0_6_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_160-11_0_6_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_160-11_0_6_node_62 | 0.4 | n |  | TRUE
16 | bus_LV_160-11_0_6_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_160-11_0_6_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_160-11_0_6_node_82 | 0.4 | n |  | TRUE
19 | bus_LV_160-11_0_6_node_92 | 0.4 | n |  | TRUE
20 | bus_LV_160-11_0_6_node_64 | 0.4 | n |  | TRUE
21 | bus_LV_160-11_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_160-11_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_160-11_0_6_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_160-11_0_6_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_160-11_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_160-11_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_160-11_0_6_node_131 | 0.4 | n |  | TRUE
28 | bus_LV_160-11_0_6_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_160-11_0_6_node_99 | 0.4 | n |  | TRUE
30 | bus_LV_160-11_0_6_node_109 | 0.4 | n |  | TRUE
31 | bus_LV_160-11_0_6_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_160-11_0_6_node_106 | 0.4 | n |  | TRUE
33 | bus_LV_160-11_0_6_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_160-11_0_6_node_76 | 0.4 | n |  | TRUE
35 | bus_LV_160-11_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_160-11_0_6_node_112 | 0.4 | n |  | TRUE
37 | bus_LV_160-11_0_6_node_133 | 0.4 | n |  | TRUE
38 | bus_LV_160-11_0_6_node_110 | 0.4 | n |  | TRUE
39 | bus_LV_160-11_0_6_node_67 | 0.4 | n |  | TRUE
40 | bus_LV_160-11_0_6_node_59 | 0.4 | n |  | TRUE
41 | bus_LV_160-11_0_6_node_89 | 0.4 | n |  | TRUE
42 | bus_LV_160-11_0_6_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_160-11_0_6_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_160-11_0_6_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_160-11_0_6_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_160-11_0_6_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_160-11_0_6_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_160-11_0_6_node_107 | 0.4 | n |  | TRUE
49 | bus_LV_160-11_0_6_node_125 | 0.4 | n |  | TRUE
50 | bus_LV_160-11_0_6_node_122 | 0.4 | n |  | TRUE
51 | bus_LV_160-11_0_6_node_130 | 0.4 | n |  | TRUE
52 | bus_LV_160-11_0_6_node_97 | 0.4 | n |  | TRUE
53 | bus_LV_160-11_0_6_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_160-11_0_6_node_105 | 0.4 | n |  | TRUE
55 | bus_LV_160-11_0_6_node_74 | 0.4 | n |  | TRUE
56 | bus_LV_160-11_0_6_node_75 | 0.4 | n |  | TRUE
57 | bus_LV_160-11_0_6_node_25 | 0.4 | n |  | TRUE
58 | bus_LV_160-11_0_6_node_26 | 0.4 | n |  | TRUE
59 | bus_LV_160-11_0_6_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_160-11_0_6_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_160-11_0_6_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_160-11_0_6_node_29 | 0.4 | n |  | TRUE
63 | bus_LV_160-11_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_160-11_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_160-11_0_6_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_160-11_0_6_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_160-11_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_160-11_0_6_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_160-11_0_6_node_34 | 0.4 | n |  | TRUE
70 | bus_LV_160-11_0_6_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_160-11_0_6_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_160-11_0_6_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_160-11_0_6_node_35 | 0.4 | n |  | TRUE
74 | bus_LV_160-11_0_6_node_36 | 0.4 | n |  | TRUE
75 | bus_LV_160-11_0_6_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_160-11_0_6_node_37 | 0.4 | n |  | TRUE
77 | bus_LV_160-11_0_6_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_160-11_0_6_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_160-11_0_6_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_160-11_0_6_node_55 | 0.4 | n |  | TRUE
81 | bus_LV_160-11_0_6_node_39 | 0.4 | n |  | TRUE
82 | bus_LV_160-11_0_6_node_40 | 0.4 | n |  | TRUE
83 | bus_LV_160-11_0_6_node_41 | 0.4 | n |  | TRUE
84 | bus_LV_160-11_0_6_node_42 | 0.4 | n |  | TRUE
85 | bus_LV_160-11_0_6_node_43 | 0.4 | n |  | TRUE
86 | bus_LV_160-11_0_6_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_160-11_0_6_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_160-11_0_6_node_48 | 0.4 | n |  | TRUE
89 | bus_LV_160-11_0_6_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_160-11_0_6_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_160-11_0_6_node_49 | 0.4 | n |  | TRUE
92 | bus_LV_160-11_0_6_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_160-11_0_6_node_50 | 0.4 | n |  | TRUE
94 | bus_LV_160-11_0_6_node_124 | 0.4 | n |  | TRUE
95 | bus_LV_160-11_0_6_node_126 | 0.4 | n |  | TRUE
96 | bus_LV_160-11_0_6_node_123 | 0.4 | n |  | TRUE
97 | bus_LV_160-11_0_6_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_160-11_0_6_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_160-11_0_6_node_72 | 0.4 | n |  | TRUE
100 | bus_LV_160-11_0_6_node_70 | 0.4 | n |  | TRUE
101 | bus_LV_160-11_0_6_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_160-11_0_6_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_160-11_0_6_node_116 | 0.4 | n |  | TRUE
104 | bus_LV_160-11_0_6_node_118 | 0.4 | n |  | TRUE
105 | bus_LV_160-11_0_6_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_160-11_0_6_node_73 | 0.4 | n |  | TRUE
107 | bus_LV_160-11_0_6_node_81 | 0.4 | n |  | TRUE
108 | bus_LV_160-11_0_6_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_160-11_0_6_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_160-11_0_6_node_115 | 0.4 | n |  | TRUE
111 | bus_LV_160-11_0_6_node_119 | 0.4 | n |  | TRUE
112 | bus_LV_160-11_0_6_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_160-11_0_6_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_160-11_0_6_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_160-11_0_6_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_160-11_0_6_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_160-11_0_6_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_160-11_0_6_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_160-11_0_6_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_160-11_0_6_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_160-11_0_6_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_160-11_0_6_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_160-11_0_6_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_160-11_0_6_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_160-11_0_6_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_160-11_0_6_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_160-11_0_6_node_128 | 0.4 | n |  | TRUE
128 | bus_MV_364_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_160-11_0_6_load_0 | 0 | 0.0032269 | 0.00080875 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_160-11_0_6_load_2 | 2 | 0.0035144 | 0.00088079 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_160-11_0_6_load_132 | 5 | 0.010697 | 0.002681 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_160-11_0_6_load_20 | 8 | 0.010109 | 0.0025335 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_160-11_0_6_load_79 | 10 | 0.0097096 | 0.0024335 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_160-11_0_6_load_66 | 11 | 0.0060189 | 0.0015085 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_160-11_0_6_load_62 | 15 | 0.0070533 | 0.0017677 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_160-11_0_6_load_82 | 18 | 0.0060078 | 0.0015057 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_160-11_0_6_load_92 | 19 | 0.0048698 | 0.0012205 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_160-11_0_6_load_64 | 20 | 0.0054854 | 0.0013748 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_160-11_0_6_load_21 | 21 | 0.0063234 | 0.0015848 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_160-11_0_6_load_108 | 24 | 0.0094842 | 0.002377 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_160-11_0_6_load_131 | 27 | 0.00066358 | 0.00016631 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_160-11_0_6_load_109 | 30 | 0.0067126 | 0.0016823 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_160-11_0_6_load_106 | 32 | 0.0037796 | 0.00094727 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_160-11_0_6_load_104 | 33 | 0.0036195 | 0.00090712 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_160-11_0_6_load_76 | 34 | 0.0020993 | 0.00052614 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_160-11_0_6_load_112 | 36 | 0.010385 | 0.0026028 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_160-11_0_6_load_133 | 37 | 0.010521 | 0.0026368 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_160-11_0_6_load_110 | 38 | 0.0064476 | 0.0016159 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_160-11_0_6_load_67 | 39 | 0.0029072 | 0.00072862 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_160-11_0_6_load_59 | 40 | 0.0013219 | 0.0003313 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_160-11_0_6_load_89 | 41 | 0.0026795 | 0.00067154 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_160-11_0_6_load_86 | 42 | 0.0030567 | 0.00076607 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_160-11_0_6_load_63 | 43 | 0.0073408 | 0.0018398 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_160-11_0_6_load_80 | 44 | 0.0077804 | 0.00195 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_160-11_0_6_load_91 | 45 | 0.016269 | 0.0040774 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_160-11_0_6_load_24 | 46 | 0.0087405 | 0.0021906 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_160-11_0_6_load_100 | 47 | 0.0064069 | 0.0016057 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_160-11_0_6_load_122 | 50 | 0.0097514 | 0.0024439 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_160-11_0_6_load_130 | 51 | 0.0012462 | 0.00031233 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_160-11_0_6_load_97 | 52 | 0.013215 | 0.0033119 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_160-11_0_6_load_105 | 54 | 0.011732 | 0.0029404 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_160-11_0_6_load_74 | 55 | 0.002252 | 0.00056441 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_160-11_0_6_load_75 | 56 | 0.0037279 | 0.00093429 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_160-11_0_6_load_25 | 57 | 0.0070914 | 0.0017773 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_160-11_0_6_load_26 | 58 | 0.003683 | 0.00092303 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_160-11_0_6_load_27 | 59 | 0.0071428 | 0.0017902 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_160-11_0_6_load_28 | 60 | 0.0018505 | 0.00046379 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_160-11_0_6_load_30 | 61 | 0.0040331 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_160-11_0_6_load_47 | 64 | 0.0030378 | 0.00076136 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_160-11_0_6_load_45 | 65 | 0.0018203 | 0.0004562 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_160-11_0_6_load_54 | 66 | 0.0025566 | 0.00064073 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_160-11_0_6_load_53 | 67 | 0.0055159 | 0.0013824 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_160-11_0_6_load_34 | 69 | 0.0023388 | 0.00058615 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_160-11_0_6_load_31 | 70 | 0.001349 | 0.00033808 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_160-11_0_6_load_32 | 71 | 0.0024305 | 0.00060915 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_160-11_0_6_load_35 | 73 | 0.0024383 | 0.00061109 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_160-11_0_6_load_36 | 74 | 0.0014677 | 0.00036783 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_160-11_0_6_load_51 | 75 | 0.0025382 | 0.00063613 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_160-11_0_6_load_60 | 78 | 0.0034007 | 0.0008523 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_160-11_0_6_load_55 | 80 | 0.0021712 | 0.00054415 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_160-11_0_6_load_39 | 81 | 0.009358 | 0.0023453 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_160-11_0_6_load_40 | 82 | 0.014859 | 0.0037239 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_160-11_0_6_load_42 | 84 | 0.0028727 | 0.00071996 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_160-11_0_6_load_43 | 85 | 0.003609 | 0.00090449 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_160-11_0_6_load_44 | 86 | 0.0024576 | 0.00061594 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_160-11_0_6_load_77 | 87 | 0.00076462 | 0.00019163 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_160-11_0_6_load_48 | 88 | 0.0042607 | 0.0010678 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_160-11_0_6_load_68 | 89 | 0.014492 | 0.003632 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_160-11_0_6_load_78 | 90 | 0.0016192 | 0.0004058 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_160-11_0_6_load_49 | 91 | 0.0028251 | 0.00070804 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_160-11_0_6_load_69 | 92 | 0.010151 | 0.0025441 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_160-11_0_6_load_50 | 93 | 0.0071924 | 0.0018026 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_160-11_0_6_load_126 | 95 | 0.0068904 | 0.0017269 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_160-11_0_6_load_123 | 96 | 0.00064196 | 0.00016089 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_160-11_0_6_load_87 | 97 | 0.0074094 | 0.001857 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_160-11_0_6_load_71 | 98 | 0.0049714 | 0.001246 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_160-11_0_6_load_72 | 99 | 0.00098166 | 0.00024603 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_160-11_0_6_load_85 | 102 | 0.0085402 | 0.0021404 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_160-11_0_6_load_116 | 103 | 0.0037312 | 0.00093513 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_160-11_0_6_load_118 | 104 | 0.0074495 | 0.001867 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_160-11_0_6_load_84 | 105 | 0.0085748 | 0.002149 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_160-11_0_6_load_73 | 106 | 0.00085134 | 0.00021337 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_160-11_0_6_load_81 | 107 | 0.022807 | 0.0057159 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_160-11_0_6_load_83 | 108 | 0.0054328 | 0.0013616 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_160-11_0_6_load_88 | 109 | 0.0020647 | 0.00051746 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_160-11_0_6_load_115 | 110 | 0.013512 | 0.0033865 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_160-11_0_6_load_119 | 111 | 0.0034969 | 0.00087639 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_160-11_0_6_load_93 | 112 | 0.046298 | 0.011603 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_160-11_0_6_load_94 | 113 | 0.0022094 | 0.00055374 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_160-11_0_6_load_95 | 114 | 0.0027369 | 0.00068593 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_160-11_0_6_load_96 | 115 | 0.014304 | 0.003585 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_160-11_0_6_load_101 | 116 | 0.0061545 | 0.0015425 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_160-11_0_6_load_102 | 117 | 0.011408 | 0.0028591 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_160-11_0_6_load_98 | 118 | 0.0048871 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_160-11_0_6_load_114 | 120 | 0.0059369 | 0.0014879 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_160-11_0_6_load_121 | 122 | 0.0076663 | 0.0019214 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_160-11_0_6_load_117 | 123 | 0.0072123 | 0.0018076 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_160-11_0_6_load_129 | 124 | 0.0015769 | 0.00039521 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_160-11_0_6_load_120 | 125 | 0.0023446 | 0.0005876 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_160-11_0_6_load_127 | 126 | 0.0034406 | 0.0008623 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_160-11_0_6_load_128 | 127 | 0.0018292 | 0.00045843 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_160-11_0_6_line_0 |  | 0 | 1 | 0.042871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_160-11_0_6_line_1 |  | 0 | 2 | 9.0275e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_160-11_0_6_line_2 |  | 1 | 3 | 0.085087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_160-11_0_6_line_3 |  | 3 | 11 | 0.034589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_160-11_0_6_line_4 |  | 4 | 5 | 0.015327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_160-11_0_6_line_5 |  | 4 | 6 | 0.019071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_160-11_0_6_line_6 |  | 6 | 7 | 0.0092297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_160-11_0_6_line_7 |  | 6 | 8 | 0.017234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_160-11_0_6_line_8 |  | 7 | 9 | 0.035395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_160-11_0_6_line_9 |  | 7 | 10 | 0.0083655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_160-11_0_6_line_10 |  | 8 | 17 | 0.036818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_160-11_0_6_line_11 |  | 9 | 20 | 0.041764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_160-11_0_6_line_12 |  | 11 | 39 | 0.037515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_160-11_0_6_line_13 |  | 11 | 40 | 0.030006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_160-11_0_6_line_14 |  | 12 | 13 | 0.024823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_160-11_0_6_line_15 |  | 12 | 14 | 0.035738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_160-11_0_6_line_16 |  | 12 | 15 | 0.023343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_160-11_0_6_line_17 |  | 13 | 41 | 0.027063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_160-11_0_6_line_18 |  | 13 | 42 | 0.011644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_160-11_0_6_line_19 |  | 14 | 30 | 0.012779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_160-11_0_6_line_20 |  | 15 | 43 | 0.030895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_160-11_0_6_line_21 |  | 16 | 17 | 0.029198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_160-11_0_6_line_22 |  | 16 | 18 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_160-11_0_6_line_23 |  | 16 | 19 | 0.042263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_160-11_0_6_line_24 |  | 17 | 21 | 0.0018472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_160-11_0_6_line_25 |  | 18 | 44 | 0.017395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_160-11_0_6_line_26 |  | 19 | 45 | 0.026544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_160-11_0_6_line_27 |  | 20 | 43 | 0.0091603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_160-11_0_6_line_28 |  | 21 | 46 | 0.026491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_160-11_0_6_line_29 |  | 22 | 23 | 0.087295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_160-11_0_6_line_30 |  | 22 | 24 | 0.013918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_160-11_0_6_line_31 |  | 23 | 34 | 0.014779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_160-11_0_6_line_32 |  | 24 | 47 | 0.027139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_160-11_0_6_line_33 |  | 25 | 26 | 0.13527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_160-11_0_6_line_34 |  | 25 | 27 | 0.046963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_160-11_0_6_line_35 |  | 26 | 38 | 0.013836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_160-11_0_6_line_36 |  | 27 | 51 | 0.028426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_160-11_0_6_line_37 |  | 28 | 29 | 0.030126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_160-11_0_6_line_38 |  | 28 | 30 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_160-11_0_6_line_39 |  | 29 | 47 | 0.019296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_160-11_0_6_line_40 |  | 29 | 52 | 0.024439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_160-11_0_6_line_41 |  | 31 | 32 | 0.023045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_160-11_0_6_line_42 |  | 31 | 33 | 0.014183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_160-11_0_6_line_43 |  | 32 | 53 | 0.021782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_160-11_0_6_line_44 |  | 33 | 54 | 0.047841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_160-11_0_6_line_45 |  | 34 | 56 | 0.00475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_160-11_0_6_line_46 |  | 35 | 36 | 0.034918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_160-11_0_6_line_47 |  | 35 | 37 | 0.030433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_160-11_0_6_line_48 |  | 36 | 53 | 0.033182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_160-11_0_6_line_49 |  | 38 | 53 | 0.021864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_160-11_0_6_line_50 |  | 39 | 98 | 0.016248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_160-11_0_6_line_51 |  | 40 | 68 | 0.054179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_160-11_0_6_line_52 |  | 42 | 97 | 0.029422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_160-11_0_6_line_53 |  | 44 | 107 | 0.029142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_160-11_0_6_line_54 |  | 45 | 112 | 0.00081303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_160-11_0_6_line_55 |  | 48 | 49 | 0.03689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_160-11_0_6_line_56 |  | 48 | 50 | 0.0054057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_160-11_0_6_line_57 |  | 49 | 124 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_160-11_0_6_line_58 |  | 50 | 96 | 0.019413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_160-11_0_6_line_59 |  | 51 | 120 | 0.040722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_160-11_0_6_line_60 |  | 52 | 118 | 0.042224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_160-11_0_6_line_61 |  | 55 | 56 | 0.044329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_160-11_0_6_line_62 |  | 57 | 58 | 0.011763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_160-11_0_6_line_63 |  | 57 | 59 | 0.020404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_160-11_0_6_line_64 |  | 58 | 60 | 0.025355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_160-11_0_6_line_65 |  | 60 | 61 | 0.00091901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_160-11_0_6_line_66 |  | 61 | 65 | 0.025488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_160-11_0_6_line_67 |  | 62 | 63 | 0.055149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_160-11_0_6_line_68 |  | 62 | 64 | 0.027965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_160-11_0_6_line_69 |  | 63 | 66 | 0.0097123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_160-11_0_6_line_70 |  | 63 | 67 | 0.095018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_160-11_0_6_line_71 |  | 64 | 68 | 0.0050491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_160-11_0_6_line_72 |  | 65 | 69 | 0.0097145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_160-11_0_6_line_73 |  | 67 | 79 | 0.088452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_160-11_0_6_line_74 |  | 69 | 71 | 0.0011852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_160-11_0_6_line_75 |  | 70 | 71 | 0.015958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_160-11_0_6_line_76 |  | 70 | 72 | 0.024126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_160-11_0_6_line_77 |  | 72 | 73 | 0.014984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_160-11_0_6_line_78 |  | 72 | 74 | 0.05378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_160-11_0_6_line_79 |  | 73 | 75 | 0.01217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_160-11_0_6_line_80 |  | 74 | 76 | 0.023817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_160-11_0_6_line_81 |  | 76 | 77 | 0.010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_160-11_0_6_line_82 |  | 77 | 78 | 0.020011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_160-11_0_6_line_83 |  | 78 | 93 | 0.0063966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_160-11_0_6_line_84 |  | 79 | 80 | 0.098411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_160-11_0_6_line_85 |  | 81 | 82 | 0.020014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_160-11_0_6_line_86 |  | 81 | 83 | 0.011461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_160-11_0_6_line_87 |  | 82 | 84 | 0.023597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_160-11_0_6_line_88 |  | 83 | 85 | 0.042069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_160-11_0_6_line_89 |  | 83 | 86 | 0.017487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_160-11_0_6_line_90 |  | 84 | 87 | 0.0075609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_160-11_0_6_line_91 |  | 85 | 88 | 0.0067089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_160-11_0_6_line_92 |  | 86 | 89 | 0.029227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_160-11_0_6_line_93 |  | 87 | 90 | 0.015617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_160-11_0_6_line_94 |  | 88 | 91 | 0.016231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_160-11_0_6_line_95 |  | 89 | 92 | 0.0073093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_160-11_0_6_line_96 |  | 90 | 106 | 0.020561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_160-11_0_6_line_97 |  | 91 | 93 | 0.021328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_160-11_0_6_line_98 |  | 92 | 100 | 0.021641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_160-11_0_6_line_99 |  | 94 | 95 | 0.02791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_160-11_0_6_line_100 |  | 94 | 96 | 0.0067913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_160-11_0_6_line_101 |  | 95 | 126 | 0.034728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_160-11_0_6_line_102 |  | 97 | 109 | 0.028658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_160-11_0_6_line_103 |  | 98 | 99 | 0.0020334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_160-11_0_6_line_104 |  | 99 | 106 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_160-11_0_6_line_105 |  | 100 | 101 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_160-11_0_6_line_106 |  | 100 | 102 | 0.025393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_160-11_0_6_line_107 |  | 101 | 103 | 0.014972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_160-11_0_6_line_108 |  | 101 | 104 | 0.016867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_160-11_0_6_line_109 |  | 102 | 105 | 0.02877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_160-11_0_6_line_110 |  | 103 | 110 | 0.031162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_160-11_0_6_line_111 |  | 104 | 111 | 0.028753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_160-11_0_6_line_112 |  | 105 | 108 | 0.040335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_160-11_0_6_line_113 |  | 107 | 108 | 0.0059009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_160-11_0_6_line_114 |  | 110 | 123 | 0.003767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_160-11_0_6_line_115 |  | 111 | 125 | 0.0046883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_160-11_0_6_line_116 |  | 112 | 113 | 0.030307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_160-11_0_6_line_117 |  | 113 | 114 | 0.034619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_160-11_0_6_line_118 |  | 114 | 115 | 0.0067878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_160-11_0_6_line_119 |  | 115 | 116 | 0.028451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_160-11_0_6_line_120 |  | 116 | 117 | 0.027379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_160-11_0_6_line_121 |  | 117 | 119 | 0.0077084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_160-11_0_6_line_122 |  | 119 | 120 | 0.023523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_160-11_0_6_line_123 |  | 121 | 122 | 0.034652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_160-11_0_6_line_124 |  | 121 | 123 | 0.02595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_160-11_0_6_line_125 |  | 124 | 127 | 0.02959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_160-11_0_6_line_126 |  | 125 | 126 | 0.0098459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_160-11_0_6_trafo_84 | 0.63 MVA 20/0.4 kV | 128 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2689770.1078 | 1242936.1311 | 2689798.2899 | 1242903.8246
1 | 2689798.2899 | 1242903.8246 | 2689798.3492 | 1242903.7566
2 | 2689770.1078 | 1242936.1311 | 2689778.7563 | 1242942.6 | 2689798.8113 | 1242957.6145 | 2689837.6782 | 1242987.8362
3 | 2689837.6782 | 1242987.8362 | 2689864.7737 | 1242966.2416
4 | 2689761.0772 | 1242863.007 | 2689749.3664 | 1242853.0781
5 | 2689749.3664 | 1242853.0781 | 2689750.4939 | 1242851.5051 | 2689750.3321 | 1242848.2114 | 2689749.6258 | 1242841.9294 | 2689750.0189 | 1242837.9324 | 2689751.5558 | 1242834.7866
6 | 2689743.4272 | 1242830.416 | 2689747.1831 | 1242832.4966 | 2689751.5558 | 1242834.7866
7 | 2689751.5558 | 1242834.7866 | 2689752.0237 | 1242833.8374 | 2689759.16 | 1242819.3212
8 | 2689756.7889 | 1242797.705 | 2689752.7138 | 1242809.7189 | 2689746.4887 | 1242824.936 | 2689743.4272 | 1242830.416
9 | 2689743.4272 | 1242830.416 | 2689739.0924 | 1242837.5708
10 | 2689779.7475 | 1242791.7367 | 2689773.7213 | 1242793.3023 | 2689768.9861 | 1242796.4886 | 2689764.9136 | 1242804.8331 | 2689760.3852 | 1242816.8291 | 2689759.16 | 1242819.3212
11 | 2689756.7889 | 1242797.705 | 2689755.1073 | 1242797.4238 | 2689742.3963 | 1242801.1232 | 2689733.7036 | 1242801.0584 | 2689727.298 | 1242798.7265 | 2689725.417 | 1242795.1398 | 2689726.4588 | 1242787.9542
12 | 2689864.7737 | 1242966.2416 | 2689895.4115 | 1242944.5915
13 | 2689864.7737 | 1242966.2416 | 2689886.8951 | 1242986.5153
14 | 2689729.8616 | 1242725.222 | 2689740.2089 | 1242729.8597 | 2689752.4278 | 1242735.7043
15 | 2689746.3615 | 1242721.9357 | 2689755.1402 | 1242726.3162 | 2689761.4295 | 1242728.8465 | 2689760.3744 | 1242734.1233 | 2689759.2602 | 1242739.8107 | 2689752.4278 | 1242735.7043
16 | 2689752.4278 | 1242735.7043 | 2689751.5641 | 1242737.3258 | 2689743.2101 | 1242745.8502 | 2689741.9786 | 1242747.2993 | 2689740.7262 | 1242750.6273 | 2689738.95 | 1242752.6019 | 2689737.8173 | 1242753.5188
17 | 2689729.8616 | 1242725.222 | 2689723.0896 | 1242722.1173 | 2689713.1333 | 1242717.1187 | 2689706.0808 | 1242712.424
18 | 2689729.8616 | 1242725.222 | 2689724.9484 | 1242735.7791
19 | 2689746.3615 | 1242721.9357 | 2689757.733 | 1242716.1059
20 | 2689737.8173 | 1242753.5188 | 2689737.4783 | 1242755.4373 | 2689738.1565 | 1242757.5825 | 2689740.4034 | 1242762.9649 | 2689738.1479 | 1242764.1427 | 2689732.2534 | 1242769.0016 | 2689728.9759 | 1242779.1677
21 | 2689779.7475 | 1242791.7367 | 2689779.6178 | 1242785.3189 | 2689802.3676 | 1242784.1622
22 | 2689802.3676 | 1242784.1622 | 2689820.5133 | 1242783.5669
23 | 2689802.3676 | 1242784.1622 | 2689802.3621 | 1242772.5424 | 2689804.0743 | 1242761.3156 | 2689808.3347 | 1242747.5588 | 2689810.3051 | 1242743.0884
24 | 2689779.7475 | 1242791.7367 | 2689781.5834 | 1242791.5329
25 | 2689837.8988 | 1242782.9966 | 2689820.5133 | 1242783.5669
26 | 2689825.0121 | 1242721.286 | 2689821.4027 | 1242724.7842 | 2689813.6269 | 1242735.5522 | 2689810.3051 | 1242743.0884
27 | 2689726.4588 | 1242787.9542 | 2689726.7168 | 1242786.1751 | 2689728.9759 | 1242779.1677
28 | 2689807.9535 | 1242789.0082 | 2689795.2386 | 1242790.1588 | 2689785.1239 | 1242791.1398 | 2689781.5834 | 1242791.5329
29 | 2689659.0429 | 1242708.0946 | 2689659.2328 | 1242695.0323 | 2689673.0224 | 1242687.0125 | 2689681.7872 | 1242681.3185 | 2689687.9986 | 1242689.5073 | 2689693.5265 | 1242695.3952 | 2689701.7555 | 1242703.1364 | 2689711.5989 | 1242710.6018 | 2689714.3527 | 1242705.473
30 | 2689714.3527 | 1242705.473 | 2689719.0902 | 1242696.6492 | 2689722.5893 | 1242694.9194
31 | 2689659.0429 | 1242708.0946 | 2689658.4898 | 1242722.8636
32 | 2689746.9242 | 1242682.9061 | 2689734.8265 | 1242688.8702 | 2689722.5893 | 1242694.9194
33 | 2690000.1059 | 1242581.5743 | 2690012.3683 | 1242606.979 | 2690091.3894 | 1242605.7215 | 2690092.352 | 1242611.5293 | 2690092.8315 | 1242618.286 | 2690084.8924 | 1242618.3545 | 2690079.5598 | 1242623.5218
34 | 2690079.5598 | 1242623.5218 | 2690078.0021 | 1242625.0326 | 2690065.5775 | 1242627.7572 | 2690033.8049 | 1242632.1405
35 | 2690000.1059 | 1242581.5743 | 2689987.2494 | 1242586.3496 | 2689987.202 | 1242586.2383
36 | 2690006.0123 | 1242637.5425 | 2690013.3724 | 1242634.9594 | 2690033.8049 | 1242632.1405
37 | 2689763.0474 | 1242682.8925 | 2689765.7868 | 1242688.7049 | 2689766.9515 | 1242691.1688 | 2689767.7867 | 1242692.9272 | 2689765.1049 | 1242694.2988 | 2689765.6994 | 1242695.4753 | 2689766.6907 | 1242697.4139 | 2689769.1135 | 1242702.1652 | 2689770.3983 | 1242704.6865 | 2689772.388 | 1242708.5861
38 | 2689772.388 | 1242708.5861 | 2689768.5479 | 1242710.5629 | 2689765.9118 | 1242711.9129 | 2689757.733 | 1242716.1059
39 | 2689763.0474 | 1242682.8925 | 2689761.4345 | 1242679.5657 | 2689755.6811 | 1242678.5891 | 2689746.9242 | 1242682.9061
40 | 2689763.0474 | 1242682.8925 | 2689769.0088 | 1242679.6136 | 2689784.1204 | 1242670.5232
41 | 2689937.2036 | 1242583.2554 | 2689958.4993 | 1242574.4494
42 | 2689937.2036 | 1242583.2554 | 2689923.5553 | 1242587.1142
43 | 2689978.6279 | 1242566.1261 | 2689958.4993 | 1242574.4494
44 | 2689877.5185 | 1242600.1304 | 2689923.5553 | 1242587.1142
45 | 2689658.312 | 1242727.6102 | 2689658.4898 | 1242722.8636
46 | 2690041.712 | 1242540.0302 | 2690009.3635 | 1242553.405
47 | 2690041.712 | 1242540.0302 | 2690039.51 | 1242565.0597 | 2690038.1545 | 1242570.1874
48 | 2690009.3635 | 1242553.405 | 2689978.6279 | 1242566.1261
49 | 2689978.6279 | 1242566.1261 | 2689987.202 | 1242586.2383
50 | 2689908.6806 | 1242935.215 | 2689895.4115 | 1242944.5915
51 | 2689927.9523 | 1243021.8397 | 2689902.3144 | 1243000.6467 | 2689886.8951 | 1242986.5153
52 | 2689724.9484 | 1242735.7791 | 2689712.5344 | 1242762.4535
53 | 2689837.8988 | 1242782.9966 | 2689845.7293 | 1242782.7397 | 2689866.4998 | 1242787.493
54 | 2689825.0121 | 1242721.286 | 2689825.5959 | 1242720.7201
55 | 2690080.0047 | 1242736.0785 | 2690069.8073 | 1242708.1475 | 2690065.3339 | 1242702.5422
56 | 2690080.0047 | 1242736.0785 | 2690081.1177 | 1242741.3684
57 | 2690065.3339 | 1242702.5422 | 2690056.5478 | 1242700.1515 | 2690046.7552 | 1242702.3186
58 | 2690081.1177 | 1242741.3684 | 2690085.1144 | 1242760.3655
59 | 2689967.9732 | 1242652.0563 | 2689991.9924 | 1242642.463 | 2690006.0123 | 1242637.5425
60 | 2689784.1204 | 1242670.5232 | 2689820.302 | 1242648.7581
61 | 2689656.7494 | 1242771.9111 | 2689657.5091 | 1242749.0462 | 2689658.312 | 1242727.6102
62 | 2690060.2615 | 1242938.5648 | 2690066.1233 | 1242935.2931 | 2690070.8324 | 1242933.4696
63 | 2690042.4447 | 1242948.509 | 2690060.2615 | 1242938.5648
64 | 2690094.4762 | 1242924.3141 | 2690070.8324 | 1242933.4696
65 | 2690094.4762 | 1242924.3141 | 2690095.3332 | 1242923.9823
66 | 2690095.3332 | 1242923.9823 | 2690119.1018 | 1242914.7785
67 | 2689969.1335 | 1243050.9187 | 2689972.402 | 1243043.2626 | 2689973.7732 | 1243036.0892 | 2689972.806 | 1243029.0916 | 2689968.8315 | 1243021.0031 | 2689954.5928 | 1243002.3401
68 | 2689954.5928 | 1243002.3401 | 2689932.0266 | 1243018.8575
69 | 2689969.1335 | 1243050.9187 | 2689965.2233 | 1243059.8092
70 | 2689969.1335 | 1243050.9187 | 2689973.0583 | 1243051.323 | 2689975.8513 | 1243049.5974 | 2689982.5278 | 1243043.5163 | 2689991.2676 | 1243035.4762 | 2690001.3583 | 1243030.5701 | 2690023.7187 | 1243024.627 | 2690041.3641 | 1243018.0454 | 2690053.9972 | 1243012.7626
71 | 2689927.9523 | 1243021.8397 | 2689932.0266 | 1243018.8575
72 | 2690128.1609 | 1242911.2706 | 2690119.1018 | 1242914.7785
73 | 2690099.0515 | 1243072.2166 | 2690091.4055 | 1243063.9833 | 2690085.3582 | 1243051.5267 | 2690082.0172 | 1243041.0571 | 2690079.9522 | 1243031.6855 | 2690076.0512 | 1243015.7812 | 2690074.0322 | 1243011.8365 | 2690070.1117 | 1243008.6636 | 2690063.7386 | 1243008.6891 | 2690053.9972 | 1243012.7626
74 | 2690128.1609 | 1242911.2706 | 2690129.2661 | 1242910.8426
75 | 2690129.2661 | 1242910.8426 | 2690144.1471 | 1242905.0803
76 | 2690166.6453 | 1242896.3684 | 2690144.1471 | 1242905.0803
77 | 2690166.6453 | 1242896.3684 | 2690177.2622 | 1242906.9426
78 | 2690166.6453 | 1242896.3684 | 2690137.2401 | 1242851.3397
79 | 2690185.9503 | 1242915.4448 | 2690185.59 | 1242915.2369 | 2690177.2622 | 1242906.9426
80 | 2690124.2176 | 1242831.3981 | 2690137.2401 | 1242851.3397
81 | 2690124.2176 | 1242831.3981 | 2690113.8138 | 1242833.4972
82 | 2690113.8138 | 1242833.4972 | 2690094.6313 | 1242839.1972
83 | 2690088.4996 | 1242841.0192 | 2690094.6313 | 1242839.1972
84 | 2690099.0515 | 1243072.2166 | 2690087.4953 | 1243085.5066 | 2690032.9462 | 1243141.309 | 2690031.1903 | 1243143.444
85 | 2689980.653 | 1242887.2985 | 2689992.316 | 1242880.1994 | 2689997.8747 | 1242877.1091
86 | 2690007.8918 | 1242871.5403 | 2689997.8747 | 1242877.1091
87 | 2689960.557 | 1242899.6635 | 2689962.8715 | 1242898.1218 | 2689980.653 | 1242887.2985
88 | 2690007.8918 | 1242871.5403 | 2690026.1734 | 1242862.9223 | 2690046.4962 | 1242854.8754
89 | 2690007.8918 | 1242871.5403 | 2690002.7303 | 1242863.456 | 2689998.3805 | 1242856.8667
90 | 2689960.557 | 1242899.6635 | 2689954.2644 | 1242903.8553
91 | 2690052.7339 | 1242852.4056 | 2690046.4962 | 1242854.8754
92 | 2689982.2791 | 1242832.4753 | 2689998.3805 | 1242856.8667
93 | 2689941.2667 | 1242912.5135 | 2689954.2644 | 1242903.8553
94 | 2690052.7339 | 1242852.4056 | 2690060.4129 | 1242849.3651 | 2690068.0551 | 1242847.0942
95 | 2689982.2791 | 1242832.4753 | 2689978.2523 | 1242826.3752
96 | 2689924.3245 | 1242924.1602 | 2689933.2332 | 1242917.865 | 2689941.2667 | 1242912.5135
97 | 2690088.4996 | 1242841.0192 | 2690068.0551 | 1242847.0942
98 | 2689964.3687 | 1242809.8903 | 2689966.8101 | 1242812.4069 | 2689973.7621 | 1242819.5732 | 2689978.2523 | 1242826.3752
99 | 2690086.5126 | 1242767.0113 | 2690059.7228 | 1242774.8404
100 | 2690086.5126 | 1242767.0113 | 2690085.1144 | 1242760.3655
101 | 2690059.7228 | 1242774.8404 | 2690026.3888 | 1242784.582
102 | 2689700.4427 | 1242788.4352 | 2689712.5344 | 1242762.4535
103 | 2689908.6806 | 1242935.215 | 2689910.3412 | 1242934.0415
104 | 2689924.3245 | 1242924.1602 | 2689910.3412 | 1242934.0415
105 | 2689964.3687 | 1242809.8903 | 2689967.609 | 1242797.1188
106 | 2689964.3687 | 1242809.8903 | 2689939.6155 | 1242804.2255
107 | 2689967.609 | 1242797.1188 | 2689965.1151 | 1242789.5866 | 2689962.9056 | 1242782.9049
108 | 2689967.609 | 1242797.1188 | 2689984.1836 | 1242793.991
109 | 2689911.5704 | 1242797.8074 | 2689939.6155 | 1242804.2255
110 | 2689953.1218 | 1242753.3188 | 2689962.9056 | 1242782.9049
111 | 2689984.1836 | 1242793.991 | 2690012.4382 | 1242788.659
112 | 2689911.5704 | 1242797.8074 | 2689872.252 | 1242788.8094
113 | 2689872.252 | 1242788.8094 | 2689866.4998 | 1242787.493
114 | 2689953.1218 | 1242753.3188 | 2689951.9391 | 1242749.7423
115 | 2690012.4382 | 1242788.659 | 2690012.4382 | 1242788.659 | 2690016.9382 | 1242787.3439
116 | 2689850.2612 | 1242703.4344 | 2689849.4199 | 1242703.8038 | 2689832.6199 | 1242713.9126 | 2689825.5959 | 1242720.7201
117 | 2689850.2612 | 1242703.4344 | 2689881.9596 | 1242689.5161
118 | 2689881.9596 | 1242689.5161 | 2689888.1747 | 1242686.7872
119 | 2689914.2254 | 1242675.3487 | 2689888.1747 | 1242686.7872
120 | 2689914.2254 | 1242675.3487 | 2689939.2941 | 1242664.3415
121 | 2689946.1281 | 1242660.7813 | 2689940.2365 | 1242663.9277 | 2689939.2941 | 1242664.3415
122 | 2689946.1281 | 1242660.7813 | 2689967.9732 | 1242652.0563
123 | 2689943.7917 | 1242725.1046 | 2689977.6247 | 1242717.6173
124 | 2689943.7917 | 1242725.1046 | 2689951.9391 | 1242749.7423
125 | 2690017.8646 | 1242708.7122 | 2690046.7552 | 1242702.3186
126 | 2690026.3888 | 1242784.582 | 2690016.9382 | 1242787.3439

## bus_geodata
| x | y | coords
0 | 2689798.2899 | 1242903.8246
1 | 2689770.1078 | 1242936.1311
2 | 2689798.3492 | 1242903.7566
3 | 2689837.6782 | 1242987.8362
4 | 2689749.3664 | 1242853.0781
5 | 2689761.0772 | 1242863.007
6 | 2689751.5558 | 1242834.7866
7 | 2689743.4272 | 1242830.416
8 | 2689759.16 | 1242819.3212
9 | 2689756.7889 | 1242797.705
10 | 2689739.0924 | 1242837.5708
11 | 2689864.7737 | 1242966.2416
12 | 2689752.4278 | 1242735.7043
13 | 2689729.8616 | 1242725.222
14 | 2689746.3615 | 1242721.9357
15 | 2689737.8173 | 1242753.5188
16 | 2689802.3676 | 1242784.1622
17 | 2689779.7475 | 1242791.7367
18 | 2689820.5133 | 1242783.5669
19 | 2689810.3051 | 1242743.0884
20 | 2689726.4588 | 1242787.9542
21 | 2689781.5834 | 1242791.5329
22 | 2689714.3527 | 1242705.473
23 | 2689659.0429 | 1242708.0946
24 | 2689722.5893 | 1242694.9194
25 | 2690079.5598 | 1242623.5218
26 | 2690000.1059 | 1242581.5743
27 | 2690033.8049 | 1242632.1405
28 | 2689772.388 | 1242708.5861
29 | 2689763.0474 | 1242682.8925
30 | 2689757.733 | 1242716.1059
31 | 2689937.2036 | 1242583.2554
32 | 2689958.4993 | 1242574.4494
33 | 2689923.5553 | 1242587.1142
34 | 2689658.4898 | 1242722.8636
35 | 2690041.712 | 1242540.0302
36 | 2690009.3635 | 1242553.405
37 | 2690038.1545 | 1242570.1874
38 | 2689987.202 | 1242586.2383
39 | 2689895.4115 | 1242944.5915
40 | 2689886.8951 | 1242986.5153
41 | 2689706.0808 | 1242712.424
42 | 2689724.9484 | 1242735.7791
43 | 2689728.9759 | 1242779.1677
44 | 2689837.8988 | 1242782.9966
45 | 2689825.0121 | 1242721.286
46 | 2689807.9535 | 1242789.0082
47 | 2689746.9242 | 1242682.9061
48 | 2690080.0047 | 1242736.0785
49 | 2690065.3339 | 1242702.5422
50 | 2690081.1177 | 1242741.3684
51 | 2690006.0123 | 1242637.5425
52 | 2689784.1204 | 1242670.5232
53 | 2689978.6279 | 1242566.1261
54 | 2689877.5185 | 1242600.1304
55 | 2689656.7494 | 1242771.9111
56 | 2689658.312 | 1242727.6102
57 | 2690060.2615 | 1242938.5648
58 | 2690070.8324 | 1242933.4696
59 | 2690042.4447 | 1242948.509
60 | 2690094.4762 | 1242924.3141
61 | 2690095.3332 | 1242923.9823
62 | 2689954.5928 | 1243002.3401
63 | 2689969.1335 | 1243050.9187
64 | 2689932.0266 | 1243018.8575
65 | 2690119.1018 | 1242914.7785
66 | 2689965.2233 | 1243059.8092
67 | 2690053.9972 | 1243012.7626
68 | 2689927.9523 | 1243021.8397
69 | 2690128.1609 | 1242911.2706
70 | 2690144.1471 | 1242905.0803
71 | 2690129.2661 | 1242910.8426
72 | 2690166.6453 | 1242896.3684
73 | 2690177.2622 | 1242906.9426
74 | 2690137.2401 | 1242851.3397
75 | 2690185.9503 | 1242915.4448
76 | 2690124.2176 | 1242831.3981
77 | 2690113.8138 | 1242833.4972
78 | 2690094.6313 | 1242839.1972
79 | 2690099.0515 | 1243072.2166
80 | 2690031.1903 | 1243143.444
81 | 2689997.8747 | 1242877.1091
82 | 2689980.653 | 1242887.2985
83 | 2690007.8918 | 1242871.5403
84 | 2689960.557 | 1242899.6635
85 | 2690046.4962 | 1242854.8754
86 | 2689998.3805 | 1242856.8667
87 | 2689954.2644 | 1242903.8553
88 | 2690052.7339 | 1242852.4056
89 | 2689982.2791 | 1242832.4753
90 | 2689941.2667 | 1242912.5135
91 | 2690068.0551 | 1242847.0942
92 | 2689978.2523 | 1242826.3752
93 | 2690088.4996 | 1242841.0192
94 | 2690086.5126 | 1242767.0113
95 | 2690059.7228 | 1242774.8404
96 | 2690085.1144 | 1242760.3655
97 | 2689712.5344 | 1242762.4535
98 | 2689908.6806 | 1242935.215
99 | 2689910.3412 | 1242934.0415
100 | 2689964.3687 | 1242809.8903
101 | 2689967.609 | 1242797.1188
102 | 2689939.6155 | 1242804.2255
103 | 2689962.9056 | 1242782.9049
104 | 2689984.1836 | 1242793.991
105 | 2689911.5704 | 1242797.8074
106 | 2689924.3245 | 1242924.1602
107 | 2689866.4998 | 1242787.493
108 | 2689872.252 | 1242788.8094
109 | 2689700.4427 | 1242788.4352
110 | 2689953.1218 | 1242753.3188
111 | 2690012.4382 | 1242788.659
112 | 2689825.5959 | 1242720.7201
113 | 2689850.2612 | 1242703.4344
114 | 2689881.9596 | 1242689.5161
115 | 2689888.1747 | 1242686.7872
116 | 2689914.2254 | 1242675.3487
117 | 2689939.2941 | 1242664.3415
118 | 2689820.302 | 1242648.7581
119 | 2689946.1281 | 1242660.7813
120 | 2689967.9732 | 1242652.0563
121 | 2689943.7917 | 1242725.1046
122 | 2689977.6247 | 1242717.6173
123 | 2689951.9391 | 1242749.7423
124 | 2690046.7552 | 1242702.3186
125 | 2690016.9382 | 1242787.3439
126 | 2690026.3888 | 1242784.582
127 | 2690017.8646 | 1242708.7122
128 | 2689964.3687 | 1242809.8903

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98197 | -0.3474 | 0.0032269 | 0.00080875
1 | 0.98223 | -0.34218 | 0 | 0
2 | 0.98197 | -0.3474 | 0.0035144 | 0.00088079
3 | 0.98276 | -0.33181 | 0 | 0
4 | 0.98618 | -0.26381 | 0 | 0
5 | 0.98603 | -0.26675 | 0.010697 | 0.002681
6 | 0.98637 | -0.26015 | 0 | 0
7 | 0.98597 | -0.2679 | 0 | 0
8 | 0.98693 | -0.24943 | 0.010109 | 0.0025335
9 | 0.98459 | -0.29455 | 0 | 0
10 | 0.9859 | -0.26935 | 0.0097096 | 0.0024335
11 | 0.98298 | -0.3276 | 0.0060189 | 0.0015085
12 | 0.97723 | -0.43787 | 0 | 0
13 | 0.97688 | -0.44477 | 0 | 0
14 | 0.9756 | -0.46975 | 0 | 0
15 | 0.97862 | -0.41064 | 0.0070533 | 0.0017677
16 | 0.9894 | -0.20187 | 0 | 0
17 | 0.98823 | -0.22433 | 0 | 0
18 | 0.99101 | -0.17087 | 0.0060078 | 0.0015057
19 | 0.98733 | -0.24174 | 0.0048698 | 0.0012205
20 | 0.98133 | -0.35776 | 0.0054854 | 0.0013748
21 | 0.98821 | -0.22483 | 0.0063234 | 0.0015848
22 | 0.97221 | -0.53658 | 0 | 0
23 | 0.97155 | -0.5496 | 0 | 0
24 | 0.97232 | -0.5345 | 0.0094842 | 0.002377
25 | 0.97905 | -0.40221 | 0 | 0
26 | 0.97317 | -0.51725 | 0 | 0
27 | 0.98109 | -0.36258 | 0.00066358 | 0.00016631
28 | 0.97437 | -0.4939 | 0 | 0
29 | 0.97319 | -0.5172 | 0 | 0
30 | 0.97502 | -0.48118 | 0.0067126 | 0.0016823
31 | 0.97104 | -0.55948 | 0 | 0
32 | 0.97137 | -0.55294 | 0.0037796 | 0.00094727
33 | 0.97083 | -0.56351 | 0.0036195 | 0.00090712
34 | 0.97144 | -0.5518 | 0.0020993 | 0.00052614
35 | 0.97077 | -0.56485 | 0 | 0
36 | 0.97111 | -0.55806 | 0.010385 | 0.0026028
37 | 0.97047 | -0.57078 | 0.010521 | 0.0026368
38 | 0.97257 | -0.5291 | 0.0064476 | 0.0016159
39 | 0.98393 | -0.30909 | 0.0029072 | 0.00072862
40 | 0.98257 | -0.33552 | 0.0013219 | 0.0003313
41 | 0.97681 | -0.44609 | 0.0026795 | 0.00067154
42 | 0.97674 | -0.44743 | 0.0030567 | 0.00076607
43 | 0.98066 | -0.37076 | 0.0073408 | 0.0018398
44 | 0.99259 | -0.14066 | 0.0077804 | 0.00195
45 | 0.98607 | -0.26609 | 0.016269 | 0.0040774
46 | 0.98799 | -0.22896 | 0.0087405 | 0.0021906
47 | 0.97276 | -0.52571 | 0.0064069 | 0.0016057
48 | 0.99236 | -0.14659 | 0 | 0
49 | 0.99224 | -0.14882 | 0 | 0
50 | 0.99238 | -0.14626 | 0.0097514 | 0.0024439
51 | 0.98172 | -0.35045 | 0.0012462 | 0.00031233
52 | 0.97278 | -0.52534 | 0.013215 | 0.0033119
53 | 0.97176 | -0.54525 | 0 | 0
54 | 0.97031 | -0.57389 | 0.011732 | 0.0029404
55 | 0.97132 | -0.55417 | 0.002252 | 0.00056441
56 | 0.97141 | -0.55233 | 0.0037279 | 0.00093429
57 | 0.97826 | -0.41948 | 0.0070914 | 0.0017773
58 | 0.97842 | -0.41643 | 0.003683 | 0.00092303
59 | 0.97813 | -0.42213 | 0.0071428 | 0.0017902
60 | 0.97884 | -0.40816 | 0.0018505 | 0.00046379
61 | 0.97886 | -0.40783 | 0.0040331 | 0.0010108
62 | 0.98158 | -0.35493 | 0 | 0
63 | 0.98106 | -0.36517 | 0 | 0
64 | 0.98184 | -0.34975 | 0.0030378 | 0.00076136
65 | 0.97942 | -0.3968 | 0.0018203 | 0.0004562
66 | 0.98103 | -0.36562 | 0.0025566 | 0.00064073
67 | 0.98038 | -0.37842 | 0.0055159 | 0.0013824
68 | 0.98191 | -0.34853 | 0 | 0
69 | 0.97965 | -0.39228 | 0.0023388 | 0.00058615
70 | 0.98013 | -0.38287 | 0.001349 | 0.00033808
71 | 0.97968 | -0.39168 | 0.0024305 | 0.00060915
72 | 0.98084 | -0.36899 | 0 | 0
73 | 0.98077 | -0.37034 | 0.0024383 | 0.00061109
74 | 0.98267 | -0.33328 | 0.0014677 | 0.00036783
75 | 0.98074 | -0.3709 | 0.0025382 | 0.00063613
76 | 0.98351 | -0.31687 | 0 | 0
77 | 0.98388 | -0.30959 | 0 | 0
78 | 0.98459 | -0.29584 | 0.0034007 | 0.0008523
79 | 0.9802 | -0.38191 | 0 | 0
80 | 0.98001 | -0.38579 | 0.0021712 | 0.00054415
81 | 0.98853 | -0.21958 | 0.009358 | 0.0023453
82 | 0.98748 | -0.24003 | 0.014859 | 0.0037239
83 | 0.98923 | -0.20598 | 0 | 0
84 | 0.98655 | -0.25791 | 0.0028727 | 0.00071996
85 | 0.98692 | -0.25065 | 0.003609 | 0.00090449
86 | 0.99127 | -0.1668 | 0.0024576 | 0.00061594
87 | 0.98628 | -0.26326 | 0.00076462 | 0.00019163
88 | 0.98657 | -0.25736 | 0.0042607 | 0.0010678
89 | 0.99473 | -0.10041 | 0.014492 | 0.003632
90 | 0.98572 | -0.2741 | 0.0016192 | 0.0004058
91 | 0.9858 | -0.27238 | 0.0028251 | 0.00070804
92 | 0.99521 | -0.091206 | 0.010151 | 0.0025441
93 | 0.98484 | -0.29106 | 0.0071924 | 0.0018026
94 | 0.99269 | -0.14009 | 0 | 0
95 | 0.99305 | -0.13327 | 0.0068904 | 0.0017269
96 | 0.99261 | -0.14174 | 0.00064196 | 0.00016089
97 | 0.97648 | -0.45253 | 0.0074094 | 0.001857
98 | 0.98438 | -0.30023 | 0.0049714 | 0.001246
99 | 0.98445 | -0.29894 | 0.00098166 | 0.00024603
100 | 0.99623 | -0.071783 | 0 | 0
101 | 0.9954 | -0.087891 | 0 | 0
102 | 0.99796 | -0.038734 | 0.0085402 | 0.0021404
103 | 0.99496 | -0.096356 | 0.0037312 | 0.00093513
104 | 0.99482 | -0.099003 | 0.0074495 | 0.001867
105 | 1 | 0 | -0.57101 | -0.14579
106 | 0.98502 | -0.28779 | 0.00085134 | 0.00021337
107 | 0.99531 | -0.088916 | 0.022807 | 0.0057159
108 | 0.9959 | -0.077685 | 0.0054328 | 0.0013616
109 | 0.97643 | -0.45361 | 0.0020647 | 0.00051746
110 | 0.99415 | -0.11195 | 0.013512 | 0.0033865
111 | 0.99403 | -0.1142 | 0.0034969 | 0.00087639
112 | 0.98604 | -0.26676 | 0.046298 | 0.011603
113 | 0.98518 | -0.28329 | 0.0022094 | 0.00055374
114 | 0.98423 | -0.30174 | 0.0027369 | 0.00068593
115 | 0.98405 | -0.30525 | 0.014304 | 0.003585
116 | 0.98342 | -0.31754 | 0.0061545 | 0.0015425
117 | 0.98286 | -0.32836 | 0.011408 | 0.0028591
118 | 0.97259 | -0.52914 | 0.0048871 | 0.0012248
119 | 0.98273 | -0.33088 | 0 | 0
120 | 0.98233 | -0.33857 | 0.0059369 | 0.0014879
121 | 0.99392 | -0.11645 | 0 | 0
122 | 0.99368 | -0.12113 | 0.0076663 | 0.0019214
123 | 0.9941 | -0.11293 | 0.0072123 | 0.0018076
124 | 0.99218 | -0.14997 | 0.0015769 | 0.00039521
125 | 0.99392 | -0.11639 | 0.0023446 | 0.0005876
126 | 0.9937 | -0.12058 | 0.0034406 | 0.0008623
127 | 0.99213 | -0.15093 | 0.0018292 | 0.00045843
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0067413 | -0.0016895 | 0.006743 | 0.0016901 | 1.6777e-06 | 5.3122e-07 | 0.010215 | 0.010215 | 0.010215 | 0.98197 | -0.3474 | 0.98223 | -0.34218 | 2.8064
1 | 0.0035144 | 0.00088079 | -0.0035144 | -0.00088079 | 9.6034e-10 | -5.2781e-10 | 0.0053255 | 0.0053255 | 0.0053255 | 0.98197 | -0.3474 | 0.98197 | -0.3474 | 1.4631
2 | -0.006743 | -0.0016901 | 0.0067464 | 0.0016911 | 3.3295e-06 | 1.0533e-06 | 0.010215 | 0.010215 | 0.010215 | 0.98223 | -0.34218 | 0.98276 | -0.33181 | 2.8064
3 | -0.0067464 | -0.0016911 | 0.0067477 | 0.0016916 | 1.3534e-06 | 4.2781e-07 | 0.010215 | 0.010215 | 0.010215 | 0.98276 | -0.33181 | 0.98298 | -0.3276 | 2.8063
4 | 0.010699 | 0.0026818 | -0.010697 | -0.002681 | 1.4979e-06 | 7.631e-07 | 0.016143 | 0.016143 | 0.016143 | 0.98618 | -0.26381 | 0.98603 | -0.26675 | 4.435
5 | -0.010699 | -0.0026818 | 0.010701 | 0.0026827 | 1.8637e-06 | 9.4941e-07 | 0.016143 | 0.016143 | 0.016143 | 0.98618 | -0.26381 | 0.98637 | -0.26015 | 4.435
6 | 0.094469 | 0.024012 | -0.094434 | -0.02399 | 3.5208e-05 | 2.2297e-05 | 0.14263 | 0.14263 | 0.14263 | 0.98637 | -0.26015 | 0.98597 | -0.2679 | 19.5926
7 | -0.10517 | -0.026695 | 0.10522 | 0.026729 | 5.4308e-05 | 3.4097e-05 | 0.15878 | 0.15878 | 0.15878 | 0.98637 | -0.26015 | 0.98693 | -0.24943 | 14.5401
8 | 0.084724 | 0.021556 | -0.084615 | -0.021488 | 0.0001087 | 6.8666e-05 | 0.12798 | 0.12798 | 0.12798 | 0.98597 | -0.2679 | 0.98459 | -0.29455 | 17.5797
9 | 0.0097103 | 0.0024338 | -0.0097096 | -0.0024335 | 6.7372e-07 | 3.245e-07 | 0.014655 | 0.014655 | 0.014655 | 0.98597 | -0.2679 | 0.9859 | -0.26935 | 4.026
10 | -0.11533 | -0.029263 | 0.11547 | 0.02935 | 0.00013937 | 8.7782e-05 | 0.17402 | 0.17402 | 0.17402 | 0.98693 | -0.24943 | 0.98823 | -0.22433 | 15.9358
11 | 0.084615 | 0.021488 | -0.084359 | -0.021324 | 0.00025652 | 0.00016364 | 0.12798 | 0.12798 | 0.12798 | 0.98459 | -0.29455 | 0.98133 | -0.35776 | 35.1594
12 | -0.027398 | -0.0068719 | 0.027422 | 0.0068869 | 2.4201e-05 | 1.5013e-05 | 0.041476 | 0.041476 | 0.041476 | 0.98298 | -0.3276 | 0.98393 | -0.30909 | 11.3946
13 | 0.014631 | 0.0036719 | -0.014626 | -0.0036687 | 5.5208e-06 | 3.1531e-06 | 0.02215 | 0.02215 | 0.02215 | 0.98298 | -0.3276 | 0.98257 | -0.33552 | 6.0853
14 | 0.015219 | 0.0038164 | -0.015214 | -0.0038135 | 4.9996e-06 | 2.8888e-06 | 0.023175 | 0.023175 | 0.023175 | 0.97723 | -0.43787 | 0.97688 | -0.44477 | 6.3668
15 | 0.04899 | 0.012354 | -0.048916 | -0.012306 | 7.4633e-05 | 4.7318e-05 | 0.074625 | 0.074625 | 0.074625 | 0.97723 | -0.43787 | 0.9756 | -0.46975 | 20.5013
16 | -0.06421 | -0.01617 | 0.064293 | 0.016223 | 8.3728e-05 | 5.3293e-05 | 0.0978 | 0.0978 | 0.0978 | 0.97723 | -0.43787 | 0.97862 | -0.41064 | 26.8681
17 | 0.0026797 | 0.00067131 | -0.0026795 | -0.00067154 | 1.6908e-07 | -2.3058e-07 | 0.0040817 | 0.0040818 | 0.0040818 | 0.97688 | -0.44477 | 0.97681 | -0.44609 | 1.1214
18 | 0.012535 | 0.0031422 | -0.012533 | -0.0031413 | 1.5919e-06 | 8.7307e-07 | 0.019094 | 0.019094 | 0.019094 | 0.97688 | -0.44477 | 0.97674 | -0.44743 | 5.2455
19 | 0.048916 | 0.012306 | -0.048889 | -0.012289 | 2.6686e-05 | 1.692e-05 | 0.074625 | 0.074625 | 0.074625 | 0.9756 | -0.46975 | 0.97502 | -0.48118 | 20.5013
20 | -0.071347 | -0.017991 | 0.071483 | 0.018078 | 0.00013645 | 8.694e-05 | 0.10852 | 0.10852 | 0.10852 | 0.97862 | -0.41064 | 0.98066 | -0.37076 | 29.8144
21 | 0.13068 | 0.033216 | -0.13054 | -0.033127 | 0.00014122 | 8.9256e-05 | 0.1967 | 0.1967 | 0.1967 | 0.9894 | -0.20187 | 0.98823 | -0.22433 | 18.0131
22 | -0.29052 | -0.073752 | 0.29096 | 0.074029 | 0.00043393 | 0.00027701 | 0.43727 | 0.43727 | 0.43727 | 0.9894 | -0.20187 | 0.99101 | -0.17087 | 40.0431
23 | 0.15984 | 0.040536 | -0.15954 | -0.040342 | 0.00030574 | 0.00019405 | 0.24057 | 0.24057 | 0.24057 | 0.9894 | -0.20187 | 0.98733 | -0.24174 | 22.0301
24 | 0.015066 | 0.0037763 | -0.015066 | -0.0037761 | 3.5648e-07 | 2.0448e-07 | 0.022685 | 0.022686 | 0.022686 | 0.98823 | -0.22433 | 0.98821 | -0.22483 | 6.2323
25 | -0.29697 | -0.075534 | 0.2974 | 0.075811 | 0.00043308 | 0.0002765 | 0.44629 | 0.44629 | 0.44629 | 0.99101 | -0.17087 | 0.99259 | -0.14066 | 40.8692
26 | 0.15467 | 0.039121 | -0.15449 | -0.039007 | 0.00018049 | 0.0001145 | 0.23323 | 0.23323 | 0.23323 | 0.98733 | -0.24174 | 0.98607 | -0.26609 | 21.358
27 | 0.078873 | 0.019949 | -0.078824 | -0.019918 | 4.9188e-05 | 3.1365e-05 | 0.11966 | 0.11966 | 0.11966 | 0.98133 | -0.35776 | 0.98066 | -0.37076 | 32.8744
28 | 0.0087422 | 0.0021913 | -0.0087405 | -0.0021906 | 1.7215e-06 | 7.6243e-07 | 0.013164 | 0.013164 | 0.013164 | 0.98821 | -0.22483 | 0.98799 | -0.22896 | 3.6165
29 | 0.0080854 | 0.0020269 | -0.0080804 | -0.0020248 | 5.0136e-06 | 2.1269e-06 | 0.012375 | 0.012376 | 0.012376 | 0.97221 | -0.53658 | 0.97155 | -0.5496 | 3.3999
30 | -0.0080854 | -0.0020269 | 0.0080862 | 0.0020273 | 7.9934e-07 | 3.3897e-07 | 0.012375 | 0.012375 | 0.012375 | 0.97221 | -0.53658 | 0.97232 | -0.5345 | 3.3998
31 | 0.0080804 | 0.0020248 | -0.0080796 | -0.0020245 | 8.4884e-07 | 3.6026e-07 | 0.012376 | 0.012376 | 0.012376 | 0.97155 | -0.5496 | 0.97144 | -0.5518 | 3.3999
32 | -0.01757 | -0.0044042 | 0.017578 | 0.0044086 | 7.3585e-06 | 4.3727e-06 | 0.02689 | 0.02689 | 0.02689 | 0.97232 | -0.5345 | 0.97276 | -0.52571 | 7.3873
33 | 0.04684 | 0.011872 | -0.046582 | -0.011709 | 0.00025742 | 0.00016306 | 0.071238 | 0.071238 | 0.071238 | 0.97905 | -0.40221 | 0.97317 | -0.51725 | 19.571
34 | -0.04684 | -0.011872 | 0.046929 | 0.011929 | 8.9373e-05 | 5.6607e-05 | 0.071238 | 0.071237 | 0.071238 | 0.97905 | -0.40221 | 0.98109 | -0.36258 | 19.5708
35 | 0.046582 | 0.011709 | -0.046556 | -0.011693 | 2.633e-05 | 1.668e-05 | 0.071238 | 0.071238 | 0.071238 | 0.97317 | -0.51725 | 0.97257 | -0.5291 | 19.571
36 | -0.047593 | -0.012095 | 0.04762 | 0.012112 | 2.7818e-05 | 1.7085e-05 | 0.072244 | 0.072244 | 0.072244 | 0.98109 | -0.36258 | 0.98172 | -0.35045 | 9.9236
37 | 0.042151 | 0.010591 | -0.042104 | -0.010561 | 4.6826e-05 | 2.9594e-05 | 0.064381 | 0.064381 | 0.064381 | 0.97437 | -0.4939 | 0.97319 | -0.5172 | 17.687
38 | -0.042151 | -0.010591 | 0.042177 | 0.010607 | 2.5602e-05 | 1.618e-05 | 0.064381 | 0.06438 | 0.064381 | 0.97437 | -0.4939 | 0.97502 | -0.48118 | 17.687
39 | 0.023994 | 0.0060203 | -0.023985 | -0.0060143 | 9.7408e-06 | 5.9945e-06 | 0.03669 | 0.03669 | 0.03669 | 0.97319 | -0.5172 | 0.97276 | -0.52571 | 10.0797
40 | 0.01811 | 0.004541 | -0.018103 | -0.0045368 | 7.0272e-06 | 4.1939e-06 | 0.027691 | 0.027691 | 0.027691 | 0.97319 | -0.5172 | 0.97278 | -0.52534 | 7.6074
41 | -0.015361 | -0.0038524 | 0.015365 | 0.0038552 | 4.7885e-06 | 2.7794e-06 | 0.02354 | 0.02354 | 0.02354 | 0.97104 | -0.55948 | 0.97137 | -0.55294 | 6.4669
42 | 0.015361 | 0.0038524 | -0.015358 | -0.0038507 | 2.9472e-06 | 1.7108e-06 | 0.02354 | 0.02354 | 0.02354 | 0.97104 | -0.55948 | 0.97083 | -0.56351 | 6.4669
43 | -0.019145 | -0.0048024 | 0.019152 | 0.0048067 | 7.0263e-06 | 4.2271e-06 | 0.029329 | 0.029329 | 0.029329 | 0.97137 | -0.55294 | 0.97176 | -0.54525 | 8.0575
44 | 0.011738 | 0.0029435 | -0.011732 | -0.0029404 | 5.8077e-06 | 3.1257e-06 | 0.017992 | 0.017992 | 0.017992 | 0.97083 | -0.56351 | 0.97031 | -0.57389 | 4.9429
45 | 0.0059802 | 0.0014983 | -0.0059801 | -0.0014983 | 1.4946e-07 | 3.6849e-08 | 0.0091601 | 0.0091601 | 0.0091601 | 0.97144 | -0.5518 | 0.97141 | -0.55233 | 2.5165
46 | -0.010524 | -0.0026383 | 0.010527 | 0.0026401 | 3.4075e-06 | 1.7489e-06 | 0.016132 | 0.016131 | 0.016132 | 0.97077 | -0.56485 | 0.97111 | -0.55806 | 4.4318
47 | 0.010524 | 0.0026383 | -0.010521 | -0.0026368 | 2.9699e-06 | 1.5246e-06 | 0.016132 | 0.016132 | 0.016132 | 0.97077 | -0.56485 | 0.97047 | -0.57078 | 4.4318
48 | -0.020912 | -0.0052428 | 0.020925 | 0.0052506 | 1.2777e-05 | 7.7667e-06 | 0.032045 | 0.032044 | 0.032045 | 0.97111 | -0.55806 | 0.97176 | -0.54525 | 8.8034
49 | 0.040108 | 0.010077 | -0.040077 | -0.010057 | 3.0883e-05 | 1.9494e-05 | 0.061374 | 0.061374 | 0.061374 | 0.97257 | -0.5291 | 0.97176 | -0.54525 | 16.8609
50 | -0.030329 | -0.0076155 | 0.030342 | 0.0076235 | 1.2821e-05 | 7.9992e-06 | 0.045873 | 0.045873 | 0.045873 | 0.98393 | -0.30909 | 0.98438 | -0.30023 | 12.6024
51 | 0.013304 | 0.0033374 | -0.013295 | -0.0033328 | 8.248e-06 | 4.5929e-06 | 0.020148 | 0.020149 | 0.020149 | 0.98257 | -0.33552 | 0.98191 | -0.34853 | 5.5353
52 | 0.0094765 | 0.0023752 | -0.0094742 | -0.0023741 | 2.2996e-06 | 1.1036e-06 | 0.014437 | 0.014437 | 0.014437 | 0.97674 | -0.44743 | 0.97648 | -0.45253 | 3.9662
53 | -0.30518 | -0.077761 | 0.30594 | 0.078249 | 0.00076397 | 0.00048781 | 0.45795 | 0.45795 | 0.45795 | 0.99259 | -0.14066 | 0.99531 | -0.088916 | 41.9373
54 | 0.13822 | 0.034929 | -0.13821 | -0.034926 | 4.4256e-06 | 2.8013e-06 | 0.20868 | 0.20868 | 0.20868 | 0.98607 | -0.26609 | 0.98604 | -0.26676 | 19.1098
55 | 0.0034067 | 0.00085294 | -0.0034064 | -0.00085319 | 3.6095e-07 | -2.4554e-07 | 0.005108 | 0.0051081 | 0.0051081 | 0.99236 | -0.14659 | 0.99224 | -0.14882 | 1.4033
56 | -0.0034067 | -0.00085294 | 0.0034068 | 0.00085291 | 5.2891e-08 | -3.599e-08 | 0.005108 | 0.0051079 | 0.005108 | 0.99236 | -0.14659 | 0.99238 | -0.14626 | 1.4033
57 | 0.0034064 | 0.00085319 | -0.0034062 | -0.00085332 | 1.8724e-07 | -1.2731e-07 | 0.0051081 | 0.0051082 | 0.0051082 | 0.99224 | -0.14882 | 0.99218 | -0.14997 | 1.4034
58 | -0.013158 | -0.0032968 | 0.013161 | 0.0032984 | 2.8338e-06 | 1.5627e-06 | 0.01973 | 0.01973 | 0.01973 | 0.99238 | -0.14626 | 0.99261 | -0.14174 | 5.4203
59 | -0.048867 | -0.012425 | 0.048895 | 0.012441 | 2.7974e-05 | 1.6358e-05 | 0.074133 | 0.074132 | 0.074133 | 0.98172 | -0.35045 | 0.98233 | -0.33857 | 6.7887
60 | 0.004888 | 0.0012249 | -0.0048871 | -0.0012248 | 8.852e-07 | 4.2436e-08 | 0.0074769 | 0.0074771 | 0.0074771 | 0.97278 | -0.52534 | 0.97259 | -0.52914 | 2.0541
61 | -0.002252 | -0.00056441 | 0.0022522 | 0.00056399 | 1.9785e-07 | -4.2211e-07 | 0.00345 | 0.0034498 | 0.00345 | 0.97132 | -0.55417 | 0.97141 | -0.55233 | 0.9478
62 | -0.014235 | -0.0035677 | 0.014237 | 0.0035689 | 2.0681e-06 | 1.1759e-06 | 0.021653 | 0.021653 | 0.021653 | 0.97826 | -0.41948 | 0.97842 | -0.41643 | 5.9486
63 | 0.0071437 | 0.0017905 | -0.0071428 | -0.0017902 | 9.0346e-07 | 3.2207e-07 | 0.010866 | 0.010866 | 0.010866 | 0.97826 | -0.41948 | 0.97813 | -0.42213 | 2.9852
64 | -0.01792 | -0.004492 | 0.017927 | 0.0044962 | 7.0622e-06 | 4.2013e-06 | 0.027254 | 0.027254 | 0.027254 | 0.97842 | -0.41643 | 0.97884 | -0.40816 | 7.4873
65 | -0.019778 | -0.0049599 | 0.019778 | 0.0049601 | 3.1155e-07 | 1.8784e-07 | 0.030067 | 0.030067 | 0.030067 | 0.97884 | -0.40816 | 0.97886 | -0.40783 | 8.2601
66 | -0.023811 | -0.0059709 | 0.023824 | 0.0059786 | 1.2524e-05 | 7.6947e-06 | 0.036198 | 0.036198 | 0.036198 | 0.97886 | -0.40783 | 0.97942 | -0.3968 | 9.9445
67 | 0.010254 | 0.0025698 | -0.010249 | -0.0025673 | 4.9975e-06 | 2.5016e-06 | 0.015545 | 0.015545 | 0.015545 | 0.98158 | -0.35493 | 0.98106 | -0.36517 | 4.2706
68 | -0.010254 | -0.0025698 | 0.010257 | 0.002571 | 2.5341e-06 | 1.2682e-06 | 0.015545 | 0.015545 | 0.015545 | 0.98158 | -0.35493 | 0.98184 | -0.34975 | 4.2706
69 | 0.0025566 | 0.00064064 | -0.0025566 | -0.00064073 | 5.4765e-08 | -8.7585e-08 | 0.0038777 | 0.0038777 | 0.0038777 | 0.98106 | -0.36517 | 0.98103 | -0.36562 | 1.0653
70 | 0.0076927 | 0.0019266 | -0.0076879 | -0.0019247 | 4.8507e-06 | 1.9055e-06 | 0.011667 | 0.011668 | 0.011668 | 0.98106 | -0.36517 | 0.98038 | -0.37842 | 3.2055
71 | -0.013295 | -0.0033324 | 0.013295 | 0.0033328 | 7.6867e-07 | 4.2809e-07 | 0.020149 | 0.020149 | 0.020149 | 0.98184 | -0.34975 | 0.98191 | -0.34853 | 5.5354
72 | -0.025644 | -0.0064348 | 0.025649 | 0.0064382 | 5.5305e-06 | 3.4172e-06 | 0.038963 | 0.038963 | 0.038963 | 0.97942 | -0.3968 | 0.97965 | -0.39228 | 10.7042
73 | 0.0021719 | 0.00054228 | -0.0021716 | -0.00054317 | 3.6034e-07 | -8.8452e-07 | 0.0032958 | 0.0032962 | 0.0032962 | 0.98038 | -0.37842 | 0.9802 | -0.38191 | 0.90555
74 | -0.027988 | -0.0070244 | 0.027989 | 0.0070249 | 8.034e-07 | 4.9925e-07 | 0.042516 | 0.042516 | 0.042516 | 0.97965 | -0.39228 | 0.97968 | -0.39168 | 11.6801
75 | 0.030432 | 0.007642 | -0.03042 | -0.007634 | 1.2777e-05 | 7.9761e-06 | 0.046207 | 0.046207 | 0.046207 | 0.98013 | -0.38287 | 0.97968 | -0.39168 | 12.6943
76 | -0.031781 | -0.0079801 | 0.031802 | 0.0079933 | 2.1067e-05 | 1.3179e-05 | 0.048255 | 0.048255 | 0.048255 | 0.98013 | -0.38287 | 0.98084 | -0.36899 | 13.2569
77 | 0.0049768 | 0.0012471 | -0.0049765 | -0.0012471 | 3.2033e-07 | 1.59e-08 | 0.0075502 | 0.0075503 | 0.0075503 | 0.98084 | -0.36899 | 0.98077 | -0.37034 | 2.0743
78 | -0.036779 | -0.0092404 | 0.036842 | 0.0092799 | 6.2806e-05 | 3.9516e-05 | 0.055805 | 0.055805 | 0.055805 | 0.98084 | -0.36899 | 0.98267 | -0.33328 | 15.3311
79 | 0.0025383 | 0.00063602 | -0.0025382 | -0.00063613 | 6.768e-08 | -1.1026e-07 | 0.003851 | 0.003851 | 0.003851 | 0.98077 | -0.37034 | 0.98074 | -0.3709 | 1.058
80 | -0.03831 | -0.0096477 | 0.03834 | 0.0096667 | 3.0074e-05 | 1.8945e-05 | 0.058027 | 0.058027 | 0.058027 | 0.98267 | -0.33328 | 0.98351 | -0.31687 | 15.9416
81 | -0.03834 | -0.0096667 | 0.038353 | 0.0096751 | 1.3364e-05 | 8.4188e-06 | 0.058027 | 0.058027 | 0.058027 | 0.98351 | -0.31687 | 0.98388 | -0.30959 | 15.9416
82 | -0.038353 | -0.0096751 | 0.038378 | 0.009691 | 2.5268e-05 | 1.5917e-05 | 0.058027 | 0.058027 | 0.058027 | 0.98388 | -0.30959 | 0.98459 | -0.29584 | 15.9416
83 | -0.041779 | -0.010543 | 0.041789 | 0.010549 | 9.571e-06 | 6.0441e-06 | 0.063167 | 0.063167 | 0.063167 | 0.98459 | -0.29584 | 0.98484 | -0.29106 | 17.3535
84 | 0.0021716 | 0.00054317 | -0.0021712 | -0.00054415 | 4.0102e-07 | -9.8357e-07 | 0.0032962 | 0.0032967 | 0.0032967 | 0.9802 | -0.38191 | 0.98001 | -0.38579 | 0.90568
85 | 0.05743 | 0.014477 | -0.057374 | -0.014441 | 5.6127e-05 | 3.5665e-05 | 0.086478 | 0.086478 | 0.086478 | 0.98853 | -0.21958 | 0.98748 | -0.24003 | 23.7577
86 | -0.066788 | -0.016822 | 0.066831 | 0.01685 | 4.3465e-05 | 2.7671e-05 | 0.10056 | 0.10056 | 0.10056 | 0.98853 | -0.21958 | 0.98923 | -0.20598 | 27.6275
87 | 0.042515 | 0.010717 | -0.042479 | -0.010694 | 3.6345e-05 | 2.2959e-05 | 0.064088 | 0.064088 | 0.064088 | 0.98748 | -0.24003 | 0.98655 | -0.25791 | 17.6066
88 | 0.059903 | 0.015177 | -0.059775 | -0.015095 | 0.00012825 | 8.1544e-05 | 0.090165 | 0.090166 | 0.090166 | 0.98923 | -0.20598 | 0.98692 | -0.25065 | 24.7708
89 | -0.12673 | -0.032026 | 0.12697 | 0.032179 | 0.00023855 | 0.00015245 | 0.19073 | 0.19073 | 0.19073 | 0.98923 | -0.20598 | 0.99127 | -0.1668 | 52.3982
90 | 0.039606 | 0.0099742 | -0.039596 | -0.0099678 | 1.0124e-05 | 6.3829e-06 | 0.059755 | 0.059755 | 0.059755 | 0.98655 | -0.25791 | 0.98628 | -0.26326 | 16.4162
91 | 0.056166 | 0.014191 | -0.056148 | -0.014179 | 1.8059e-05 | 1.1472e-05 | 0.084724 | 0.084724 | 0.084724 | 0.98692 | -0.25065 | 0.98657 | -0.25736 | 23.2759
92 | -0.12943 | -0.032795 | 0.12985 | 0.03306 | 0.00041427 | 0.00026476 | 0.19442 | 0.19442 | 0.19442 | 0.99127 | -0.1668 | 0.99473 | -0.10041 | 53.4117
93 | 0.038832 | 0.0097762 | -0.038811 | -0.0097635 | 2.0112e-05 | 1.2673e-05 | 0.058602 | 0.058602 | 0.058602 | 0.98628 | -0.26326 | 0.98572 | -0.2741 | 16.0993
94 | 0.051887 | 0.013111 | -0.05185 | -0.013088 | 3.7316e-05 | 2.3675e-05 | 0.078298 | 0.078298 | 0.078298 | 0.98657 | -0.25736 | 0.9858 | -0.27238 | 21.5105
95 | -0.14434 | -0.036692 | 0.1444 | 0.036732 | 6.3999e-05 | 4.077e-05 | 0.2161 | 0.2161 | 0.2161 | 0.99473 | -0.10041 | 0.99521 | -0.091206 | 29.6836
96 | 0.037192 | 0.0093577 | -0.037168 | -0.0093424 | 2.4316e-05 | 1.53e-05 | 0.056157 | 0.056157 | 0.056157 | 0.98572 | -0.2741 | 0.98502 | -0.28779 | 15.4279
97 | 0.049025 | 0.01238 | -0.048981 | -0.012352 | 4.3837e-05 | 2.7784e-05 | 0.074034 | 0.074034 | 0.074034 | 0.9858 | -0.27238 | 0.98484 | -0.29106 | 20.339
98 | -0.15455 | -0.039276 | 0.1547 | 0.039368 | 0.00014469 | 9.1758e-05 | 0.23127 | 0.23127 | 0.23127 | 0.99521 | -0.091206 | 0.99623 | -0.071783 | 21.1789
99 | -0.013804 | -0.0034599 | 0.013809 | 0.0034624 | 4.4812e-06 | 2.507e-06 | 0.020692 | 0.020692 | 0.020692 | 0.99269 | -0.14009 | 0.99305 | -0.13327 | 5.6846
100 | 0.013804 | 0.0034599 | -0.013803 | -0.0034593 | 1.0904e-06 | 6.1007e-07 | 0.020692 | 0.020692 | 0.020692 | 0.99269 | -0.14009 | 0.99261 | -0.14174 | 5.6846
101 | -0.020699 | -0.0051893 | 0.020711 | 0.0051969 | 1.2529e-05 | 7.5687e-06 | 0.031017 | 0.031016 | 0.031017 | 0.99305 | -0.13327 | 0.9937 | -0.12058 | 8.521
102 | 0.0020648 | 0.00051717 | -0.0020647 | -0.00051746 | 1.0639e-07 | -2.9038e-07 | 0.0031463 | 0.0031465 | 0.0031465 | 0.97648 | -0.45253 | 0.97643 | -0.45361 | 0.86441
103 | -0.035313 | -0.0088695 | 0.035316 | 0.0088709 | 2.1734e-06 | 1.3651e-06 | 0.053388 | 0.053388 | 0.053388 | 0.98438 | -0.30023 | 0.98445 | -0.29894 | 14.6669
104 | -0.036297 | -0.0091169 | 0.036317 | 0.009129 | 1.9332e-05 | 1.2155e-05 | 0.054871 | 0.054871 | 0.054871 | 0.98445 | -0.29894 | 0.98502 | -0.28779 | 15.0746
105 | 0.069706 | 0.017528 | -0.069652 | -0.017494 | 5.3582e-05 | 3.4121e-05 | 0.10414 | 0.10414 | 0.10414 | 0.99623 | -0.071783 | 0.9954 | -0.087891 | 28.6089
106 | -0.2244 | -0.056897 | 0.22476 | 0.057124 | 0.00035709 | 0.00022754 | 0.33541 | 0.33541 | 0.33541 | 0.99623 | -0.071783 | 0.99796 | -0.038734 | 30.7152
107 | 0.03216 | 0.0080733 | -0.032147 | -0.0080652 | 1.2979e-05 | 8.1122e-06 | 0.048081 | 0.048081 | 0.048081 | 0.9954 | -0.087891 | 0.99496 | -0.096356 | 13.209
108 | 0.037492 | 0.0094209 | -0.037472 | -0.0094084 | 1.9875e-05 | 1.2501e-05 | 0.056056 | 0.056056 | 0.056056 | 0.9954 | -0.087891 | 0.99482 | -0.099003 | 15.3999
109 | -0.2333 | -0.059264 | 0.23374 | 0.059542 | 0.00043588 | 0.00027783 | 0.34814 | 0.34814 | 0.34814 | 0.99796 | -0.038734 | 1 | 0 | 31.8812
110 | 0.028416 | 0.0071301 | -0.028395 | -0.007117 | 2.1108e-05 | 1.3105e-05 | 0.0425 | 0.042501 | 0.042501 | 0.99496 | -0.096356 | 0.99415 | -0.11195 | 11.676
111 | 0.030023 | 0.0075414 | -0.030001 | -0.0075278 | 2.175e-05 | 1.3547e-05 | 0.044913 | 0.044913 | 0.044913 | 0.99482 | -0.099003 | 0.99403 | -0.1142 | 12.3388
112 | 0.33562 | 0.086246 | -0.33436 | -0.08544 | 0.0012613 | 0.00080566 | 0.50017 | 0.50017 | 0.50017 | 1 | 0 | 0.9959 | -0.077685 | 45.803
113 | -0.32875 | -0.083964 | 0.32893 | 0.084078 | 0.00017859 | 0.00011407 | 0.49205 | 0.49205 | 0.49205 | 0.99531 | -0.088916 | 0.9959 | -0.077685 | 45.0596
114 | 0.014882 | 0.0037305 | -0.014882 | -0.0037301 | 7.0095e-07 | 3.9977e-07 | 0.022276 | 0.022276 | 0.022276 | 0.99415 | -0.11195 | 0.9941 | -0.11293 | 6.1197
115 | 0.026504 | 0.0066514 | -0.026501 | -0.0066497 | 2.7679e-06 | 1.7107e-06 | 0.039679 | 0.039679 | 0.039679 | 0.99403 | -0.1142 | 0.99392 | -0.11639 | 10.9007
116 | 0.091916 | 0.023323 | -0.091843 | -0.023277 | 7.2997e-05 | 4.5559e-05 | 0.13881 | 0.13881 | 0.13881 | 0.98604 | -0.26676 | 0.98518 | -0.28329 | 12.7117
117 | 0.089633 | 0.022724 | -0.089554 | -0.022674 | 7.9423e-05 | 4.951e-05 | 0.13547 | 0.13547 | 0.13547 | 0.98518 | -0.28329 | 0.98423 | -0.30174 | 12.4061
118 | 0.086817 | 0.021988 | -0.086802 | -0.021979 | 1.4636e-05 | 9.1081e-06 | 0.13134 | 0.13134 | 0.13134 | 0.98423 | -0.30174 | 0.98405 | -0.30525 | 12.0272
119 | 0.072498 | 0.018394 | -0.072455 | -0.018368 | 4.2804e-05 | 2.6311e-05 | 0.10971 | 0.10971 | 0.10971 | 0.98405 | -0.30525 | 0.98342 | -0.31754 | 10.0465
120 | 0.066301 | 0.016825 | -0.066266 | -0.016804 | 3.4495e-05 | 2.1035e-05 | 0.1004 | 0.1004 | 0.1004 | 0.98342 | -0.31754 | 0.98286 | -0.32836 | 9.1938
121 | 0.054858 | 0.013945 | -0.054852 | -0.013941 | 6.6578e-06 | 3.968e-06 | 0.083125 | 0.083125 | 0.083125 | 0.98286 | -0.32836 | 0.98273 | -0.33088 | 7.6122
122 | 0.054852 | 0.013941 | -0.054831 | -0.013929 | 2.0317e-05 | 1.2109e-05 | 0.083125 | 0.083125 | 0.083125 | 0.98273 | -0.33088 | 0.98233 | -0.33857 | 7.6122
123 | 0.007668 | 0.001922 | -0.0076663 | -0.0019214 | 1.7126e-06 | 6.4706e-07 | 0.01148 | 0.01148 | 0.01148 | 0.99392 | -0.11645 | 0.99368 | -0.12113 | 3.1539
124 | -0.007668 | -0.001922 | 0.0076693 | 0.0019225 | 1.2825e-06 | 4.8441e-07 | 0.01148 | 0.01148 | 0.01148 | 0.99392 | -0.11645 | 0.9941 | -0.11293 | 3.1539
125 | 0.0018293 | 0.00045811 | -0.0018292 | -0.00045843 | 8.3509e-08 | -3.2869e-07 | 0.0027433 | 0.0027434 | 0.0027434 | 0.99218 | -0.14997 | 0.99213 | -0.15093 | 0.75369
126 | 0.024157 | 0.0060621 | -0.024152 | -0.0060592 | 4.83e-06 | 2.9636e-06 | 0.036169 | 0.036169 | 0.036169 | 0.99392 | -0.11639 | 0.9937 | -0.12058 | 9.9364

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57958 | 0.14794

## res_load
| p_mw | q_mvar
0 | 0.0032269 | 0.00080875
1 | 0.0035144 | 0.00088079
2 | 0.010697 | 0.002681
3 | 0.010109 | 0.0025335
4 | 0.0097096 | 0.0024335
5 | 0.0060189 | 0.0015085
6 | 0.0070533 | 0.0017677
7 | 0.0060078 | 0.0015057
8 | 0.0048698 | 0.0012205
9 | 0.0054854 | 0.0013748
10 | 0.0063234 | 0.0015848
11 | 0.0094842 | 0.002377
12 | 0.00066358 | 0.00016631
13 | 0.0067126 | 0.0016823
14 | 0.0037796 | 0.00094727
15 | 0.0036195 | 0.00090712
16 | 0.0020993 | 0.00052614
17 | 0.010385 | 0.0026028
18 | 0.010521 | 0.0026368
19 | 0.0064476 | 0.0016159
20 | 0.0029072 | 0.00072862
21 | 0.0013219 | 0.0003313
22 | 0.0026795 | 0.00067154
23 | 0.0030567 | 0.00076607
24 | 0.0073408 | 0.0018398
25 | 0.0077804 | 0.00195
26 | 0.016269 | 0.0040774
27 | 0.0087405 | 0.0021906
28 | 0.0064069 | 0.0016057
29 | 0.0097514 | 0.0024439
30 | 0.0012462 | 0.00031233
31 | 0.013215 | 0.0033119
32 | 0.011732 | 0.0029404
33 | 0.002252 | 0.00056441
34 | 0.0037279 | 0.00093429
35 | 0.0070914 | 0.0017773
36 | 0.003683 | 0.00092303
37 | 0.0071428 | 0.0017902
38 | 0.0018505 | 0.00046379
39 | 0.0040331 | 0.0010108
40 | 0.0030378 | 0.00076136
41 | 0.0018203 | 0.0004562
42 | 0.0025566 | 0.00064073
43 | 0.0055159 | 0.0013824
44 | 0.0023388 | 0.00058615
45 | 0.001349 | 0.00033808
46 | 0.0024305 | 0.00060915
47 | 0.0024383 | 0.00061109
48 | 0.0014677 | 0.00036783
49 | 0.0025382 | 0.00063613
50 | 0.0034007 | 0.0008523
51 | 0.0021712 | 0.00054415
52 | 0.009358 | 0.0023453
53 | 0.014859 | 0.0037239
54 | 0.0028727 | 0.00071996
55 | 0.003609 | 0.00090449
56 | 0.0024576 | 0.00061594
57 | 0.00076462 | 0.00019163
58 | 0.0042607 | 0.0010678
59 | 0.014492 | 0.003632
60 | 0.0016192 | 0.0004058
61 | 0.0028251 | 0.00070804
62 | 0.010151 | 0.0025441
63 | 0.0071924 | 0.0018026
64 | 0.0068904 | 0.0017269
65 | 0.00064196 | 0.00016089
66 | 0.0074094 | 0.001857
67 | 0.0049714 | 0.001246
68 | 0.00098166 | 0.00024603
69 | 0.0085402 | 0.0021404
70 | 0.0037312 | 0.00093513
71 | 0.0074495 | 0.001867
72 | 0.0085748 | 0.002149
73 | 0.00085134 | 0.00021337
74 | 0.022807 | 0.0057159
75 | 0.0054328 | 0.0013616
76 | 0.0020647 | 0.00051746
77 | 0.013512 | 0.0033865
78 | 0.0034969 | 0.00087639
79 | 0.046298 | 0.011603
80 | 0.0022094 | 0.00055374
81 | 0.0027369 | 0.00068593
82 | 0.014304 | 0.003585
83 | 0.0061545 | 0.0015425
84 | 0.011408 | 0.0028591
85 | 0.0048871 | 0.0012248
86 | 0.0059369 | 0.0014879
87 | 0.0076663 | 0.0019214
88 | 0.0072123 | 0.0018076
89 | 0.0015769 | 0.00039521
90 | 0.0023446 | 0.0005876
91 | 0.0034406 | 0.0008623
92 | 0.0018292 | 0.00045843

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1