## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-10_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_161-10_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_161-10_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_161-10_0_4_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_161-10_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_161-10_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_161-10_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_161-10_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_161-10_0_4_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_161-10_0_4_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_161-10_0_4_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_161-10_0_4_node_54 | 0.4 | n |  | TRUE
14 | bus_LV_161-10_0_4_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_161-10_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_161-10_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_161-10_0_4_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_161-10_0_4_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_161-10_0_4_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_161-10_0_4_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_161-10_0_4_node_55 | 0.4 | n |  | TRUE
22 | bus_LV_161-10_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_161-10_0_4_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_161-10_0_4_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_161-10_0_4_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_161-10_0_4_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_161-10_0_4_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_161-10_0_4_node_47 | 0.4 | n |  | TRUE
29 | bus_LV_161-10_0_4_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_161-10_0_4_node_51 | 0.4 | n |  | TRUE
31 | bus_LV_161-10_0_4_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_161-10_0_4_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_161-10_0_4_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_161-10_0_4_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_161-10_0_4_node_67 | 0.4 | n |  | TRUE
36 | bus_LV_161-10_0_4_node_125 | 0.4 | n |  | TRUE
37 | bus_LV_161-10_0_4_node_155 | 0.4 | n |  | TRUE
38 | bus_LV_161-10_0_4_node_124 | 0.4 | n |  | TRUE
39 | bus_LV_161-10_0_4_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_161-10_0_4_node_58 | 0.4 | n |  | TRUE
41 | bus_LV_161-10_0_4_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_161-10_0_4_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_161-10_0_4_node_134 | 0.4 | n |  | TRUE
44 | bus_LV_161-10_0_4_node_138 | 0.4 | n |  | TRUE
45 | bus_LV_161-10_0_4_node_76 | 0.4 | n |  | TRUE
46 | bus_LV_161-10_0_4_node_77 | 0.4 | n |  | TRUE
47 | bus_LV_161-10_0_4_node_78 | 0.4 | n |  | TRUE
48 | bus_LV_161-10_0_4_node_80 | 0.4 | n |  | TRUE
49 | bus_LV_161-10_0_4_node_81 | 0.4 | n |  | TRUE
50 | bus_LV_161-10_0_4_node_137 | 0.4 | n |  | TRUE
51 | bus_LV_161-10_0_4_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_161-10_0_4_node_135 | 0.4 | n |  | TRUE
53 | bus_LV_161-10_0_4_node_140 | 0.4 | n |  | TRUE
54 | bus_LV_161-10_0_4_node_132 | 0.4 | n |  | TRUE
55 | bus_LV_161-10_0_4_node_151 | 0.4 | n |  | TRUE
56 | bus_LV_161-10_0_4_node_136 | 0.4 | n |  | TRUE
57 | bus_LV_161-10_0_4_node_144 | 0.4 | n |  | TRUE
58 | bus_LV_161-10_0_4_node_130 | 0.4 | n |  | TRUE
59 | bus_LV_161-10_0_4_node_121 | 0.4 | n |  | TRUE
60 | bus_LV_161-10_0_4_node_122 | 0.4 | n |  | TRUE
61 | bus_LV_161-10_0_4_node_123 | 0.4 | n |  | TRUE
62 | bus_LV_161-10_0_4_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_161-10_0_4_node_127 | 0.4 | n |  | TRUE
64 | bus_LV_161-10_0_4_node_131 | 0.4 | n |  | TRUE
65 | bus_LV_161-10_0_4_node_139 | 0.4 | n |  | TRUE
66 | bus_LV_161-10_0_4_node_143 | 0.4 | n |  | TRUE
67 | bus_LV_161-10_0_4_node_129 | 0.4 | n |  | TRUE
68 | bus_LV_161-10_0_4_node_142 | 0.4 | n |  | TRUE
69 | bus_LV_161-10_0_4_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_161-10_0_4_node_133 | 0.4 | n |  | TRUE
71 | bus_LV_161-10_0_4_node_152 | 0.4 | n |  | TRUE
72 | bus_LV_161-10_0_4_node_145 | 0.4 | n |  | TRUE
73 | bus_LV_161-10_0_4_node_146 | 0.4 | n |  | TRUE
74 | bus_LV_161-10_0_4_node_149 | 0.4 | n |  | TRUE
75 | bus_LV_161-10_0_4_node_154 | 0.4 | n |  | TRUE
76 | bus_LV_161-10_0_4_node_153 | 0.4 | n |  | TRUE
77 | bus_MV_494_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-10_0_4_load_0 | 0 | 0.0054057 | 0.0013548 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-10_0_4_load_3 | 2 | 0.001481 | 0.00037117 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-10_0_4_load_5 | 3 | 0.0019054 | 0.00047754 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-10_0_4_load_6 | 4 | 0.0021542 | 0.0005399 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-10_0_4_load_21 | 5 | 0.0017991 | 0.0004509 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-10_0_4_load_7 | 6 | 0.0051467 | 0.0012899 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-10_0_4_load_19 | 7 | 0.0014112 | 0.00035368 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-10_0_4_load_18 | 8 | 0.0015629 | 0.00039169 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-10_0_4_load_22 | 10 | 0.0012797 | 0.00032072 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-10_0_4_load_23 | 11 | 0.0015959 | 0.00039998 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-10_0_4_load_35 | 12 | 0.0012236 | 0.00030665 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-10_0_4_load_54 | 13 | 0.0009056 | 0.00022697 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-10_0_4_load_53 | 14 | 0.0010673 | 0.00026749 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-10_0_4_load_25 | 15 | 0.0022388 | 0.00056111 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-10_0_4_load_27 | 16 | 0.002964 | 0.00074285 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-10_0_4_load_31 | 17 | 0.0021242 | 0.00053237 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-10_0_4_load_29 | 18 | 0.0023649 | 0.00059269 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-10_0_4_load_56 | 19 | 0.0028411 | 0.00071206 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-10_0_4_load_32 | 20 | 0.002368 | 0.00059348 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-10_0_4_load_55 | 21 | 0.0022528 | 0.00056461 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-10_0_4_load_42 | 23 | 0.0022625 | 0.00056703 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-10_0_4_load_41 | 24 | 0.0021007 | 0.00052648 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-10_0_4_load_44 | 26 | 0.0015747 | 0.00039465 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-10_0_4_load_47 | 28 | 0.0039643 | 0.00099355 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-10_0_4_load_51 | 30 | 0.024216 | 0.0060692 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-10_0_4_load_49 | 32 | 0.026446 | 0.0066281 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-10_0_4_load_48 | 33 | 0.023186 | 0.0058111 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-10_0_4_load_68 | 34 | 0.0065629 | 0.0016448 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-10_0_4_load_67 | 35 | 0.017441 | 0.0043711 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-10_0_4_load_125 | 36 | 0.0061217 | 0.0015343 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-10_0_4_load_155 | 37 | 0.0039627 | 0.00099314 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-10_0_4_load_57 | 39 | 0.0046794 | 0.0011728 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-10_0_4_load_58 | 40 | 0.0048824 | 0.0012236 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-10_0_4_load_59 | 41 | 0.0046412 | 0.0011632 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-10_0_4_load_60 | 42 | 0.0042313 | 0.0010605 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-10_0_4_load_134 | 43 | 0.0051409 | 0.0012884 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-10_0_4_load_138 | 44 | 0.0037914 | 0.00095022 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-10_0_4_load_76 | 45 | 0.0038421 | 0.00096293 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-10_0_4_load_77 | 46 | 0.0016448 | 0.00041223 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-10_0_4_load_80 | 48 | 0.002986 | 0.00074837 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-10_0_4_load_137 | 50 | 0.0067674 | 0.0016961 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-10_0_4_load_135 | 52 | 0.010759 | 0.0026965 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-10_0_4_load_140 | 53 | 0.0018471 | 0.00046294 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-10_0_4_load_132 | 54 | 0.0059849 | 0.0015 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-10_0_4_load_151 | 55 | 0.0029646 | 0.00074299 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-10_0_4_load_136 | 56 | 0.0021404 | 0.00053645 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-10_0_4_load_144 | 57 | 0.0024438 | 0.00061248 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-10_0_4_load_121 | 59 | 0.0056802 | 0.0014236 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-10_0_4_load_122 | 60 | 0.0043367 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-10_0_4_load_123 | 61 | 0.0033056 | 0.00082846 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-10_0_4_load_127 | 63 | 0.006284 | 0.0015749 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-10_0_4_load_131 | 64 | 0.0024209 | 0.00060674 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-10_0_4_load_139 | 65 | 0.0034135 | 0.0008555 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-10_0_4_load_143 | 66 | 0.006041 | 0.001514 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-10_0_4_load_129 | 67 | 0.0023727 | 0.00059466 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-10_0_4_load_142 | 68 | 0.0023039 | 0.0005774 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-10_0_4_load_128 | 69 | 0.0059326 | 0.0014869 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-10_0_4_load_133 | 70 | 0.0018923 | 0.00047425 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-10_0_4_load_152 | 71 | 0.0042989 | 0.0010774 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-10_0_4_load_145 | 72 | 0.0022382 | 0.00056094 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-10_0_4_load_146 | 73 | 0.0038062 | 0.00095392 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-10_0_4_load_149 | 74 | 0.0026885 | 0.00067379 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-10_0_4_load_153 | 76 | 0.0077284 | 0.0019369 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-10_0_4_line_0 |  | 0 | 1 | 0.020354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-10_0_4_line_1 |  | 1 | 2 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-10_0_4_line_2 |  | 1 | 3 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_161-10_0_4_line_3 |  | 2 | 4 | 0.013996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-10_0_4_line_4 |  | 3 | 5 | 0.00033215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_161-10_0_4_line_5 |  | 4 | 6 | 0.0028431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_161-10_0_4_line_6 |  | 5 | 7 | 0.011247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-10_0_4_line_7 |  | 7 | 8 | 0.010736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_161-10_0_4_line_8 |  | 8 | 9 | 0.015441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_161-10_0_4_line_9 |  | 9 | 10 | 0.041781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-10_0_4_line_10 |  | 9 | 11 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-10_0_4_line_11 |  | 10 | 12 | 0.0078235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_161-10_0_4_line_12 |  | 11 | 13 | 0.0098634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_161-10_0_4_line_13 |  | 13 | 14 | 0.0077209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-10_0_4_line_14 |  | 14 | 22 | 0.013514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-10_0_4_line_15 |  | 15 | 16 | 0.0085494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-10_0_4_line_16 |  | 16 | 17 | 0.00082874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_161-10_0_4_line_17 |  | 17 | 20 | 0.0098185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_161-10_0_4_line_18 |  | 18 | 19 | 0.0077089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-10_0_4_line_19 |  | 19 | 21 | 0.0023897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-10_0_4_line_20 |  | 20 | 22 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-10_0_4_line_21 |  | 21 | 39 | 0.020152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-10_0_4_line_22 |  | 22 | 23 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-10_0_4_line_23 |  | 23 | 24 | 0.015755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_161-10_0_4_line_24 |  | 24 | 25 | 0.0086674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_161-10_0_4_line_25 |  | 25 | 26 | 0.032912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_161-10_0_4_line_26 |  | 25 | 27 | 0.092709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_161-10_0_4_line_27 |  | 26 | 28 | 0.01176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_161-10_0_4_line_28 |  | 27 | 29 | 0.0334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_161-10_0_4_line_29 |  | 27 | 30 | 0.013097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_161-10_0_4_line_30 |  | 27 | 31 | 0.076487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_161-10_0_4_line_31 |  | 27 | 32 | 0.01332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_161-10_0_4_line_32 |  | 28 | 33 | 0.0092701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_161-10_0_4_line_33 |  | 29 | 34 | 0.0179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-10_0_4_line_34 |  | 29 | 35 | 0.012344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_161-10_0_4_line_35 |  | 31 | 36 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_161-10_0_4_line_36 |  | 33 | 37 | 0.0019458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_161-10_0_4_line_37 |  | 36 | 38 | 0.013072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_161-10_0_4_line_38 |  | 38 | 62 | 0.056736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_161-10_0_4_line_39 |  | 38 | 63 | 0.020766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-10_0_4_line_40 |  | 38 | 60 | 0.021212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_161-10_0_4_line_41 |  | 39 | 40 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_161-10_0_4_line_42 |  | 40 | 41 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_161-10_0_4_line_43 |  | 41 | 42 | 0.013246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_161-10_0_4_line_44 |  | 42 | 43 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_161-10_0_4_line_45 |  | 43 | 44 | 0.021299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_161-10_0_4_line_46 |  | 44 | 62 | 0.019823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_161-10_0_4_line_47 |  | 45 | 46 | 0.0027636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-10_0_4_line_48 |  | 45 | 47 | 0.044647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-10_0_4_line_49 |  | 47 | 48 | 0.014857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-10_0_4_line_50 |  | 47 | 49 | 0.018818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-10_0_4_line_51 |  | 49 | 50 | 0.03139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-10_0_4_line_52 |  | 49 | 51 | 0.021775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-10_0_4_line_53 |  | 49 | 52 | 0.050423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-10_0_4_line_54 |  | 50 | 55 | 0.010087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_161-10_0_4_line_55 |  | 51 | 53 | 0.024286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_161-10_0_4_line_56 |  | 51 | 54 | 0.017918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_161-10_0_4_line_57 |  | 52 | 56 | 0.0035143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-10_0_4_line_58 |  | 53 | 57 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_161-10_0_4_line_59 |  | 54 | 58 | 0.041226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-10_0_4_line_60 |  | 55 | 71 | 0.034951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-10_0_4_line_61 |  | 57 | 72 | 0.01074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-10_0_4_line_62 |  | 58 | 70 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-10_0_4_line_63 |  | 58 | 69 | 0.015992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-10_0_4_line_64 |  | 59 | 60 | 0.019554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_161-10_0_4_line_65 |  | 59 | 61 | 0.0084263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_161-10_0_4_line_66 |  | 62 | 64 | 0.012212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_161-10_0_4_line_67 |  | 62 | 65 | 0.016904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-10_0_4_line_68 |  | 63 | 66 | 0.00021464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-10_0_4_line_69 |  | 64 | 67 | 0.01187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-10_0_4_line_70 |  | 65 | 68 | 0.026648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_161-10_0_4_line_71 |  | 67 | 69 | 0.0099159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_161-10_0_4_line_72 |  | 71 | 75 | 0.0080478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-10_0_4_line_73 |  | 72 | 73 | 0.0025392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-10_0_4_line_74 |  | 74 | 75 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-10_0_4_line_75 |  | 75 | 76 | 0.026384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-10_0_4_trafo_58 | 0.63 MVA 20/0.4 kV | 77 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2686107.9703 | 1243628.9195 | 2686095.8699 | 1243645.2867
1 | 2686107.9703 | 1243628.9195 | 2686090.8635 | 1243616.8557
2 | 2686107.9703 | 1243628.9195 | 2686112.7323 | 1243632.0354 | 2686119.6186 | 1243636.0173
3 | 2686080.7074 | 1243607.3132 | 2686087.38 | 1243614.3991 | 2686090.8635 | 1243616.8557
4 | 2686119.6186 | 1243636.0173 | 2686119.9061 | 1243636.1836
5 | 2686080.7074 | 1243607.3132 | 2686078.7583 | 1243605.2433
6 | 2686119.9061 | 1243636.1836 | 2686129.6428 | 1243641.8139
7 | 2686129.6428 | 1243641.8139 | 2686138.9371 | 1243647.1883
8 | 2686152.2859 | 1243654.9485 | 2686148.8085 | 1243652.8965 | 2686138.9371 | 1243647.1883
9 | 2686152.2859 | 1243654.9485 | 2686169.8096 | 1243617.0201
10 | 2686152.2859 | 1243654.9485 | 2686155.4126 | 1243656.684 | 2686165.486 | 1243662.2619
11 | 2686173.0909 | 1243609.918 | 2686169.8096 | 1243617.0201
12 | 2686165.486 | 1243662.2619 | 2686174.1149 | 1243667.0398
13 | 2686180.8694 | 1243670.7799 | 2686174.1149 | 1243667.0398
14 | 2686192.9272 | 1243676.8436 | 2686188.202 | 1243674.8401 | 2686180.8694 | 1243670.7799
15 | 2686225.6668 | 1243693.3388 | 2686223.8341 | 1243692.4262 | 2686221.4051 | 1243690.534 | 2686218.3201 | 1243689.0509
16 | 2686217.5732 | 1243688.6919 | 2686218.3201 | 1243689.0509
17 | 2686208.7242 | 1243684.4378 | 2686217.5732 | 1243688.6919
18 | 2686251.5009 | 1243770.1089 | 2686247.5135 | 1243776.7064
19 | 2686246.2774 | 1243778.7516 | 2686247.5135 | 1243776.7064
20 | 2686192.9272 | 1243676.8436 | 2686208.7242 | 1243684.4378
21 | 2686246.2774 | 1243778.7516 | 2686235.8535 | 1243795.9986
22 | 2686192.9272 | 1243676.8436 | 2686185.8306 | 1243690.8927
23 | 2686177.2819 | 1243704.0649 | 2686179.1537 | 1243701.9397 | 2686184.1175 | 1243694.284 | 2686185.8306 | 1243690.8927
24 | 2686171.553 | 1243710.569 | 2686177.2819 | 1243704.0649
25 | 2686171.553 | 1243710.569 | 2686200.2116 | 1243726.7514
26 | 2686142.2058 | 1243772.8552 | 2686133.5902 | 1243770.7064 | 2686134.4254 | 1243763.68 | 2686132.3655 | 1243732.2159 | 2686167.1724 | 1243715.5424 | 2686171.553 | 1243710.569
27 | 2686205.1565 | 1243734.0088 | 2686207.0659 | 1243730.6217 | 2686200.2116 | 1243726.7514
28 | 2686173.9326 | 1243783.4792 | 2686149.7142 | 1243774.7323 | 2686142.2058 | 1243772.8552
29 | 2686142.2058 | 1243772.8552 | 2686141.7334 | 1243778.319 | 2686139.424 | 1243785.5735
30 | 2686116.2897 | 1243835.2026 | 2686121.7808 | 1243825.0526 | 2686121.4597 | 1243820.6225 | 2686122.1709 | 1243818.4868 | 2686124.7628 | 1243811.7639 | 2686129.7028 | 1243796.8914 | 2686131.3614 | 1243789.3766 | 2686132.3333 | 1243781.2625 | 2686133.5902 | 1243770.7064 | 2686142.2058 | 1243772.8552
31 | 2686142.2058 | 1243772.8552 | 2686144.4805 | 1243765.594 | 2686144.9 | 1243759.8985
32 | 2686200.6042 | 1243742.0842 | 2686205.1565 | 1243734.0088
33 | 2686173.9326 | 1243783.4792 | 2686166.2075 | 1243799.6344
34 | 2686173.9326 | 1243783.4792 | 2686179.6268 | 1243772.527
35 | 2686116.2897 | 1243835.2026 | 2686121.2712 | 1243837.243 | 2686131.814 | 1243843.8233
36 | 2686199.6487 | 1243743.7792 | 2686200.6042 | 1243742.0842
37 | 2686142.9034 | 1243850.7447 | 2686131.814 | 1243843.8233
38 | 2686191.7915 | 1243879.7759 | 2686150.3412 | 1243855.3894 | 2686142.9034 | 1243850.7447
39 | 2686142.9034 | 1243850.7447 | 2686155.0256 | 1243833.8842
40 | 2686142.9034 | 1243850.7447 | 2686142.8514 | 1243855.3584 | 2686137.0199 | 1243870.8983
41 | 2686228.7342 | 1243807.778 | 2686235.8535 | 1243795.9986
42 | 2686228.7342 | 1243807.778 | 2686227.6792 | 1243809.5235 | 2686221.4692 | 1243820.8206
43 | 2686221.4692 | 1243820.8206 | 2686215.0885 | 1243832.4285
44 | 2686209.4695 | 1243842.6505 | 2686215.0885 | 1243832.4285
45 | 2686200.2707 | 1243861.8577 | 2686208.6815 | 1243844.0839 | 2686209.4695 | 1243842.6505
46 | 2686191.7915 | 1243879.7759 | 2686200.2707 | 1243861.8577
47 | 2686322.5538 | 1243823.8882 | 2686321.1801 | 1243826.2861
48 | 2686305.9764 | 1243866.0921 | 2686303.8956 | 1243858.9789 | 2686304.1504 | 1243856.0138 | 2686321.1801 | 1243826.2861
49 | 2686305.9764 | 1243866.0921 | 2686320.3004 | 1243862.1474
50 | 2686305.9764 | 1243866.0921 | 2686295.6407 | 1243868.9328 | 2686296.2152 | 1243872.566 | 2686296.709 | 1243874.9861 | 2686296.8243 | 1243876.9337
51 | 2686296.8243 | 1243876.9337 | 2686299.9317 | 1243878.4244 | 2686315.6187 | 1243901.5497
52 | 2686282.8869 | 1243873.8176 | 2686289.8166 | 1243870.7828 | 2686295.6407 | 1243868.9328 | 2686296.2152 | 1243872.566 | 2686296.709 | 1243874.9861 | 2686296.8243 | 1243876.9337
53 | 2686296.8243 | 1243876.9337 | 2686294.0565 | 1243883.7873 | 2686280.191 | 1243924.5236
54 | 2686315.6187 | 1243901.5497 | 2686321.2814 | 1243909.8976
55 | 2686282.8869 | 1243873.8176 | 2686277.1623 | 1243861.0361 | 2686276.7454 | 1243853.847 | 2686277.7063 | 1243850.9213
56 | 2686282.8869 | 1243873.8176 | 2686276.1955 | 1243878.1346 | 2686267.9537 | 1243883.7178
57 | 2686279.0586 | 1243927.8505 | 2686280.191 | 1243924.5236
58 | 2686281.1433 | 1243840.4567 | 2686277.7063 | 1243850.9213
59 | 2686233.8223 | 1243906.8397 | 2686267.9537 | 1243883.7178
60 | 2686321.2814 | 1243909.8976 | 2686330.1139 | 1243922.9183 | 2686340.0331 | 1243931.5467 | 2686345.1728 | 1243934.777
61 | 2686281.1433 | 1243840.4567 | 2686284.4944 | 1243830.2534
62 | 2686233.8223 | 1243906.8397 | 2686215.8049 | 1243917.5456
63 | 2686233.8223 | 1243906.8397 | 2686220.3765 | 1243898.1819
64 | 2686130.1497 | 1243889.2059 | 2686137.0199 | 1243870.8983
65 | 2686127.1892 | 1243897.095 | 2686130.1497 | 1243889.2059
66 | 2686191.7915 | 1243879.7759 | 2686202.0594 | 1243886.3875
67 | 2686191.7915 | 1243879.7759 | 2686185.3592 | 1243895.4081
68 | 2686155.1509 | 1243833.71 | 2686155.0256 | 1243833.8842
69 | 2686202.0594 | 1243886.3875 | 2686212.0395 | 1243892.8137
70 | 2686176.3488 | 1243920.4781 | 2686176.6286 | 1243919.3736 | 2686184.3326 | 1243897.9031 | 2686185.3592 | 1243895.4081
71 | 2686220.3765 | 1243898.1819 | 2686212.0395 | 1243892.8137
72 | 2686351.9866 | 1243939.0595 | 2686345.1728 | 1243934.777
73 | 2686285.2867 | 1243827.841 | 2686284.4944 | 1243830.2534
74 | 2686351.9866 | 1243939.0595 | 2686359.8369 | 1243927.4003
75 | 2686351.9866 | 1243939.0595 | 2686377.1146 | 1243947.1027

## bus_geodata
| x | y | coords
0 | 2686095.8699 | 1243645.2867
1 | 2686107.9703 | 1243628.9195
2 | 2686090.8635 | 1243616.8557
3 | 2686119.6186 | 1243636.0173
4 | 2686080.7074 | 1243607.3132
5 | 2686119.9061 | 1243636.1836
6 | 2686078.7583 | 1243605.2433
7 | 2686129.6428 | 1243641.8139
8 | 2686138.9371 | 1243647.1883
9 | 2686152.2859 | 1243654.9485
10 | 2686169.8096 | 1243617.0201
11 | 2686165.486 | 1243662.2619
12 | 2686173.0909 | 1243609.918
13 | 2686174.1149 | 1243667.0398
14 | 2686180.8694 | 1243670.7799
15 | 2686225.6668 | 1243693.3388
16 | 2686218.3201 | 1243689.0509
17 | 2686217.5732 | 1243688.6919
18 | 2686251.5009 | 1243770.1089
19 | 2686247.5135 | 1243776.7064
20 | 2686208.7242 | 1243684.4378
21 | 2686246.2774 | 1243778.7516
22 | 2686192.9272 | 1243676.8436
23 | 2686185.8306 | 1243690.8927
24 | 2686177.2819 | 1243704.0649
25 | 2686171.553 | 1243710.569
26 | 2686200.2116 | 1243726.7514
27 | 2686142.2058 | 1243772.8552
28 | 2686205.1565 | 1243734.0088
29 | 2686173.9326 | 1243783.4792
30 | 2686139.424 | 1243785.5735
31 | 2686116.2897 | 1243835.2026
32 | 2686144.9 | 1243759.8985
33 | 2686200.6042 | 1243742.0842
34 | 2686166.2075 | 1243799.6344
35 | 2686179.6268 | 1243772.527
36 | 2686131.814 | 1243843.8233
37 | 2686199.6487 | 1243743.7792
38 | 2686142.9034 | 1243850.7447
39 | 2686235.8535 | 1243795.9986
40 | 2686228.7342 | 1243807.778
41 | 2686221.4692 | 1243820.8206
42 | 2686215.0885 | 1243832.4285
43 | 2686209.4695 | 1243842.6505
44 | 2686200.2707 | 1243861.8577
45 | 2686321.1801 | 1243826.2861
46 | 2686322.5538 | 1243823.8882
47 | 2686305.9764 | 1243866.0921
48 | 2686320.3004 | 1243862.1474
49 | 2686296.8243 | 1243876.9337
50 | 2686315.6187 | 1243901.5497
51 | 2686282.8869 | 1243873.8176
52 | 2686280.191 | 1243924.5236
53 | 2686277.7063 | 1243850.9213
54 | 2686267.9537 | 1243883.7178
55 | 2686321.2814 | 1243909.8976
56 | 2686279.0586 | 1243927.8505
57 | 2686281.1433 | 1243840.4567
58 | 2686233.8223 | 1243906.8397
59 | 2686130.1497 | 1243889.2059
60 | 2686137.0199 | 1243870.8983
61 | 2686127.1892 | 1243897.095
62 | 2686191.7915 | 1243879.7759
63 | 2686155.0256 | 1243833.8842
64 | 2686202.0594 | 1243886.3875
65 | 2686185.3592 | 1243895.4081
66 | 2686155.1509 | 1243833.71
67 | 2686212.0395 | 1243892.8137
68 | 2686176.3488 | 1243920.4781
69 | 2686220.3765 | 1243898.1819
70 | 2686215.8049 | 1243917.5456
71 | 2686345.1728 | 1243934.777
72 | 2686284.4944 | 1243830.2534
73 | 2686285.2867 | 1243827.841
74 | 2686359.8369 | 1243927.4003
75 | 2686351.9866 | 1243939.0595
76 | 2686377.1146 | 1243947.1027
77 | 2686191.7915 | 1243879.7759

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97362 | -0.50943 | 0.0054057 | 0.0013548
1 | 0.97372 | -0.5074 | 0 | 0
2 | 0.97355 | -0.51079 | 0.001481 | 0.00037117
3 | 0.9739 | -0.50385 | 0.0019054 | 0.00047754
4 | 0.97346 | -0.51266 | 0.0021542 | 0.0005399
5 | 0.97391 | -0.50375 | 0.0017991 | 0.0004509
6 | 0.97344 | -0.51293 | 0.0051467 | 0.0012899
7 | 0.97409 | -0.50005 | 0.0014112 | 0.00035368
8 | 0.97429 | -0.49624 | 0.0015629 | 0.00039169
9 | 0.97459 | -0.49033 | 0 | 0
10 | 0.97449 | -0.49225 | 0.0012797 | 0.00032072
11 | 0.97492 | -0.48386 | 0.0015959 | 0.00039998
12 | 0.97448 | -0.49242 | 0.0012236 | 0.00030665
13 | 0.97515 | -0.47934 | 0.0009056 | 0.00022697
14 | 0.97533 | -0.47568 | 0.0010673 | 0.00026749
15 | 0.97542 | -0.47387 | 0.0022388 | 0.00056111
16 | 0.97544 | -0.47352 | 0.002964 | 0.00074285
17 | 0.97545 | -0.47344 | 0.0021242 | 0.00053237
18 | 0.99968 | -0.0060688 | 0.0023649 | 0.00059269
19 | 0.9997 | -0.0057508 | 0.0028411 | 0.00071206
20 | 0.97551 | -0.47212 | 0.002368 | 0.00059348
21 | 0.99971 | -0.0055339 | 0.0022528 | 0.00056461
22 | 0.97567 | -0.46901 | 0 | 0
23 | 0.97621 | -0.45846 | 0.0022625 | 0.00056703
24 | 0.97678 | -0.44725 | 0.0021007 | 0.00052648
25 | 0.97711 | -0.44076 | 0 | 0
26 | 0.97611 | -0.46042 | 0.0015747 | 0.00039465
27 | 0.98346 | -0.31684 | 0 | 0
28 | 0.97577 | -0.46712 | 0.0039643 | 0.00099355
29 | 0.98272 | -0.3313 | 0 | 0
30 | 0.98317 | -0.32256 | 0.024216 | 0.0060692
31 | 0.98872 | -0.21513 | 0 | 0
32 | 0.98314 | -0.32319 | 0.026446 | 0.0066281
33 | 0.97553 | -0.47173 | 0.023186 | 0.0058111
34 | 0.98261 | -0.33342 | 0.0065629 | 0.0016448
35 | 0.98252 | -0.33519 | 0.017441 | 0.0043711
36 | 0.98954 | -0.19944 | 0.0061217 | 0.0015343
37 | 0.97553 | -0.47187 | 0.0039627 | 0.00099314
38 | 0.99016 | -0.18746 | 0 | 0
39 | 0.99985 | -0.0029126 | 0.0046794 | 0.0011728
40 | 1 | 0 | -0.29642 | -0.075503
41 | 0.99872 | -0.024186 | 0.0046412 | 0.0011632
42 | 0.9976 | -0.045336 | 0.0042313 | 0.0010605
43 | 0.99664 | -0.063711 | 0.0051409 | 0.0012884
44 | 0.9949 | -0.096712 | 0.0037914 | 0.00095022
45 | 0.98553 | -0.27773 | 0.0038421 | 0.00096293
46 | 0.98553 | -0.27782 | 0.0016448 | 0.00041223
47 | 0.98575 | -0.27334 | 0 | 0
48 | 0.98571 | -0.27414 | 0.002986 | 0.00074837
49 | 0.9859 | -0.27048 | 0 | 0
50 | 0.98519 | -0.28425 | 0.0067674 | 0.0016961
51 | 0.98682 | -0.2526 | 0 | 0
52 | 0.9853 | -0.28215 | 0.010759 | 0.0026965
53 | 0.98659 | -0.2571 | 0.0018471 | 0.00046294
54 | 0.98775 | -0.23461 | 0.0059849 | 0.0015
55 | 0.98503 | -0.28746 | 0.0029646 | 0.00074299
56 | 0.9853 | -0.28229 | 0.0021404 | 0.00053645
57 | 0.9865 | -0.25877 | 0.0024438 | 0.00061248
58 | 0.9901 | -0.18894 | 0 | 0
59 | 0.98974 | -0.19562 | 0.0056802 | 0.0014236
60 | 0.9899 | -0.19249 | 0.0043367 | 0.0010869
61 | 0.98972 | -0.19611 | 0.0033056 | 0.00082846
62 | 0.99331 | -0.12709 | 0 | 0
63 | 0.98993 | -0.19201 | 0.006284 | 0.0015749
64 | 0.99247 | -0.14323 | 0.0024209 | 0.00060674
65 | 0.99322 | -0.1288 | 0.0034135 | 0.0008555
66 | 0.98993 | -0.19204 | 0.006041 | 0.001514
67 | 0.99168 | -0.15844 | 0.0023727 | 0.00059466
68 | 0.99317 | -0.12988 | 0.0023039 | 0.0005774
69 | 0.99105 | -0.17075 | 0.0059326 | 0.0014869
70 | 0.99007 | -0.18965 | 0.0018923 | 0.00047425
71 | 0.98456 | -0.2967 | 0.0042989 | 0.0010774
72 | 0.98644 | -0.25993 | 0.0022382 | 0.00056094
73 | 0.98643 | -0.26011 | 0.0038062 | 0.00095392
74 | 0.98445 | -0.29889 | 0.0026885 | 0.00067379
75 | 0.98448 | -0.29821 | 0 | 0
76 | 0.98429 | -0.30188 | 0.0077284 | 0.0019369
77 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0054057 | -0.0013548 | 0.0054063 | 0.0013549 | 5.2099e-07 | 8.0277e-08 | 0.0082618 | 0.0082617 | 0.0082618 | 0.97362 | -0.50943 | 0.97372 | -0.5074 | 2.2697
1 | 0.008784 | 0.0022018 | -0.0087826 | -0.0022012 | 1.4145e-06 | 6.4493e-07 | 0.013424 | 0.013424 | 0.013424 | 0.97372 | -0.5074 | 0.97355 | -0.51079 | 3.6878
2 | -0.01419 | -0.0035567 | 0.014193 | 0.0035581 | 2.4063e-06 | 1.3703e-06 | 0.021685 | 0.021685 | 0.021685 | 0.97372 | -0.5074 | 0.9739 | -0.50385 | 5.9575
3 | 0.0073016 | 0.00183 | -0.0073009 | -0.0018298 | 6.5368e-07 | 2.4434e-07 | 0.01116 | 0.01116 | 0.01116 | 0.97355 | -0.51079 | 0.97346 | -0.51266 | 3.066
4 | -0.016098 | -0.0040356 | 0.016098 | 0.0040357 | 7.5354e-08 | 4.4093e-08 | 0.024596 | 0.024596 | 0.024596 | 0.9739 | -0.50385 | 0.97391 | -0.50375 | 6.7573
5 | 0.0051467 | 0.0012899 | -0.0051467 | -0.0012899 | 6.5989e-08 | 6.8875e-09 | 0.0078672 | 0.0078672 | 0.0078672 | 0.97346 | -0.51266 | 0.97344 | -0.51293 | 2.1613
6 | -0.017897 | -0.0044866 | 0.0179 | 0.0044885 | 3.1539e-06 | 1.8785e-06 | 0.027345 | 0.027345 | 0.027345 | 0.97391 | -0.50375 | 0.97409 | -0.50005 | 7.5124
7 | -0.019312 | -0.0048421 | 0.019315 | 0.0048442 | 3.5039e-06 | 2.1089e-06 | 0.029501 | 0.029501 | 0.029501 | 0.97409 | -0.50005 | 0.97429 | -0.49624 | 8.1047
8 | -0.020878 | -0.0052359 | 0.020884 | 0.0052395 | 5.8877e-06 | 3.5758e-06 | 0.031888 | 0.031888 | 0.031888 | 0.97429 | -0.49624 | 0.97459 | -0.49033 | 8.7604
9 | 0.0025035 | 0.00062691 | -0.0025033 | -0.00062728 | 2.289e-07 | -3.7408e-07 | 0.0038222 | 0.0038224 | 0.0038224 | 0.97459 | -0.49033 | 0.97449 | -0.49225 | 1.0501
10 | -0.023387 | -0.0058664 | 0.023395 | 0.0058708 | 7.2164e-06 | 4.4304e-06 | 0.03571 | 0.03571 | 0.03571 | 0.97459 | -0.49033 | 0.97492 | -0.48386 | 9.8104
11 | 0.0012236 | 0.00030656 | -0.0012236 | -0.00030665 | 1.0241e-08 | -9.0914e-08 | 0.0018683 | 0.0018684 | 0.0018684 | 0.97449 | -0.49225 | 0.97448 | -0.49242 | 0.51329
12 | -0.02499 | -0.0062708 | 0.024996 | 0.0062741 | 5.3821e-06 | 3.3215e-06 | 0.038146 | 0.038146 | 0.038146 | 0.97492 | -0.48386 | 0.97515 | -0.47934 | 10.4796
13 | -0.025901 | -0.0065011 | 0.025906 | 0.0065039 | 4.5238e-06 | 2.7989e-06 | 0.039528 | 0.039528 | 0.039528 | 0.97515 | -0.47934 | 0.97533 | -0.47568 | 10.8592
14 | -0.026973 | -0.0067714 | 0.026982 | 0.0067767 | 8.5838e-06 | 5.3249e-06 | 0.041156 | 0.041156 | 0.041156 | 0.97533 | -0.47568 | 0.97567 | -0.46901 | 11.3066
15 | -0.0022388 | -0.00056111 | 0.0022389 | 0.00056103 | 3.7397e-08 | -8.2784e-08 | 0.0034154 | 0.0034153 | 0.0034154 | 0.97542 | -0.47387 | 0.97544 | -0.47352 | 0.93829
16 | -0.0052029 | -0.0013039 | 0.0052029 | 0.0013039 | 1.9577e-08 | 2.1844e-09 | 0.0079369 | 0.0079369 | 0.0079369 | 0.97544 | -0.47352 | 0.97545 | -0.47344 | 2.1805
17 | -0.0073271 | -0.0018363 | 0.0073276 | 0.0018364 | 4.5999e-07 | 1.7182e-07 | 0.011177 | 0.011177 | 0.011177 | 0.97545 | -0.47344 | 0.97551 | -0.47212 | 3.0707
18 | -0.0023649 | -0.00059269 | 0.0023649 | 0.00059261 | 3.582e-08 | -7.8149e-08 | 0.0035201 | 0.00352 | 0.0035201 | 0.99968 | -0.0060688 | 0.9997 | -0.0057508 | 0.96705
19 | -0.005206 | -0.0013047 | 0.0052061 | 0.0013047 | 5.3809e-08 | 3.1053e-09 | 0.0077489 | 0.0077489 | 0.0077489 | 0.9997 | -0.0057508 | 0.99971 | -0.0055339 | 2.1288
20 | -0.0096956 | -0.0024299 | 0.009697 | 0.0024306 | 1.4376e-06 | 7.0122e-07 | 0.014789 | 0.014789 | 0.014789 | 0.97551 | -0.47212 | 0.97567 | -0.46901 | 4.063
21 | -0.0074589 | -0.0018693 | 0.0074598 | 0.0018696 | 9.3146e-07 | 3.3187e-07 | 0.011102 | 0.011102 | 0.011102 | 0.99971 | -0.0055339 | 0.99985 | -0.0029126 | 3.05
22 | -0.036679 | -0.0092073 | 0.036697 | 0.009219 | 1.8474e-05 | 1.1626e-05 | 0.055945 | 0.055945 | 0.055945 | 0.97567 | -0.46901 | 0.97621 | -0.45846 | 15.3695
23 | -0.03896 | -0.009786 | 0.038981 | 0.0097991 | 2.0842e-05 | 1.3142e-05 | 0.059394 | 0.059394 | 0.059394 | 0.97621 | -0.45846 | 0.97678 | -0.44725 | 16.3169
24 | -0.041081 | -0.010326 | 0.041094 | 0.010334 | 1.2735e-05 | 8.0416e-06 | 0.062594 | 0.062594 | 0.062594 | 0.97678 | -0.44725 | 0.97711 | -0.44076 | 17.1961
25 | 0.032735 | 0.0082215 | -0.032704 | -0.0082023 | 3.0679e-05 | 1.9223e-05 | 0.049857 | 0.049857 | 0.049857 | 0.97711 | -0.44076 | 0.97611 | -0.46042 | 13.6971
26 | -0.073829 | -0.018555 | 0.074268 | 0.018835 | 0.00043962 | 0.00028019 | 0.11245 | 0.11245 | 0.11245 | 0.97711 | -0.44076 | 0.98346 | -0.31684 | 30.8931
27 | 0.031129 | 0.0078077 | -0.031119 | -0.0078015 | 9.9318e-06 | 6.2094e-06 | 0.047457 | 0.047457 | 0.047457 | 0.97611 | -0.46042 | 0.97577 | -0.46712 | 13.0376
28 | 0.024024 | 0.0060282 | -0.024008 | -0.0060181 | 1.6552e-05 | 1.017e-05 | 0.036352 | 0.036353 | 0.036353 | 0.98346 | -0.31684 | 0.98272 | -0.3313 | 9.987
29 | 0.024223 | 0.0060733 | -0.024216 | -0.0060692 | 6.5976e-06 | 4.0564e-06 | 0.036651 | 0.036651 | 0.036651 | 0.98346 | -0.31684 | 0.98317 | -0.32256 | 10.069
30 | -0.14897 | -0.03757 | 0.1497 | 0.038035 | 0.00072914 | 0.0004647 | 0.22548 | 0.22548 | 0.22548 | 0.98346 | -0.31684 | 0.98872 | -0.21513 | 30.9727
31 | 0.026454 | 0.006633 | -0.026446 | -0.0066281 | 8.0031e-06 | 4.953e-06 | 0.040028 | 0.040028 | 0.040028 | 0.98346 | -0.31684 | 0.98314 | -0.32319 | 10.9966
32 | 0.027155 | 0.0068079 | -0.027149 | -0.0068042 | 5.9615e-06 | 3.6996e-06 | 0.041412 | 0.041412 | 0.041412 | 0.97577 | -0.46712 | 0.97553 | -0.47173 | 11.3768
33 | 0.0065636 | 0.001645 | -0.0065629 | -0.0016448 | 6.6301e-07 | 1.9756e-07 | 0.0099384 | 0.0099385 | 0.0099385 | 0.98272 | -0.3313 | 0.98261 | -0.33342 | 2.7304
34 | 0.017444 | 0.0043731 | -0.017441 | -0.0043711 | 3.2297e-06 | 1.9107e-06 | 0.026414 | 0.026414 | 0.026414 | 0.98272 | -0.3313 | 0.98252 | -0.33519 | 7.2567
35 | -0.1497 | -0.038035 | 0.14981 | 0.038106 | 0.00011319 | 7.1757e-05 | 0.22548 | 0.22548 | 0.22548 | 0.98872 | -0.21513 | 0.98954 | -0.19944 | 20.6484
36 | 0.0039627 | 0.00099313 | -0.0039627 | -0.00099314 | 2.6658e-08 | -7.2316e-09 | 0.0060444 | 0.0060445 | 0.0060445 | 0.97553 | -0.47173 | 0.97553 | -0.47187 | 1.6606
37 | -0.15593 | -0.039641 | 0.15602 | 0.039698 | 8.9997e-05 | 5.7094e-05 | 0.23469 | 0.23469 | 0.23469 | 0.98954 | -0.19944 | 0.99016 | -0.18746 | 21.4914
38 | -0.18168 | -0.046129 | 0.18221 | 0.046466 | 0.00052949 | 0.00033668 | 0.27324 | 0.27324 | 0.27324 | 0.99016 | -0.18746 | 0.99331 | -0.12709 | 25.022
39 | 0.012328 | 0.0030904 | -0.012325 | -0.0030889 | 2.6728e-06 | 1.4435e-06 | 0.018526 | 0.018526 | 0.018526 | 0.99016 | -0.18746 | 0.98993 | -0.19201 | 5.0897
40 | 0.013327 | 0.0033413 | -0.013324 | -0.0033395 | 3.1909e-06 | 1.7694e-06 | 0.020028 | 0.020029 | 0.020029 | 0.99016 | -0.18746 | 0.9899 | -0.19249 | 5.5024
41 | -0.012139 | -0.0030424 | 0.012141 | 0.0030433 | 1.6846e-06 | 8.9759e-07 | 0.018066 | 0.018066 | 0.018066 | 0.99985 | -0.0029126 | 1 | 0 | 4.9632
42 | 0.28263 | 0.07246 | -0.2823 | -0.072248 | 0.00033102 | 0.00021126 | 0.42114 | 0.42114 | 0.42114 | 1 | 0 | 0.99872 | -0.024186 | 38.5659
43 | 0.27766 | 0.071085 | -0.27738 | -0.070904 | 0.0002841 | 0.0001813 | 0.41422 | 0.41422 | 0.41422 | 0.99872 | -0.024186 | 0.9976 | -0.045336 | 37.9326
44 | 0.27315 | 0.069843 | -0.2729 | -0.069689 | 0.00024261 | 0.00015482 | 0.40791 | 0.40791 | 0.40791 | 0.9976 | -0.045336 | 0.99664 | -0.063711 | 37.3547
45 | 0.26776 | 0.0684 | -0.26734 | -0.068128 | 0.00042649 | 0.00027212 | 0.40024 | 0.40024 | 0.40024 | 0.99664 | -0.063711 | 0.9949 | -0.096712 | 36.6518
46 | 0.26354 | 0.067178 | -0.26316 | -0.066932 | 0.00038577 | 0.00024612 | 0.39457 | 0.39457 | 0.39457 | 0.9949 | -0.096712 | 0.99331 | -0.12709 | 36.1326
47 | 0.0016448 | 0.0004122 | -0.0016448 | -0.00041223 | 6.3917e-09 | -3.1123e-08 | 0.0024835 | 0.0024835 | 0.0024835 | 0.98553 | -0.27773 | 0.98553 | -0.27782 | 0.68227
48 | -0.005487 | -0.0013751 | 0.0054881 | 0.0013753 | 1.1491e-06 | 1.6638e-07 | 0.0082846 | 0.0082844 | 0.0082846 | 0.98553 | -0.27773 | 0.98575 | -0.27334 | 2.276
49 | 0.0029861 | 0.00074825 | -0.002986 | -0.00074837 | 1.132e-07 | -1.1694e-07 | 0.0045076 | 0.0045076 | 0.0045076 | 0.98575 | -0.27334 | 0.98571 | -0.27414 | 1.2384
50 | -0.0084742 | -0.0021235 | 0.0084754 | 0.002124 | 1.1547e-06 | 4.9909e-07 | 0.012792 | 0.012792 | 0.012792 | 0.98575 | -0.27334 | 0.9859 | -0.27048 | 3.5143
51 | 0.024475 | 0.0061431 | -0.024459 | -0.0061333 | 1.6066e-05 | 9.8821e-06 | 0.036943 | 0.036944 | 0.036944 | 0.9859 | -0.27048 | 0.98519 | -0.28425 | 10.1493
52 | -0.045857 | -0.011504 | 0.045896 | 0.011529 | 3.9121e-05 | 2.4759e-05 | 0.069216 | 0.069216 | 0.069216 | 0.9859 | -0.27048 | 0.98682 | -0.2526 | 19.0154
53 | 0.012907 | 0.0032369 | -0.0129 | -0.0032329 | 7.176e-06 | 3.95e-06 | 0.019481 | 0.019481 | 0.019481 | 0.9859 | -0.27048 | 0.9853 | -0.28215 | 5.352
54 | 0.017692 | 0.0044372 | -0.017689 | -0.0044356 | 2.7012e-06 | 1.6003e-06 | 0.026722 | 0.026722 | 0.026722 | 0.98519 | -0.28425 | 0.98503 | -0.28746 | 7.3413
55 | 0.010339 | 0.0025918 | -0.010336 | -0.0025906 | 2.2134e-06 | 1.1064e-06 | 0.01559 | 0.01559 | 0.01559 | 0.98682 | -0.2526 | 0.98659 | -0.2571 | 4.2829
56 | -0.056235 | -0.014121 | 0.056283 | 0.014151 | 4.8325e-05 | 3.0699e-05 | 0.084806 | 0.084806 | 0.084806 | 0.98682 | -0.2526 | 0.98775 | -0.23461 | 23.2983
57 | 0.0021405 | 0.00053641 | -0.0021404 | -0.00053645 | 1.3771e-08 | -3.5947e-08 | 0.0032325 | 0.0032325 | 0.0032325 | 0.9853 | -0.28215 | 0.9853 | -0.28229 | 0.88806
58 | 0.0084893 | 0.0021277 | -0.0084886 | -0.0021274 | 6.7715e-07 | 2.9273e-07 | 0.012804 | 0.012804 | 0.012804 | 0.98659 | -0.2571 | 0.9865 | -0.25877 | 3.5176
59 | -0.062268 | -0.015651 | 0.062404 | 0.015738 | 0.00013608 | 8.6565e-05 | 0.093822 | 0.093822 | 0.093822 | 0.98775 | -0.23461 | 0.9901 | -0.18894 | 25.7752
60 | 0.014724 | 0.0036926 | -0.014718 | -0.0036889 | 6.4851e-06 | 3.7058e-06 | 0.022244 | 0.022244 | 0.022244 | 0.98503 | -0.28746 | 0.98456 | -0.2967 | 6.111
61 | 0.0060448 | 0.0015149 | -0.0060444 | -0.0015149 | 3.3481e-07 | 7.7167e-08 | 0.0091177 | 0.0091178 | 0.0091178 | 0.9865 | -0.25877 | 0.98644 | -0.25993 | 2.5049
62 | 0.0018923 | 0.00047402 | -0.0018923 | -0.00047425 | 6.3565e-08 | -2.2885e-07 | 0.0028439 | 0.002844 | 0.002844 | 0.9901 | -0.18894 | 0.99007 | -0.18965 | 0.78131
63 | -0.064297 | -0.016212 | 0.064353 | 0.016247 | 5.6037e-05 | 3.5658e-05 | 0.096665 | 0.096665 | 0.096665 | 0.9901 | -0.18894 | 0.99105 | -0.17075 | 26.5564
64 | -0.0089859 | -0.002252 | 0.0089873 | 0.0022526 | 1.3383e-06 | 6.052e-07 | 0.01351 | 0.01351 | 0.01351 | 0.98974 | -0.19562 | 0.9899 | -0.19249 | 3.7115
65 | 0.0033057 | 0.00082841 | -0.0033056 | -0.00082846 | 7.8049e-08 | -5.8337e-08 | 0.0049699 | 0.0049699 | 0.0049699 | 0.98974 | -0.19562 | 0.98972 | -0.19611 | 1.3654
66 | 0.075232 | 0.019033 | -0.075173 | -0.018996 | 5.8232e-05 | 3.7111e-05 | 0.11276 | 0.11276 | 0.11276 | 0.99331 | -0.12709 | 0.99247 | -0.14323 | 30.9788
67 | 0.0057179 | 0.0014327 | -0.0057175 | -0.0014326 | 4.6508e-07 | 7.8861e-08 | 0.0085655 | 0.0085656 | 0.0085656 | 0.99331 | -0.12709 | 0.99322 | -0.1288 | 2.3532
68 | 0.006041 | 0.001514 | -0.006041 | -0.001514 | 6.6367e-09 | 1.4881e-09 | 0.0090806 | 0.0090806 | 0.0090806 | 0.98993 | -0.19201 | 0.98993 | -0.19204 | 2.4947
69 | 0.072753 | 0.018389 | -0.072699 | -0.018355 | 5.3015e-05 | 3.3776e-05 | 0.10913 | 0.10913 | 0.10913 | 0.99247 | -0.14323 | 0.99168 | -0.15844 | 29.9816
70 | 0.002304 | 0.00057713 | -0.0023039 | -0.0005774 | 1.1906e-07 | -2.6867e-07 | 0.0034516 | 0.0034518 | 0.0034518 | 0.99322 | -0.1288 | 0.99317 | -0.12988 | 0.94829
71 | 0.070327 | 0.017761 | -0.070285 | -0.017734 | 4.1445e-05 | 2.6397e-05 | 0.10557 | 0.10557 | 0.10557 | 0.99168 | -0.15844 | 0.99105 | -0.17075 | 29.0036
72 | 0.010419 | 0.0026115 | -0.010418 | -0.0026111 | 7.4834e-07 | 3.766e-07 | 0.015747 | 0.015747 | 0.015747 | 0.98456 | -0.2967 | 0.98448 | -0.29821 | 4.3261
73 | 0.0038062 | 0.00095391 | -0.0038062 | -0.00095392 | 3.139e-08 | -1.2326e-08 | 0.0057416 | 0.0057416 | 0.0057416 | 0.98644 | -0.25993 | 0.98643 | -0.26011 | 1.5774
74 | -0.0026885 | -0.00067379 | 0.0026885 | 0.00067367 | 8.704e-08 | -1.2301e-07 | 0.0040637 | 0.0040636 | 0.0040637 | 0.98445 | -0.29889 | 0.98448 | -0.29821 | 1.1164
75 | 0.0077297 | 0.0019374 | -0.0077284 | -0.0019369 | 1.3506e-06 | 5.2894e-07 | 0.011683 | 0.011683 | 0.011683 | 0.98448 | -0.29821 | 0.98429 | -0.30188 | 3.2097

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30131 | 0.076727

## res_load
| p_mw | q_mvar
0 | 0.0054057 | 0.0013548
1 | 0.001481 | 0.00037117
2 | 0.0019054 | 0.00047754
3 | 0.0021542 | 0.0005399
4 | 0.0017991 | 0.0004509
5 | 0.0051467 | 0.0012899
6 | 0.0014112 | 0.00035368
7 | 0.0015629 | 0.00039169
8 | 0.0012797 | 0.00032072
9 | 0.0015959 | 0.00039998
10 | 0.0012236 | 0.00030665
11 | 0.0009056 | 0.00022697
12 | 0.0010673 | 0.00026749
13 | 0.0022388 | 0.00056111
14 | 0.002964 | 0.00074285
15 | 0.0021242 | 0.00053237
16 | 0.0023649 | 0.00059269
17 | 0.0028411 | 0.00071206
18 | 0.002368 | 0.00059348
19 | 0.0022528 | 0.00056461
20 | 0.0022625 | 0.00056703
21 | 0.0021007 | 0.00052648
22 | 0.0015747 | 0.00039465
23 | 0.0039643 | 0.00099355
24 | 0.024216 | 0.0060692
25 | 0.026446 | 0.0066281
26 | 0.023186 | 0.0058111
27 | 0.0065629 | 0.0016448
28 | 0.017441 | 0.0043711
29 | 0.0061217 | 0.0015343
30 | 0.0039627 | 0.00099314
31 | 0.0046794 | 0.0011728
32 | 0.0048824 | 0.0012236
33 | 0.0046412 | 0.0011632
34 | 0.0042313 | 0.0010605
35 | 0.0051409 | 0.0012884
36 | 0.0037914 | 0.00095022
37 | 0.0038421 | 0.00096293
38 | 0.0016448 | 0.00041223
39 | 0.002986 | 0.00074837
40 | 0.0067674 | 0.0016961
41 | 0.010759 | 0.0026965
42 | 0.0018471 | 0.00046294
43 | 0.0059849 | 0.0015
44 | 0.0029646 | 0.00074299
45 | 0.0021404 | 0.00053645
46 | 0.0024438 | 0.00061248
47 | 0.0056802 | 0.0014236
48 | 0.0043367 | 0.0010869
49 | 0.0033056 | 0.00082846
50 | 0.006284 | 0.0015749
51 | 0.0024209 | 0.00060674
52 | 0.0034135 | 0.0008555
53 | 0.006041 | 0.001514
54 | 0.0023727 | 0.00059466
55 | 0.0023039 | 0.0005774
56 | 0.0059326 | 0.0014869
57 | 0.0018923 | 0.00047425
58 | 0.0042989 | 0.0010774
59 | 0.0022382 | 0.00056094
60 | 0.0038062 | 0.00095392
61 | 0.0026885 | 0.00067379
62 | 0.0077284 | 0.0019369

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1