## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-16_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-16_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-16_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_161-16_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_161-16_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_161-16_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_161-16_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_161-16_0_4_node_72 | 0.4 | n |  | TRUE
8 | bus_LV_161-16_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_161-16_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_161-16_0_4_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_161-16_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_161-16_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_161-16_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_161-16_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_161-16_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_161-16_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_161-16_0_4_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_161-16_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_161-16_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_161-16_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_161-16_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_161-16_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_161-16_0_4_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_161-16_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_161-16_0_4_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_161-16_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_161-16_0_4_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_161-16_0_4_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_161-16_0_4_node_51 | 0.4 | n |  | TRUE
30 | bus_LV_161-16_0_4_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_161-16_0_4_node_86 | 0.4 | n |  | TRUE
32 | bus_LV_161-16_0_4_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_161-16_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_161-16_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_161-16_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_161-16_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_161-16_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_161-16_0_4_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_161-16_0_4_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_161-16_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_161-16_0_4_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_161-16_0_4_node_93 | 0.4 | n |  | TRUE
43 | bus_LV_161-16_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_161-16_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_161-16_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_161-16_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_161-16_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_161-16_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_161-16_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_161-16_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_161-16_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_161-16_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_161-16_0_4_node_105 | 0.4 | n |  | TRUE
54 | bus_LV_161-16_0_4_node_109 | 0.4 | n |  | TRUE
55 | bus_LV_161-16_0_4_node_128 | 0.4 | n |  | TRUE
56 | bus_LV_161-16_0_4_node_104 | 0.4 | n |  | TRUE
57 | bus_LV_161-16_0_4_node_107 | 0.4 | n |  | TRUE
58 | bus_LV_161-16_0_4_node_101 | 0.4 | n |  | TRUE
59 | bus_LV_161-16_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_161-16_0_4_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_161-16_0_4_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_161-16_0_4_node_94 | 0.4 | n |  | TRUE
63 | bus_LV_161-16_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_161-16_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_161-16_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_161-16_0_4_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_161-16_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_161-16_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_161-16_0_4_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_161-16_0_4_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_161-16_0_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_161-16_0_4_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_161-16_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_161-16_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_161-16_0_4_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_161-16_0_4_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_161-16_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_161-16_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_161-16_0_4_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_161-16_0_4_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_161-16_0_4_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_161-16_0_4_node_92 | 0.4 | n |  | TRUE
83 | bus_LV_161-16_0_4_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_161-16_0_4_node_106 | 0.4 | n |  | TRUE
85 | bus_LV_161-16_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_161-16_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_161-16_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_161-16_0_4_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_161-16_0_4_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_161-16_0_4_node_97 | 0.4 | n |  | TRUE
91 | bus_LV_161-16_0_4_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_161-16_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_161-16_0_4_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_161-16_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_161-16_0_4_node_127 | 0.4 | n |  | TRUE
96 | bus_LV_161-16_0_4_node_100 | 0.4 | n |  | TRUE
97 | bus_LV_161-16_0_4_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_161-16_0_4_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_161-16_0_4_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_161-16_0_4_node_111 | 0.4 | n |  | TRUE
101 | bus_LV_161-16_0_4_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_161-16_0_4_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_161-16_0_4_node_112 | 0.4 | n |  | TRUE
104 | bus_LV_161-16_0_4_node_113 | 0.4 | n |  | TRUE
105 | bus_LV_161-16_0_4_node_124 | 0.4 | n |  | TRUE
106 | bus_LV_161-16_0_4_node_126 | 0.4 | n |  | TRUE
107 | bus_LV_161-16_0_4_node_122 | 0.4 | n |  | TRUE
108 | bus_LV_161-16_0_4_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_161-16_0_4_node_102 | 0.4 | n |  | TRUE
110 | bus_LV_161-16_0_4_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_161-16_0_4_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_161-16_0_4_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_161-16_0_4_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_161-16_0_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_161-16_0_4_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_161-16_0_4_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_161-16_0_4_node_137 | 0.4 | n |  | TRUE
118 | bus_LV_161-16_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_161-16_0_4_node_117 | 0.4 | n |  | TRUE
120 | bus_LV_161-16_0_4_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_161-16_0_4_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_161-16_0_4_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_161-16_0_4_node_121 | 0.4 | n |  | TRUE
124 | bus_LV_161-16_0_4_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_161-16_0_4_node_130 | 0.4 | n |  | TRUE
126 | bus_LV_161-16_0_4_node_131 | 0.4 | n |  | TRUE
127 | bus_LV_161-16_0_4_node_132 | 0.4 | n |  | TRUE
128 | bus_LV_161-16_0_4_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_161-16_0_4_node_136 | 0.4 | n |  | TRUE
130 | bus_LV_161-16_0_4_node_134 | 0.4 | n |  | TRUE
131 | bus_MV_494_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-16_0_4_load_0 | 0 | 0.001546 | 0.00038746 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-16_0_4_load_1 | 1 | 0.0017824 | 0.00044672 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-16_0_4_load_2 | 2 | 0.002175 | 0.00054509 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-16_0_4_load_3 | 3 | 0.0016317 | 0.00040894 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-16_0_4_load_7 | 4 | 0.0062674 | 0.0015708 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-16_0_4_load_5 | 5 | 0.0030462 | 0.00076344 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-16_0_4_load_23 | 6 | 0.0036028 | 0.00090294 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-16_0_4_load_6 | 8 | 0.0059771 | 0.001498 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-16_0_4_load_17 | 10 | 0.0041479 | 0.0010396 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-16_0_4_load_19 | 15 | 0.017775 | 0.0044549 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-16_0_4_load_9 | 16 | 0.0023676 | 0.00059337 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-16_0_4_load_41 | 17 | 0.0043282 | 0.0010847 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-16_0_4_load_20 | 18 | 0.0053425 | 0.0013389 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-16_0_4_load_13 | 19 | 0.0048586 | 0.0012177 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-16_0_4_load_14 | 20 | 0.00547 | 0.0013709 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-16_0_4_load_16 | 21 | 0.0050346 | 0.0012618 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-16_0_4_load_18 | 22 | 0.0030259 | 0.00075836 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-16_0_4_load_44 | 23 | 0.0032448 | 0.00081324 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-16_0_4_load_34 | 24 | 0.00387 | 0.00096992 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-16_0_4_load_52 | 27 | 0.0036745 | 0.00092091 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-16_0_4_load_60 | 28 | 0.0031844 | 0.0007981 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-16_0_4_load_51 | 29 | 0.0036761 | 0.00092131 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-16_0_4_load_42 | 30 | 0.0022389 | 0.00056112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-16_0_4_load_86 | 31 | 0.0045678 | 0.0011448 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-16_0_4_load_71 | 32 | 0.0028422 | 0.00071231 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-16_0_4_load_24 | 33 | 0.0020627 | 0.00051696 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-16_0_4_load_25 | 34 | 0.0021557 | 0.00054027 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-16_0_4_load_26 | 35 | 0.0020415 | 0.00051164 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-16_0_4_load_27 | 36 | 0.0078208 | 0.0019601 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-16_0_4_load_55 | 38 | 0.0058064 | 0.0014552 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-16_0_4_load_40 | 39 | 0.0057732 | 0.0014469 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-16_0_4_load_37 | 40 | 0.0065242 | 0.0016351 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-16_0_4_load_54 | 41 | 0.0053913 | 0.0013512 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-16_0_4_load_93 | 42 | 0.0052505 | 0.0013159 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-16_0_4_load_38 | 43 | 0.0032547 | 0.00081571 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-16_0_4_load_29 | 44 | 0.0016224 | 0.00040661 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-16_0_4_load_30 | 45 | 0.0050088 | 0.0012553 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-16_0_4_load_31 | 46 | 0.0035562 | 0.00089126 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-16_0_4_load_33 | 48 | 0.0026376 | 0.00066106 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-16_0_4_load_36 | 49 | 0.0059434 | 0.0014895 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-16_0_4_load_50 | 50 | 0.004466 | 0.0011193 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-16_0_4_load_43 | 51 | 0.0054831 | 0.0013742 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-16_0_4_load_105 | 53 | 0.0019007 | 0.00047635 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-16_0_4_load_109 | 54 | 0.0024681 | 0.00061855 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-16_0_4_load_128 | 55 | 0.0016654 | 0.00041739 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-16_0_4_load_104 | 56 | 0.0037063 | 0.00092889 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-16_0_4_load_107 | 57 | 0.0016104 | 0.00040361 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-16_0_4_load_101 | 58 | 0.0021775 | 0.00054573 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-16_0_4_load_39 | 59 | 0.0027188 | 0.00068139 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-16_0_4_load_61 | 60 | 0.0030585 | 0.00076654 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-16_0_4_load_59 | 61 | 0.0031485 | 0.00078908 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-16_0_4_load_94 | 62 | 0.0043177 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-16_0_4_load_45 | 63 | 0.0069714 | 0.0017472 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-16_0_4_load_46 | 64 | 0.0024511 | 0.0006143 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-16_0_4_load_47 | 65 | 0.015316 | 0.0038387 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-16_0_4_load_49 | 66 | 0.0046961 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-16_0_4_load_53 | 67 | 0.0043007 | 0.0010779 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-16_0_4_load_58 | 68 | 0.0037731 | 0.00094562 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-16_0_4_load_57 | 69 | 0.0033286 | 0.00083423 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-16_0_4_load_62 | 70 | 0.0030999 | 0.00077692 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-16_0_4_load_64 | 72 | 0.0025049 | 0.00062778 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-16_0_4_load_65 | 73 | 0.0026738 | 0.00067011 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-16_0_4_load_70 | 74 | 0.0036819 | 0.00092277 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_161-16_0_4_load_67 | 75 | 0.0043871 | 0.0010995 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_161-16_0_4_load_66 | 76 | 0.0034219 | 0.00085761 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_161-16_0_4_load_68 | 77 | 0.0033956 | 0.00085101 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_161-16_0_4_load_76 | 79 | 0.0065794 | 0.0016489 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_161-16_0_4_load_73 | 80 | 0.0032065 | 0.00080362 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_161-16_0_4_load_77 | 81 | 0.0034936 | 0.00087558 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_161-16_0_4_load_74 | 83 | 0.0027727 | 0.0006949 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_161-16_0_4_load_106 | 84 | 0.0027666 | 0.00069337 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_161-16_0_4_load_75 | 85 | 0.0033676 | 0.000844 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_161-16_0_4_load_78 | 86 | 0.0038329 | 0.00096061 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_161-16_0_4_load_79 | 87 | 0.0042214 | 0.001058 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_161-16_0_4_load_84 | 88 | 0.0033104 | 0.00082967 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_161-16_0_4_load_99 | 89 | 0.0033281 | 0.00083409 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_161-16_0_4_load_81 | 91 | 0.005852 | 0.0014666 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_161-16_0_4_load_82 | 92 | 0.003039 | 0.00076163 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_161-16_0_4_load_83 | 93 | 0.0075587 | 0.0018944 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_161-16_0_4_load_85 | 94 | 0.0054126 | 0.0013565 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_161-16_0_4_load_127 | 95 | 0.003266 | 0.00081855 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_161-16_0_4_load_100 | 96 | 0.0019999 | 0.00050123 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_161-16_0_4_load_87 | 97 | 0.0053265 | 0.0013349 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_161-16_0_4_load_88 | 98 | 0.0044527 | 0.001116 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_161-16_0_4_load_89 | 99 | 0.0035373 | 0.00088652 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_161-16_0_4_load_111 | 100 | 0.0054221 | 0.0013589 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_161-16_0_4_load_90 | 101 | 0.007767 | 0.0019466 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_161-16_0_4_load_91 | 102 | 0.0051526 | 0.0012914 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_161-16_0_4_load_112 | 103 | 0.0078115 | 0.0019577 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_161-16_0_4_load_126 | 106 | 0.0010198 | 0.00025559 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_161-16_0_4_load_122 | 107 | 0.0012349 | 0.00030949 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_161-16_0_4_load_103 | 108 | 0.0024724 | 0.00061963 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_161-16_0_4_load_102 | 109 | 0.0033711 | 0.00084488 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_161-16_0_4_load_95 | 110 | 0.0037946 | 0.000951 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_161-16_0_4_load_96 | 111 | 0.0039906 | 0.0010001 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_161-16_0_4_load_98 | 112 | 0.0038896 | 0.00097483 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_161-16_0_4_load_116 | 113 | 0.0078171 | 0.0019591 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_161-16_0_4_load_114 | 114 | 0.0065614 | 0.0016444 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_161-16_0_4_load_108 | 115 | 0.0070242 | 0.0017604 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_161-16_0_4_load_110 | 116 | 0.0033556 | 0.00084099 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_161-16_0_4_load_137 | 117 | 0.00073622 | 0.00018452 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_161-16_0_4_load_115 | 118 | 0.0029874 | 0.00074872 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_161-16_0_4_load_117 | 119 | 0.0074475 | 0.0018665 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_161-16_0_4_load_120 | 120 | 0.00079644 | 0.00019961 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_161-16_0_4_load_118 | 122 | 0.0011144 | 0.00027928 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_161-16_0_4_load_121 | 123 | 0.00039298 | 9.849e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_161-16_0_4_load_129 | 124 | 0.003629 | 0.00090952 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_161-16_0_4_load_130 | 125 | 0.0018715 | 0.00046905 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_161-16_0_4_load_131 | 126 | 0.0033274 | 0.00083394 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_161-16_0_4_load_132 | 127 | 0.0051458 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_161-16_0_4_load_133 | 128 | 0.0030551 | 0.00076569 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_161-16_0_4_load_134 | 130 | 0.0030185 | 0.0007565 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 108 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-16_0_4_line_0 |  | 0 | 1 | 0.02448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-16_0_4_line_1 |  | 0 | 2 | 0.0022391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-16_0_4_line_2 |  | 1 | 3 | 1.8306e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_161-16_0_4_line_3 |  | 3 | 4 | 0.024322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-16_0_4_line_4 |  | 4 | 5 | 0.046647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_161-16_0_4_line_5 |  | 5 | 8 | 0.010462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_161-16_0_4_line_6 |  | 6 | 7 | 0.020061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-16_0_4_line_7 |  | 7 | 31 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_161-16_0_4_line_8 |  | 7 | 32 | 0.013577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_161-16_0_4_line_9 |  | 8 | 9 | 0.00042687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-16_0_4_line_10 |  | 9 | 10 | 0.035561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-16_0_4_line_11 |  | 9 | 11 | 0.040956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_161-16_0_4_line_12 |  | 10 | 12 | 0.0093737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_161-16_0_4_line_13 |  | 11 | 16 | 0.029085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-16_0_4_line_14 |  | 12 | 22 | 0.02015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-16_0_4_line_15 |  | 12 | 19 | 0.012598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-16_0_4_line_16 |  | 13 | 14 | 0.018724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_161-16_0_4_line_17 |  | 13 | 15 | 0.027971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_161-16_0_4_line_18 |  | 14 | 17 | 0.044493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-16_0_4_line_19 |  | 15 | 18 | 0.0062006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-16_0_4_line_20 |  | 17 | 30 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-16_0_4_line_21 |  | 19 | 20 | 0.020836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-16_0_4_line_22 |  | 20 | 21 | 0.0045685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-16_0_4_line_23 |  | 21 | 23 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_161-16_0_4_line_24 |  | 22 | 24 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_161-16_0_4_line_25 |  | 23 | 25 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_161-16_0_4_line_26 |  | 25 | 28 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_161-16_0_4_line_27 |  | 25 | 26 | 0.00315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_161-16_0_4_line_28 |  | 26 | 27 | 0.011991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_161-16_0_4_line_29 |  | 27 | 29 | 0.023955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_161-16_0_4_line_30 |  | 28 | 68 | 0.01009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_161-16_0_4_line_31 |  | 29 | 50 | 0.0061917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_161-16_0_4_line_32 |  | 30 | 51 | 0.0087716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_161-16_0_4_line_33 |  | 31 | 84 | 0.0020139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-16_0_4_line_34 |  | 32 | 74 | 0.0021308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_161-16_0_4_line_35 |  | 33 | 34 | 0.0096902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_161-16_0_4_line_36 |  | 33 | 35 | 0.007988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_161-16_0_4_line_37 |  | 34 | 36 | 0.0060326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_161-16_0_4_line_38 |  | 35 | 37 | 0.008387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_161-16_0_4_line_39 |  | 36 | 38 | 0.026967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-16_0_4_line_40 |  | 37 | 39 | 0.02045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_161-16_0_4_line_41 |  | 37 | 40 | 0.023282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_161-16_0_4_line_42 |  | 38 | 41 | 0.001974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_161-16_0_4_line_43 |  | 39 | 42 | 0.026485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_161-16_0_4_line_44 |  | 40 | 43 | 0.029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_161-16_0_4_line_45 |  | 41 | 67 | 0.017692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_161-16_0_4_line_46 |  | 42 | 62 | 0.0054593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_161-16_0_4_line_47 |  | 43 | 59 | 0.0041248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-16_0_4_line_48 |  | 44 | 45 | 0.015088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-16_0_4_line_49 |  | 44 | 46 | 0.0062197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-16_0_4_line_50 |  | 45 | 47 | 0.016016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-16_0_4_line_51 |  | 46 | 48 | 0.0040397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-16_0_4_line_52 |  | 47 | 49 | 0.016351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-16_0_4_line_53 |  | 48 | 50 | 0.022188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-16_0_4_line_54 |  | 49 | 51 | 0.035701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_161-16_0_4_line_55 |  | 52 | 53 | 0.014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_161-16_0_4_line_56 |  | 52 | 54 | 0.015469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_161-16_0_4_line_57 |  | 52 | 55 | 0.032871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-16_0_4_line_58 |  | 53 | 56 | 0.018684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_161-16_0_4_line_59 |  | 54 | 57 | 0.016239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-16_0_4_line_60 |  | 55 | 58 | 0.0011532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-16_0_4_line_61 |  | 56 | 84 | 0.011623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-16_0_4_line_62 |  | 57 | 115 | 0.013719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-16_0_4_line_63 |  | 59 | 60 | 0.0042386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-16_0_4_line_64 |  | 60 | 61 | 0.012523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_161-16_0_4_line_65 |  | 61 | 69 | 0.0012583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_161-16_0_4_line_66 |  | 62 | 108 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_161-16_0_4_line_67 |  | 63 | 64 | 0.0037663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-16_0_4_line_68 |  | 63 | 65 | 0.015199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-16_0_4_line_69 |  | 65 | 66 | 0.0095343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-16_0_4_line_70 |  | 66 | 67 | 0.01499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_161-16_0_4_line_71 |  | 68 | 69 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_161-16_0_4_line_72 |  | 70 | 71 | 0.040775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-16_0_4_line_73 |  | 71 | 72 | 0.017927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-16_0_4_line_74 |  | 71 | 73 | 0.014184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-16_0_4_line_75 |  | 72 | 74 | 0.024169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_161-16_0_4_line_76 |  | 73 | 75 | 0.014045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_161-16_0_4_line_77 |  | 75 | 76 | 0.01663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_161-16_0_4_line_78 |  | 76 | 77 | 0.026521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_161-16_0_4_line_79 |  | 77 | 78 | 0.013385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_161-16_0_4_line_80 |  | 78 | 79 | 0.036623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_161-16_0_4_line_81 |  | 78 | 80 | 0.016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_161-16_0_4_line_82 |  | 80 | 83 | 0.029906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_161-16_0_4_line_83 |  | 81 | 82 | 0.031521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_161-16_0_4_line_84 |  | 82 | 88 | 0.015048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_161-16_0_4_line_85 |  | 83 | 85 | 0.0019442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_161-16_0_4_line_86 |  | 85 | 86 | 0.029557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_161-16_0_4_line_87 |  | 86 | 87 | 0.018174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_161-16_0_4_line_88 |  | 87 | 89 | 0.01338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_161-16_0_4_line_89 |  | 88 | 92 | 0.0050528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_161-16_0_4_line_90 |  | 89 | 90 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_161-16_0_4_line_91 |  | 90 | 96 | 0.040031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_161-16_0_4_line_92 |  | 90 | 109 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_161-16_0_4_line_93 |  | 90 | 110 | 0.031081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_161-16_0_4_line_94 |  | 91 | 92 | 0.035024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_161-16_0_4_line_95 |  | 91 | 93 | 0.019479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_161-16_0_4_line_96 |  | 93 | 94 | 0.010605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_161-16_0_4_line_97 |  | 94 | 95 | 0.025025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_161-16_0_4_line_98 |  | 95 | 96 | 0.0088585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_161-16_0_4_line_99 |  | 97 | 98 | 0.0056698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_161-16_0_4_line_100 |  | 97 | 99 | 0.018198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_161-16_0_4_line_101 |  | 97 | 100 | 0.079087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_161-16_0_4_line_102 |  | 98 | 101 | 0.04462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_161-16_0_4_line_103 |  | 99 | 102 | 0.020042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_161-16_0_4_line_104 |  | 100 | 103 | 0.015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_161-16_0_4_line_105 |  | 101 | 106 | 0.01438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_161-16_0_4_line_106 |  | 103 | 104 | 0.042162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_161-16_0_4_line_107 |  | 104 | 105 | 0.042372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_161-16_0_4_line_108 |  | 105 | 117 | 0.0062199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_161-16_0_4_line_109 |  | 106 | 107 | 0.021523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_161-16_0_4_line_110 |  | 107 | 121 | 0.022632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_161-16_0_4_line_111 |  | 108 | 109 | 0.025679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_161-16_0_4_line_112 |  | 110 | 111 | 0.00088311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_161-16_0_4_line_113 |  | 111 | 112 | 0.0084372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_161-16_0_4_line_114 |  | 112 | 113 | 0.028085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_161-16_0_4_line_115 |  | 113 | 114 | 0.0022531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_161-16_0_4_line_116 |  | 114 | 118 | 0.02535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_161-16_0_4_line_117 |  | 115 | 116 | 0.014559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_161-16_0_4_line_118 |  | 118 | 119 | 0.0028753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_161-16_0_4_line_119 |  | 119 | 120 | 0.023438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_161-16_0_4_line_120 |  | 120 | 121 | 0.016585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_161-16_0_4_line_121 |  | 121 | 123 | 0.021787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_161-16_0_4_line_122 |  | 121 | 122 | 0.025633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_161-16_0_4_line_123 |  | 123 | 124 | 0.036432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_161-16_0_4_line_124 |  | 124 | 125 | 0.016373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_161-16_0_4_line_125 |  | 125 | 126 | 0.019021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_161-16_0_4_line_126 |  | 126 | 127 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_161-16_0_4_line_127 |  | 127 | 128 | 0.0070035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_161-16_0_4_line_128 |  | 128 | 129 | 0.023957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_161-16_0_4_line_129 |  | 129 | 130 | 0.040202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-16_0_4_trafo_103 | 0.63 MVA 20/0.4 kV | 131 | 108 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2686027.7508 | 1244183.0999 | 2686028.6717 | 1244158.6375
1 | 2686027.7508 | 1244183.0999 | 2686027.6665 | 1244185.3374
2 | 2686028.6717 | 1244158.6375 | 2686028.6723 | 1244158.6192
3 | 2686028.6723 | 1244158.6192 | 2686029.5873 | 1244134.3148
4 | 2686031.342 | 1244087.7011 | 2686029.5873 | 1244134.3148
5 | 2686031.342 | 1244087.7011 | 2686031.7356 | 1244077.2468
6 | 2686101.3322 | 1244231.2762 | 2686081.4981 | 1244228.2671
7 | 2686101.3322 | 1244231.2762 | 2686106.6661 | 1244210.6484
8 | 2686101.3322 | 1244231.2762 | 2686100.007 | 1244244.788
9 | 2686031.7356 | 1244077.2468 | 2686031.7517 | 1244076.8202
10 | 2686031.7517 | 1244076.8202 | 2686045.3278 | 1244078.7629 | 2686063.3471 | 1244091.1158
11 | 2686014.3048 | 1244054.6288 | 2686021.3943 | 1244054.6204 | 2686028.9551 | 1244054.4299 | 2686033.3009 | 1244054.9488 | 2686032.3671 | 1244067.2221 | 2686031.7517 | 1244076.8202
12 | 2686071.0785 | 1244096.416 | 2686063.3471 | 1244091.1158
13 | 2686014.3048 | 1244054.6288 | 2686006.5453 | 1244062.789 | 2685999.0078 | 1244078.9415
14 | 2686071.0785 | 1244096.416 | 2686082.1183 | 1244107.5176 | 2686084.1115 | 1244111.5447
15 | 2686071.0785 | 1244096.416 | 2686081.2211 | 1244088.9432
16 | 2686047.2028 | 1243993.8278 | 2686042.059 | 1244011.8331
17 | 2686042.059 | 1244011.8331 | 2686055.3008 | 1244019.1194 | 2686067.3873 | 1244023.5026
18 | 2686047.2028 | 1243993.8278 | 2686061.9401 | 1243996.499 | 2686064.1594 | 1243996.6869 | 2686071.6579 | 1243995.0612 | 2686077.5301 | 1243991.9663 | 2686089.0087 | 1243985.9102
19 | 2686073.2164 | 1244025.6165 | 2686067.3873 | 1244023.5026
20 | 2686089.0087 | 1243985.9102 | 2686109.8854 | 1243974.8955
21 | 2686097.996 | 1244076.5837 | 2686081.2211 | 1244088.9432
22 | 2686097.996 | 1244076.5837 | 2686101.2706 | 1244074.171 | 2686101.5808 | 1244073.7775
23 | 2686101.5808 | 1244073.7775 | 2686115.945 | 1244055.5587
24 | 2686084.1115 | 1244111.5447 | 2686095.1953 | 1244133.9379 | 2686097.1697 | 1244137.1678
25 | 2686123.6282 | 1244044.9518 | 2686117.4094 | 1244053.7013 | 2686115.945 | 1244055.5587
26 | 2686123.6282 | 1244044.9518 | 2686125.9394 | 1244046.6199 | 2686137.6972 | 1244051.6361
27 | 2686125.3969 | 1244042.3423 | 2686123.6282 | 1244044.9518
28 | 2686125.3969 | 1244042.3423 | 2686131.617 | 1244032.0911
29 | 2686131.617 | 1244032.0911 | 2686132.1182 | 1244031.265 | 2686136.7692 | 1244022.2259 | 2686142.2502 | 1244010.6335
30 | 2686147.4883 | 1244053.9797 | 2686138.9718 | 1244052.1798 | 2686137.6972 | 1244051.6361
31 | 2686144.8967 | 1244005.0359 | 2686142.2502 | 1244010.6335
32 | 2686109.8854 | 1243974.8955 | 2686117.6434 | 1243970.8024
33 | 2686107.1703 | 1244208.6987 | 2686106.6661 | 1244210.6484
34 | 2686099.799 | 1244246.9087 | 2686100.007 | 1244244.788
35 | 2686239.3061 | 1244053.484 | 2686242.2435 | 1244044.2497
36 | 2686239.3061 | 1244053.484 | 2686236.8847 | 1244061.0962
37 | 2686242.2435 | 1244044.2497 | 2686244.0722 | 1244038.501
38 | 2686234.3423 | 1244069.0886 | 2686236.8847 | 1244061.0962
39 | 2686244.0722 | 1244038.501 | 2686248.2739 | 1244025.2922 | 2686252.1267 | 1244012.7648
40 | 2686234.3423 | 1244069.0886 | 2686228.1519 | 1244088.579
41 | 2686234.3423 | 1244069.0886 | 2686212.0052 | 1244062.5219
42 | 2686252.707 | 1244010.878 | 2686252.1267 | 1244012.7648
43 | 2686228.1519 | 1244088.579 | 2686220.1345 | 1244113.8219
44 | 2686212.0052 | 1244062.5219 | 2686186.5533 | 1244055.0395 | 2686183.2489 | 1244055.0654
45 | 2686257.9076 | 1243993.9681 | 2686252.707 | 1244010.878
46 | 2686220.1345 | 1244113.8219 | 2686218.4819 | 1244119.0251
47 | 2686183.2489 | 1244055.0654 | 2686179.1243 | 1244055.0976
48 | 2686158.7659 | 1243975.7021 | 2686165.2152 | 1243962.0614 | 2686165.2152 | 1243962.0614
49 | 2686158.7659 | 1243975.7021 | 2686156.1074 | 1243981.325
50 | 2686163.6949 | 1243946.5391 | 2686165.8082 | 1243952.463 | 2686166.2463 | 1243957.1617 | 2686165.2152 | 1243962.0614
51 | 2686156.1074 | 1243981.325 | 2686154.3806 | 1243984.977
52 | 2686163.6949 | 1243946.5391 | 2686153.87 | 1243951.6891 | 2686149.2195 | 1243954.1427
53 | 2686144.8967 | 1244005.0359 | 2686154.3806 | 1243984.977
54 | 2686149.2195 | 1243954.1427 | 2686117.6434 | 1243970.8024
55 | 2686124.8107 | 1244167.5145 | 2686118.3086 | 1244180.677
56 | 2686124.8107 | 1244167.5145 | 2686133.7265 | 1244154.8739
57 | 2686124.8107 | 1244167.5145 | 2686138.078 | 1244171.977 | 2686150.6145 | 1244174.7166 | 2686156.6546 | 1244174.824
58 | 2686110.0801 | 1244197.4458 | 2686110.1404 | 1244197.2123 | 2686118.3086 | 1244180.677
59 | 2686133.7265 | 1244154.8739 | 2686143.0864 | 1244141.6035
60 | 2686157.8077 | 1244174.8445 | 2686156.6546 | 1244174.824
61 | 2686107.1703 | 1244208.6987 | 2686110.0801 | 1244197.4458
62 | 2686143.0864 | 1244141.6035 | 2686150.9935 | 1244130.3929
63 | 2686174.8859 | 1244055.1307 | 2686179.1243 | 1244055.0976
64 | 2686174.8859 | 1244055.1307 | 2686162.3628 | 1244055.2286
65 | 2686161.1046 | 1244055.2385 | 2686162.3628 | 1244055.2286
66 | 2686212.7133 | 1244138.1597 | 2686214.129 | 1244132.7305 | 2686218.4819 | 1244119.0251
67 | 2686269.5847 | 1243955.9999 | 2686270.5904 | 1243952.7301 | 2686270.7016 | 1243952.4032
68 | 2686265.1169 | 1243970.527 | 2686269.5847 | 1243955.9999
69 | 2686265.1169 | 1243970.527 | 2686262.3142 | 1243979.6401
70 | 2686257.9076 | 1243993.9681 | 2686262.3142 | 1243979.6401
71 | 2686161.1046 | 1244055.2385 | 2686153.7176 | 1244055.2962 | 2686147.4883 | 1244053.9797
72 | 2686095.6901 | 1244288.8032 | 2686095.0246 | 1244295.5985 | 2686090.5349 | 1244329.2471
73 | 2686095.6901 | 1244288.8032 | 2686097.4399 | 1244270.962
74 | 2686095.6901 | 1244288.8032 | 2686109.6657 | 1244291.2274
75 | 2686099.799 | 1244246.9087 | 2686097.4399 | 1244270.962
76 | 2686123.5037 | 1244293.6278 | 2686109.6657 | 1244291.2274
77 | 2686139.9936 | 1244295.7816 | 2686123.6738 | 1244293.6573 | 2686123.5037 | 1244293.6278
78 | 2686139.9936 | 1244295.7816 | 2686155.2129 | 1244297.7626 | 2686166.1151 | 1244300.2076
79 | 2686179.1758 | 1244303.1368 | 2686166.1151 | 1244300.2076
80 | 2686179.1758 | 1244303.1368 | 2686175.0153 | 1244339.5229
81 | 2686179.1758 | 1244303.1368 | 2686182.4154 | 1244286.8028
82 | 2686182.4154 | 1244286.8028 | 2686186.8745 | 1244264.3201 | 2686188.0979 | 1244257.4429
83 | 2686256.6285 | 1244319.1406 | 2686225.1102 | 1244319.5169
84 | 2686256.6285 | 1244319.1406 | 2686253.0909 | 1244314.508 | 2686247.5195 | 1244307.1625
85 | 2686188.4384 | 1244255.5288 | 2686188.0979 | 1244257.4429
86 | 2686193.6152 | 1244226.4284 | 2686188.4384 | 1244255.5288
87 | 2686193.6152 | 1244226.4284 | 2686196.7981 | 1244208.5358
88 | 2686199.1416 | 1244195.3622 | 2686196.7981 | 1244208.5358
89 | 2686244.466 | 1244303.1367 | 2686247.5195 | 1244307.1625
90 | 2686202.0266 | 1244179.1443 | 2686199.1416 | 1244195.3622
91 | 2686202.0266 | 1244179.1443 | 2686205.4149 | 1244183.1409 | 2686227.9319 | 1244209.6632
92 | 2686202.0266 | 1244179.1443 | 2686206.2341 | 1244163.0081
93 | 2686202.0266 | 1244179.1443 | 2686205.7514 | 1244178.7092 | 2686225.2382 | 1244176.4462 | 2686232.9402 | 1244176.0345
94 | 2686235.8713 | 1244270.2748 | 2686235.164 | 1244281.2564 | 2686240.8109 | 1244298.3176 | 2686244.466 | 1244303.1367
95 | 2686237.118 | 1244250.8359 | 2686236.0133 | 1244268.0701 | 2686235.8713 | 1244270.2748
96 | 2686237.118 | 1244250.8359 | 2686237.7963 | 1244240.2529
97 | 2686233.3311 | 1244216.6477 | 2686238.692 | 1244226.2784 | 2686237.7963 | 1244240.2529
98 | 2686233.3311 | 1244216.6477 | 2686232.321 | 1244214.8329 | 2686227.9319 | 1244209.6632
99 | 2686316.732 | 1244263.901 | 2686317.543 | 1244258.2895
100 | 2686316.732 | 1244263.901 | 2686314.4861 | 1244279.4417 | 2686314.1295 | 1244281.9115
101 | 2686316.732 | 1244263.901 | 2686394.4736 | 1244278.4261
102 | 2686324.1095 | 1244214.155 | 2686318.2176 | 1244253.6215 | 2686317.543 | 1244258.2895
103 | 2686311.2656 | 1244301.7482 | 2686314.1295 | 1244281.9115
104 | 2686394.4736 | 1244278.4261 | 2686399.5528 | 1244264.0907 | 2686399.5528 | 1244264.0907
105 | 2686324.1095 | 1244214.155 | 2686326.2328 | 1244199.9324
106 | 2686438.2699 | 1244280.7668 | 2686417.1593 | 1244272.0752 | 2686399.5528 | 1244264.0907
107 | 2686438.2699 | 1244280.7668 | 2686455.8448 | 1244242.1945
108 | 2686455.8448 | 1244242.1945 | 2686461.6077 | 1244239.8546
109 | 2686331.8605 | 1244179.2123 | 2686327.0694 | 1244194.3289 | 2686326.2328 | 1244199.9324
110 | 2686338.6986 | 1244157.6378 | 2686331.8605 | 1244179.2123
111 | 2686212.7133 | 1244138.1597 | 2686206.2341 | 1244163.0081
112 | 2686232.9402 | 1244176.0345 | 2686233.8221 | 1244175.9874
113 | 2686242.2473 | 1244175.537 | 2686233.8221 | 1244175.9874
114 | 2686269.8876 | 1244171.4257 | 2686265.8119 | 1244172.5998 | 2686256.9605 | 1244174.7505 | 2686242.2473 | 1244175.537
115 | 2686269.8876 | 1244171.4257 | 2686272.0527 | 1244170.8021
116 | 2686272.0527 | 1244170.8021 | 2686283.1922 | 1244167.5933 | 2686296.4109 | 1244163.7803
117 | 2686150.9935 | 1244130.3929 | 2686159.3849 | 1244118.4958
118 | 2686299.1735 | 1244162.9834 | 2686296.4109 | 1244163.7803
119 | 2686322.1769 | 1244159.0851 | 2686308.5495 | 1244160.2789 | 2686299.1735 | 1244162.9834
120 | 2686338.6986 | 1244157.6378 | 2686322.1769 | 1244159.0851
121 | 2686338.6986 | 1244157.6378 | 2686346.2963 | 1244137.2189
122 | 2686338.6986 | 1244157.6378 | 2686363.9193 | 1244162.2136
123 | 2686346.2963 | 1244137.2189 | 2686351.3073 | 1244123.7519 | 2686361.9323 | 1244104.4162
124 | 2686369.8173 | 1244090.0668 | 2686361.9323 | 1244104.4162
125 | 2686369.8173 | 1244090.0668 | 2686378.9773 | 1244073.397
126 | 2686378.9773 | 1244073.397 | 2686385.1663 | 1244062.134
127 | 2686388.5391 | 1244055.9962 | 2686385.1663 | 1244062.134
128 | 2686406.3484 | 1244040.9924 | 2686402.6175 | 1244042.3613 | 2686395.6688 | 1244046.7077 | 2686390.592 | 1244052.2601 | 2686388.5391 | 1244055.9962
129 | 2686406.3484 | 1244040.9924 | 2686400.6421 | 1244018.1703 | 2686398.987 | 1244005.7148 | 2686398.6977 | 1244001.6125

## bus_geodata
| x | y | coords
0 | 2686027.7508 | 1244183.0999
1 | 2686028.6717 | 1244158.6375
2 | 2686027.6665 | 1244185.3374
3 | 2686028.6723 | 1244158.6192
4 | 2686029.5873 | 1244134.3148
5 | 2686031.342 | 1244087.7011
6 | 2686081.4981 | 1244228.2671
7 | 2686101.3322 | 1244231.2762
8 | 2686031.7356 | 1244077.2468
9 | 2686031.7517 | 1244076.8202
10 | 2686063.3471 | 1244091.1158
11 | 2686014.3048 | 1244054.6288
12 | 2686071.0785 | 1244096.416
13 | 2686042.059 | 1244011.8331
14 | 2686047.2028 | 1243993.8278
15 | 2686067.3873 | 1244023.5026
16 | 2685999.0078 | 1244078.9415
17 | 2686089.0087 | 1243985.9102
18 | 2686073.2164 | 1244025.6165
19 | 2686081.2211 | 1244088.9432
20 | 2686097.996 | 1244076.5837
21 | 2686101.5808 | 1244073.7775
22 | 2686084.1115 | 1244111.5447
23 | 2686115.945 | 1244055.5587
24 | 2686097.1697 | 1244137.1678
25 | 2686123.6282 | 1244044.9518
26 | 2686125.3969 | 1244042.3423
27 | 2686131.617 | 1244032.0911
28 | 2686137.6972 | 1244051.6361
29 | 2686142.2502 | 1244010.6335
30 | 2686109.8854 | 1243974.8955
31 | 2686106.6661 | 1244210.6484
32 | 2686100.007 | 1244244.788
33 | 2686239.3061 | 1244053.484
34 | 2686242.2435 | 1244044.2497
35 | 2686236.8847 | 1244061.0962
36 | 2686244.0722 | 1244038.501
37 | 2686234.3423 | 1244069.0886
38 | 2686252.1267 | 1244012.7648
39 | 2686228.1519 | 1244088.579
40 | 2686212.0052 | 1244062.5219
41 | 2686252.707 | 1244010.878
42 | 2686220.1345 | 1244113.8219
43 | 2686183.2489 | 1244055.0654
44 | 2686158.7659 | 1243975.7021
45 | 2686165.2152 | 1243962.0614
46 | 2686156.1074 | 1243981.3249
47 | 2686163.6949 | 1243946.539
48 | 2686154.3806 | 1243984.977
49 | 2686149.2195 | 1243954.1427
50 | 2686144.8967 | 1244005.0359
51 | 2686117.6434 | 1243970.8024
52 | 2686124.8107 | 1244167.5145
53 | 2686118.3086 | 1244180.677
54 | 2686133.7265 | 1244154.8739
55 | 2686156.6546 | 1244174.824
56 | 2686110.0801 | 1244197.4458
57 | 2686143.0864 | 1244141.6035
58 | 2686157.8077 | 1244174.8445
59 | 2686179.1243 | 1244055.0976
60 | 2686174.8859 | 1244055.1307
61 | 2686162.3628 | 1244055.2286
62 | 2686218.4819 | 1244119.0251
63 | 2686269.5847 | 1243955.9999
64 | 2686270.7016 | 1243952.4032
65 | 2686265.1169 | 1243970.527
66 | 2686262.3142 | 1243979.6401
67 | 2686257.9076 | 1243993.9681
68 | 2686147.4883 | 1244053.9797
69 | 2686161.1046 | 1244055.2385
70 | 2686090.5349 | 1244329.2471
71 | 2686095.6901 | 1244288.8032
72 | 2686097.4399 | 1244270.962
73 | 2686109.6657 | 1244291.2274
74 | 2686099.799 | 1244246.9087
75 | 2686123.5037 | 1244293.6278
76 | 2686139.9936 | 1244295.7816
77 | 2686166.1151 | 1244300.2076
78 | 2686179.1758 | 1244303.1368
79 | 2686175.0153 | 1244339.5229
80 | 2686182.4154 | 1244286.8028
81 | 2686225.1102 | 1244319.5169
82 | 2686256.6285 | 1244319.1406
83 | 2686188.0979 | 1244257.4429
84 | 2686107.1703 | 1244208.6987
85 | 2686188.4384 | 1244255.5288
86 | 2686193.6152 | 1244226.4284
87 | 2686196.7981 | 1244208.5358
88 | 2686247.5195 | 1244307.1625
89 | 2686199.1416 | 1244195.3622
90 | 2686202.0266 | 1244179.1443
91 | 2686235.8713 | 1244270.2748
92 | 2686244.466 | 1244303.1367
93 | 2686237.118 | 1244250.8359
94 | 2686237.7963 | 1244240.2529
95 | 2686233.3311 | 1244216.6477
96 | 2686227.9319 | 1244209.6632
97 | 2686316.732 | 1244263.901
98 | 2686317.543 | 1244258.2895
99 | 2686314.1295 | 1244281.9115
100 | 2686394.4736 | 1244278.4261
101 | 2686324.1095 | 1244214.155
102 | 2686311.2656 | 1244301.7482
103 | 2686399.5528 | 1244264.0907
104 | 2686438.2699 | 1244280.7668
105 | 2686455.8448 | 1244242.1945
106 | 2686326.2328 | 1244199.9324
107 | 2686331.8605 | 1244179.2123
108 | 2686212.7133 | 1244138.1597
109 | 2686206.2341 | 1244163.0081
110 | 2686232.9402 | 1244176.0345
111 | 2686233.8221 | 1244175.9874
112 | 2686242.2473 | 1244175.537
113 | 2686269.8876 | 1244171.4257
114 | 2686272.0527 | 1244170.8021
115 | 2686150.9935 | 1244130.3929
116 | 2686159.3849 | 1244118.4958
117 | 2686461.6077 | 1244239.8545
118 | 2686296.4109 | 1244163.7803
119 | 2686299.1735 | 1244162.9834
120 | 2686322.1769 | 1244159.0851
121 | 2686338.6986 | 1244157.6378
122 | 2686363.9193 | 1244162.2136
123 | 2686346.2963 | 1244137.2189
124 | 2686361.9323 | 1244104.4162
125 | 2686369.8173 | 1244090.0668
126 | 2686378.9773 | 1244073.397
127 | 2686385.1663 | 1244062.134
128 | 2686388.5391 | 1244055.9962
129 | 2686406.3484 | 1244040.9924
130 | 2686398.6977 | 1244001.6125
131 | 2686202.0266 | 1244179.1443

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97668 | -0.44909 | 0.001546 | 0.00038746
1 | 0.97676 | -0.44742 | 0.0017824 | 0.00044672
2 | 0.97667 | -0.44917 | 0.002175 | 0.00054509
3 | 0.97676 | -0.44742 | 0.0016317 | 0.00040894
4 | 0.97692 | -0.44425 | 0.0062674 | 0.0015708
5 | 0.9775 | -0.43284 | 0.0030462 | 0.00076344
6 | 0.98015 | -0.38215 | 0.0036028 | 0.00090294
7 | 0.98022 | -0.38084 | 0 | 0
8 | 0.97766 | -0.4297 | 0.0059771 | 0.001498
9 | 0.97767 | -0.42952 | 0 | 0
10 | 0.97849 | -0.41346 | 0.0041479 | 0.0010396
11 | 0.97758 | -0.43129 | 0 | 0
12 | 0.97874 | -0.40852 | 0 | 0
13 | 0.97241 | -0.53279 | 0 | 0
14 | 0.97281 | -0.52482 | 0 | 0
15 | 0.9718 | -0.54472 | 0.017775 | 0.0044549
16 | 0.97752 | -0.43255 | 0.0023676 | 0.00059337
17 | 0.97377 | -0.50589 | 0.0043282 | 0.0010847
18 | 0.97177 | -0.54533 | 0.0053425 | 0.0013389
19 | 0.97916 | -0.4003 | 0.0048586 | 0.0012177
20 | 0.97995 | -0.3849 | 0.00547 | 0.0013709
21 | 0.98014 | -0.38107 | 0.0050346 | 0.0012618
22 | 0.97861 | -0.41105 | 0.0030259 | 0.00075836
23 | 0.98124 | -0.35954 | 0.0032448 | 0.00081324
24 | 0.97851 | -0.41307 | 0.00387 | 0.00096992
25 | 0.98191 | -0.34663 | 0 | 0
26 | 0.98171 | -0.35038 | 0 | 0
27 | 0.98098 | -0.36465 | 0.0036745 | 0.00092091
28 | 0.98365 | -0.31272 | 0.0031844 | 0.0007981
29 | 0.9796 | -0.39162 | 0.0036761 | 0.00092131
30 | 0.97437 | -0.49399 | 0.0022389 | 0.00056112
31 | 0.9796 | -0.39292 | 0.0045678 | 0.0011448
32 | 0.98066 | -0.37226 | 0.0028422 | 0.00071231
33 | 0.99192 | -0.15369 | 0.0020627 | 0.00051696
34 | 0.99144 | -0.16312 | 0.0021557 | 0.00054027
35 | 0.99234 | -0.14563 | 0.0020415 | 0.00051164
36 | 0.99114 | -0.16877 | 0.0078208 | 0.0019601
37 | 0.99279 | -0.13687 | 0 | 0
38 | 0.99003 | -0.19029 | 0.0058064 | 0.0014552
39 | 0.99476 | -0.099298 | 0.0057732 | 0.0014469
40 | 0.99118 | -0.16764 | 0.0065242 | 0.0016351
41 | 0.98996 | -0.19166 | 0.0053913 | 0.0013512
42 | 0.99738 | -0.049512 | 0.0052505 | 0.0013159
43 | 0.98921 | -0.20548 | 0.0032547 | 0.00081571
44 | 0.97768 | -0.42917 | 0.0016224 | 0.00040661
45 | 0.97703 | -0.44186 | 0.0050088 | 0.0012553
46 | 0.97795 | -0.42375 | 0.0035562 | 0.00089126
47 | 0.97641 | -0.4539 | 0 | 0
48 | 0.97814 | -0.41998 | 0.0026376 | 0.00066106
49 | 0.97579 | -0.46619 | 0.0059434 | 0.0014895
50 | 0.97926 | -0.3982 | 0.004466 | 0.0011193
51 | 0.97462 | -0.48921 | 0.0054831 | 0.0013742
52 | 0.9787 | -0.4107 | 0 | 0
53 | 0.97894 | -0.40581 | 0.0019007 | 0.00047635
54 | 0.97849 | -0.41477 | 0.0024681 | 0.00061855
55 | 0.97858 | -0.413 | 0.0016654 | 0.00041739
56 | 0.97929 | -0.39895 | 0.0037063 | 0.00092889
57 | 0.97831 | -0.41832 | 0.0016104 | 0.00040361
58 | 0.97858 | -0.41304 | 0.0021775 | 0.00054573
59 | 0.98868 | -0.21573 | 0.0027188 | 0.00068139
60 | 0.98814 | -0.22606 | 0.0030585 | 0.00076654
61 | 0.98658 | -0.25599 | 0.0031485 | 0.00078908
62 | 0.99794 | -0.039031 | 0.0043177 | 0.0010821
63 | 0.98866 | -0.2169 | 0.0069714 | 0.0017472
64 | 0.98866 | -0.21707 | 0.0024511 | 0.0006143
65 | 0.9888 | -0.21435 | 0.015316 | 0.0038387
66 | 0.98901 | -0.21014 | 0.0046961 | 0.001177
67 | 0.98942 | -0.20228 | 0.0043007 | 0.0010779
68 | 0.98481 | -0.29031 | 0.0037731 | 0.00094562
69 | 0.98643 | -0.25893 | 0.0033286 | 0.00083423
70 | 0.98227 | -0.34076 | 0.0030999 | 0.00077692
71 | 0.98239 | -0.33848 | 0 | 0
72 | 0.98166 | -0.3527 | 0.0025049 | 0.00062778
73 | 0.983 | -0.32645 | 0.0026738 | 0.00067011
74 | 0.98073 | -0.3708 | 0.0036819 | 0.00092277
75 | 0.98365 | -0.31388 | 0.0043871 | 0.0010995
76 | 0.98448 | -0.2977 | 0.0034219 | 0.00085761
77 | 0.98589 | -0.27033 | 0.0033956 | 0.00085101
78 | 0.98664 | -0.25574 | 0 | 0
79 | 0.98642 | -0.26005 | 0.0065794 | 0.0016489
80 | 0.98768 | -0.23565 | 0.0032065 | 0.00080362
81 | 0.99245 | -0.14451 | 0.0034936 | 0.00087558
82 | 0.99255 | -0.14256 | 0 | 0
83 | 0.98963 | -0.19797 | 0.0027727 | 0.0006949
84 | 0.97955 | -0.3939 | 0.0027666 | 0.00069337
85 | 0.98977 | -0.19543 | 0.0033676 | 0.000844
86 | 0.99186 | -0.15513 | 0.0038329 | 0.00096061
87 | 0.99322 | -0.12921 | 0.0042214 | 0.001058
88 | 0.9926 | -0.14163 | 0.0033104 | 0.00082967
89 | 0.99426 | -0.10917 | 0.0033281 | 0.00083409
90 | 0.9956 | -0.083596 | 0 | 0
91 | 0.99295 | -0.13493 | 0.005852 | 0.0014666
92 | 0.99263 | -0.14102 | 0.003039 | 0.00076163
93 | 0.99322 | -0.12952 | 0.0075587 | 0.0018944
94 | 0.99345 | -0.12517 | 0.0054126 | 0.0013565
95 | 0.99411 | -0.1125 | 0.003266 | 0.00081855
96 | 0.99436 | -0.10751 | 0.0019999 | 0.00050123
97 | 0.98134 | -0.35934 | 0.0053265 | 0.0013349
98 | 0.98149 | -0.35647 | 0.0044527 | 0.001116
99 | 0.9812 | -0.3622 | 0.0035373 | 0.00088652
100 | 0.98032 | -0.37936 | 0.0054221 | 0.0013589
101 | 0.98283 | -0.33031 | 0.007767 | 0.0019466
102 | 0.9811 | -0.36407 | 0.0051526 | 0.0012914
103 | 0.9802 | -0.38172 | 0.0078115 | 0.0019577
104 | 0.98017 | -0.38229 | 0 | 0
105 | 0.98014 | -0.38285 | 0 | 0
106 | 0.98336 | -0.31988 | 0.0010198 | 0.00025559
107 | 0.98418 | -0.3039 | 0.0012349 | 0.00030949
108 | 1 | 0 | -0.45852 | -0.11703
109 | 0.99732 | -0.050894 | 0.0033711 | 0.00084488
110 | 0.9927 | -0.13913 | 0.0037946 | 0.000951
111 | 0.99262 | -0.14065 | 0.0039906 | 0.0010001
112 | 0.9919 | -0.15463 | 0.0038896 | 0.00097483
113 | 0.98958 | -0.19933 | 0.0078171 | 0.0019591
114 | 0.98941 | -0.20261 | 0.0065614 | 0.0016444
115 | 0.97818 | -0.42091 | 0.0070242 | 0.0017604
116 | 0.97813 | -0.4218 | 0.0033556 | 0.00084099
117 | 0.98014 | -0.38294 | 0.00073622 | 0.00018452
118 | 0.98764 | -0.23664 | 0.0029874 | 0.00074872
119 | 0.98745 | -0.24036 | 0.0074475 | 0.0018665
120 | 0.98605 | -0.26756 | 0.00079644 | 0.00019961
121 | 0.98507 | -0.28661 | 0 | 0
122 | 0.98504 | -0.28713 | 0.0011144 | 0.00027928
123 | 0.98466 | -0.29462 | 0.00039298 | 9.849e-05
124 | 0.98399 | -0.30776 | 0.003629 | 0.00090952
125 | 0.98374 | -0.3126 | 0.0018715 | 0.00046905
126 | 0.98348 | -0.31759 | 0.0033274 | 0.00083394
127 | 0.98335 | -0.32019 | 0.0051458 | 0.0012897
128 | 0.98331 | -0.32095 | 0.0030551 | 0.00076569
129 | 0.98324 | -0.32226 | 0 | 0
130 | 0.98313 | -0.32445 | 0.0030185 | 0.0007565
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0037209 | -0.00093253 | 0.0037212 | 0.00093241 | 2.9501e-07 | -1.1757e-07 | 0.005669 | 0.0056689 | 0.005669 | 0.97668 | -0.44909 | 0.97676 | -0.44742 | 1.5574
1 | 0.002175 | 0.00054507 | -0.002175 | -0.00054509 | 9.2195e-09 | -2.212e-08 | 0.0033136 | 0.0033137 | 0.0033137 | 0.97668 | -0.44909 | 0.97667 | -0.44917 | 0.91035
2 | -0.0055037 | -0.0013791 | 0.0055037 | 0.0013791 | 4.8076e-10 | 7.7874e-11 | 0.0083843 | 0.0083843 | 0.0083843 | 0.97676 | -0.44742 | 0.97676 | -0.44742 | 2.3034
3 | -0.0071354 | -0.0017881 | 0.0071364 | 0.0017885 | 1.0777e-06 | 3.8523e-07 | 0.01087 | 0.01087 | 0.01087 | 0.97676 | -0.44742 | 0.97692 | -0.44425 | 2.9863
4 | -0.013404 | -0.0033592 | 0.013411 | 0.0033633 | 7.2912e-06 | 4.082e-06 | 0.020416 | 0.020416 | 0.020416 | 0.97692 | -0.44425 | 0.9775 | -0.43284 | 5.6089
5 | -0.016457 | -0.0041267 | 0.01646 | 0.0041282 | 2.4624e-06 | 1.4448e-06 | 0.025053 | 0.025053 | 0.025053 | 0.9775 | -0.43284 | 0.97766 | -0.4297 | 6.8827
6 | -0.0036028 | -0.00090294 | 0.003603 | 0.00090283 | 2.2505e-07 | -1.0883e-07 | 0.0054696 | 0.0054695 | 0.0054696 | 0.98015 | -0.38215 | 0.98022 | -0.38084 | 1.5026
7 | 0.031285 | 0.0078553 | -0.031267 | -0.0078441 | 1.8025e-05 | 1.1268e-05 | 0.047497 | 0.047498 | 0.047498 | 0.98022 | -0.38084 | 0.9796 | -0.39292 | 13.0488
8 | -0.034888 | -0.0087582 | 0.034902 | 0.0087671 | 1.4283e-05 | 8.9702e-06 | 0.052967 | 0.052967 | 0.052967 | 0.98022 | -0.38084 | 0.98066 | -0.37226 | 14.5513
9 | -0.022437 | -0.0056262 | 0.022437 | 0.0056263 | 1.8669e-07 | 1.1413e-07 | 0.03415 | 0.03415 | 0.03415 | 0.97766 | -0.4297 | 0.97767 | -0.42952 | 9.3819
10 | -0.024805 | -0.006219 | 0.024824 | 0.0062307 | 1.9008e-05 | 1.1719e-05 | 0.037754 | 0.037754 | 0.037754 | 0.97767 | -0.42952 | 0.97849 | -0.41346 | 10.372
11 | 0.0023679 | 0.00059271 | -0.0023677 | -0.0005931 | 1.9947e-07 | -3.8588e-07 | 0.0036037 | 0.0036039 | 0.0036039 | 0.97767 | -0.42952 | 0.97758 | -0.43129 | 0.99008
12 | -0.028972 | -0.0072703 | 0.028979 | 0.0072746 | 6.8244e-06 | 4.2498e-06 | 0.044062 | 0.044062 | 0.044062 | 0.97849 | -0.41346 | 0.97874 | -0.40852 | 12.1049
13 | 0.0023677 | 0.0005931 | -0.0023676 | -0.00059337 | 1.4166e-07 | -2.7397e-07 | 0.0036039 | 0.003604 | 0.003604 | 0.97758 | -0.43129 | 0.97752 | -0.43255 | 0.99011
14 | 0.0068971 | 0.0017284 | -0.0068963 | -0.0017282 | 8.3083e-07 | 2.7853e-07 | 0.010486 | 0.010486 | 0.010486 | 0.97874 | -0.40852 | 0.97861 | -0.41105 | 2.8808
15 | -0.035876 | -0.009003 | 0.03589 | 0.0090118 | 1.4057e-05 | 8.838e-06 | 0.054547 | 0.054547 | 0.054547 | 0.97874 | -0.40852 | 0.97916 | -0.4003 | 14.9856
16 | -0.023131 | -0.0058019 | 0.02314 | 0.0058073 | 8.7979e-06 | 5.3983e-06 | 0.035398 | 0.035398 | 0.035398 | 0.97241 | -0.53279 | 0.97281 | -0.52482 | 9.7246
17 | 0.023131 | 0.0058019 | -0.023118 | -0.0057938 | 1.3143e-05 | 8.0646e-06 | 0.035398 | 0.035398 | 0.035398 | 0.97241 | -0.53279 | 0.9718 | -0.54472 | 9.7247
18 | -0.02314 | -0.0058073 | 0.023161 | 0.0058201 | 2.0906e-05 | 1.2827e-05 | 0.035398 | 0.035397 | 0.035398 | 0.97281 | -0.52482 | 0.97377 | -0.50589 | 9.7246
19 | 0.0053426 | 0.001339 | -0.0053425 | -0.0013389 | 1.5561e-07 | 2.2767e-08 | 0.0081806 | 0.0081806 | 0.0081806 | 0.9718 | -0.54472 | 0.97177 | -0.54533 | 2.2474
20 | -0.027489 | -0.0069049 | 0.027504 | 0.0069146 | 1.5623e-05 | 9.7046e-06 | 0.042011 | 0.042011 | 0.042011 | 0.97377 | -0.50589 | 0.97437 | -0.49399 | 11.5415
21 | -0.040749 | -0.01023 | 0.040778 | 0.010248 | 2.9969e-05 | 1.8918e-05 | 0.061931 | 0.061931 | 0.061931 | 0.97916 | -0.4003 | 0.97995 | -0.3849 | 17.014
22 | -0.046248 | -0.011619 | 0.046257 | 0.011625 | 8.4515e-06 | 5.3514e-06 | 0.070237 | 0.070237 | 0.070237 | 0.97995 | -0.3849 | 0.98014 | -0.38107 | 19.2958
23 | -0.051291 | -0.012886 | 0.051344 | 0.01292 | 5.2769e-05 | 3.3479e-05 | 0.07788 | 0.07788 | 0.07788 | 0.98014 | -0.38107 | 0.98124 | -0.35954 | 21.3956
24 | 0.0038704 | 0.00096979 | -0.00387 | -0.00096992 | 3.7368e-07 | -1.223e-07 | 0.005885 | 0.0058851 | 0.0058851 | 0.97861 | -0.41105 | 0.97851 | -0.41307 | 1.6168
25 | -0.054589 | -0.013733 | 0.054623 | 0.013755 | 3.3679e-05 | 2.1389e-05 | 0.082801 | 0.082801 | 0.082801 | 0.98124 | -0.35954 | 0.98191 | -0.34663 | 22.7474
26 | -0.12079 | -0.030496 | 0.12099 | 0.030621 | 0.00019661 | 0.00012563 | 0.18313 | 0.18313 | 0.18313 | 0.98191 | -0.34663 | 0.98365 | -0.31272 | 50.3104
27 | 0.066168 | 0.016741 | -0.066156 | -0.016733 | 1.189e-05 | 7.5701e-06 | 0.10033 | 0.10033 | 0.10033 | 0.98191 | -0.34663 | 0.98171 | -0.35038 | 27.563
28 | 0.066156 | 0.016733 | -0.06611 | -0.016705 | 4.5262e-05 | 2.8816e-05 | 0.10033 | 0.10033 | 0.10033 | 0.98171 | -0.35038 | 0.98098 | -0.36465 | 27.563
29 | 0.062436 | 0.015784 | -0.062355 | -0.015732 | 8.0655e-05 | 5.1317e-05 | 0.094756 | 0.094756 | 0.094756 | 0.98098 | -0.36465 | 0.9796 | -0.39162 | 26.0318
30 | -0.12417 | -0.031419 | 0.12431 | 0.031505 | 0.00013366 | 8.5416e-05 | 0.18795 | 0.18795 | 0.18795 | 0.98365 | -0.31272 | 0.98481 | -0.29031 | 51.6338
31 | 0.058679 | 0.014811 | -0.058661 | -0.014799 | 1.8463e-05 | 1.1738e-05 | 0.089172 | 0.089172 | 0.089172 | 0.9796 | -0.39162 | 0.97926 | -0.3982 | 24.4978
32 | -0.029743 | -0.0074757 | 0.02975 | 0.0074799 | 6.7889e-06 | 4.2356e-06 | 0.04543 | 0.04543 | 0.04543 | 0.97437 | -0.49399 | 0.97462 | -0.48921 | 12.4808
33 | 0.026699 | 0.0066993 | -0.026698 | -0.0066985 | 1.2423e-06 | 7.6975e-07 | 0.040559 | 0.040559 | 0.040559 | 0.9796 | -0.39292 | 0.97955 | -0.3939 | 11.1426
34 | -0.037745 | -0.0094794 | 0.037747 | 0.0094811 | 2.6217e-06 | 1.651e-06 | 0.057279 | 0.057279 | 0.057279 | 0.98066 | -0.37226 | 0.98073 | -0.3708 | 15.7361
35 | 0.055032 | 0.013838 | -0.055007 | -0.013823 | 2.4776e-05 | 1.5731e-05 | 0.082571 | 0.082571 | 0.082571 | 0.99192 | -0.15369 | 0.99144 | -0.16312 | 22.6845
36 | -0.057095 | -0.014355 | 0.057117 | 0.014369 | 2.1983e-05 | 1.3966e-05 | 0.085666 | 0.085666 | 0.085666 | 0.99192 | -0.15369 | 0.99234 | -0.14563 | 23.5345
37 | 0.052851 | 0.013282 | -0.052837 | -0.013273 | 1.4239e-05 | 9.0352e-06 | 0.079336 | 0.079336 | 0.079336 | 0.99144 | -0.16312 | 0.99114 | -0.16877 | 21.7956
38 | -0.059158 | -0.014881 | 0.059183 | 0.014897 | 2.476e-05 | 1.5738e-05 | 0.088727 | 0.088727 | 0.088727 | 0.99234 | -0.14563 | 0.99279 | -0.13687 | 24.3755
39 | 0.045016 | 0.011313 | -0.04497 | -0.011284 | 4.6206e-05 | 2.9225e-05 | 0.067595 | 0.067595 | 0.067595 | 0.99114 | -0.16877 | 0.99003 | -0.19029 | 18.57
40 | -0.21033 | -0.053528 | 0.21071 | 0.053772 | 0.00038175 | 0.00024379 | 0.31553 | 0.31553 | 0.31553 | 0.99279 | -0.13687 | 0.99476 | -0.099298 | 43.3423
41 | 0.15114 | 0.038632 | -0.15092 | -0.038488 | 0.00022456 | 0.00014312 | 0.22681 | 0.22681 | 0.22681 | 0.99279 | -0.13687 | 0.99118 | -0.16764 | 31.1546
42 | 0.039164 | 0.0098289 | -0.039161 | -0.0098273 | 2.5653e-06 | 1.6164e-06 | 0.058868 | 0.058868 | 0.058868 | 0.99003 | -0.19029 | 0.98996 | -0.19166 | 16.1725
43 | -0.21648 | -0.055219 | 0.217 | 0.055552 | 0.00052185 | 0.0003333 | 0.32417 | 0.32417 | 0.32417 | 0.99476 | -0.099298 | 0.99738 | -0.049512 | 44.5285
44 | 0.1444 | 0.036853 | -0.14413 | -0.036685 | 0.00026343 | 0.00016783 | 0.21701 | 0.21701 | 0.21701 | 0.99118 | -0.16764 | 0.98921 | -0.20548 | 29.8092
45 | 0.03377 | 0.0084761 | -0.033753 | -0.0084654 | 1.7097e-05 | 1.0715e-05 | 0.050764 | 0.050764 | 0.050764 | 0.98996 | -0.19166 | 0.98942 | -0.20228 | 13.9462
46 | -0.22225 | -0.056868 | 0.22237 | 0.05694 | 0.00011283 | 7.2068e-05 | 0.332 | 0.332 | 0.332 | 0.99738 | -0.049512 | 0.99794 | -0.039031 | 45.6044
47 | 0.14088 | 0.03587 | -0.14081 | -0.035825 | 6.9594e-05 | 4.4487e-05 | 0.21212 | 0.21212 | 0.21212 | 0.98921 | -0.20548 | 0.98868 | -0.21573 | 58.2735
48 | 0.0463 | 0.011671 | -0.046272 | -0.011654 | 2.8117e-05 | 1.7806e-05 | 0.070493 | 0.070493 | 0.070493 | 0.97768 | -0.42917 | 0.97703 | -0.44186 | 19.3662
49 | -0.047923 | -0.012078 | 0.047935 | 0.012086 | 1.2416e-05 | 7.8685e-06 | 0.072962 | 0.072962 | 0.072962 | 0.97768 | -0.42917 | 0.97795 | -0.42375 | 20.0446
50 | 0.041263 | 0.010398 | -0.04124 | -0.010383 | 2.3735e-05 | 1.499e-05 | 0.062865 | 0.062865 | 0.062865 | 0.97703 | -0.44186 | 0.97641 | -0.4539 | 17.2705
51 | -0.051491 | -0.012977 | 0.051501 | 0.012983 | 9.305e-06 | 5.9045e-06 | 0.078373 | 0.078373 | 0.078373 | 0.97795 | -0.42375 | 0.97814 | -0.41998 | 21.5311
52 | 0.04124 | 0.010383 | -0.041215 | -0.010368 | 2.4232e-05 | 1.5304e-05 | 0.062865 | 0.062865 | 0.062865 | 0.97641 | -0.4539 | 0.97579 | -0.46619 | 17.2706
53 | -0.054138 | -0.013644 | 0.054195 | 0.01368 | 5.6475e-05 | 3.5865e-05 | 0.082386 | 0.082386 | 0.082386 | 0.97814 | -0.41998 | 0.97926 | -0.3982 | 22.6335
54 | 0.035272 | 0.0088785 | -0.035233 | -0.0088541 | 3.8753e-05 | 2.4357e-05 | 0.053802 | 0.053802 | 0.053802 | 0.97579 | -0.46619 | 0.97462 | -0.48921 | 14.7807
55 | -0.018308 | -0.0045898 | 0.018312 | 0.0045923 | 4.2657e-06 | 2.5455e-06 | 0.027836 | 0.027836 | 0.027836 | 0.9787 | -0.4107 | 0.97894 | -0.40581 | 7.6472
56 | 0.014465 | 0.0036268 | -0.014462 | -0.0036252 | 2.8057e-06 | 1.6013e-06 | 0.021993 | 0.021993 | 0.021993 | 0.9787 | -0.4107 | 0.97849 | -0.41477 | 6.0419
57 | 0.0038433 | 0.00096296 | -0.0038429 | -0.00096311 | 4.2089e-07 | -1.4364e-07 | 0.0058433 | 0.0058435 | 0.0058435 | 0.9787 | -0.4107 | 0.97858 | -0.413 | 1.6053
58 | -0.020213 | -0.0050687 | 0.020219 | 0.0050727 | 6.6142e-06 | 3.9981e-06 | 0.030725 | 0.030725 | 0.030725 | 0.97894 | -0.40581 | 0.97929 | -0.39895 | 8.4409
59 | 0.011994 | 0.0030067 | -0.011992 | -0.0030056 | 2.0259e-06 | 1.0926e-06 | 0.018239 | 0.018239 | 0.018239 | 0.97849 | -0.41477 | 0.97831 | -0.41832 | 5.0109
60 | 0.0021775 | 0.00054572 | -0.0021775 | -0.00054573 | 4.7411e-09 | -1.1454e-08 | 0.0033111 | 0.0033111 | 0.0033111 | 0.97858 | -0.413 | 0.97858 | -0.41304 | 0.90963
61 | -0.023926 | -0.0060016 | 0.023931 | 0.0060051 | 5.7612e-06 | 3.5409e-06 | 0.036356 | 0.036356 | 0.036356 | 0.97929 | -0.39895 | 0.97955 | -0.3939 | 9.988
62 | 0.010381 | 0.002602 | -0.01038 | -0.0026013 | 1.2826e-06 | 6.4866e-07 | 0.01579 | 0.01579 | 0.01579 | 0.97831 | -0.41832 | 0.97818 | -0.42091 | 4.3379
63 | 0.13809 | 0.035144 | -0.13802 | -0.0351 | 6.8782e-05 | 4.3966e-05 | 0.20802 | 0.20802 | 0.20802 | 0.98868 | -0.21573 | 0.98814 | -0.22606 | 57.1493
64 | 0.13496 | 0.034333 | -0.13477 | -0.034209 | 0.00019433 | 0.00012421 | 0.20342 | 0.20342 | 0.20342 | 0.98814 | -0.22606 | 0.98658 | -0.25599 | 55.884
65 | 0.13162 | 0.03342 | -0.1316 | -0.033408 | 1.8624e-05 | 1.1903e-05 | 0.19867 | 0.19867 | 0.19867 | 0.98658 | -0.25599 | 0.98643 | -0.25893 | 54.5794
66 | -0.22668 | -0.058022 | 0.22711 | 0.058297 | 0.00042933 | 0.00027425 | 0.33844 | 0.33844 | 0.33844 | 0.99794 | -0.039031 | 1 | 0 | 46.4888
67 | 0.0024511 | 0.00061426 | -0.0024511 | -0.0006143 | 1.9221e-08 | -3.5995e-08 | 0.0036891 | 0.0036891 | 0.0036891 | 0.98866 | -0.2169 | 0.98866 | -0.21707 | 1.0135
68 | -0.0094225 | -0.0023615 | 0.0094236 | 0.002362 | 1.1463e-06 | 5.3867e-07 | 0.014182 | 0.014181 | 0.014182 | 0.98866 | -0.2169 | 0.9888 | -0.21435 | 3.896
69 | -0.02474 | -0.0062006 | 0.024745 | 0.0062037 | 4.9559e-06 | 3.0495e-06 | 0.037231 | 0.037231 | 0.037231 | 0.9888 | -0.21435 | 0.98901 | -0.21014 | 10.2282
70 | -0.029441 | -0.0073806 | 0.029452 | 0.0073875 | 1.103e-05 | 6.8667e-06 | 0.044296 | 0.044296 | 0.044296 | 0.98901 | -0.21014 | 0.98942 | -0.20228 | 12.1693
71 | -0.12808 | -0.03245 | 0.12827 | 0.032574 | 0.00019341 | 0.00012361 | 0.19365 | 0.19365 | 0.19365 | 0.98481 | -0.29031 | 0.98643 | -0.25893 | 53.2
72 | -0.0030999 | -0.00077692 | 0.0031003 | 0.00077662 | 3.3718e-07 | -3.004e-07 | 0.004696 | 0.0046958 | 0.004696 | 0.98227 | -0.34076 | 0.98239 | -0.33848 | 1.2901
73 | 0.044 | 0.011073 | -0.04397 | -0.011054 | 2.9874e-05 | 1.8893e-05 | 0.066663 | 0.066663 | 0.066663 | 0.98239 | -0.33848 | 0.98166 | -0.3527 | 18.3139
74 | -0.0471 | -0.01185 | 0.047127 | 0.011867 | 2.7085e-05 | 1.7155e-05 | 0.071358 | 0.071358 | 0.071358 | 0.98239 | -0.33848 | 0.983 | -0.32645 | 19.604
75 | 0.041465 | 0.010426 | -0.041429 | -0.010404 | 3.5819e-05 | 2.2619e-05 | 0.062866 | 0.062866 | 0.062866 | 0.98166 | -0.3527 | 0.98073 | -0.3708 | 17.2708
76 | -0.049801 | -0.012537 | 0.049831 | 0.012556 | 2.9947e-05 | 1.8988e-05 | 0.075406 | 0.075406 | 0.075406 | 0.983 | -0.32645 | 0.98365 | -0.31388 | 20.7159
77 | -0.054218 | -0.013656 | 0.05426 | 0.013682 | 4.1976e-05 | 2.6653e-05 | 0.082042 | 0.082042 | 0.082042 | 0.98365 | -0.31388 | 0.98448 | -0.2977 | 22.5391
78 | -0.057682 | -0.01454 | 0.057757 | 0.014588 | 7.5647e-05 | 4.8076e-05 | 0.087214 | 0.087214 | 0.087214 | 0.98448 | -0.2977 | 0.98589 | -0.27033 | 23.96
79 | -0.061153 | -0.015439 | 0.061196 | 0.015466 | 4.2799e-05 | 2.722e-05 | 0.092339 | 0.092339 | 0.092339 | 0.98589 | -0.27033 | 0.98664 | -0.25574 | 25.3679
80 | 0.0065807 | 0.0016493 | -0.0065794 | -0.0016489 | 1.3528e-06 | 3.9818e-07 | 0.0099248 | 0.009925 | 0.009925 | 0.98664 | -0.25574 | 0.98642 | -0.26005 | 2.7266
81 | -0.067777 | -0.017115 | 0.067842 | 0.017157 | 6.5305e-05 | 4.1582e-05 | 0.10226 | 0.10226 | 0.10226 | 0.98664 | -0.25574 | 0.98768 | -0.23565 | 28.0945
82 | -0.071048 | -0.017961 | 0.071177 | 0.018043 | 0.00012862 | 8.1936e-05 | 0.10709 | 0.10709 | 0.10709 | 0.98768 | -0.23565 | 0.98963 | -0.19797 | 29.4216
83 | -0.0034936 | -0.00087558 | 0.0034939 | 0.00087538 | 3.2431e-07 | -1.9979e-07 | 0.0052381 | 0.0052379 | 0.0052381 | 0.99245 | -0.14451 | 0.99255 | -0.14256 | 1.439
84 | -0.0034939 | -0.00087538 | 0.0034941 | 0.00087529 | 1.5482e-07 | -9.5415e-08 | 0.0052379 | 0.0052379 | 0.0052379 | 0.99255 | -0.14256 | 0.9926 | -0.14163 | 1.439
85 | -0.07395 | -0.018738 | 0.073959 | 0.018743 | 9.0254e-06 | 5.7513e-06 | 0.11126 | 0.11126 | 0.11126 | 0.98963 | -0.19797 | 0.98977 | -0.19543 | 30.5669
86 | -0.077326 | -0.019587 | 0.077476 | 0.019683 | 0.00014999 | 9.5611e-05 | 0.11633 | 0.11633 | 0.11633 | 0.98977 | -0.19543 | 0.99186 | -0.15513 | 31.9578
87 | -0.081309 | -0.020643 | 0.081411 | 0.020708 | 0.00010156 | 6.4765e-05 | 0.12208 | 0.12208 | 0.12208 | 0.99186 | -0.15513 | 0.99322 | -0.12921 | 33.5375
88 | -0.085632 | -0.021766 | 0.085715 | 0.021819 | 8.2725e-05 | 5.2771e-05 | 0.1284 | 0.1284 | 0.1284 | 0.99322 | -0.12921 | 0.99426 | -0.10917 | 35.2749
89 | -0.0068045 | -0.001705 | 0.0068047 | 0.001705 | 1.9716e-07 | 6.0867e-08 | 0.010201 | 0.010201 | 0.010201 | 0.9926 | -0.14163 | 0.99263 | -0.14102 | 2.8024
90 | -0.089043 | -0.022653 | 0.089153 | 0.022723 | 0.0001099 | 7.0119e-05 | 0.13338 | 0.13338 | 0.13338 | 0.99426 | -0.10917 | 0.9956 | -0.083596 | 36.6432
91 | 0.034008 | 0.0085505 | -0.03397 | -0.0085262 | 3.8798e-05 | 2.4311e-05 | 0.050838 | 0.050838 | 0.050838 | 0.9956 | -0.083596 | 0.99436 | -0.10751 | 13.9666
92 | -0.22547 | -0.057297 | 0.22582 | 0.057524 | 0.00035564 | 0.00022718 | 0.33726 | 0.33726 | 0.33726 | 0.9956 | -0.083596 | 0.99732 | -0.050894 | 46.327
93 | 0.10231 | 0.026024 | -0.10203 | -0.025849 | 0.00027299 | 0.00017431 | 0.15304 | 0.15304 | 0.15304 | 0.9956 | -0.083596 | 0.9927 | -0.13913 | 42.0444
94 | 0.0098465 | 0.002468 | -0.0098437 | -0.0024667 | 2.8598e-06 | 1.3774e-06 | 0.014756 | 0.014756 | 0.014756 | 0.99295 | -0.13493 | 0.99263 | -0.14102 | 4.0539
95 | -0.015698 | -0.0039347 | 0.015703 | 0.003937 | 4.0428e-06 | 2.3353e-06 | 0.023526 | 0.023526 | 0.023526 | 0.99295 | -0.13493 | 0.99322 | -0.12952 | 6.4631
96 | -0.023261 | -0.0058314 | 0.023266 | 0.0058344 | 4.8298e-06 | 2.9538e-06 | 0.03485 | 0.03485 | 0.03485 | 0.99322 | -0.12952 | 0.99345 | -0.12517 | 9.5741
97 | -0.028679 | -0.0071909 | 0.028696 | 0.0072016 | 1.7317e-05 | 1.0759e-05 | 0.042957 | 0.042957 | 0.042957 | 0.99345 | -0.12517 | 0.99411 | -0.1125 | 11.8013
98 | -0.031962 | -0.0080202 | 0.03197 | 0.0080249 | 7.6046e-06 | 4.7521e-06 | 0.047846 | 0.047845 | 0.047846 | 0.99411 | -0.1125 | 0.99436 | -0.10751 | 13.1444
99 | -0.028002 | -0.0070214 | 0.028006 | 0.0070238 | 3.8334e-06 | 2.3817e-06 | 0.042461 | 0.042461 | 0.042461 | 0.98134 | -0.35934 | 0.98149 | -0.35647 | 11.6651
100 | 0.0086915 | 0.0021785 | -0.0086903 | -0.0021779 | 1.1853e-06 | 5.2869e-07 | 0.013179 | 0.013179 | 0.013179 | 0.98134 | -0.35934 | 0.9812 | -0.3622 | 3.6206
101 | 0.013984 | 0.003508 | -0.013971 | -0.0035005 | 1.3336e-05 | 7.5371e-06 | 0.021205 | 0.021206 | 0.021206 | 0.98134 | -0.35934 | 0.98032 | -0.37936 | 5.8257
102 | -0.032459 | -0.0081397 | 0.032499 | 0.0081651 | 4.0523e-05 | 2.537e-05 | 0.049212 | 0.049211 | 0.049212 | 0.98149 | -0.35647 | 0.98283 | -0.33031 | 13.5197
103 | 0.0051531 | 0.0012914 | -0.0051526 | -0.0012914 | 4.59e-07 | 4.0639e-08 | 0.0078147 | 0.0078148 | 0.0078148 | 0.9812 | -0.3622 | 0.9811 | -0.36407 | 2.1469
104 | 0.0085487 | 0.0021416 | -0.0085477 | -0.0021411 | 9.6024e-07 | 4.2283e-07 | 0.012976 | 0.012976 | 0.012976 | 0.98032 | -0.37936 | 0.9802 | -0.38172 | 3.5647
105 | -0.040266 | -0.010112 | 0.040286 | 0.010124 | 2.0047e-05 | 1.2648e-05 | 0.060971 | 0.060971 | 0.060971 | 0.98283 | -0.33031 | 0.98336 | -0.31988 | 16.7502
106 | 0.00073627 | 0.0001834 | -0.00073625 | -0.00018392 | 1.9741e-08 | -5.188e-07 | 0.0011173 | 0.0011175 | 0.0011175 | 0.9802 | -0.38172 | 0.98017 | -0.38229 | 0.307
107 | 0.00073625 | 0.00018392 | -0.00073623 | -0.00018444 | 1.9846e-08 | -5.2135e-07 | 0.0011175 | 0.0011177 | 0.0011177 | 0.98017 | -0.38229 | 0.98014 | -0.38285 | 0.30706
108 | 0.00073623 | 0.00018444 | -0.00073622 | -0.00018452 | 2.9138e-09 | -7.6527e-08 | 0.0011177 | 0.0011177 | 0.0011177 | 0.98014 | -0.38285 | 0.98014 | -0.38294 | 0.30706
109 | -0.041306 | -0.01038 | 0.041338 | 0.0104 | 3.1542e-05 | 1.9914e-05 | 0.062514 | 0.062514 | 0.062514 | 0.98336 | -0.31988 | 0.98418 | -0.3039 | 17.1742
110 | -0.042573 | -0.010709 | 0.042608 | 0.010732 | 3.5178e-05 | 2.2226e-05 | 0.064381 | 0.064381 | 0.064381 | 0.98418 | -0.3039 | 0.98507 | -0.28661 | 17.6871
111 | 0.22976 | 0.05873 | -0.22919 | -0.058369 | 0.00056412 | 0.00036036 | 0.34229 | 0.34229 | 0.34229 | 1 | 0 | 0.99732 | -0.050894 | 47.0179
112 | 0.098239 | 0.024898 | -0.098231 | -0.024894 | 7.1907e-06 | 4.5906e-06 | 0.14735 | 0.14735 | 0.14735 | 0.9927 | -0.13913 | 0.99262 | -0.14065 | 40.4818
113 | 0.094241 | 0.023893 | -0.094177 | -0.023853 | 6.3235e-05 | 4.0361e-05 | 0.14137 | 0.14137 | 0.14137 | 0.99262 | -0.14065 | 0.9919 | -0.15463 | 38.8383
114 | 0.090288 | 0.022878 | -0.090094 | -0.022755 | 0.00019347 | 0.00012346 | 0.13554 | 0.13554 | 0.13554 | 0.9919 | -0.15463 | 0.98958 | -0.19933 | 37.2353
115 | 0.082277 | 0.020796 | -0.082264 | -0.020787 | 1.2946e-05 | 8.2564e-06 | 0.12378 | 0.12378 | 0.12378 | 0.98958 | -0.19933 | 0.98941 | -0.20261 | 34.0061
116 | 0.075703 | 0.019143 | -0.07558 | -0.019064 | 0.00012336 | 7.8624e-05 | 0.11391 | 0.11391 | 0.11391 | 0.98941 | -0.20261 | 0.98764 | -0.23664 | 31.2951
117 | 0.0033557 | 0.0008409 | -0.0033556 | -0.00084099 | 1.4227e-07 | -9.1694e-08 | 0.0051048 | 0.0051048 | 0.0051048 | 0.97818 | -0.42091 | 0.97813 | -0.4218 | 1.4024
118 | 0.072592 | 0.018316 | -0.072579 | -0.018307 | 1.2908e-05 | 8.2242e-06 | 0.10941 | 0.10941 | 0.10941 | 0.98764 | -0.23664 | 0.98745 | -0.24036 | 30.0586
119 | 0.065132 | 0.016441 | -0.065047 | -0.016387 | 8.474e-05 | 5.3934e-05 | 0.098191 | 0.098191 | 0.098191 | 0.98745 | -0.24036 | 0.98605 | -0.26756 | 26.9755
120 | 0.064251 | 0.016187 | -0.064192 | -0.01615 | 5.8504e-05 | 3.7231e-05 | 0.096989 | 0.096989 | 0.096989 | 0.98605 | -0.26756 | 0.98507 | -0.28661 | 26.6453
121 | 0.02047 | 0.0051396 | -0.020462 | -0.0051349 | 7.8133e-06 | 4.7233e-06 | 0.030925 | 0.030925 | 0.030925 | 0.98507 | -0.28661 | 0.98466 | -0.29462 | 8.4958
122 | 0.0011144 | 0.00027897 | -0.0011144 | -0.00027928 | 2.7236e-08 | -3.0887e-07 | 0.0016832 | 0.0016834 | 0.0016834 | 0.98507 | -0.28661 | 0.98504 | -0.28713 | 0.46246
123 | 0.020069 | 0.0050364 | -0.020057 | -0.0050288 | 1.2569e-05 | 7.5808e-06 | 0.030331 | 0.030331 | 0.030331 | 0.98466 | -0.29462 | 0.98399 | -0.30776 | 8.3327
124 | 0.016428 | 0.0041193 | -0.016424 | -0.0041171 | 3.7895e-06 | 2.2174e-06 | 0.024843 | 0.024843 | 0.024843 | 0.98399 | -0.30776 | 0.98374 | -0.3126 | 6.8251
125 | 0.014552 | 0.003648 | -0.014549 | -0.0036461 | 3.4562e-06 | 1.9705e-06 | 0.022012 | 0.022013 | 0.022013 | 0.98374 | -0.3126 | 0.98348 | -0.31759 | 6.0474
126 | 0.011221 | 0.0028121 | -0.01122 | -0.0028114 | 1.3892e-06 | 7.2602e-07 | 0.016978 | 0.016978 | 0.016978 | 0.98348 | -0.31759 | 0.98335 | -0.32019 | 4.6643
127 | 0.0060743 | 0.0015217 | -0.0060741 | -0.0015217 | 2.2188e-07 | 5.3161e-08 | 0.0091915 | 0.0091915 | 0.0091915 | 0.98335 | -0.32019 | 0.98331 | -0.32095 | 2.5251
128 | 0.003019 | 0.000756 | -0.0030188 | -0.00075619 | 1.8749e-07 | -1.8388e-07 | 0.0045683 | 0.0045684 | 0.0045684 | 0.98331 | -0.32095 | 0.98324 | -0.32226 | 1.2551
129 | 0.0030188 | 0.00075619 | -0.0030185 | -0.0007565 | 3.1465e-07 | -3.0846e-07 | 0.0045684 | 0.0045686 | 0.0045686 | 0.98324 | -0.32226 | 0.98313 | -0.32445 | 1.2551

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46099 | 0.11765

## res_load
| p_mw | q_mvar
0 | 0.001546 | 0.00038746
1 | 0.0017824 | 0.00044672
2 | 0.002175 | 0.00054509
3 | 0.0016317 | 0.00040894
4 | 0.0062674 | 0.0015708
5 | 0.0030462 | 0.00076344
6 | 0.0036028 | 0.00090294
7 | 0.0059771 | 0.001498
8 | 0.0041479 | 0.0010396
9 | 0.017775 | 0.0044549
10 | 0.0023676 | 0.00059337
11 | 0.0043282 | 0.0010847
12 | 0.0053425 | 0.0013389
13 | 0.0048586 | 0.0012177
14 | 0.00547 | 0.0013709
15 | 0.0050346 | 0.0012618
16 | 0.0030259 | 0.00075836
17 | 0.0032448 | 0.00081324
18 | 0.00387 | 0.00096992
19 | 0.0036745 | 0.00092091
20 | 0.0031844 | 0.0007981
21 | 0.0036761 | 0.00092131
22 | 0.0022389 | 0.00056112
23 | 0.0045678 | 0.0011448
24 | 0.0028422 | 0.00071231
25 | 0.0020627 | 0.00051696
26 | 0.0021557 | 0.00054027
27 | 0.0020415 | 0.00051164
28 | 0.0078208 | 0.0019601
29 | 0.0058064 | 0.0014552
30 | 0.0057732 | 0.0014469
31 | 0.0065242 | 0.0016351
32 | 0.0053913 | 0.0013512
33 | 0.0052505 | 0.0013159
34 | 0.0032547 | 0.00081571
35 | 0.0016224 | 0.00040661
36 | 0.0050088 | 0.0012553
37 | 0.0035562 | 0.00089126
38 | 0.0026376 | 0.00066106
39 | 0.0059434 | 0.0014895
40 | 0.004466 | 0.0011193
41 | 0.0054831 | 0.0013742
42 | 0.0019007 | 0.00047635
43 | 0.0024681 | 0.00061855
44 | 0.0016654 | 0.00041739
45 | 0.0037063 | 0.00092889
46 | 0.0016104 | 0.00040361
47 | 0.0021775 | 0.00054573
48 | 0.0027188 | 0.00068139
49 | 0.0030585 | 0.00076654
50 | 0.0031485 | 0.00078908
51 | 0.0043177 | 0.0010821
52 | 0.0069714 | 0.0017472
53 | 0.0024511 | 0.0006143
54 | 0.015316 | 0.0038387
55 | 0.0046961 | 0.001177
56 | 0.0043007 | 0.0010779
57 | 0.0037731 | 0.00094562
58 | 0.0033286 | 0.00083423
59 | 0.0030999 | 0.00077692
60 | 0.0025049 | 0.00062778
61 | 0.0026738 | 0.00067011
62 | 0.0036819 | 0.00092277
63 | 0.0043871 | 0.0010995
64 | 0.0034219 | 0.00085761
65 | 0.0033956 | 0.00085101
66 | 0.0065794 | 0.0016489
67 | 0.0032065 | 0.00080362
68 | 0.0034936 | 0.00087558
69 | 0.0027727 | 0.0006949
70 | 0.0027666 | 0.00069337
71 | 0.0033676 | 0.000844
72 | 0.0038329 | 0.00096061
73 | 0.0042214 | 0.001058
74 | 0.0033104 | 0.00082967
75 | 0.0033281 | 0.00083409
76 | 0.005852 | 0.0014666
77 | 0.003039 | 0.00076163
78 | 0.0075587 | 0.0018944
79 | 0.0054126 | 0.0013565
80 | 0.003266 | 0.00081855
81 | 0.0019999 | 0.00050123
82 | 0.0053265 | 0.0013349
83 | 0.0044527 | 0.001116
84 | 0.0035373 | 0.00088652
85 | 0.0054221 | 0.0013589
86 | 0.007767 | 0.0019466
87 | 0.0051526 | 0.0012914
88 | 0.0078115 | 0.0019577
89 | 0.0010198 | 0.00025559
90 | 0.0012349 | 0.00030949
91 | 0.0024724 | 0.00061963
92 | 0.0033711 | 0.00084488
93 | 0.0037946 | 0.000951
94 | 0.0039906 | 0.0010001
95 | 0.0038896 | 0.00097483
96 | 0.0078171 | 0.0019591
97 | 0.0065614 | 0.0016444
98 | 0.0070242 | 0.0017604
99 | 0.0033556 | 0.00084099
100 | 0.00073622 | 0.00018452
101 | 0.0029874 | 0.00074872
102 | 0.0074475 | 0.0018665
103 | 0.00079644 | 0.00019961
104 | 0.0011144 | 0.00027928
105 | 0.00039298 | 9.849e-05
106 | 0.003629 | 0.00090952
107 | 0.0018715 | 0.00046905
108 | 0.0033274 | 0.00083394
109 | 0.0051458 | 0.0012897
110 | 0.0030551 | 0.00076569
111 | 0.0030185 | 0.0007565

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1