## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_161-1_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_161-1_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_161-1_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_161-1_0_4_node_136 | 0.4 | n |  | TRUE
7 | bus_LV_161-1_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_161-1_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_161-1_0_4_node_61 | 0.4 | n |  | TRUE
10 | bus_LV_161-1_0_4_node_98 | 0.4 | n |  | TRUE
11 | bus_LV_161-1_0_4_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_161-1_0_4_node_154 | 0.4 | n |  | TRUE
13 | bus_LV_161-1_0_4_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_161-1_0_4_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_161-1_0_4_node_62 | 0.4 | n |  | TRUE
16 | bus_LV_161-1_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_161-1_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_161-1_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_161-1_0_4_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_161-1_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_161-1_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_161-1_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_161-1_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_161-1_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_161-1_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_161-1_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_161-1_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_161-1_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_161-1_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_161-1_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_161-1_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_161-1_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_161-1_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_161-1_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_161-1_0_4_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_161-1_0_4_node_123 | 0.4 | n |  | TRUE
37 | bus_LV_161-1_0_4_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_161-1_0_4_node_68 | 0.4 | n |  | TRUE
39 | bus_LV_161-1_0_4_node_124 | 0.4 | n |  | TRUE
40 | bus_LV_161-1_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_161-1_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_161-1_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_161-1_0_4_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_161-1_0_4_node_120 | 0.4 | n |  | TRUE
45 | bus_LV_161-1_0_4_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_161-1_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_161-1_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_161-1_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_161-1_0_4_node_77 | 0.4 | n |  | TRUE
50 | bus_LV_161-1_0_4_node_78 | 0.4 | n |  | TRUE
51 | bus_LV_161-1_0_4_node_134 | 0.4 | n |  | TRUE
52 | bus_LV_161-1_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_161-1_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_161-1_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_161-1_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_161-1_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_161-1_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_161-1_0_4_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_161-1_0_4_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_161-1_0_4_node_99 | 0.4 | n |  | TRUE
61 | bus_LV_161-1_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_161-1_0_4_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_161-1_0_4_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_161-1_0_4_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_161-1_0_4_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_161-1_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_161-1_0_4_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_161-1_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_161-1_0_4_node_140 | 0.4 | n |  | TRUE
70 | bus_LV_161-1_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_161-1_0_4_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_161-1_0_4_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_161-1_0_4_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_161-1_0_4_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_161-1_0_4_node_102 | 0.4 | n |  | TRUE
76 | bus_LV_161-1_0_4_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_161-1_0_4_node_101 | 0.4 | n |  | TRUE
78 | bus_LV_161-1_0_4_node_111 | 0.4 | n |  | TRUE
79 | bus_LV_161-1_0_4_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_161-1_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_161-1_0_4_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_161-1_0_4_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_161-1_0_4_node_137 | 0.4 | n |  | TRUE
84 | bus_LV_161-1_0_4_node_142 | 0.4 | n |  | TRUE
85 | bus_LV_161-1_0_4_node_139 | 0.4 | n |  | TRUE
86 | bus_LV_161-1_0_4_node_85 | 0.4 | n |  | TRUE
87 | bus_LV_161-1_0_4_node_138 | 0.4 | n |  | TRUE
88 | bus_LV_161-1_0_4_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_161-1_0_4_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_161-1_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_161-1_0_4_node_116 | 0.4 | n |  | TRUE
92 | bus_LV_161-1_0_4_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_161-1_0_4_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_161-1_0_4_node_100 | 0.4 | n |  | TRUE
95 | bus_LV_161-1_0_4_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_161-1_0_4_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_161-1_0_4_node_132 | 0.4 | n |  | TRUE
98 | bus_LV_161-1_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_161-1_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_161-1_0_4_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_161-1_0_4_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_161-1_0_4_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_161-1_0_4_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_161-1_0_4_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_161-1_0_4_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_161-1_0_4_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_161-1_0_4_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_161-1_0_4_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_161-1_0_4_node_113 | 0.4 | n |  | TRUE
110 | bus_LV_161-1_0_4_node_144 | 0.4 | n |  | TRUE
111 | bus_LV_161-1_0_4_node_135 | 0.4 | n |  | TRUE
112 | bus_LV_161-1_0_4_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_161-1_0_4_node_153 | 0.4 | n |  | TRUE
114 | bus_LV_161-1_0_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_161-1_0_4_node_145 | 0.4 | n |  | TRUE
116 | bus_LV_161-1_0_4_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_161-1_0_4_node_143 | 0.4 | n |  | TRUE
118 | bus_LV_161-1_0_4_node_88 | 0.4 | n |  | TRUE
119 | bus_LV_161-1_0_4_node_89 | 0.4 | n |  | TRUE
120 | bus_LV_161-1_0_4_node_90 | 0.4 | n |  | TRUE
121 | bus_LV_161-1_0_4_node_91 | 0.4 | n |  | TRUE
122 | bus_LV_161-1_0_4_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_161-1_0_4_node_92 | 0.4 | n |  | TRUE
124 | bus_LV_161-1_0_4_node_148 | 0.4 | n |  | TRUE
125 | bus_LV_161-1_0_4_node_147 | 0.4 | n |  | TRUE
126 | bus_LV_161-1_0_4_node_152 | 0.4 | n |  | TRUE
127 | bus_LV_161-1_0_4_node_93 | 0.4 | n |  | TRUE
128 | bus_LV_161-1_0_4_node_103 | 0.4 | n |  | TRUE
129 | bus_LV_161-1_0_4_node_104 | 0.4 | n |  | TRUE
130 | bus_LV_161-1_0_4_node_149 | 0.4 | n |  | TRUE
131 | bus_LV_161-1_0_4_node_150 | 0.4 | n |  | TRUE
132 | bus_LV_161-1_0_4_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_161-1_0_4_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_161-1_0_4_node_129 | 0.4 | n |  | TRUE
135 | bus_LV_161-1_0_4_node_115 | 0.4 | n |  | TRUE
136 | bus_LV_161-1_0_4_node_122 | 0.4 | n |  | TRUE
137 | bus_LV_161-1_0_4_node_125 | 0.4 | n |  | TRUE
138 | bus_LV_161-1_0_4_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_161-1_0_4_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_161-1_0_4_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_161-1_0_4_node_133 | 0.4 | n |  | TRUE
142 | bus_LV_161-1_0_4_node_131 | 0.4 | n |  | TRUE
143 | bus_LV_161-1_0_4_node_130 | 0.4 | n |  | TRUE
144 | bus_LV_161-1_0_4_node_146 | 0.4 | n |  | TRUE
145 | bus_LV_161-1_0_4_node_151 | 0.4 | n |  | TRUE
146 | bus_MV_494_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-1_0_4_load_0 | 0 | 0.0014565 | 0.00036503 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-1_0_4_load_136 | 6 | 0.00955 | 0.0023934 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-1_0_4_load_61 | 9 | 0.0021302 | 0.00053389 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-1_0_4_load_98 | 10 | 0.0027796 | 0.00069663 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-1_0_4_load_30 | 11 | 0.0055475 | 0.0013903 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-1_0_4_load_154 | 12 | 0.007778 | 0.0019493 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-1_0_4_load_34 | 13 | 0.0061943 | 0.0015524 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-1_0_4_load_35 | 14 | 0.0035554 | 0.00089106 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-1_0_4_load_62 | 15 | 0.0041595 | 0.0010425 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-1_0_4_load_29 | 16 | 0.0082079 | 0.0020571 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-1_0_4_load_11 | 17 | 0.0072727 | 0.0018227 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-1_0_4_load_14 | 20 | 0.0020952 | 0.00052511 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-1_0_4_load_15 | 21 | 0.0028637 | 0.00071772 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-1_0_4_load_28 | 22 | 0.0040797 | 0.0010225 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-1_0_4_load_19 | 23 | 0.0032807 | 0.00082223 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-1_0_4_load_16 | 25 | 0.0045086 | 0.00113 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-1_0_4_load_22 | 27 | 0.0019347 | 0.00048488 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-1_0_4_load_20 | 28 | 0.0026071 | 0.0006534 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-1_0_4_load_26 | 29 | 0.0026294 | 0.00065899 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-1_0_4_load_23 | 31 | 0.0017618 | 0.00044154 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-1_0_4_load_24 | 32 | 0.0012874 | 0.00032266 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-1_0_4_load_25 | 33 | 0.0019042 | 0.00047724 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-1_0_4_load_39 | 34 | 0.0012384 | 0.00031038 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-1_0_4_load_123 | 36 | 0.00092623 | 0.00023214 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-1_0_4_load_71 | 37 | 0.0014596 | 0.00036581 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-1_0_4_load_68 | 38 | 0.005513 | 0.0013817 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-1_0_4_load_124 | 39 | 0.00057523 | 0.00014417 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-1_0_4_load_31 | 40 | 0.0043585 | 0.0010923 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-1_0_4_load_32 | 41 | 0.0020426 | 0.00051192 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-1_0_4_load_33 | 42 | 0.0029943 | 0.00075044 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-1_0_4_load_120 | 44 | 0.0037493 | 0.00093966 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-1_0_4_load_73 | 45 | 0.0016586 | 0.00041569 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-1_0_4_load_36 | 46 | 0.0054326 | 0.0013615 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-1_0_4_load_37 | 47 | 0.0077982 | 0.0019544 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-1_0_4_load_77 | 49 | 0.003337 | 0.00083634 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-1_0_4_load_78 | 50 | 0.0021628 | 0.00054205 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-1_0_4_load_134 | 51 | 0.0028995 | 0.00072668 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-1_0_4_load_40 | 52 | 0.0057582 | 0.0014431 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-1_0_4_load_41 | 53 | 0.0024756 | 0.00062045 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-1_0_4_load_43 | 55 | 0.0056842 | 0.0014246 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-1_0_4_load_44 | 56 | 0.0012364 | 0.00030988 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-1_0_4_load_45 | 57 | 0.0023929 | 0.00059971 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-1_0_4_load_49 | 58 | 0.002182 | 0.00054686 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-1_0_4_load_99 | 60 | 0.0017163 | 0.00043016 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-1_0_4_load_47 | 61 | 0.0064373 | 0.0016133 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-1_0_4_load_66 | 63 | 0.0018004 | 0.00045123 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-1_0_4_load_67 | 64 | 0.0042493 | 0.001065 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-1_0_4_load_59 | 65 | 0.0026476 | 0.00066355 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-1_0_4_load_46 | 66 | 0.0033682 | 0.00084415 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-1_0_4_load_48 | 67 | 0.0058174 | 0.001458 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-1_0_4_load_50 | 68 | 0.003916 | 0.00098144 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-1_0_4_load_140 | 69 | 0.0059887 | 0.0015009 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-1_0_4_load_51 | 70 | 0.0082 | 0.0020551 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-1_0_4_load_52 | 71 | 0.0070896 | 0.0017768 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-1_0_4_load_53 | 72 | 0.0019122 | 0.00047924 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-1_0_4_load_54 | 73 | 0.009031 | 0.0022634 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-1_0_4_load_55 | 74 | 0.0019103 | 0.00047877 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-1_0_4_load_102 | 75 | 0.0082844 | 0.0020763 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-1_0_4_load_110 | 76 | 0.0086551 | 0.0021692 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-1_0_4_load_101 | 77 | 0.0043997 | 0.0011027 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-1_0_4_load_56 | 79 | 0.0010093 | 0.00025296 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-1_0_4_load_58 | 80 | 0.0012548 | 0.00031447 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-1_0_4_load_57 | 81 | 0.0052615 | 0.0013186 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_161-1_0_4_load_60 | 82 | 0.004056 | 0.0010165 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_161-1_0_4_load_137 | 83 | 0.0019747 | 0.00049491 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_161-1_0_4_load_138 | 87 | 0.0026264 | 0.00065824 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_161-1_0_4_load_76 | 88 | 0.0034159 | 0.0008561 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_161-1_0_4_load_117 | 89 | 0.0039547 | 0.00099115 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_161-1_0_4_load_74 | 90 | 0.00054698 | 0.00013709 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_161-1_0_4_load_116 | 91 | 0.0012622 | 0.00031634 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_161-1_0_4_load_69 | 92 | 0.0077045 | 0.0019309 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_161-1_0_4_load_100 | 94 | 0.0063353 | 0.0015878 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_161-1_0_4_load_94 | 95 | 0.0089738 | 0.0022491 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_161-1_0_4_load_72 | 96 | 0.0023016 | 0.00057684 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_161-1_0_4_load_132 | 97 | 0.0012908 | 0.0003235 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_161-1_0_4_load_79 | 98 | 0.0018605 | 0.00046629 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_161-1_0_4_load_83 | 102 | 0.0014819 | 0.0003714 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_161-1_0_4_load_86 | 103 | 0.0023644 | 0.00059257 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_161-1_0_4_load_87 | 104 | 0.001527 | 0.00038269 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_161-1_0_4_load_107 | 105 | 0.0052197 | 0.0013082 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_161-1_0_4_load_105 | 106 | 0.0020445 | 0.0005124 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_161-1_0_4_load_113 | 109 | 0.0024829 | 0.00062227 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_161-1_0_4_load_144 | 110 | 0.0020882 | 0.00052334 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_161-1_0_4_load_135 | 111 | 0.0019548 | 0.00048991 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_161-1_0_4_load_153 | 113 | 0.00055929 | 0.00014017 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_161-1_0_4_load_114 | 114 | 0.0053224 | 0.0013339 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_161-1_0_4_load_145 | 115 | 0.00138 | 0.00034586 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_161-1_0_4_load_119 | 116 | 0.0047031 | 0.0011787 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_161-1_0_4_load_143 | 117 | 0.0019166 | 0.00048034 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_161-1_0_4_load_88 | 118 | 0.0047196 | 0.0011828 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_161-1_0_4_load_89 | 119 | 0.0076908 | 0.0019275 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_161-1_0_4_load_90 | 120 | 0.0019676 | 0.00049312 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_161-1_0_4_load_91 | 121 | 0.0032074 | 0.00080385 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_161-1_0_4_load_121 | 122 | 0.0040229 | 0.0010082 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_161-1_0_4_load_147 | 125 | 0.0056579 | 0.001418 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_161-1_0_4_load_152 | 126 | 0.0071709 | 0.0017972 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_161-1_0_4_load_93 | 127 | 0.0072996 | 0.0018294 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_161-1_0_4_load_103 | 128 | 0.0041548 | 0.0010413 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_161-1_0_4_load_104 | 129 | 0.0013657 | 0.00034228 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_161-1_0_4_load_149 | 130 | 0.0040363 | 0.0010116 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_161-1_0_4_load_150 | 131 | 0.0037637 | 0.00094328 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_161-1_0_4_load_112 | 132 | 0.0035879 | 0.00089922 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_161-1_0_4_load_128 | 133 | 0.010691 | 0.0026793 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_161-1_0_4_load_129 | 134 | 0.0061992 | 0.0015537 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_161-1_0_4_load_115 | 135 | 0.0032113 | 0.00080482 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_161-1_0_4_load_122 | 136 | 0.0016237 | 0.00040694 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_161-1_0_4_load_125 | 137 | 0.0032608 | 0.00081723 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_161-1_0_4_load_118 | 138 | 0.0036154 | 0.00090609 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_161-1_0_4_load_126 | 139 | 0.0025697 | 0.00064402 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_161-1_0_4_load_127 | 140 | 0.002091 | 0.00052406 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_161-1_0_4_load_133 | 141 | 0.0056296 | 0.0014109 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_161-1_0_4_load_131 | 142 | 0.0013486 | 0.00033799 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_161-1_0_4_load_130 | 143 | 0.0042702 | 0.0010702 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_161-1_0_4_load_146 | 144 | 0.001695 | 0.00042481 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 138 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-1_0_4_line_0 |  | 0 | 1 | 0.0093884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-1_0_4_line_1 |  | 0 | 2 | 0.0065116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-1_0_4_line_2 |  | 1 | 3 | 0.026348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_161-1_0_4_line_3 |  | 2 | 4 | 0.042621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-1_0_4_line_4 |  | 2 | 5 | 0.038519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_161-1_0_4_line_5 |  | 3 | 6 | 0.0039402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_161-1_0_4_line_6 |  | 4 | 12 | 0.00939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-1_0_4_line_7 |  | 5 | 11 | 0.022091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_161-1_0_4_line_8 |  | 5 | 7 | 0.009699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_161-1_0_4_line_9 |  | 7 | 8 | 0.012887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-1_0_4_line_10 |  | 7 | 9 | 0.02447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-1_0_4_line_11 |  | 8 | 10 | 0.0035983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_161-1_0_4_line_12 |  | 9 | 15 | 0.025387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_161-1_0_4_line_13 |  | 11 | 16 | 0.0024651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-1_0_4_line_14 |  | 13 | 14 | 0.0033029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-1_0_4_line_15 |  | 14 | 46 | 0.0089106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-1_0_4_line_16 |  | 15 | 19 | 0.015457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_161-1_0_4_line_17 |  | 16 | 22 | 0.03743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_161-1_0_4_line_18 |  | 17 | 18 | 0.040889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-1_0_4_line_19 |  | 18 | 20 | 0.018759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-1_0_4_line_20 |  | 18 | 21 | 0.020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-1_0_4_line_21 |  | 19 | 85 | 0.007632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-1_0_4_line_22 |  | 20 | 22 | 0.0011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-1_0_4_line_23 |  | 21 | 23 | 0.016267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_161-1_0_4_line_24 |  | 23 | 24 | 0.061244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_161-1_0_4_line_25 |  | 24 | 26 | 0.049653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_161-1_0_4_line_26 |  | 24 | 25 | 0.039349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_161-1_0_4_line_27 |  | 26 | 27 | 0.020689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_161-1_0_4_line_28 |  | 26 | 28 | 0.019249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_161-1_0_4_line_29 |  | 27 | 29 | 0.029276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_161-1_0_4_line_30 |  | 30 | 31 | 0.014568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_161-1_0_4_line_31 |  | 30 | 32 | 0.014367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_161-1_0_4_line_32 |  | 30 | 33 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_161-1_0_4_line_33 |  | 31 | 34 | 0.021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-1_0_4_line_34 |  | 32 | 35 | 0.016003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_161-1_0_4_line_35 |  | 33 | 36 | 0.022762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_161-1_0_4_line_36 |  | 35 | 37 | 0.013269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_161-1_0_4_line_37 |  | 35 | 38 | 0.0090545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_161-1_0_4_line_38 |  | 36 | 39 | 0.0024341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_161-1_0_4_line_39 |  | 37 | 93 | 0.017992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-1_0_4_line_40 |  | 38 | 92 | 0.011755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_161-1_0_4_line_41 |  | 39 | 62 | 0.022005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_161-1_0_4_line_42 |  | 40 | 41 | 0.0087871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_161-1_0_4_line_43 |  | 41 | 42 | 0.02652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_161-1_0_4_line_44 |  | 42 | 43 | 0.038128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_161-1_0_4_line_45 |  | 43 | 44 | 0.01456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_161-1_0_4_line_46 |  | 43 | 45 | 0.020438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_161-1_0_4_line_47 |  | 44 | 87 | 0.0040164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-1_0_4_line_48 |  | 45 | 96 | 0.018608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-1_0_4_line_49 |  | 46 | 47 | 0.0057669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-1_0_4_line_50 |  | 47 | 48 | 0.026809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-1_0_4_line_51 |  | 48 | 49 | 0.014623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-1_0_4_line_52 |  | 48 | 50 | 0.0035761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-1_0_4_line_53 |  | 49 | 51 | 0.0285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-1_0_4_line_54 |  | 51 | 97 | 0.018705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_161-1_0_4_line_55 |  | 52 | 53 | 0.0090107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_161-1_0_4_line_56 |  | 52 | 54 | 0.0081486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_161-1_0_4_line_57 |  | 53 | 55 | 0.01879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-1_0_4_line_58 |  | 54 | 56 | 0.024844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_161-1_0_4_line_59 |  | 54 | 57 | 0.023277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-1_0_4_line_60 |  | 55 | 58 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-1_0_4_line_61 |  | 56 | 59 | 0.011737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-1_0_4_line_62 |  | 57 | 60 | 0.0077333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-1_0_4_line_63 |  | 58 | 61 | 0.015691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-1_0_4_line_64 |  | 59 | 62 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_161-1_0_4_line_65 |  | 59 | 63 | 0.014402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_161-1_0_4_line_66 |  | 59 | 64 | 0.014762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_161-1_0_4_line_67 |  | 60 | 65 | 0.0093499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-1_0_4_line_68 |  | 61 | 66 | 0.011241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-1_0_4_line_69 |  | 62 | 88 | 0.011122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-1_0_4_line_70 |  | 63 | 89 | 0.011065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_161-1_0_4_line_71 |  | 65 | 81 | 0.0030427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_161-1_0_4_line_72 |  | 66 | 67 | 0.013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-1_0_4_line_73 |  | 67 | 68 | 0.0097999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-1_0_4_line_74 |  | 68 | 69 | 0.025364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-1_0_4_line_75 |  | 70 | 71 | 0.001559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_161-1_0_4_line_76 |  | 70 | 72 | 0.020611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_161-1_0_4_line_77 |  | 71 | 73 | 0.022671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_161-1_0_4_line_78 |  | 72 | 74 | 0.021865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_161-1_0_4_line_79 |  | 73 | 75 | 0.0043501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_161-1_0_4_line_80 |  | 74 | 76 | 0.012699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_161-1_0_4_line_81 |  | 75 | 77 | 0.025689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_161-1_0_4_line_82 |  | 76 | 78 | 0.025096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_161-1_0_4_line_83 |  | 77 | 128 | 0.012783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_161-1_0_4_line_84 |  | 78 | 132 | 0.024336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_161-1_0_4_line_85 |  | 78 | 108 | 0.030542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_161-1_0_4_line_86 |  | 79 | 80 | 0.008834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_161-1_0_4_line_87 |  | 80 | 82 | 0.0038688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_161-1_0_4_line_88 |  | 82 | 83 | 0.0048227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_161-1_0_4_line_89 |  | 83 | 84 | 0.011017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_161-1_0_4_line_90 |  | 84 | 117 | 0.04723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_161-1_0_4_line_91 |  | 84 | 104 | 0.023264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_161-1_0_4_line_92 |  | 85 | 86 | 0.053604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_161-1_0_4_line_93 |  | 85 | 87 | 0.033637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_161-1_0_4_line_94 |  | 86 | 110 | 0.028056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_161-1_0_4_line_95 |  | 88 | 90 | 0.019538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_161-1_0_4_line_96 |  | 89 | 91 | 0.023148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_161-1_0_4_line_97 |  | 90 | 96 | 0.0082525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_161-1_0_4_line_98 |  | 91 | 138 | 0.010223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_161-1_0_4_line_99 |  | 93 | 94 | 0.014017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_161-1_0_4_line_100 |  | 93 | 95 | 0.025727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_161-1_0_4_line_101 |  | 95 | 127 | 0.040428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_161-1_0_4_line_102 |  | 97 | 143 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_161-1_0_4_line_103 |  | 98 | 99 | 0.015242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_161-1_0_4_line_104 |  | 98 | 100 | 0.02341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_161-1_0_4_line_105 |  | 99 | 101 | 0.005624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_161-1_0_4_line_106 |  | 99 | 102 | 0.0054808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_161-1_0_4_line_107 |  | 100 | 103 | 0.018914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_161-1_0_4_line_108 |  | 100 | 104 | 0.023316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_161-1_0_4_line_109 |  | 101 | 105 | 0.0077167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_161-1_0_4_line_110 |  | 102 | 106 | 0.017079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_161-1_0_4_line_111 |  | 103 | 111 | 0.004783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_161-1_0_4_line_112 |  | 106 | 108 | 0.007078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_161-1_0_4_line_113 |  | 107 | 108 | 0.013914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_161-1_0_4_line_114 |  | 107 | 109 | 0.050848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_161-1_0_4_line_115 |  | 108 | 112 | 0.015511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_161-1_0_4_line_116 |  | 109 | 114 | 0.0011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_161-1_0_4_line_117 |  | 110 | 115 | 0.010443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_161-1_0_4_line_118 |  | 111 | 116 | 0.013757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_161-1_0_4_line_119 |  | 112 | 113 | 0.029607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_161-1_0_4_line_120 |  | 114 | 135 | 0.029793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_161-1_0_4_line_121 |  | 115 | 144 | 0.013888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_161-1_0_4_line_122 |  | 116 | 138 | 0.0048841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_161-1_0_4_line_123 |  | 117 | 122 | 0.0093931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_161-1_0_4_line_124 |  | 118 | 119 | 0.019949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_161-1_0_4_line_125 |  | 118 | 120 | 0.035541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_161-1_0_4_line_126 |  | 119 | 121 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_161-1_0_4_line_127 |  | 121 | 122 | 0.0027042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_161-1_0_4_line_128 |  | 123 | 124 | 0.007612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_161-1_0_4_line_129 |  | 123 | 125 | 0.019445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_161-1_0_4_line_130 |  | 124 | 126 | 0.035412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_161-1_0_4_line_131 |  | 126 | 145 | 0.021606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_161-1_0_4_line_132 |  | 128 | 129 | 0.0020157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_161-1_0_4_line_133 |  | 129 | 130 | 0.0093322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_161-1_0_4_line_134 |  | 130 | 131 | 0.028819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_161-1_0_4_line_135 |  | 131 | 145 | 0.016212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_161-1_0_4_line_136 |  | 132 | 133 | 0.032954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_161-1_0_4_line_137 |  | 133 | 134 | 0.019428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_161-1_0_4_line_138 |  | 135 | 136 | 0.00040682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_161-1_0_4_line_139 |  | 136 | 137 | 0.022021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_161-1_0_4_line_140 |  | 137 | 139 | 0.027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_161-1_0_4_line_141 |  | 139 | 140 | 0.027925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_161-1_0_4_line_142 |  | 140 | 141 | 0.0099528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_161-1_0_4_line_143 |  | 141 | 142 | 0.0010362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_161-1_0_4_line_144 |  | 142 | 143 | 0.044703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-1_0_4_trafo_118 | 0.63 MVA 20/0.4 kV | 146 | 138 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2685499.8932 | 1243552.9385 | 2685496.5399 | 1243561.7076
1 | 2685494.2142 | 1243567.7897 | 2685496.5399 | 1243561.7076
2 | 2685518.0521 | 1243542.2367 | 2685514.4578 | 1243540.4169 | 2685512.1091 | 1243539.2267 | 2685506.4571 | 1243550.6313 | 2685499.8932 | 1243552.9385
3 | 2685461.7764 | 1243572.248 | 2685473.9875 | 1243577.2164 | 2685475.2425 | 1243577.7237 | 2685478.0394 | 1243570.3697 | 2685479.3201 | 1243567.5194 | 2685489.01 | 1243571.7287 | 2685494.2142 | 1243567.7897
4 | 2685492.3498 | 1243598.0183 | 2685486.6242 | 1243595.6563 | 2685492.6705 | 1243582.5894 | 2685494.4377 | 1243579.0234 | 2685498.1971 | 1243575.6862 | 2685497.2362 | 1243574.705 | 2685495.8972 | 1243571.639 | 2685494.2142 | 1243567.7897
5 | 2685518.0521 | 1243542.2367 | 2685516.4101 | 1243545.8185
6 | 2685461.7764 | 1243572.248 | 2685465.4836 | 1243563.6173
7 | 2685492.3498 | 1243598.0183 | 2685512.359 | 1243607.3803
8 | 2685492.3498 | 1243598.0183 | 2685488.0521 | 1243606.7183
9 | 2685476.4005 | 1243601.2131 | 2685483.7578 | 1243604.6883 | 2685488.0521 | 1243606.7183
10 | 2685488.0521 | 1243606.7183 | 2685476.3817 | 1243628.2263
11 | 2685476.4005 | 1243601.2131 | 2685474.9633 | 1243604.5119
12 | 2685464.1937 | 1243650.4955 | 2685467.584 | 1243644.4399 | 2685476.3817 | 1243628.2263
13 | 2685514.6362 | 1243608.317 | 2685513.462 | 1243607.8964 | 2685512.359 | 1243607.3803
14 | 2685478.7405 | 1243484.4711 | 2685475.5138 | 1243483.7655
15 | 2685466.809 | 1243481.8618 | 2685475.5138 | 1243483.7655
16 | 2685456.6298 | 1243663.9854 | 2685464.1937 | 1243650.4955
17 | 2685514.6362 | 1243608.317 | 2685536.4873 | 1243616.1454 | 2685550.4981 | 1243618.5718
18 | 2685570.1069 | 1243621.9676 | 2685573.2885 | 1243581.2021
19 | 2685570.1069 | 1243621.9676 | 2685551.623 | 1243618.7666
20 | 2685570.1069 | 1243621.9676 | 2685568.427 | 1243642.7374
21 | 2685456.6298 | 1243663.9854 | 2685452.8981 | 1243670.6476
22 | 2685551.623 | 1243618.7666 | 2685550.4981 | 1243618.5718
23 | 2685568.427 | 1243642.7374 | 2685567.2089 | 1243657.7965 | 2685567.2702 | 1243658.954
24 | 2685599.5649 | 1243708.7226 | 2685577.248 | 1243685.4615 | 2685571.7657 | 1243677.2431 | 2685567.7436 | 1243667.8894 | 2685567.2702 | 1243658.954
25 | 2685626.9208 | 1243749.9363 | 2685624.9471 | 1243745.2933 | 2685616.8809 | 1243730.733 | 2685599.5649 | 1243708.7226
26 | 2685599.5649 | 1243708.7226 | 2685607.4214 | 1243701.1637 | 2685614.2241 | 1243692.2554 | 2685617.024 | 1243675.2464
27 | 2685626.9208 | 1243749.9363 | 2685633.307 | 1243766.2071 | 2685634.1404 | 1243769.307
28 | 2685626.9208 | 1243749.9363 | 2685610.284 | 1243759.6192
29 | 2685634.1404 | 1243769.307 | 2685641.7413 | 1243797.5789
30 | 2685549.1215 | 1243780.3921 | 2685550.9087 | 1243765.9345
31 | 2685549.1215 | 1243780.3921 | 2685547.7138 | 1243794.6895
32 | 2685549.1215 | 1243780.3921 | 2685530.5704 | 1243777.9434
33 | 2685550.9087 | 1243765.9345 | 2685552.9978 | 1243749.0361 | 2685552.8037 | 1243744.1087
34 | 2685546.1458 | 1243810.6157 | 2685547.7138 | 1243794.6895
35 | 2685508.0819 | 1243779.6641 | 2685514.5235 | 1243778.0139 | 2685525.6673 | 1243777.2962 | 2685530.5704 | 1243777.9434
36 | 2685546.1458 | 1243810.6157 | 2685559.2239 | 1243812.5613 | 2685559.2688 | 1243812.5744
37 | 2685546.1458 | 1243810.6157 | 2685537.0995 | 1243810.2321
38 | 2685508.0819 | 1243779.6641 | 2685505.724 | 1243780.2682
39 | 2685576.0631 | 1243818.8865 | 2685567.8042 | 1243815.0646 | 2685559.2688 | 1243812.5744
40 | 2685537.0995 | 1243810.2321 | 2685525.3547 | 1243809.7339
41 | 2685486.917 | 1243791.3592 | 2685489.6835 | 1243789.7757 | 2685493.2442 | 1243787.6254 | 2685502.4839 | 1243781.0982 | 2685505.724 | 1243780.2682
42 | 2685542.2865 | 1243707.7182 | 2685544.3715 | 1243705.7023 | 2685548.4909 | 1243705.695 | 2685550.2584 | 1243705.6909
43 | 2685542.2865 | 1243707.7182 | 2685542.2865 | 1243707.7182 | 2685516.6706 | 1243708.2716 | 2685515.7937 | 1243708.4648
44 | 2685480.3453 | 1243714.5306 | 2685486.1901 | 1243712.8024 | 2685490.5041 | 1243708.2167 | 2685496.6367 | 1243708.5498 | 2685506.2522 | 1243710.5676 | 2685515.7937 | 1243708.4648
45 | 2685480.3453 | 1243714.5306 | 2685473.3593 | 1243701.756
46 | 2685480.3453 | 1243714.5306 | 2685486.1665 | 1243733.3171 | 2685486.2538 | 1243734.082
47 | 2685473.3593 | 1243701.756 | 2685471.4322 | 1243698.2321
48 | 2685488.3641 | 1243752.5696 | 2685486.2538 | 1243734.082
49 | 2685466.809 | 1243481.8618 | 2685461.1752 | 1243480.6297
50 | 2685434.9853 | 1243474.9022 | 2685461.1752 | 1243480.6297
51 | 2685434.9853 | 1243474.9022 | 2685433.2214 | 1243482.4379 | 2685431.7633 | 1243489.165
52 | 2685434.9853 | 1243474.9022 | 2685435.7524 | 1243471.4093
53 | 2685425.7259 | 1243517.0182 | 2685431.7633 | 1243489.165
54 | 2685425.7259 | 1243517.0182 | 2685423.6348 | 1243526.6655 | 2685421.5476 | 1243535.2492
55 | 2685474.9137 | 1243847.6088 | 2685472.6167 | 1243856.3218
56 | 2685476.991 | 1243839.7294 | 2685474.9137 | 1243847.6088
57 | 2685467.8266 | 1243874.4908 | 2685472.6167 | 1243856.3218
58 | 2685476.991 | 1243839.7294 | 2685483.3329 | 1243815.7086
59 | 2685476.991 | 1243839.7294 | 2685455.336 | 1243831.1915
60 | 2685463.5669 | 1243890.6481 | 2685467.8266 | 1243874.4908
61 | 2685486.329 | 1243804.3603 | 2685483.3329 | 1243815.7086
62 | 2685455.336 | 1243831.1915 | 2685450.5288 | 1243829.2962 | 2685448.174 | 1243828.2769
63 | 2685463.5669 | 1243890.6481 | 2685459.5669 | 1243905.8204
64 | 2685486.329 | 1243804.3603 | 2685486.917 | 1243791.3592
65 | 2685486.329 | 1243804.3603 | 2685472.8269 | 1243799.3499
66 | 2685486.329 | 1243804.3603 | 2685500.3423 | 1243807.4867 | 2685500.743 | 1243807.5385
67 | 2685448.174 | 1243828.2769 | 2685439.5934 | 1243824.5627
68 | 2685456.7014 | 1243916.6896 | 2685459.5669 | 1243905.8204
69 | 2685486.917 | 1243791.3592 | 2685487.6953 | 1243780.2645
70 | 2685462.4533 | 1243795.5005 | 2685472.8269 | 1243799.3499
71 | 2685436.8011 | 1243823.354 | 2685439.5934 | 1243824.5627
72 | 2685456.7014 | 1243916.6896 | 2685455.4037 | 1243921.6117 | 2685453.2136 | 1243929.3526
73 | 2685450.5456 | 1243938.7823 | 2685453.2136 | 1243929.3526
74 | 2685450.5456 | 1243938.7823 | 2685443.6404 | 1243963.1878
75 | 2685322.1129 | 1243873.4451 | 2685321.9629 | 1243874.9968
76 | 2685324.0951 | 1243852.9293 | 2685322.1129 | 1243873.4451
77 | 2685319.7825 | 1243897.5631 | 2685321.9629 | 1243874.9968
78 | 2685324.0951 | 1243852.9293 | 2685324.3249 | 1243850.5513 | 2685325.9261 | 1243836.4529 | 2685326.5209 | 1243831.1997
79 | 2685319.3641 | 1243901.893 | 2685319.7825 | 1243897.5631
80 | 2685326.5209 | 1243831.1997 | 2685327.9498 | 1243818.5812
81 | 2685316.9902 | 1243927.4718 | 2685318.4992 | 1243910.845 | 2685319.3641 | 1243901.893
82 | 2685331.7855 | 1243793.7838 | 2685330.2181 | 1243803.4349 | 2685328.3937 | 1243814.6614 | 2685327.9498 | 1243818.5812
83 | 2685316.9902 | 1243927.4718 | 2685315.8347 | 1243940.2029
84 | 2685331.7855 | 1243793.7838 | 2685355.4039 | 1243799.6499 | 2685355.4039 | 1243799.6499
85 | 2685331.7855 | 1243793.7838 | 2685332.1587 | 1243791.4874 | 2685338.7438 | 1243764.051
86 | 2685412.1804 | 1243813.8783 | 2685409.006 | 1243812.8642 | 2685403.5729 | 1243811.9992
87 | 2685399.7522 | 1243811.391 | 2685403.5729 | 1243811.9992
88 | 2685399.7522 | 1243811.391 | 2685398.9463 | 1243811.2627 | 2685395.1574 | 1243809.9597
89 | 2685384.7391 | 1243806.3769 | 2685395.1574 | 1243809.9597
90 | 2685384.7391 | 1243806.3769 | 2685375.1103 | 1243847.8131 | 2685374.5512 | 1243852.4693
91 | 2685384.7391 | 1243806.3769 | 2685390.4479 | 1243783.8238
92 | 2685452.8981 | 1243670.6476 | 2685426.9914 | 1243717.609
93 | 2685452.8981 | 1243670.6476 | 2685455.5569 | 1243672.3427 | 2685460.4321 | 1243678.1171 | 2685471.4322 | 1243698.2321
94 | 2685426.9914 | 1243717.609 | 2685453.0798 | 1243727.9308
95 | 2685487.6953 | 1243780.2645 | 2685489.0626 | 1243760.7742
96 | 2685440.8136 | 1243787.284 | 2685449.573 | 1243790.7209 | 2685462.4533 | 1243795.5005
97 | 2685488.3641 | 1243752.5696 | 2685488.7904 | 1243756.305 | 2685489.1527 | 1243759.4903 | 2685489.0626 | 1243760.7742
98 | 2685440.8136 | 1243787.284 | 2685431.297 | 1243783.5499
99 | 2685576.0631 | 1243818.8865 | 2685588.8105 | 1243824.7147
100 | 2685576.0631 | 1243818.8865 | 2685566.4824 | 1243842.763
101 | 2685551.427 | 1243880.2826 | 2685566.4824 | 1243842.763
102 | 2685418.115 | 1243549.3663 | 2685421.5476 | 1243535.2492
103 | 2685359.5781 | 1243754.8772 | 2685374.357 | 1243758.6045
104 | 2685397.3567 | 1243761.5701 | 2685390.8639 | 1243762.1104 | 2685384.4531 | 1243761.1508 | 2685374.357 | 1243758.6045
105 | 2685359.5781 | 1243754.8772 | 2685361.1374 | 1243749.4735
106 | 2685359.5781 | 1243754.8772 | 2685358.0361 | 1243760.1367
107 | 2685397.3567 | 1243761.5701 | 2685404.2976 | 1243772.9561 | 2685409.491 | 1243774.9939
108 | 2685397.3567 | 1243761.5701 | 2685392.1763 | 1243776.9957 | 2685390.4479 | 1243783.8238
109 | 2685361.1374 | 1243749.4735 | 2685368.5121 | 1243751.7454
110 | 2685358.0361 | 1243760.1367 | 2685350.8759 | 1243758.7327 | 2685346.895 | 1243761.722 | 2685345.4534 | 1243766.3047
111 | 2685413.9435 | 1243776.7409 | 2685409.491 | 1243774.9939
112 | 2685338.7438 | 1243764.051 | 2685345.4534 | 1243766.3047
113 | 2685342.7375 | 1243750.7209 | 2685338.7438 | 1243764.051
114 | 2685342.7375 | 1243750.7209 | 2685356.0567 | 1243714.9196 | 2685360.8132 | 1243703.1983
115 | 2685338.7438 | 1243764.051 | 2685330.0338 | 1243761.0902 | 2685331.2947 | 1243754.8816
116 | 2685360.8132 | 1243703.1983 | 2685361.2623 | 1243702.0915
117 | 2685457.5036 | 1243734.3038 | 2685458.7822 | 1243730.187 | 2685453.0798 | 1243727.9308
118 | 2685413.9435 | 1243776.7409 | 2685426.7504 | 1243781.766
119 | 2685331.2947 | 1243754.8816 | 2685328.3668 | 1243754.0278 | 2685326.8163 | 1243753.5718 | 2685305.3346 | 1243747.325 | 2685302.8502 | 1243746.6683
120 | 2685361.2623 | 1243702.0915 | 2685372.465 | 1243674.485
121 | 2685453.3845 | 1243747.5664 | 2685457.5036 | 1243734.3038
122 | 2685431.297 | 1243783.5499 | 2685426.7504 | 1243781.766
123 | 2685373.4313 | 1243861.7954 | 2685374.5512 | 1243852.4693
124 | 2685368.3098 | 1243904.9222 | 2685368.7296 | 1243900.9491 | 2685370.6317 | 1243885.1092
125 | 2685365.6892 | 1243940.3489 | 2685366.4632 | 1243922.3988 | 2685368.3098 | 1243904.9222
126 | 2685370.6317 | 1243885.1092 | 2685373.1089 | 1243864.4803
127 | 2685373.4313 | 1243861.7954 | 2685373.1089 | 1243864.4803
128 | 2685367.3648 | 1244002.5705 | 2685367.7917 | 1243994.971
129 | 2685367.7917 | 1243994.971 | 2685372.5775 | 1243990.659 | 2685380.3157 | 1243989.1692 | 2685385.4375 | 1243989.0956
130 | 2685367.3648 | 1244002.5705 | 2685363.2833 | 1244002.5784 | 2685353.0052 | 1244001.9968 | 2685332.1544 | 1243999.2119
131 | 2685310.7387 | 1243996.3515 | 2685332.1544 | 1243999.2119
132 | 2685315.6525 | 1243942.2103 | 2685315.8347 | 1243940.2029
133 | 2685315.6525 | 1243942.2103 | 2685314.809 | 1243951.5044
134 | 2685314.809 | 1243951.5044 | 2685312.2041 | 1243980.2059
135 | 2685310.7387 | 1243996.3515 | 2685312.2041 | 1243980.2059
136 | 2685355.4039 | 1243799.6499 | 2685361.7574 | 1243801.9653 | 2685363.033 | 1243804.7078 | 2685359.8235 | 1243816.5926 | 2685357.7031 | 1243827.24
137 | 2685348.5687 | 1243838.5138 | 2685355.2285 | 1243839.6656 | 2685357.7031 | 1243827.24
138 | 2685372.618 | 1243674.108 | 2685372.465 | 1243674.485
139 | 2685372.618 | 1243674.108 | 2685380.8983 | 1243653.7031
140 | 2685380.8983 | 1243653.7031 | 2685391.1694 | 1243628.3924
141 | 2685391.1694 | 1243628.3924 | 2685399.5572 | 1243607.7226 | 2685401.4442 | 1243602.4313
142 | 2685401.4442 | 1243602.4313 | 2685404.7874 | 1243593.0568
143 | 2685405.1354 | 1243592.0808 | 2685404.7874 | 1243593.0568
144 | 2685418.115 | 1243549.3663 | 2685413.2862 | 1243569.2254 | 2685405.1354 | 1243592.0808

## bus_geodata
| x | y | coords
0 | 2685496.5399 | 1243561.7076
1 | 2685499.8932 | 1243552.9385
2 | 2685494.2142 | 1243567.7897
3 | 2685518.0521 | 1243542.2367
4 | 2685461.7764 | 1243572.248
5 | 2685492.3498 | 1243598.0183
6 | 2685516.4101 | 1243545.8185
7 | 2685488.0521 | 1243606.7183
8 | 2685476.4005 | 1243601.2131
9 | 2685476.3817 | 1243628.2263
10 | 2685474.9633 | 1243604.5119
11 | 2685512.359 | 1243607.3803
12 | 2685465.4836 | 1243563.6173
13 | 2685478.7405 | 1243484.4711
14 | 2685475.5138 | 1243483.7655
15 | 2685464.1937 | 1243650.4955
16 | 2685514.6362 | 1243608.317
17 | 2685573.2885 | 1243581.2021
18 | 2685570.1069 | 1243621.9676
19 | 2685456.6298 | 1243663.9854
20 | 2685551.623 | 1243618.7666
21 | 2685568.427 | 1243642.7374
22 | 2685550.4981 | 1243618.5718
23 | 2685567.2702 | 1243658.954
24 | 2685599.5649 | 1243708.7226
25 | 2685617.024 | 1243675.2464
26 | 2685626.9208 | 1243749.9363
27 | 2685634.1404 | 1243769.307
28 | 2685610.284 | 1243759.6192
29 | 2685641.7413 | 1243797.5789
30 | 2685549.1215 | 1243780.3921
31 | 2685550.9087 | 1243765.9345
32 | 2685547.7138 | 1243794.6895
33 | 2685530.5703 | 1243777.9434
34 | 2685552.8037 | 1243744.1087
35 | 2685546.1458 | 1243810.6157
36 | 2685508.0819 | 1243779.6641
37 | 2685559.2688 | 1243812.5744
38 | 2685537.0995 | 1243810.2321
39 | 2685505.724 | 1243780.2682
40 | 2685550.2584 | 1243705.6909
41 | 2685542.2865 | 1243707.7181
42 | 2685515.7937 | 1243708.4648
43 | 2685480.3453 | 1243714.5306
44 | 2685473.3593 | 1243701.756
45 | 2685486.2538 | 1243734.082
46 | 2685466.809 | 1243481.8618
47 | 2685461.1752 | 1243480.6297
48 | 2685434.9853 | 1243474.9022
49 | 2685431.7633 | 1243489.165
50 | 2685435.7524 | 1243471.4093
51 | 2685425.7259 | 1243517.0182
52 | 2685474.9137 | 1243847.6088
53 | 2685472.6167 | 1243856.3218
54 | 2685476.991 | 1243839.7294
55 | 2685467.8266 | 1243874.4908
56 | 2685483.3329 | 1243815.7086
57 | 2685455.336 | 1243831.1915
58 | 2685463.5669 | 1243890.6481
59 | 2685486.329 | 1243804.3603
60 | 2685448.174 | 1243828.2769
61 | 2685459.5669 | 1243905.8204
62 | 2685486.917 | 1243791.3592
63 | 2685472.8269 | 1243799.3499
64 | 2685500.743 | 1243807.5385
65 | 2685439.5934 | 1243824.5627
66 | 2685456.7014 | 1243916.6896
67 | 2685453.2136 | 1243929.3526
68 | 2685450.5456 | 1243938.7823
69 | 2685443.6404 | 1243963.1878
70 | 2685322.1129 | 1243873.4451
71 | 2685321.9629 | 1243874.9968
72 | 2685324.0951 | 1243852.9293
73 | 2685319.7825 | 1243897.5631
74 | 2685326.5209 | 1243831.1997
75 | 2685319.3641 | 1243901.893
76 | 2685327.9498 | 1243818.5812
77 | 2685316.9902 | 1243927.4718
78 | 2685331.7855 | 1243793.7838
79 | 2685412.1804 | 1243813.8783
80 | 2685403.5729 | 1243811.9992
81 | 2685436.8011 | 1243823.354
82 | 2685399.7522 | 1243811.391
83 | 2685395.1574 | 1243809.9597
84 | 2685384.7391 | 1243806.3769
85 | 2685452.8981 | 1243670.6476
86 | 2685426.9914 | 1243717.609
87 | 2685471.4322 | 1243698.2321
88 | 2685487.6953 | 1243780.2645
89 | 2685462.4533 | 1243795.5005
90 | 2685489.0626 | 1243760.7742
91 | 2685440.8136 | 1243787.284
92 | 2685525.3547 | 1243809.7339
93 | 2685576.0631 | 1243818.8865
94 | 2685588.8105 | 1243824.7147
95 | 2685566.4824 | 1243842.763
96 | 2685488.3641 | 1243752.5696
97 | 2685421.5476 | 1243535.2492
98 | 2685374.357 | 1243758.6045
99 | 2685359.5781 | 1243754.8772
100 | 2685397.3567 | 1243761.5701
101 | 2685361.1374 | 1243749.4735
102 | 2685358.0361 | 1243760.1367
103 | 2685409.491 | 1243774.9939
104 | 2685390.4479 | 1243783.8238
105 | 2685368.5121 | 1243751.7454
106 | 2685345.4534 | 1243766.3047
107 | 2685342.7375 | 1243750.7209
108 | 2685338.7438 | 1243764.051
109 | 2685360.8132 | 1243703.1983
110 | 2685453.0798 | 1243727.9308
111 | 2685413.9435 | 1243776.7409
112 | 2685331.2947 | 1243754.8816
113 | 2685302.8502 | 1243746.6683
114 | 2685361.2623 | 1243702.0915
115 | 2685457.5036 | 1243734.3038
116 | 2685426.7504 | 1243781.766
117 | 2685374.5512 | 1243852.4693
118 | 2685368.3098 | 1243904.9222
119 | 2685370.6317 | 1243885.1092
120 | 2685365.6892 | 1243940.3489
121 | 2685373.1089 | 1243864.4803
122 | 2685373.4313 | 1243861.7954
123 | 2685367.7917 | 1243994.971
124 | 2685367.3648 | 1244002.5705
125 | 2685385.4375 | 1243989.0956
126 | 2685332.1544 | 1243999.2119
127 | 2685551.427 | 1243880.2826
128 | 2685315.8347 | 1243940.2029
129 | 2685315.6525 | 1243942.2103
130 | 2685314.809 | 1243951.5044
131 | 2685312.2041 | 1243980.2059
132 | 2685355.4039 | 1243799.6499
133 | 2685357.7031 | 1243827.24
134 | 2685348.5687 | 1243838.5138
135 | 2685372.465 | 1243674.485
136 | 2685372.618 | 1243674.108
137 | 2685380.8983 | 1243653.7031
138 | 2685431.297 | 1243783.5499
139 | 2685391.1694 | 1243628.3924
140 | 2685401.4442 | 1243602.4313
141 | 2685404.7874 | 1243593.0568
142 | 2685405.1354 | 1243592.0808
143 | 2685418.115 | 1243549.3663
144 | 2685453.3845 | 1243747.5664
145 | 2685310.7387 | 1243996.3515
146 | 2685397.3567 | 1243761.5701

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97652 | -0.45213 | 0.0014565 | 0.00036503
1 | 0.97644 | -0.45377 | 0 | 0
2 | 0.97659 | -0.45082 | 0 | 0
3 | 0.97621 | -0.45837 | 0 | 0
4 | 0.97628 | -0.45688 | 0 | 0
5 | 0.97726 | -0.4376 | 0 | 0
6 | 0.97617 | -0.45906 | 0.00955 | 0.0023934
7 | 0.97784 | -0.42631 | 0 | 0
8 | 0.9778 | -0.42696 | 0 | 0
9 | 0.97935 | -0.39665 | 0.0021302 | 0.00053389
10 | 0.97779 | -0.42715 | 0.0027796 | 0.00069663
11 | 0.97634 | -0.45578 | 0.0055475 | 0.0013903
12 | 0.97621 | -0.45821 | 0.007778 | 0.0019493
13 | 0.97686 | -0.44635 | 0.0061943 | 0.0015524
14 | 0.97687 | -0.44598 | 0.0035554 | 0.00089106
15 | 0.98097 | -0.36499 | 0.0041595 | 0.0010425
16 | 0.97625 | -0.45756 | 0.0082079 | 0.0020571
17 | 0.97441 | -0.49366 | 0.0072727 | 0.0018227
18 | 0.97469 | -0.4882 | 0 | 0
19 | 0.98202 | -0.3446 | 0 | 0
20 | 0.97513 | -0.47956 | 0.0020952 | 0.00052511
21 | 0.97434 | -0.49502 | 0.0028637 | 0.00071772
22 | 0.97516 | -0.47899 | 0.0040797 | 0.0010225
23 | 0.97412 | -0.49949 | 0.0032807 | 0.00082223
24 | 0.97345 | -0.51265 | 0 | 0
25 | 0.97328 | -0.51591 | 0.0045086 | 0.00113
26 | 0.97312 | -0.5192 | 0 | 0
27 | 0.97303 | -0.52094 | 0.0019347 | 0.00048488
28 | 0.97307 | -0.52012 | 0.0026071 | 0.0006534
29 | 0.97296 | -0.52236 | 0.0026294 | 0.00065899
30 | 0.99081 | -0.17575 | 0 | 0
31 | 0.99077 | -0.17653 | 0.0017618 | 0.00044154
32 | 0.9903 | -0.18559 | 0.0012874 | 0.00032266
33 | 0.99152 | -0.16195 | 0.0019042 | 0.00047724
34 | 0.99074 | -0.17701 | 0.0012384 | 0.00031038
35 | 0.98975 | -0.19621 | 0 | 0
36 | 0.99243 | -0.14441 | 0.00092623 | 0.00023214
37 | 0.98946 | -0.20189 | 0.0014596 | 0.00036581
38 | 0.98964 | -0.19834 | 0.005513 | 0.0013817
39 | 0.99252 | -0.1425 | 0.00057523 | 0.00014417
40 | 0.9859 | -0.26954 | 0.0043585 | 0.0010923
41 | 0.98594 | -0.26885 | 0.0020426 | 0.00051192
42 | 0.98609 | -0.26581 | 0.0029943 | 0.00075044
43 | 0.98642 | -0.25939 | 0 | 0
44 | 0.98528 | -0.28144 | 0.0037493 | 0.00093966
45 | 0.9882 | -0.22509 | 0.0016586 | 0.00041569
46 | 0.97696 | -0.44439 | 0.0054326 | 0.0013615
47 | 0.97704 | -0.44279 | 0.0077982 | 0.0019544
48 | 0.97761 | -0.43155 | 0 | 0
49 | 0.97795 | -0.42485 | 0.003337 | 0.00083634
50 | 0.9776 | -0.43169 | 0.0021628 | 0.00054205
51 | 0.9787 | -0.41006 | 0.0028995 | 0.00072668
52 | 0.9922 | -0.14907 | 0.0057582 | 0.0014431
53 | 0.9919 | -0.1548 | 0.0024756 | 0.00062045
54 | 0.99251 | -0.14307 | 0 | 0
55 | 0.99133 | -0.16592 | 0.0056842 | 0.0014246
56 | 0.99373 | -0.11951 | 0.0012364 | 0.00030988
57 | 0.99225 | -0.14802 | 0.0023929 | 0.00059971
58 | 0.9909 | -0.17414 | 0.002182 | 0.00054686
59 | 0.99431 | -0.10815 | 0 | 0
60 | 0.99218 | -0.14934 | 0.0017163 | 0.00043016
61 | 0.99053 | -0.18125 | 0.0064373 | 0.0016133
62 | 0.99343 | -0.125 | 0 | 0
63 | 0.99568 | -0.082047 | 0.0018004 | 0.00045123
64 | 0.99426 | -0.10925 | 0.0042493 | 0.001065
65 | 0.99211 | -0.15065 | 0.0026476 | 0.00066355
66 | 0.99034 | -0.18506 | 0.0033682 | 0.00084415
67 | 0.99015 | -0.18873 | 0.0058174 | 0.001458
68 | 0.99006 | -0.19046 | 0.003916 | 0.00098144
69 | 0.98992 | -0.19316 | 0.0059887 | 0.0015009
70 | 0.98289 | -0.3286 | 0.0082 | 0.0020551
71 | 0.98281 | -0.33014 | 0.0070896 | 0.0017768
72 | 0.98409 | -0.30514 | 0.0019122 | 0.00047924
73 | 0.98181 | -0.34975 | 0.009031 | 0.0022634
74 | 0.98541 | -0.27957 | 0.0019103 | 0.00047877
75 | 0.98165 | -0.3528 | 0.0082844 | 0.0020763
76 | 0.9862 | -0.26431 | 0.0086551 | 0.0021692
77 | 0.98093 | -0.36701 | 0.0043997 | 0.0011027
78 | 0.98795 | -0.23035 | 0 | 0
79 | 0.99443 | -0.10617 | 0.0010093 | 0.00025296
80 | 0.99444 | -0.10602 | 0.0012548 | 0.00031447
81 | 0.9921 | -0.15093 | 0.0052615 | 0.0013186
82 | 0.99445 | -0.10586 | 0.004056 | 0.0010165
83 | 0.99447 | -0.10533 | 0.0019747 | 0.00049491
84 | 0.99456 | -0.10371 | 0 | 0
85 | 0.98254 | -0.33455 | 0 | 0
86 | 0.98228 | -0.33955 | 0 | 0
87 | 0.98498 | -0.28726 | 0.0026264 | 0.00065824
88 | 0.99238 | -0.14501 | 0.0034159 | 0.0008561
89 | 0.99674 | -0.061867 | 0.0039547 | 0.00099115
90 | 0.9906 | -0.17908 | 0.00054698 | 0.00013709
91 | 0.999 | -0.018988 | 0.0012622 | 0.00031634
92 | 0.98956 | -0.19995 | 0.0077045 | 0.0019309
93 | 0.98908 | -0.20914 | 0 | 0
94 | 0.989 | -0.21072 | 0.0063353 | 0.0015878
95 | 0.9887 | -0.2166 | 0.0089738 | 0.0022491
96 | 0.98985 | -0.19343 | 0.0023016 | 0.00057684
97 | 0.97925 | -0.39939 | 0.0012908 | 0.0003235
98 | 0.99409 | -0.1124 | 0.0018605 | 0.00046629
99 | 0.99289 | -0.13527 | 0 | 0
100 | 0.99594 | -0.077003 | 0 | 0
101 | 0.99286 | -0.13579 | 0 | 0
102 | 0.99247 | -0.14325 | 0.0014819 | 0.0003714
103 | 0.99773 | -0.042975 | 0.0023644 | 0.00059257
104 | 0.99523 | -0.090677 | 0.001527 | 0.00038269
105 | 0.99283 | -0.1365 | 0.0052197 | 0.0013082
106 | 0.99119 | -0.16795 | 0.0020445 | 0.0005124
107 | 0.98983 | -0.19402 | 0 | 0
108 | 0.99066 | -0.17807 | 0 | 0
109 | 0.98679 | -0.25254 | 0.0024829 | 0.00062227
110 | 0.98215 | -0.34217 | 0.0020882 | 0.00052334
111 | 0.99819 | -0.034291 | 0.0019548 | 0.00048991
112 | 0.99065 | -0.17823 | 0 | 0
113 | 0.99064 | -0.17852 | 0.00055929 | 0.00014017
114 | 0.98672 | -0.25386 | 0.0053224 | 0.0013339
115 | 0.98212 | -0.34275 | 0.00138 | 0.00034586
116 | 0.99952 | -0.0091201 | 0.0047031 | 0.0011787
117 | 0.99354 | -0.12332 | 0.0019166 | 0.00048034
118 | 0.99292 | -0.13538 | 0.0047196 | 0.0011828
119 | 0.99304 | -0.13302 | 0.0076908 | 0.0019275
120 | 0.99286 | -0.13662 | 0.0019676 | 0.00049312
121 | 0.99332 | -0.12774 | 0.0032074 | 0.00080385
122 | 0.99336 | -0.1269 | 0.0040229 | 0.0010082
123 | 0.97928 | -0.39928 | 0 | 0
124 | 0.97932 | -0.39849 | 0 | 0
125 | 0.97918 | -0.40128 | 0.0056579 | 0.001418
126 | 0.97951 | -0.39485 | 0.0071709 | 0.0017972
127 | 0.98843 | -0.22186 | 0.0072996 | 0.0018294
128 | 0.98062 | -0.37307 | 0.0041548 | 0.0010413
129 | 0.98058 | -0.37387 | 0.0013657 | 0.00034228
130 | 0.9804 | -0.37736 | 0.0040363 | 0.0010116
131 | 0.97996 | -0.38604 | 0.0037637 | 0.00094328
132 | 0.98749 | -0.23926 | 0.0035879 | 0.00089922
133 | 0.98698 | -0.24921 | 0.010691 | 0.0026793
134 | 0.98687 | -0.25137 | 0.0061992 | 0.0015537
135 | 0.98516 | -0.28414 | 0.0032113 | 0.00080482
136 | 0.98514 | -0.28453 | 0.0016237 | 0.00040694
137 | 0.98408 | -0.30506 | 0.0032608 | 0.00081723
138 | 1 | 0 | -0.43459 | -0.11078
139 | 0.98285 | -0.32898 | 0.0025697 | 0.00064402
140 | 0.98166 | -0.35219 | 0.002091 | 0.00052406
141 | 0.98126 | -0.3601 | 0.0056296 | 0.0014109
142 | 0.98122 | -0.36082 | 0.0013486 | 0.00033799
143 | 0.97969 | -0.39076 | 0.0042702 | 0.0010702
144 | 0.9821 | -0.34317 | 0.001695 | 0.00042481
145 | 0.97976 | -0.38982 | 0 | 0
146 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0095531 | 0.002395 | -0.0095524 | -0.0023946 | 7.4608e-07 | 3.6004e-07 | 0.014557 | 0.014557 | 0.014557 | 0.97652 | -0.45213 | 0.97644 | -0.45377 | 3.9992
1 | -0.01101 | -0.00276 | 0.01101 | 0.0027604 | 6.8727e-07 | 3.5838e-07 | 0.016777 | 0.016777 | 0.016777 | 0.97652 | -0.45213 | 0.97659 | -0.45082 | 4.609
2 | 0.0095524 | 0.0023946 | -0.0095503 | -0.0023936 | 2.0938e-06 | 1.0106e-06 | 0.014557 | 0.014557 | 0.014557 | 0.97644 | -0.45377 | 0.97621 | -0.45837 | 3.9993
3 | 0.0077807 | 0.0019505 | -0.0077785 | -0.0019495 | 2.2465e-06 | 9.0464e-07 | 0.011856 | 0.011856 | 0.011856 | 0.97659 | -0.45082 | 0.97628 | -0.45688 | 3.2571
4 | -0.018791 | -0.0047108 | 0.018803 | 0.0047179 | 1.1841e-05 | 7.0962e-06 | 0.028632 | 0.028632 | 0.028632 | 0.97659 | -0.45082 | 0.97726 | -0.4376 | 7.866
5 | 0.0095503 | 0.0023936 | -0.00955 | -0.0023934 | 3.1312e-07 | 1.5114e-07 | 0.014557 | 0.014557 | 0.014557 | 0.97621 | -0.45837 | 0.97617 | -0.45906 | 3.9993
6 | 0.0077785 | 0.0019495 | -0.007778 | -0.0019493 | 4.9494e-07 | 1.9936e-07 | 0.011856 | 0.011856 | 0.011856 | 0.97628 | -0.45688 | 0.97621 | -0.45821 | 3.2571
7 | 0.045135 | 0.011349 | -0.045096 | -0.011324 | 3.9141e-05 | 2.4774e-05 | 0.068737 | 0.068737 | 0.068737 | 0.97726 | -0.4376 | 0.97634 | -0.45578 | 18.8838
8 | -0.063938 | -0.016067 | 0.063972 | 0.016089 | 3.4483e-05 | 2.1947e-05 | 0.097369 | 0.097369 | 0.097369 | 0.97726 | -0.4376 | 0.97784 | -0.42631 | 26.7497
9 | 0.0027797 | 0.0006965 | -0.0027796 | -0.0006966 | 8.6466e-08 | -1.0631e-07 | 0.0042299 | 0.00423 | 0.00423 | 0.97784 | -0.42631 | 0.9778 | -0.42696 | 1.1621
10 | -0.066752 | -0.016785 | 0.066846 | 0.016846 | 9.4721e-05 | 6.0314e-05 | 0.1016 | 0.1016 | 0.1016 | 0.97784 | -0.42631 | 0.97935 | -0.39665 | 27.9118
11 | 0.0027796 | 0.0006966 | -0.0027796 | -0.00069663 | 2.4144e-08 | -2.9682e-08 | 0.00423 | 0.00423 | 0.00423 | 0.9778 | -0.42696 | 0.97779 | -0.42715 | 1.1621
12 | -0.068977 | -0.017379 | 0.069081 | 0.017446 | 0.00010463 | 6.6643e-05 | 0.10484 | 0.10484 | 0.10484 | 0.97935 | -0.39665 | 0.98097 | -0.36499 | 28.801
13 | 0.039548 | 0.0099338 | -0.039545 | -0.0099317 | 3.3592e-06 | 2.1191e-06 | 0.060282 | 0.060282 | 0.060282 | 0.97634 | -0.45578 | 0.97625 | -0.45756 | 16.5611
14 | -0.0061943 | -0.0015524 | 0.0061944 | 0.0015525 | 1.1027e-07 | 2.9225e-08 | 0.0094356 | 0.0094356 | 0.0094356 | 0.97686 | -0.44635 | 0.97687 | -0.44598 | 2.5922
15 | -0.0097498 | -0.0024435 | 0.0097505 | 0.0024439 | 7.37e-07 | 3.6011e-07 | 0.014851 | 0.014851 | 0.014851 | 0.97687 | -0.44598 | 0.97696 | -0.44439 | 4.08
16 | -0.073241 | -0.018489 | 0.073312 | 0.018534 | 7.1603e-05 | 4.5631e-05 | 0.11114 | 0.11114 | 0.11114 | 0.98097 | -0.36499 | 0.98202 | -0.3446 | 30.5343
17 | 0.031337 | 0.0078746 | -0.031305 | -0.0078546 | 3.2033e-05 | 2.0034e-05 | 0.047772 | 0.047772 | 0.047772 | 0.97625 | -0.45756 | 0.97516 | -0.47899 | 13.1241
18 | -0.0072727 | -0.0018227 | 0.0072746 | 0.0018234 | 1.8913e-06 | 7.0094e-07 | 0.011106 | 0.011106 | 0.011106 | 0.97441 | -0.49366 | 0.97469 | -0.4882 | 3.0511
19 | -0.025119 | -0.0063001 | 0.025129 | 0.0063065 | 1.0346e-05 | 6.3873e-06 | 0.038349 | 0.038349 | 0.038349 | 0.97469 | -0.4882 | 0.97513 | -0.47956 | 10.5356
20 | 0.017844 | 0.0044767 | -0.017838 | -0.0044733 | 5.7997e-06 | 3.4522e-06 | 0.027244 | 0.027244 | 0.027244 | 0.97469 | -0.4882 | 0.97434 | -0.49502 | 7.4845
21 | -0.073312 | -0.018534 | 0.073348 | 0.018557 | 3.5355e-05 | 2.253e-05 | 0.11114 | 0.11114 | 0.11114 | 0.98202 | -0.3446 | 0.98254 | -0.33455 | 30.5343
22 | -0.027224 | -0.0068316 | 0.027225 | 0.0068321 | 7.3895e-07 | 4.5869e-07 | 0.041547 | 0.041547 | 0.041547 | 0.97513 | -0.47956 | 0.97516 | -0.47899 | 11.4139
23 | 0.014975 | 0.0037556 | -0.014971 | -0.0037537 | 3.1907e-06 | 1.8395e-06 | 0.02287 | 0.02287 | 0.02287 | 0.97434 | -0.49502 | 0.97412 | -0.49949 | 6.283
24 | 0.011691 | 0.0029315 | -0.011683 | -0.0029276 | 7.3249e-06 | 3.926e-06 | 0.017859 | 0.017859 | 0.017859 | 0.97412 | -0.49949 | 0.97345 | -0.51265 | 4.9063
25 | 0.0071741 | 0.0017977 | -0.0071718 | -0.0017968 | 2.2392e-06 | 8.1603e-07 | 0.010966 | 0.010966 | 0.010966 | 0.97345 | -0.51265 | 0.97312 | -0.5192 | 3.0127
26 | 0.0045093 | 0.0011299 | -0.0045086 | -0.00113 | 7.0108e-07 | -4.0411e-08 | 0.0068928 | 0.006893 | 0.006893 | 0.97345 | -0.51265 | 0.97328 | -0.51591 | 1.8937
27 | 0.0045646 | 0.0011436 | -0.0045643 | -0.0011436 | 3.7797e-07 | -1.5105e-08 | 0.0069798 | 0.0069798 | 0.0069798 | 0.97312 | -0.5192 | 0.97303 | -0.52094 | 1.9175
28 | 0.0026072 | 0.00065323 | -0.0026071 | -0.0006534 | 1.1473e-07 | -1.6571e-07 | 0.0039866 | 0.0039867 | 0.0039867 | 0.97312 | -0.5192 | 0.97307 | -0.52012 | 1.0953
29 | 0.0026296 | 0.00065874 | -0.0026294 | -0.00065899 | 1.7753e-07 | -2.5e-07 | 0.0040212 | 0.0040213 | 0.0040213 | 0.97303 | -0.52094 | 0.97296 | -0.52236 | 1.1048
30 | 0.0030004 | 0.00075154 | -0.0030002 | -0.00075166 | 1.1091e-07 | -1.1663e-07 | 0.0045059 | 0.0045059 | 0.0045059 | 0.99081 | -0.17575 | 0.99077 | -0.17653 | 1.2379
31 | 0.038635 | 0.0097045 | -0.038616 | -0.0096931 | 1.8142e-05 | 1.1426e-05 | 0.05803 | 0.05803 | 0.05803 | 0.99081 | -0.17575 | 0.9903 | -0.18559 | 15.9423
32 | -0.041635 | -0.010456 | 0.041662 | 0.010473 | 2.7442e-05 | 1.7321e-05 | 0.062536 | 0.062536 | 0.062536 | 0.99081 | -0.17575 | 0.99152 | -0.16195 | 17.1802
33 | 0.0012385 | 0.00031012 | -0.0012384 | -0.00031038 | 2.8487e-08 | -2.6454e-07 | 0.0018599 | 0.00186 | 0.00186 | 0.99077 | -0.17653 | 0.99074 | -0.17701 | 0.511
34 | 0.037329 | 0.0093705 | -0.03731 | -0.0093586 | 1.8884e-05 | 1.188e-05 | 0.056096 | 0.056096 | 0.056096 | 0.9903 | -0.18559 | 0.98975 | -0.19621 | 15.4109
35 | -0.043567 | -0.010951 | 0.043603 | 0.010974 | 3.6502e-05 | 2.3067e-05 | 0.065393 | 0.065393 | 0.065393 | 0.99152 | -0.16195 | 0.99243 | -0.14441 | 17.9652
36 | 0.024091 | 0.006045 | -0.024084 | -0.006041 | 6.5281e-06 | 4.0075e-06 | 0.036221 | 0.036221 | 0.036221 | 0.98975 | -0.19621 | 0.98946 | -0.20189 | 9.9509
37 | 0.013219 | 0.0033136 | -0.013218 | -0.0033128 | 1.3412e-06 | 7.4201e-07 | 0.019875 | 0.019875 | 0.019875 | 0.98975 | -0.19621 | 0.98964 | -0.19834 | 5.4601
38 | -0.044529 | -0.011206 | 0.044533 | 0.011208 | 4.0709e-06 | 2.5739e-06 | 0.066782 | 0.066782 | 0.066782 | 0.99243 | -0.14441 | 0.99252 | -0.1425 | 18.3467
39 | 0.022625 | 0.0056752 | -0.022617 | -0.0056704 | 7.8114e-06 | 4.7683e-06 | 0.034026 | 0.034026 | 0.034026 | 0.98946 | -0.20189 | 0.98908 | -0.20914 | 9.3479
40 | 0.0077051 | 0.0019312 | -0.0077045 | -0.0019309 | 5.9168e-07 | 2.2764e-07 | 0.011585 | 0.011585 | 0.011585 | 0.98964 | -0.19834 | 0.98956 | -0.19995 | 3.1828
41 | -0.045109 | -0.011353 | 0.045146 | 0.011376 | 3.7758e-05 | 2.3881e-05 | 0.067645 | 0.067644 | 0.067645 | 0.99252 | -0.1425 | 0.99343 | -0.125 | 18.5837
42 | -0.0043585 | -0.0010923 | 0.0043586 | 0.0010923 | 1.4259e-07 | -2.0798e-08 | 0.0065783 | 0.0065782 | 0.0065783 | 0.9859 | -0.26954 | 0.98594 | -0.26885 | 1.8072
43 | -0.0064012 | -0.0016042 | 0.0064022 | 0.0016045 | 9.282e-07 | 2.5579e-07 | 0.009661 | 0.0096609 | 0.009661 | 0.98594 | -0.26885 | 0.98609 | -0.26581 | 2.6541
44 | -0.0093964 | -0.0023549 | 0.0093993 | 0.0023563 | 2.8746e-06 | 1.3532e-06 | 0.014179 | 0.014179 | 0.014179 | 0.98609 | -0.26581 | 0.98642 | -0.25939 | 3.8954
45 | 0.08518 | 0.021635 | -0.08509 | -0.021577 | 9.0292e-05 | 5.7601e-05 | 0.1286 | 0.1286 | 0.1286 | 0.98642 | -0.25939 | 0.98528 | -0.28144 | 35.3287
46 | -0.094579 | -0.023991 | 0.094736 | 0.024091 | 0.00015623 | 9.9727e-05 | 0.14278 | 0.14278 | 0.14278 | 0.98642 | -0.25939 | 0.9882 | -0.22509 | 39.2241
47 | 0.081341 | 0.020637 | -0.081318 | -0.020623 | 2.2762e-05 | 1.4517e-05 | 0.12293 | 0.12293 | 0.12293 | 0.98528 | -0.28144 | 0.98498 | -0.28726 | 33.7732
48 | -0.096394 | -0.024506 | 0.096542 | 0.0246 | 0.00014726 | 9.4009e-05 | 0.14527 | 0.14527 | 0.14527 | 0.9882 | -0.22509 | 0.98985 | -0.19343 | 39.9102
49 | -0.015183 | -0.0038054 | 0.015184 | 0.0038061 | 1.1565e-06 | 6.6797e-07 | 0.023126 | 0.023126 | 0.023126 | 0.97696 | -0.44439 | 0.97704 | -0.44279 | 6.3532
50 | -0.022983 | -0.0057605 | 0.022995 | 0.0057681 | 1.2317e-05 | 7.5469e-06 | 0.035002 | 0.035002 | 0.035002 | 0.97704 | -0.44279 | 0.97761 | -0.43155 | 9.616
51 | -0.025158 | -0.0063101 | 0.025166 | 0.006315 | 8.0413e-06 | 4.963e-06 | 0.038294 | 0.038294 | 0.038294 | 0.97761 | -0.43155 | 0.97795 | -0.42485 | 10.5204
52 | 0.0021628 | 0.00054202 | -0.0021628 | -0.00054205 | 1.4534e-08 | -3.5537e-08 | 0.003292 | 0.003292 | 0.003292 | 0.97761 | -0.43155 | 0.9776 | -0.43169 | 0.90441
53 | -0.028503 | -0.0071514 | 0.028523 | 0.0071639 | 2.0104e-05 | 1.2509e-05 | 0.043372 | 0.043372 | 0.043372 | 0.97795 | -0.42485 | 0.9787 | -0.41006 | 11.9153
54 | -0.031422 | -0.0078906 | 0.031438 | 0.0079006 | 1.6013e-05 | 1.0013e-05 | 0.04778 | 0.04778 | 0.04778 | 0.9787 | -0.41006 | 0.97925 | -0.39939 | 13.1264
55 | 0.035924 | 0.0090233 | -0.035914 | -0.0090171 | 9.8107e-06 | 6.1625e-06 | 0.053883 | 0.053883 | 0.053883 | 0.9922 | -0.14907 | 0.9919 | -0.1548 | 14.8031
56 | -0.041682 | -0.010466 | 0.041694 | 0.010474 | 1.1944e-05 | 7.5387e-06 | 0.062519 | 0.062519 | 0.062519 | 0.9922 | -0.14907 | 0.99251 | -0.14307 | 17.1756
57 | 0.033439 | 0.0083967 | -0.033421 | -0.0083856 | 1.7735e-05 | 1.1108e-05 | 0.05017 | 0.05017 | 0.05017 | 0.9919 | -0.1548 | 0.99133 | -0.16592 | 13.7829
58 | -0.053717 | -0.013488 | 0.053777 | 0.013526 | 6.0438e-05 | 3.8359e-05 | 0.080544 | 0.080544 | 0.080544 | 0.99251 | -0.14307 | 0.99373 | -0.11951 | 22.1274
59 | 0.012022 | 0.0030141 | -0.012019 | -0.0030125 | 2.836e-06 | 1.5143e-06 | 0.018025 | 0.018025 | 0.018025 | 0.99251 | -0.14307 | 0.99225 | -0.14802 | 4.9519
60 | 0.027737 | 0.006961 | -0.027726 | -0.0069542 | 1.0863e-05 | 6.7372e-06 | 0.041637 | 0.041638 | 0.041638 | 0.99133 | -0.16592 | 0.9909 | -0.17414 | 11.4389
61 | -0.055014 | -0.013836 | 0.055043 | 0.013855 | 2.9881e-05 | 1.8972e-05 | 0.082395 | 0.082395 | 0.082395 | 0.99373 | -0.11951 | 0.99431 | -0.10815 | 22.636
62 | 0.0096265 | 0.0024128 | -0.0096259 | -0.0024125 | 6.0438e-07 | 2.8692e-07 | 0.014436 | 0.014436 | 0.014436 | 0.99225 | -0.14802 | 0.99218 | -0.14934 | 3.9661
63 | 0.025544 | 0.0064074 | -0.025535 | -0.006402 | 8.6587e-06 | 5.3395e-06 | 0.038361 | 0.038361 | 0.038361 | 0.9909 | -0.17414 | 0.99053 | -0.18125 | 10.5387
64 | 0.14841 | 0.037836 | -0.14828 | -0.037759 | 0.00012062 | 7.6863e-05 | 0.22232 | 0.22232 | 0.22232 | 0.99431 | -0.10815 | 0.99343 | -0.125 | 30.5385
65 | -0.2077 | -0.052756 | 0.20796 | 0.052923 | 0.0002613 | 0.00016686 | 0.31107 | 0.31107 | 0.31107 | 0.99431 | -0.10815 | 0.99568 | -0.082047 | 42.73
66 | 0.0042495 | 0.0010649 | -0.0042493 | -0.001065 | 2.2388e-07 | -4.8174e-08 | 0.0063595 | 0.0063595 | 0.0063595 | 0.99431 | -0.10815 | 0.99426 | -0.10925 | 1.7471
67 | 0.0079096 | 0.0019824 | -0.0079091 | -0.0019822 | 4.9338e-07 | 1.9502e-07 | 0.011862 | 0.011862 | 0.011862 | 0.99218 | -0.14934 | 0.99211 | -0.15065 | 3.2589
68 | 0.019098 | 0.0047887 | -0.019095 | -0.0047866 | 3.4698e-06 | 2.076e-06 | 0.028691 | 0.028691 | 0.028691 | 0.99053 | -0.18125 | 0.99034 | -0.18506 | 7.882
69 | 0.10314 | 0.026382 | -0.10304 | -0.026319 | 9.9784e-05 | 6.3718e-05 | 0.15468 | 0.15468 | 0.15468 | 0.99343 | -0.125 | 0.99238 | -0.14501 | 42.4935
70 | -0.20976 | -0.053374 | 0.20996 | 0.053504 | 0.00020425 | 0.00013043 | 0.31376 | 0.31376 | 0.31376 | 0.99568 | -0.082047 | 0.99674 | -0.061867 | 43.0996
71 | 0.0052615 | 0.0013187 | -0.0052615 | -0.0013186 | 7.1056e-08 | 6.1859e-09 | 0.0078915 | 0.0078915 | 0.0078915 | 0.99211 | -0.15065 | 0.9921 | -0.15093 | 2.168
72 | 0.015726 | 0.0039425 | -0.015724 | -0.0039409 | 2.7503e-06 | 1.5912e-06 | 0.02363 | 0.02363 | 0.02363 | 0.99034 | -0.18506 | 0.99015 | -0.18873 | 6.4917
73 | 0.0099062 | 0.0024829 | -0.0099054 | -0.0024825 | 8.145e-07 | 3.9524e-07 | 0.014887 | 0.014887 | 0.014887 | 0.99015 | -0.18873 | 0.99006 | -0.19046 | 4.0899
74 | 0.0059894 | 0.0015011 | -0.0059887 | -0.0015009 | 7.7075e-07 | 1.6715e-07 | 0.0090019 | 0.009002 | 0.009002 | 0.99006 | -0.19046 | 0.98992 | -0.19316 | 2.4731
75 | 0.055055 | 0.013835 | -0.055051 | -0.013832 | 4.0627e-06 | 2.5804e-06 | 0.083362 | 0.083362 | 0.083362 | 0.98289 | -0.3286 | 0.98281 | -0.33014 | 22.9016
76 | -0.063255 | -0.01589 | 0.063326 | 0.015935 | 7.0901e-05 | 4.5115e-05 | 0.095776 | 0.095776 | 0.095776 | 0.98289 | -0.3286 | 0.98409 | -0.30514 | 26.3121
77 | 0.047961 | 0.012055 | -0.047917 | -0.012027 | 4.4845e-05 | 2.8414e-05 | 0.072628 | 0.072628 | 0.072628 | 0.98281 | -0.33014 | 0.98181 | -0.34975 | 19.9528
78 | -0.065238 | -0.016414 | 0.065318 | 0.016465 | 7.9823e-05 | 5.0808e-05 | 0.098667 | 0.098667 | 0.098667 | 0.98409 | -0.30514 | 0.98541 | -0.27957 | 27.1064
79 | 0.038886 | 0.0097637 | -0.03888 | -0.0097601 | 5.6672e-06 | 3.572e-06 | 0.058941 | 0.058941 | 0.058941 | 0.98181 | -0.34975 | 0.98165 | -0.3528 | 16.1926
80 | -0.067228 | -0.016944 | 0.067277 | 0.016975 | 4.9111e-05 | 3.1269e-05 | 0.10155 | 0.10155 | 0.10155 | 0.98541 | -0.27957 | 0.9862 | -0.26431 | 27.8989
81 | 0.030596 | 0.0076839 | -0.030575 | -0.0076709 | 2.0725e-05 | 1.294e-05 | 0.046383 | 0.046383 | 0.046383 | 0.98165 | -0.3528 | 0.98093 | -0.36701 | 12.7427
82 | -0.075933 | -0.019144 | 0.076056 | 0.019223 | 0.00012362 | 7.8797e-05 | 0.11461 | 0.11461 | 0.11461 | 0.9862 | -0.26431 | 0.98795 | -0.23035 | 31.4866
83 | 0.026175 | 0.0065682 | -0.026168 | -0.0065636 | 7.559e-06 | 4.6764e-06 | 0.039709 | 0.039709 | 0.039709 | 0.98093 | -0.36701 | 0.98062 | -0.37307 | 10.9092
84 | 0.020495 | 0.0051424 | -0.020487 | -0.0051371 | 8.6974e-06 | 5.2549e-06 | 0.030871 | 0.030871 | 0.030871 | 0.98795 | -0.23035 | 0.98749 | -0.23926 | 8.4811
85 | -0.096551 | -0.024366 | 0.096794 | 0.02452 | 0.00024241 | 0.00015475 | 0.14548 | 0.14548 | 0.14548 | 0.98795 | -0.23035 | 0.99066 | -0.17807 | 39.9676
86 | -0.0010093 | -0.00025296 | 0.0010093 | 0.00025285 | 7.5564e-09 | -1.0977e-07 | 0.0015103 | 0.0015103 | 0.0015103 | 0.99443 | -0.10617 | 0.99444 | -0.10602 | 0.41492
87 | -0.0022641 | -0.00056733 | 0.0022641 | 0.00056729 | 1.6651e-08 | -3.9536e-08 | 0.0033878 | 0.0033878 | 0.0033878 | 0.99444 | -0.10602 | 0.99445 | -0.10586 | 0.93072
88 | -0.0063201 | -0.0015838 | 0.0063203 | 0.0015839 | 1.6174e-07 | 4.0943e-08 | 0.0094569 | 0.0094569 | 0.0094569 | 0.99445 | -0.10586 | 0.99447 | -0.10533 | 2.5981
89 | -0.008295 | -0.0020788 | 0.0082957 | 0.002079 | 6.3644e-07 | 2.6437e-07 | 0.012412 | 0.012412 | 0.012412 | 0.99447 | -0.10533 | 0.99456 | -0.10371 | 3.4098
90 | 0.023556 | 0.0059139 | -0.023534 | -0.0059004 | 2.2003e-05 | 1.347e-05 | 0.035247 | 0.035247 | 0.035247 | 0.99456 | -0.10371 | 0.99354 | -0.12332 | 9.6832
91 | -0.031851 | -0.0079929 | 0.031871 | 0.0080053 | 1.9815e-05 | 1.238e-05 | 0.047658 | 0.047658 | 0.047658 | 0.99456 | -0.10371 | 0.99523 | -0.090677 | 13.0929
92 | 0.0051651 | 0.0012939 | -0.0051639 | -0.0012938 | 1.23e-06 | 1.0846e-07 | 0.0078222 | 0.0078224 | 0.0078224 | 0.98254 | -0.33455 | 0.98228 | -0.33955 | 2.149
93 | -0.078513 | -0.019851 | 0.078691 | 0.019965 | 0.00017852 | 0.00011383 | 0.11897 | 0.11897 | 0.11897 | 0.98254 | -0.33455 | 0.98498 | -0.28726 | 32.6832
94 | 0.0051639 | 0.0012938 | -0.0051633 | -0.0012938 | 6.438e-07 | 5.6927e-08 | 0.0078224 | 0.0078225 | 0.0078225 | 0.98228 | -0.33955 | 0.98215 | -0.34217 | 2.1491
95 | 0.099622 | 0.025462 | -0.099459 | -0.025358 | 0.00016388 | 0.00010463 | 0.14955 | 0.14955 | 0.14955 | 0.99238 | -0.14501 | 0.9906 | -0.17908 | 41.0864
96 | -0.21392 | -0.054495 | 0.21436 | 0.054779 | 0.00044352 | 0.00028325 | 0.31967 | 0.31967 | 0.31967 | 0.99674 | -0.061867 | 0.999 | -0.018988 | 43.9105
97 | 0.098912 | 0.025221 | -0.098843 | -0.025177 | 6.8459e-05 | 4.3708e-05 | 0.14873 | 0.14873 | 0.14873 | 0.9906 | -0.17908 | 0.98985 | -0.19343 | 40.8607
98 | -0.21562 | -0.055095 | 0.21582 | 0.055222 | 0.00019818 | 0.00012657 | 0.32155 | 0.32155 | 0.32155 | 0.999 | -0.018988 | 1 | 0 | 44.1687
99 | 0.0063357 | 0.0015879 | -0.0063353 | -0.0015878 | 4.7755e-07 | 1.2575e-07 | 0.0095317 | 0.0095318 | 0.0095318 | 0.98908 | -0.20914 | 0.989 | -0.21072 | 2.6186
100 | 0.016281 | 0.0040825 | -0.016275 | -0.0040791 | 5.7884e-06 | 3.3745e-06 | 0.024495 | 0.024495 | 0.024495 | 0.98908 | -0.20914 | 0.9887 | -0.2166 | 6.7293
101 | 0.0073014 | 0.0018301 | -0.0072996 | -0.0018294 | 1.8307e-06 | 6.5333e-07 | 0.010989 | 0.010989 | 0.010989 | 0.9887 | -0.2166 | 0.98843 | -0.22186 | 3.019
102 | -0.032729 | -0.0082241 | 0.032743 | 0.0082325 | 1.348e-05 | 8.4442e-06 | 0.049741 | 0.049741 | 0.049741 | 0.97925 | -0.39939 | 0.97969 | -0.39076 | 13.6652
103 | 0.17173 | 0.043743 | -0.17154 | -0.043622 | 0.00018921 | 0.0001207 | 0.25731 | 0.25731 | 0.25731 | 0.99409 | -0.1124 | 0.99289 | -0.13527 | 35.3445
104 | -0.17359 | -0.044209 | 0.17389 | 0.044398 | 0.00029693 | 0.00018943 | 0.26009 | 0.26009 | 0.26009 | 0.99409 | -0.1124 | 0.99594 | -0.077003 | 35.727
105 | 0.00522 | 0.0013082 | -0.0052199 | -0.0013082 | 1.2907e-07 | 9.8704e-09 | 0.0078231 | 0.0078231 | 0.0078231 | 0.99289 | -0.13527 | 0.99286 | -0.13579 | 2.1492
106 | 0.16632 | 0.042314 | -0.16626 | -0.042273 | 6.3964e-05 | 4.0795e-05 | 0.24948 | 0.24948 | 0.24948 | 0.99289 | -0.13527 | 0.99247 | -0.14325 | 34.2699
107 | -0.20731 | -0.0528 | 0.20765 | 0.053018 | 0.00034087 | 0.00021767 | 0.31003 | 0.31003 | 0.31003 | 0.99594 | -0.077003 | 0.99773 | -0.042975 | 42.587
108 | 0.03342 | 0.0084017 | -0.033398 | -0.008388 | 2.1807e-05 | 1.3653e-05 | 0.049941 | 0.049941 | 0.049941 | 0.99594 | -0.077003 | 0.99523 | -0.090677 | 13.7201
109 | 0.0052199 | 0.0013082 | -0.0052197 | -0.0013082 | 1.771e-07 | 1.355e-08 | 0.0078231 | 0.0078231 | 0.0078231 | 0.99286 | -0.13579 | 0.99283 | -0.1365 | 2.1492
110 | 0.16478 | 0.041901 | -0.16458 | -0.041777 | 0.00019579 | 0.00012486 | 0.24726 | 0.24726 | 0.24726 | 0.99247 | -0.14325 | 0.99119 | -0.16795 | 33.9647
111 | -0.21001 | -0.05361 | 0.2101 | 0.053667 | 8.8174e-05 | 5.6306e-05 | 0.31356 | 0.31356 | 0.31356 | 0.99773 | -0.042975 | 0.99819 | -0.034291 | 43.0713
112 | 0.16253 | 0.041264 | -0.16246 | -0.041214 | 7.9137e-05 | 5.0465e-05 | 0.24419 | 0.24419 | 0.24419 | 0.99119 | -0.16795 | 0.99066 | -0.17807 | 33.5431
113 | -0.065053 | -0.016522 | 0.065103 | 0.016554 | 4.998e-05 | 3.1809e-05 | 0.097872 | 0.097872 | 0.097872 | 0.98983 | -0.19402 | 0.99066 | -0.17807 | 26.8879
114 | 0.065053 | 0.016522 | -0.06487 | -0.016406 | 0.00018265 | 0.00011625 | 0.097872 | 0.097872 | 0.097872 | 0.98983 | -0.19402 | 0.98679 | -0.25254 | 26.888
115 | 0.0005593 | 0.0001396 | -0.00055929 | -0.00013979 | 4.1035e-09 | -1.9708e-07 | 0.00083989 | 0.00083996 | 0.00083996 | 0.99066 | -0.17807 | 0.99065 | -0.17823 | 0.23076
116 | 0.062387 | 0.015784 | -0.062383 | -0.015781 | 3.9687e-06 | 2.5247e-06 | 0.094128 | 0.094128 | 0.094128 | 0.98679 | -0.25254 | 0.98672 | -0.25386 | 25.8594
117 | 0.0030751 | 0.00077043 | -0.003075 | -0.00077051 | 8.5003e-08 | -7.7755e-08 | 0.0046589 | 0.0046589 | 0.0046589 | 0.98215 | -0.34217 | 0.98212 | -0.34275 | 1.2799
118 | -0.21206 | -0.054156 | 0.21231 | 0.054321 | 0.00025835 | 0.00016499 | 0.31647 | 0.31647 | 0.31647 | 0.99819 | -0.034291 | 0.99952 | -0.0091201 | 43.4716
119 | 0.00055929 | 0.00013979 | -0.00055929 | -0.00014017 | 7.8346e-09 | -3.7618e-07 | 0.00083996 | 0.00084009 | 0.00084009 | 0.99065 | -0.17823 | 0.99064 | -0.17852 | 0.23079
120 | 0.057061 | 0.014447 | -0.056978 | -0.014395 | 8.2827e-05 | 5.2629e-05 | 0.086102 | 0.086102 | 0.086102 | 0.98672 | -0.25386 | 0.98516 | -0.28414 | 23.6544
121 | 0.001695 | 0.00042465 | -0.001695 | -0.00042481 | 3.4347e-08 | -1.5375e-07 | 0.0025681 | 0.0025682 | 0.0025682 | 0.98212 | -0.34275 | 0.9821 | -0.34317 | 0.70554
122 | -0.21702 | -0.0555 | 0.21711 | 0.055561 | 9.5823e-05 | 6.1198e-05 | 0.32347 | 0.32347 | 0.32347 | 0.99952 | -0.0091201 | 1 | 0 | 44.4333
123 | 0.021617 | 0.0054201 | -0.021613 | -0.0054178 | 3.6923e-06 | 2.2415e-06 | 0.032376 | 0.032376 | 0.032376 | 0.99354 | -0.12332 | 0.99336 | -0.1269 | 8.8946
124 | -0.0066873 | -0.0016756 | 0.0066881 | 0.0016758 | 7.5131e-07 | 2.2279e-07 | 0.010022 | 0.010022 | 0.010022 | 0.99292 | -0.13538 | 0.99304 | -0.13302 | 2.7532
125 | 0.0019677 | 0.00049274 | -0.0019676 | -0.00049312 | 1.1589e-07 | -3.8549e-07 | 0.0029487 | 0.0029489 | 0.0029489 | 0.99292 | -0.13538 | 0.99286 | -0.13662 | 0.81013
126 | -0.014379 | -0.0036033 | 0.014382 | 0.0036053 | 3.6169e-06 | 2.0459e-06 | 0.021546 | 0.021546 | 0.021546 | 0.99304 | -0.13302 | 0.99332 | -0.12774 | 5.9192
127 | -0.01759 | -0.0044092 | 0.017591 | 0.0044096 | 7.0412e-07 | 4.1563e-07 | 0.02635 | 0.02635 | 0.02635 | 0.99332 | -0.12774 | 0.99336 | -0.1269 | 7.2391
128 | -0.0056585 | -0.0014181 | 0.0056587 | 0.0014181 | 2.1102e-07 | 3.928e-08 | 0.008598 | 0.008598 | 0.008598 | 0.97928 | -0.39928 | 0.97932 | -0.39849 | 2.3621
129 | 0.0056585 | 0.0014181 | -0.0056579 | -0.001418 | 5.3905e-07 | 1.0038e-07 | 0.008598 | 0.0085981 | 0.0085981 | 0.97928 | -0.39928 | 0.97918 | -0.40128 | 2.3621
130 | -0.0056587 | -0.0014181 | 0.0056596 | 0.0014183 | 9.8167e-07 | 1.8262e-07 | 0.008598 | 0.0085978 | 0.008598 | 0.97932 | -0.39849 | 0.97951 | -0.39485 | 2.3621
131 | -0.012831 | -0.0032155 | 0.012834 | 0.0032172 | 3.0781e-06 | 1.698e-06 | 0.019491 | 0.019491 | 0.019491 | 0.97951 | -0.39485 | 0.97976 | -0.38982 | 5.3548
132 | 0.022013 | 0.0055223 | -0.022012 | -0.0055218 | 8.435e-07 | 5.1441e-07 | 0.033405 | 0.033405 | 0.033405 | 0.98062 | -0.37307 | 0.98058 | -0.37387 | 9.1771
133 | 0.020646 | 0.0051795 | -0.020643 | -0.0051774 | 3.4356e-06 | 2.0811e-06 | 0.031332 | 0.031332 | 0.031332 | 0.98058 | -0.37387 | 0.9804 | -0.37736 | 8.6078
134 | 0.016607 | 0.0041658 | -0.0166 | -0.0041618 | 6.8665e-06 | 4.0313e-06 | 0.025206 | 0.025206 | 0.025206 | 0.9804 | -0.37736 | 0.97996 | -0.38604 | 6.9248
135 | 0.012836 | 0.0032185 | -0.012834 | -0.0032172 | 2.3097e-06 | 1.274e-06 | 0.019491 | 0.019491 | 0.019491 | 0.97996 | -0.38604 | 0.97976 | -0.38982 | 5.3548
136 | 0.016899 | 0.0042379 | -0.016891 | -0.0042332 | 8.0135e-06 | 4.7073e-06 | 0.025465 | 0.025465 | 0.025465 | 0.98749 | -0.23926 | 0.98698 | -0.24921 | 6.9959
137 | 0.0061999 | 0.0015538 | -0.0061992 | -0.0015537 | 6.3655e-07 | 1.5913e-07 | 0.0093472 | 0.0093473 | 0.0093473 | 0.98698 | -0.24921 | 0.98687 | -0.25137 | 2.5679
138 | 0.053767 | 0.01359 | -0.053766 | -0.013589 | 1.0072e-06 | 6.3941e-07 | 0.081252 | 0.081252 | 0.081252 | 0.98516 | -0.28414 | 0.98514 | -0.28453 | 22.3219
139 | 0.052142 | 0.013182 | -0.052091 | -0.01315 | 5.1276e-05 | 3.2536e-05 | 0.078799 | 0.078799 | 0.078799 | 0.98514 | -0.28453 | 0.98408 | -0.30506 | 21.6482
140 | 0.04883 | 0.012332 | -0.048774 | -0.012297 | 5.5893e-05 | 3.5425e-05 | 0.073869 | 0.073869 | 0.073869 | 0.98408 | -0.30506 | 0.98285 | -0.32898 | 20.2936
141 | 0.046204 | 0.011653 | -0.046153 | -0.01162 | 5.128e-05 | 3.2466e-05 | 0.069978 | 0.069979 | 0.069979 | 0.98285 | -0.32898 | 0.98166 | -0.35219 | 19.2249
142 | 0.044062 | 0.011096 | -0.044045 | -0.011086 | 1.6659e-05 | 1.0536e-05 | 0.066809 | 0.066809 | 0.066809 | 0.98166 | -0.35219 | 0.98126 | -0.3601 | 18.3541
143 | 0.038416 | 0.0096749 | -0.038414 | -0.0096741 | 1.3194e-06 | 8.3134e-07 | 0.058272 | 0.058272 | 0.058272 | 0.98126 | -0.3601 | 0.98122 | -0.36082 | 16.0088
144 | 0.037066 | 0.0093361 | -0.037013 | -0.0093028 | 5.2998e-05 | 3.3355e-05 | 0.056227 | 0.056227 | 0.056227 | 0.98122 | -0.36082 | 0.97969 | -0.39076 | 15.447

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4382 | 0.11169

## res_load
| p_mw | q_mvar
0 | 0.0014565 | 0.00036503
1 | 0.00955 | 0.0023934
2 | 0.0021302 | 0.00053389
3 | 0.0027796 | 0.00069663
4 | 0.0055475 | 0.0013903
5 | 0.007778 | 0.0019493
6 | 0.0061943 | 0.0015524
7 | 0.0035554 | 0.00089106
8 | 0.0041595 | 0.0010425
9 | 0.0082079 | 0.0020571
10 | 0.0072727 | 0.0018227
11 | 0.0020952 | 0.00052511
12 | 0.0028637 | 0.00071772
13 | 0.0040797 | 0.0010225
14 | 0.0032807 | 0.00082223
15 | 0.0045086 | 0.00113
16 | 0.0019347 | 0.00048488
17 | 0.0026071 | 0.0006534
18 | 0.0026294 | 0.00065899
19 | 0.0017618 | 0.00044154
20 | 0.0012874 | 0.00032266
21 | 0.0019042 | 0.00047724
22 | 0.0012384 | 0.00031038
23 | 0.00092623 | 0.00023214
24 | 0.0014596 | 0.00036581
25 | 0.005513 | 0.0013817
26 | 0.00057523 | 0.00014417
27 | 0.0043585 | 0.0010923
28 | 0.0020426 | 0.00051192
29 | 0.0029943 | 0.00075044
30 | 0.0037493 | 0.00093966
31 | 0.0016586 | 0.00041569
32 | 0.0054326 | 0.0013615
33 | 0.0077982 | 0.0019544
34 | 0.003337 | 0.00083634
35 | 0.0021628 | 0.00054205
36 | 0.0028995 | 0.00072668
37 | 0.0057582 | 0.0014431
38 | 0.0024756 | 0.00062045
39 | 0.0056842 | 0.0014246
40 | 0.0012364 | 0.00030988
41 | 0.0023929 | 0.00059971
42 | 0.002182 | 0.00054686
43 | 0.0017163 | 0.00043016
44 | 0.0064373 | 0.0016133
45 | 0.0018004 | 0.00045123
46 | 0.0042493 | 0.001065
47 | 0.0026476 | 0.00066355
48 | 0.0033682 | 0.00084415
49 | 0.0058174 | 0.001458
50 | 0.003916 | 0.00098144
51 | 0.0059887 | 0.0015009
52 | 0.0082 | 0.0020551
53 | 0.0070896 | 0.0017768
54 | 0.0019122 | 0.00047924
55 | 0.009031 | 0.0022634
56 | 0.0019103 | 0.00047877
57 | 0.0082844 | 0.0020763
58 | 0.0086551 | 0.0021692
59 | 0.0043997 | 0.0011027
60 | 0.0010093 | 0.00025296
61 | 0.0012548 | 0.00031447
62 | 0.0052615 | 0.0013186
63 | 0.004056 | 0.0010165
64 | 0.0019747 | 0.00049491
65 | 0.0026264 | 0.00065824
66 | 0.0034159 | 0.0008561
67 | 0.0039547 | 0.00099115
68 | 0.00054698 | 0.00013709
69 | 0.0012622 | 0.00031634
70 | 0.0077045 | 0.0019309
71 | 0.0063353 | 0.0015878
72 | 0.0089738 | 0.0022491
73 | 0.0023016 | 0.00057684
74 | 0.0012908 | 0.0003235
75 | 0.0018605 | 0.00046629
76 | 0.0014819 | 0.0003714
77 | 0.0023644 | 0.00059257
78 | 0.001527 | 0.00038269
79 | 0.0052197 | 0.0013082
80 | 0.0020445 | 0.0005124
81 | 0.0024829 | 0.00062227
82 | 0.0020882 | 0.00052334
83 | 0.0019548 | 0.00048991
84 | 0.00055929 | 0.00014017
85 | 0.0053224 | 0.0013339
86 | 0.00138 | 0.00034586
87 | 0.0047031 | 0.0011787
88 | 0.0019166 | 0.00048034
89 | 0.0047196 | 0.0011828
90 | 0.0076908 | 0.0019275
91 | 0.0019676 | 0.00049312
92 | 0.0032074 | 0.00080385
93 | 0.0040229 | 0.0010082
94 | 0.0056579 | 0.001418
95 | 0.0071709 | 0.0017972
96 | 0.0072996 | 0.0018294
97 | 0.0041548 | 0.0010413
98 | 0.0013657 | 0.00034228
99 | 0.0040363 | 0.0010116
100 | 0.0037637 | 0.00094328
101 | 0.0035879 | 0.00089922
102 | 0.010691 | 0.0026793
103 | 0.0061992 | 0.0015537
104 | 0.0032113 | 0.00080482
105 | 0.0016237 | 0.00040694
106 | 0.0032608 | 0.00081723
107 | 0.0036154 | 0.00090609
108 | 0.0025697 | 0.00064402
109 | 0.002091 | 0.00052406
110 | 0.0056296 | 0.0014109
111 | 0.0013486 | 0.00033799
112 | 0.0042702 | 0.0010702
113 | 0.001695 | 0.00042481

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1