## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-21_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-21_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-21_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_161-21_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_161-21_0_6_node_113 | 0.4 | n |  | TRUE
5 | bus_LV_161-21_0_6_node_143 | 0.4 | n |  | TRUE
6 | bus_LV_161-21_0_6_node_114 | 0.4 | n |  | TRUE
7 | bus_LV_161-21_0_6_node_148 | 0.4 | n |  | TRUE
8 | bus_LV_161-21_0_6_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_161-21_0_6_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_161-21_0_6_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_161-21_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_161-21_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_161-21_0_6_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_161-21_0_6_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_161-21_0_6_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_161-21_0_6_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_161-21_0_6_node_141 | 0.4 | n |  | TRUE
18 | bus_LV_161-21_0_6_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_161-21_0_6_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_161-21_0_6_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_161-21_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_161-21_0_6_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_161-21_0_6_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_161-21_0_6_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_161-21_0_6_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_161-21_0_6_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_161-21_0_6_node_71 | 0.4 | n |  | TRUE
28 | bus_LV_161-21_0_6_node_146 | 0.4 | n |  | TRUE
29 | bus_LV_161-21_0_6_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_161-21_0_6_node_12 | 0.4 | n |  | TRUE
31 | bus_LV_161-21_0_6_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_161-21_0_6_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_161-21_0_6_node_102 | 0.4 | n |  | TRUE
34 | bus_LV_161-21_0_6_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_161-21_0_6_node_101 | 0.4 | n |  | TRUE
36 | bus_LV_161-21_0_6_node_15 | 0.4 | n |  | TRUE
37 | bus_LV_161-21_0_6_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_161-21_0_6_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_161-21_0_6_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_161-21_0_6_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_161-21_0_6_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_161-21_0_6_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_161-21_0_6_node_48 | 0.4 | n |  | TRUE
44 | bus_LV_161-21_0_6_node_93 | 0.4 | n |  | TRUE
45 | bus_LV_161-21_0_6_node_56 | 0.4 | n |  | TRUE
46 | bus_LV_161-21_0_6_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_161-21_0_6_node_91 | 0.4 | n |  | TRUE
48 | bus_LV_161-21_0_6_node_21 | 0.4 | n |  | TRUE
49 | bus_LV_161-21_0_6_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_161-21_0_6_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_161-21_0_6_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_161-21_0_6_node_25 | 0.4 | n |  | TRUE
53 | bus_LV_161-21_0_6_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_161-21_0_6_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_161-21_0_6_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_161-21_0_6_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_161-21_0_6_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_161-21_0_6_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_161-21_0_6_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_161-21_0_6_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_161-21_0_6_node_117 | 0.4 | n |  | TRUE
62 | bus_LV_161-21_0_6_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_161-21_0_6_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_161-21_0_6_node_123 | 0.4 | n |  | TRUE
65 | bus_LV_161-21_0_6_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_161-21_0_6_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_161-21_0_6_node_30 | 0.4 | n |  | TRUE
68 | bus_LV_161-21_0_6_node_31 | 0.4 | n |  | TRUE
69 | bus_LV_161-21_0_6_node_33 | 0.4 | n |  | TRUE
70 | bus_LV_161-21_0_6_node_89 | 0.4 | n |  | TRUE
71 | bus_LV_161-21_0_6_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_161-21_0_6_node_88 | 0.4 | n |  | TRUE
73 | bus_LV_161-21_0_6_node_108 | 0.4 | n |  | TRUE
74 | bus_LV_161-21_0_6_node_106 | 0.4 | n |  | TRUE
75 | bus_LV_161-21_0_6_node_39 | 0.4 | n |  | TRUE
76 | bus_LV_161-21_0_6_node_40 | 0.4 | n |  | TRUE
77 | bus_LV_161-21_0_6_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_161-21_0_6_node_42 | 0.4 | n |  | TRUE
79 | bus_LV_161-21_0_6_node_97 | 0.4 | n |  | TRUE
80 | bus_LV_161-21_0_6_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_161-21_0_6_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_161-21_0_6_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_161-21_0_6_node_100 | 0.4 | n |  | TRUE
84 | bus_LV_161-21_0_6_node_136 | 0.4 | n |  | TRUE
85 | bus_LV_161-21_0_6_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_161-21_0_6_node_140 | 0.4 | n |  | TRUE
87 | bus_LV_161-21_0_6_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_161-21_0_6_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_161-21_0_6_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_161-21_0_6_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_161-21_0_6_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_161-21_0_6_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_161-21_0_6_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_161-21_0_6_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_161-21_0_6_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_161-21_0_6_node_157 | 0.4 | n |  | TRUE
97 | bus_LV_161-21_0_6_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_161-21_0_6_node_145 | 0.4 | n |  | TRUE
99 | bus_LV_161-21_0_6_node_155 | 0.4 | n |  | TRUE
100 | bus_LV_161-21_0_6_node_154 | 0.4 | n |  | TRUE
101 | bus_LV_161-21_0_6_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_161-21_0_6_node_132 | 0.4 | n |  | TRUE
103 | bus_LV_161-21_0_6_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_161-21_0_6_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_161-21_0_6_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_161-21_0_6_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_161-21_0_6_node_72 | 0.4 | n |  | TRUE
108 | bus_LV_161-21_0_6_node_77 | 0.4 | n |  | TRUE
109 | bus_LV_161-21_0_6_node_139 | 0.4 | n |  | TRUE
110 | bus_LV_161-21_0_6_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_161-21_0_6_node_74 | 0.4 | n |  | TRUE
112 | bus_LV_161-21_0_6_node_75 | 0.4 | n |  | TRUE
113 | bus_LV_161-21_0_6_node_135 | 0.4 | n |  | TRUE
114 | bus_LV_161-21_0_6_node_115 | 0.4 | n |  | TRUE
115 | bus_LV_161-21_0_6_node_147 | 0.4 | n |  | TRUE
116 | bus_LV_161-21_0_6_node_121 | 0.4 | n |  | TRUE
117 | bus_LV_161-21_0_6_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_161-21_0_6_node_79 | 0.4 | n |  | TRUE
119 | bus_LV_161-21_0_6_node_126 | 0.4 | n |  | TRUE
120 | bus_LV_161-21_0_6_node_125 | 0.4 | n |  | TRUE
121 | bus_LV_161-21_0_6_node_80 | 0.4 | n |  | TRUE
122 | bus_LV_161-21_0_6_node_81 | 0.4 | n |  | TRUE
123 | bus_LV_161-21_0_6_node_82 | 0.4 | n |  | TRUE
124 | bus_LV_161-21_0_6_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_161-21_0_6_node_96 | 0.4 | n |  | TRUE
126 | bus_LV_161-21_0_6_node_95 | 0.4 | n |  | TRUE
127 | bus_LV_161-21_0_6_node_83 | 0.4 | n |  | TRUE
128 | bus_LV_161-21_0_6_node_120 | 0.4 | n |  | TRUE
129 | bus_LV_161-21_0_6_node_92 | 0.4 | n |  | TRUE
130 | bus_LV_161-21_0_6_node_94 | 0.4 | n |  | TRUE
131 | bus_LV_161-21_0_6_node_159 | 0.4 | n |  | TRUE
132 | bus_LV_161-21_0_6_node_156 | 0.4 | n |  | TRUE
133 | bus_LV_161-21_0_6_node_158 | 0.4 | n |  | TRUE
134 | bus_LV_161-21_0_6_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_161-21_0_6_node_153 | 0.4 | n |  | TRUE
136 | bus_LV_161-21_0_6_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_161-21_0_6_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_161-21_0_6_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_161-21_0_6_node_124 | 0.4 | n |  | TRUE
140 | bus_LV_161-21_0_6_node_105 | 0.4 | n |  | TRUE
141 | bus_LV_161-21_0_6_node_107 | 0.4 | n |  | TRUE
142 | bus_LV_161-21_0_6_node_109 | 0.4 | n |  | TRUE
143 | bus_LV_161-21_0_6_node_110 | 0.4 | n |  | TRUE
144 | bus_LV_161-21_0_6_node_134 | 0.4 | n |  | TRUE
145 | bus_LV_161-21_0_6_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_161-21_0_6_node_128 | 0.4 | n |  | TRUE
147 | bus_LV_161-21_0_6_node_127 | 0.4 | n |  | TRUE
148 | bus_LV_161-21_0_6_node_144 | 0.4 | n |  | TRUE
149 | bus_LV_161-21_0_6_node_129 | 0.4 | n |  | TRUE
150 | bus_LV_161-21_0_6_node_130 | 0.4 | n |  | TRUE
151 | bus_LV_161-21_0_6_node_149 | 0.4 | n |  | TRUE
152 | bus_LV_161-21_0_6_node_150 | 0.4 | n |  | TRUE
153 | bus_LV_161-21_0_6_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_161-21_0_6_node_152 | 0.4 | n |  | TRUE
155 | bus_MV_494_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-21_0_6_load_0 | 0 | 0.0069776 | 0.0017488 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-21_0_6_load_113 | 4 | 0.004064 | 0.0010185 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-21_0_6_load_143 | 5 | 0.0082478 | 0.0020671 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-21_0_6_load_114 | 6 | 0.0044939 | 0.0011263 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-21_0_6_load_148 | 7 | 0.008673 | 0.0021737 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-21_0_6_load_51 | 8 | 0.007829 | 0.0019621 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-21_0_6_load_50 | 9 | 0.0076109 | 0.0019075 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-21_0_6_load_5 | 11 | 0.0072473 | 0.0018163 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-21_0_6_load_38 | 15 | 0.004448 | 0.0011148 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-21_0_6_load_141 | 17 | 0.0049682 | 0.0012451 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-21_0_6_load_7 | 19 | 0.0040551 | 0.0010163 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-21_0_6_load_8 | 20 | 0.0039711 | 0.00099525 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-21_0_6_load_9 | 21 | 0.0019933 | 0.00049958 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-21_0_6_load_11 | 23 | 0.0029599 | 0.00074181 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-21_0_6_load_98 | 24 | 0.008195 | 0.0020539 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-21_0_6_load_99 | 25 | 0.0030182 | 0.00075643 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-21_0_6_load_28 | 26 | 0.0057196 | 0.0014335 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-21_0_6_load_71 | 27 | 0.01245 | 0.0031203 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-21_0_6_load_146 | 28 | 0.0029189 | 0.00073154 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-21_0_6_load_12 | 30 | 0.006312 | 0.0015819 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-21_0_6_load_13 | 31 | 0.0077216 | 0.0019352 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-21_0_6_load_14 | 32 | 0.0057854 | 0.00145 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-21_0_6_load_103 | 34 | 0.011193 | 0.0028051 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-21_0_6_load_101 | 35 | 0.0086276 | 0.0021623 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-21_0_6_load_15 | 36 | 0.0021633 | 0.00054218 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-21_0_6_load_16 | 37 | 0.0022036 | 0.00055228 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-21_0_6_load_18 | 39 | 0.0024555 | 0.0006154 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-21_0_6_load_19 | 40 | 0.0020063 | 0.00050282 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-21_0_6_load_20 | 41 | 0.0039695 | 0.00099484 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-21_0_6_load_55 | 42 | 0.0045846 | 0.001149 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-21_0_6_load_48 | 43 | 0.0033638 | 0.00084304 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-21_0_6_load_93 | 44 | 0.0030099 | 0.00075435 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-21_0_6_load_49 | 46 | 0.0030082 | 0.00075393 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-21_0_6_load_91 | 47 | 0.0030752 | 0.00077073 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-21_0_6_load_21 | 48 | 0.0010981 | 0.00027521 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-21_0_6_load_26 | 50 | 0.0074356 | 0.0018635 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-21_0_6_load_25 | 52 | 0.0059743 | 0.0014973 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-21_0_6_load_45 | 54 | 0.0054501 | 0.0013659 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-21_0_6_load_37 | 55 | 0.0044092 | 0.001105 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-21_0_6_load_35 | 56 | 0.0075411 | 0.00189 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-21_0_6_load_59 | 57 | 0.0075724 | 0.0018978 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-21_0_6_load_60 | 58 | 0.0078977 | 0.0019794 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-21_0_6_load_44 | 59 | 0.0015412 | 0.00038627 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-21_0_6_load_36 | 60 | 0.0077415 | 0.0019402 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-21_0_6_load_117 | 61 | 0.0050714 | 0.001271 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-21_0_6_load_76 | 62 | 0.0062137 | 0.0015573 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-21_0_6_load_57 | 63 | 0.0043513 | 0.0010905 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-21_0_6_load_43 | 66 | 0.0033564 | 0.00084118 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-21_0_6_load_30 | 67 | 0.0068612 | 0.0017196 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-21_0_6_load_31 | 68 | 0.0084446 | 0.0021164 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-21_0_6_load_33 | 69 | 0.0075855 | 0.0019011 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-21_0_6_load_119 | 71 | 0.0058935 | 0.0014771 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-21_0_6_load_108 | 73 | 0.0021507 | 0.00053902 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-21_0_6_load_106 | 74 | 0.0016042 | 0.00040205 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-21_0_6_load_39 | 75 | 0.0046412 | 0.0011632 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-21_0_6_load_40 | 76 | 0.0013321 | 0.00033386 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-21_0_6_load_41 | 77 | 0.0045695 | 0.0011452 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-21_0_6_load_42 | 78 | 0.0014151 | 0.00035465 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-21_0_6_load_97 | 79 | 0.0033379 | 0.00083656 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-21_0_6_load_47 | 80 | 0.0012047 | 0.00030193 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-21_0_6_load_65 | 81 | 0.0063721 | 0.001597 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-21_0_6_load_66 | 82 | 0.0064022 | 0.0016046 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-21_0_6_load_100 | 83 | 0.004532 | 0.0011358 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_161-21_0_6_load_140 | 86 | 0.0059725 | 0.0014969 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_161-21_0_6_load_68 | 87 | 0.0040032 | 0.0010033 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_161-21_0_6_load_78 | 89 | 0.0065124 | 0.0016322 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_161-21_0_6_load_87 | 90 | 0.0098639 | 0.0024721 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_161-21_0_6_load_86 | 91 | 0.0090182 | 0.0022602 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_161-21_0_6_load_61 | 92 | 0.0034006 | 0.00085228 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_161-21_0_6_load_62 | 93 | 0.0039265 | 0.00098409 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_161-21_0_6_load_145 | 98 | 0.0017522 | 0.00043914 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_161-21_0_6_load_155 | 99 | 0.0020457 | 0.0005127 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_161-21_0_6_load_154 | 100 | 0.0013859 | 0.00034733 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_161-21_0_6_load_84 | 101 | 0.0055653 | 0.0013948 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_161-21_0_6_load_132 | 102 | 0.00099656 | 0.00024976 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_161-21_0_6_load_122 | 104 | 0.0061631 | 0.0015446 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_161-21_0_6_load_90 | 105 | 0.0076259 | 0.0019112 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_161-21_0_6_load_70 | 106 | 0.0055351 | 0.0013872 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_161-21_0_6_load_72 | 107 | 0.0093763 | 0.0023499 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_161-21_0_6_load_112 | 110 | 0.0013011 | 0.00032608 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_161-21_0_6_load_74 | 111 | 0.0019949 | 0.00049996 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_161-21_0_6_load_135 | 113 | 0.012786 | 0.0032045 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_161-21_0_6_load_147 | 115 | 0.0086 | 0.0021554 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_161-21_0_6_load_111 | 117 | 0.001539 | 0.00038572 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_161-21_0_6_load_79 | 118 | 0.00381 | 0.00095488 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_161-21_0_6_load_126 | 119 | 0.0085103 | 0.0021329 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_161-21_0_6_load_125 | 120 | 0.0083157 | 0.0020841 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_161-21_0_6_load_80 | 121 | 0.0029173 | 0.00073115 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_161-21_0_6_load_81 | 122 | 0.0012908 | 0.0003235 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_161-21_0_6_load_104 | 124 | 0.0045678 | 0.0011448 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_161-21_0_6_load_96 | 125 | 0.0044815 | 0.0011232 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_161-21_0_6_load_95 | 126 | 0.0014451 | 0.00036217 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_161-21_0_6_load_83 | 127 | 0.005278 | 0.0013228 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_161-21_0_6_load_120 | 128 | 0.0060769 | 0.001523 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_161-21_0_6_load_92 | 129 | 0.0028005 | 0.00070187 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_161-21_0_6_load_94 | 130 | 0.0012797 | 0.00032072 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_161-21_0_6_load_156 | 132 | 0.0027884 | 0.00069885 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_161-21_0_6_load_158 | 133 | 0.0041321 | 0.0010356 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_161-21_0_6_load_133 | 134 | 0.0027668 | 0.00069343 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_161-21_0_6_load_153 | 135 | 0.0039867 | 0.00099916 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_161-21_0_6_load_131 | 136 | 0.0017123 | 0.00042914 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_161-21_0_6_load_137 | 137 | 0.0064096 | 0.0016064 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_161-21_0_6_load_138 | 138 | 0.0028851 | 0.00072307 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_161-21_0_6_load_124 | 139 | 0.003688 | 0.00092429 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_161-21_0_6_load_105 | 140 | 0.0016253 | 0.00040734 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_161-21_0_6_load_107 | 141 | 0.0018046 | 0.00045226 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_161-21_0_6_load_109 | 142 | 0.0029073 | 0.00072863 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_161-21_0_6_load_110 | 143 | 0.0015909 | 0.00039872 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_161-21_0_6_load_134 | 144 | 0.013645 | 0.0034198 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_161-21_0_6_load_142 | 145 | 0.0078652 | 0.0019712 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_161-21_0_6_load_128 | 146 | 0.013314 | 0.0033367 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_161-21_0_6_load_127 | 147 | 0.0083607 | 0.0020954 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_161-21_0_6_load_144 | 148 | 0.0022972 | 0.00057572 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_161-21_0_6_load_129 | 149 | 0.0014822 | 0.00037148 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_161-21_0_6_load_130 | 150 | 0.0016549 | 0.00041475 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_161-21_0_6_load_149 | 151 | 0.0013359 | 0.00033481 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_161-21_0_6_load_150 | 152 | 0.00096197 | 0.00024109 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_161-21_0_6_load_151 | 153 | 0.0013598 | 0.00034079 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_161-21_0_6_load_152 | 154 | 0.0014733 | 0.00036924 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-21_0_6_line_0 |  | 0 | 1 | 0.023621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-21_0_6_line_1 |  | 1 | 2 | 0.009285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-21_0_6_line_2 |  | 1 | 3 | 0.028588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_161-21_0_6_line_3 |  | 2 | 4 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-21_0_6_line_4 |  | 3 | 5 | 0.01635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_161-21_0_6_line_5 |  | 4 | 6 | 0.034188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_161-21_0_6_line_6 |  | 5 | 7 | 0.041008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-21_0_6_line_7 |  | 6 | 114 | 0.020669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_161-21_0_6_line_8 |  | 7 | 12 | 0.030922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_161-21_0_6_line_9 |  | 8 | 9 | 0.045809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-21_0_6_line_10 |  | 9 | 18 | 0.025807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-21_0_6_line_11 |  | 10 | 11 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_161-21_0_6_line_12 |  | 10 | 12 | 0.033628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_161-21_0_6_line_13 |  | 11 | 13 | 0.0078975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-21_0_6_line_14 |  | 12 | 14 | 0.019918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-21_0_6_line_15 |  | 13 | 15 | 0.022821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-21_0_6_line_16 |  | 13 | 16 | 0.033364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_161-21_0_6_line_17 |  | 14 | 17 | 0.025535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_161-21_0_6_line_18 |  | 14 | 18 | 0.017956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-21_0_6_line_19 |  | 15 | 55 | 0.015881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-21_0_6_line_20 |  | 16 | 50 | 0.019856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-21_0_6_line_21 |  | 17 | 86 | 0.016816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-21_0_6_line_22 |  | 18 | 85 | 0.010702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-21_0_6_line_23 |  | 19 | 20 | 0.003817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_161-21_0_6_line_24 |  | 19 | 21 | 0.025798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_161-21_0_6_line_25 |  | 20 | 22 | 0.031255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_161-21_0_6_line_26 |  | 21 | 23 | 0.0002718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_161-21_0_6_line_27 |  | 22 | 24 | 0.0011169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_161-21_0_6_line_28 |  | 22 | 25 | 0.011681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_161-21_0_6_line_29 |  | 23 | 26 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_161-21_0_6_line_30 |  | 24 | 27 | 0.033431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_161-21_0_6_line_31 |  | 25 | 28 | 0.014644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_161-21_0_6_line_32 |  | 26 | 29 | 0.020118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_161-21_0_6_line_33 |  | 27 | 45 | 0.014251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-21_0_6_line_34 |  | 28 | 112 | 0.021148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_161-21_0_6_line_35 |  | 29 | 61 | 0.044533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_161-21_0_6_line_36 |  | 29 | 62 | 0.02608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_161-21_0_6_line_37 |  | 29 | 63 | 0.020781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_161-21_0_6_line_38 |  | 30 | 31 | 0.0045922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_161-21_0_6_line_39 |  | 31 | 32 | 0.037641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-21_0_6_line_40 |  | 32 | 33 | 0.019436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_161-21_0_6_line_41 |  | 33 | 34 | 0.00045013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_161-21_0_6_line_42 |  | 33 | 35 | 0.025718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_161-21_0_6_line_43 |  | 35 | 85 | 0.0056102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_161-21_0_6_line_44 |  | 36 | 37 | 0.0031924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_161-21_0_6_line_45 |  | 36 | 38 | 0.015732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_161-21_0_6_line_46 |  | 37 | 39 | 0.02207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_161-21_0_6_line_47 |  | 38 | 40 | 0.011223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-21_0_6_line_48 |  | 38 | 41 | 0.0027731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-21_0_6_line_49 |  | 39 | 42 | 0.0035606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-21_0_6_line_50 |  | 40 | 43 | 0.030267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-21_0_6_line_51 |  | 41 | 44 | 0.027773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-21_0_6_line_52 |  | 42 | 45 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-21_0_6_line_53 |  | 43 | 46 | 0.01168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-21_0_6_line_54 |  | 44 | 47 | 0.0013443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_161-21_0_6_line_55 |  | 45 | 87 | 0.030698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_161-21_0_6_line_56 |  | 46 | 83 | 0.017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_161-21_0_6_line_57 |  | 47 | 129 | 0.02004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-21_0_6_line_58 |  | 48 | 49 | 0.0049031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_161-21_0_6_line_59 |  | 49 | 51 | 0.028897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-21_0_6_line_60 |  | 50 | 54 | 0.0048363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-21_0_6_line_61 |  | 51 | 55 | 0.014506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-21_0_6_line_62 |  | 51 | 56 | 0.022835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-21_0_6_line_63 |  | 52 | 53 | 0.011007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-21_0_6_line_64 |  | 53 | 57 | 0.019449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_161-21_0_6_line_65 |  | 53 | 58 | 0.022836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_161-21_0_6_line_66 |  | 54 | 59 | 0.027146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_161-21_0_6_line_67 |  | 56 | 60 | 0.032413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-21_0_6_line_68 |  | 57 | 89 | 0.00019878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-21_0_6_line_69 |  | 58 | 90 | 0.035881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-21_0_6_line_70 |  | 61 | 64 | 0.012784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_161-21_0_6_line_71 |  | 62 | 65 | 0.02477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_161-21_0_6_line_72 |  | 63 | 66 | 0.0029344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-21_0_6_line_73 |  | 64 | 139 | 0.017695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-21_0_6_line_74 |  | 64 | 124 | 0.027996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-21_0_6_line_75 |  | 65 | 108 | 0.008607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_161-21_0_6_line_76 |  | 65 | 107 | 0.012721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_161-21_0_6_line_77 |  | 66 | 77 | 0.02991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_161-21_0_6_line_78 |  | 67 | 68 | 0.032971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_161-21_0_6_line_79 |  | 68 | 69 | 0.012312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_161-21_0_6_line_80 |  | 69 | 70 | 0.039583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_161-21_0_6_line_81 |  | 70 | 71 | 0.020156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_161-21_0_6_line_82 |  | 70 | 72 | 0.005486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_161-21_0_6_line_83 |  | 71 | 128 | 0.028715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_161-21_0_6_line_84 |  | 72 | 105 | 0.028779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_161-21_0_6_line_85 |  | 72 | 91 | 0.036276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_161-21_0_6_line_86 |  | 73 | 74 | 0.0011876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_161-21_0_6_line_87 |  | 74 | 140 | 0.010017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_161-21_0_6_line_88 |  | 75 | 76 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_161-21_0_6_line_89 |  | 75 | 77 | 0.0028489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_161-21_0_6_line_90 |  | 76 | 78 | 0.018567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_161-21_0_6_line_91 |  | 78 | 79 | 0.010727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_161-21_0_6_line_92 |  | 80 | 81 | 0.031424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_161-21_0_6_line_93 |  | 81 | 82 | 0.025204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_161-21_0_6_line_94 |  | 82 | 103 | 0.045692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_161-21_0_6_line_95 |  | 83 | 84 | 0.01789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_161-21_0_6_line_96 |  | 84 | 137 | 0.0082344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_161-21_0_6_line_97 |  | 84 | 138 | 0.019372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_161-21_0_6_line_98 |  | 87 | 88 | 0.023721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_161-21_0_6_line_99 |  | 88 | 106 | 0.022359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_161-21_0_6_line_100 |  | 90 | 91 | 0.002962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_161-21_0_6_line_101 |  | 92 | 93 | 0.036184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_161-21_0_6_line_102 |  | 92 | 94 | 0.02127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_161-21_0_6_line_103 |  | 94 | 95 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_161-21_0_6_line_104 |  | 94 | 96 | 0.031906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_161-21_0_6_line_105 |  | 95 | 97 | 0.018825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_161-21_0_6_line_106 |  | 95 | 98 | 0.015683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_161-21_0_6_line_107 |  | 96 | 99 | 0.033524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_161-21_0_6_line_108 |  | 97 | 101 | 0.017204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_161-21_0_6_line_109 |  | 98 | 102 | 0.023443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_161-21_0_6_line_110 |  | 99 | 100 | 0.011135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_161-21_0_6_line_111 |  | 100 | 154 | 0.025192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_161-21_0_6_line_112 |  | 101 | 127 | 0.037417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_161-21_0_6_line_113 |  | 102 | 150 | 0.011951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_161-21_0_6_line_114 |  | 103 | 104 | 0.014208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_161-21_0_6_line_115 |  | 104 | 105 | 0.012201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_161-21_0_6_line_116 |  | 108 | 109 | 0.023031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_161-21_0_6_line_117 |  | 108 | 110 | 0.018444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_161-21_0_6_line_118 |  | 109 | 115 | 0.027722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_161-21_0_6_line_119 |  | 109 | 116 | 0.039072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_161-21_0_6_line_120 |  | 110 | 117 | 0.0088537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_161-21_0_6_line_121 |  | 111 | 112 | 0.009171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_161-21_0_6_line_122 |  | 112 | 113 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_161-21_0_6_line_123 |  | 113 | 114 | 0.020315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_161-21_0_6_line_124 |  | 114 | 144 | 0.026719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_161-21_0_6_line_125 |  | 115 | 145 | 0.0026818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_161-21_0_6_line_126 |  | 116 | 146 | 0.018919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_161-21_0_6_line_127 |  | 116 | 128 | 0.0085955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
128 | LV_161-21_0_6_line_128 |  | 117 | 143 | 0.022727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_161-21_0_6_line_129 |  | 118 | 119 | 0.0153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_161-21_0_6_line_130 |  | 119 | 120 | 0.0082068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_161-21_0_6_line_131 |  | 120 | 147 | 0.022591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_161-21_0_6_line_132 |  | 121 | 122 | 0.015842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_161-21_0_6_line_133 |  | 122 | 123 | 0.016146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_161-21_0_6_line_134 |  | 123 | 124 | 0.0067975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_161-21_0_6_line_135 |  | 123 | 125 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_161-21_0_6_line_136 |  | 125 | 126 | 0.023611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_161-21_0_6_line_137 |  | 129 | 130 | 0.0075472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_161-21_0_6_line_138 |  | 130 | 134 | 0.0025282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_161-21_0_6_line_139 |  | 131 | 132 | 0.011495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_161-21_0_6_line_140 |  | 131 | 133 | 0.017937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_161-21_0_6_line_141 |  | 132 | 135 | 0.011223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_161-21_0_6_line_142 |  | 134 | 136 | 0.022936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_161-21_0_6_line_143 |  | 135 | 153 | 0.016777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_161-21_0_6_line_144 |  | 136 | 149 | 0.00056932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_161-21_0_6_line_145 |  | 139 | 148 | 0.025689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_161-21_0_6_line_146 |  | 140 | 141 | 0.019456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_161-21_0_6_line_147 |  | 141 | 142 | 0.0035186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_161-21_0_6_line_148 |  | 142 | 143 | 0.0060112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_161-21_0_6_line_149 |  | 146 | 147 | 0.024305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_161-21_0_6_line_150 |  | 149 | 150 | 0.0091234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_161-21_0_6_line_151 |  | 151 | 152 | 0.022174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_161-21_0_6_line_152 |  | 151 | 153 | 0.020489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_161-21_0_6_line_153 |  | 152 | 154 | 0.0057507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-21_0_6_trafo_114 | 0.63 MVA 20/0.4 kV | 155 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2685929.8147 | 1244623.5112 | 2685920.2496 | 1244645.1091
1 | 2685929.8147 | 1244623.5112 | 2685933.4602 | 1244614.9688
2 | 2685929.8147 | 1244623.5112 | 2685955.483 | 1244632.6342 | 2685955.0101 | 1244633.9727
3 | 2685933.4602 | 1244614.9688 | 2685943.2826 | 1244618.7583 | 2685949.6294 | 1244620.1016
4 | 2685955.0101 | 1244633.9727 | 2685951.0338 | 1244645.5236 | 2685949.3578 | 1244649.3022
5 | 2685949.6294 | 1244620.1016 | 2685951.1784 | 1244620.4295 | 2685958.1242 | 1244625.6006 | 2685962.4504 | 1244625.8857 | 2685964.2583 | 1244624.7221 | 2685972.3764 | 1244626.6968 | 2685973.9037 | 1244624.5618 | 2685976.0439 | 1244618.4452
6 | 2685935.2818 | 1244686.0095 | 2685940.7732 | 1244673.0063 | 2685939.9614 | 1244672.7054 | 2685944.9805 | 1244661.1585 | 2685944.2369 | 1244660.8475 | 2685949.3578 | 1244649.3022
7 | 2685980.3024 | 1244600.2255 | 2685978.8032 | 1244600.9487 | 2685976.7577 | 1244602.8538 | 2685975.7279 | 1244606.6417 | 2685977.5619 | 1244614.1071 | 2685976.0439 | 1244618.4452
8 | 2685925.5293 | 1244715.3166 | 2685931.6083 | 1244697.3804 | 2685933.2683 | 1244690.7773 | 2685935.2818 | 1244686.0095
9 | 2685969.5184 | 1244700.4093 | 2685975.6412 | 1244679.8498 | 2685980.5172 | 1244655.9853
10 | 2685962.1524 | 1244725.1432 | 2685969.5184 | 1244700.4093
11 | 2685897.2663 | 1244697.005 | 2685883.5903 | 1244688.4897 | 2685878.2904 | 1244685.8871
12 | 2685925.5293 | 1244715.3166 | 2685921.9588 | 1244713.4747 | 2685897.2663 | 1244697.005
13 | 2685871.2015 | 1244682.4059 | 2685878.2904 | 1244685.8871
14 | 2685944.5136 | 1244721.5184 | 2685925.5293 | 1244715.3166
15 | 2685871.2015 | 1244682.4059 | 2685860.9123 | 1244702.7759
16 | 2685839.7517 | 1244671.2204 | 2685863.7577 | 1244678.751 | 2685871.2015 | 1244682.4059
17 | 2685944.5136 | 1244721.5184 | 2685949.7122 | 1244739.2956 | 2685946.8889 | 1244745.7152
18 | 2685944.5136 | 1244721.5184 | 2685962.1524 | 1244725.1432
19 | 2685860.9123 | 1244702.7759 | 2685858.0373 | 1244708.4679 | 2685855.303 | 1244717.5699
20 | 2685839.7517 | 1244671.2204 | 2685820.4581 | 1244666.5299
21 | 2685941.2217 | 1244761.5276 | 2685944.7655 | 1244750.5434 | 2685946.8889 | 1244745.7152
22 | 2685972.8298 | 1244726.2432 | 2685962.1524 | 1244725.1432
23 | 2686035.7983 | 1244585.5629 | 2686036.0217 | 1244589.3734
24 | 2686035.7983 | 1244585.5629 | 2686034.2886 | 1244559.8087
25 | 2686037.8508 | 1244620.5747 | 2686036.0217 | 1244589.3734
26 | 2686034.2727 | 1244559.5374 | 2686034.2886 | 1244559.8087
27 | 2686037.8508 | 1244620.5747 | 2686037.9743 | 1244621.6848
28 | 2686037.8508 | 1244620.5747 | 2686030.5751 | 1244619.9131 | 2686027.0302 | 1244617.3487
29 | 2686032.9624 | 1244537.1861 | 2686034.2727 | 1244559.5374
30 | 2686037.9743 | 1244621.6848 | 2686041.4474 | 1244652.9062 | 2686041.8664 | 1244654.8789
31 | 2686021.6094 | 1244603.7449 | 2686027.0302 | 1244617.3487
32 | 2686031.8327 | 1244517.1002 | 2686032.1261 | 1244522.9199 | 2686032.9624 | 1244537.1861
33 | 2686044.9956 | 1244668.7804 | 2686043.5059 | 1244662.5987 | 2686041.8664 | 1244654.8789
34 | 2686013.781 | 1244584.0989 | 2686021.6094 | 1244603.7449
35 | 2686031.8327 | 1244517.1002 | 2686028.3373 | 1244472.7047
36 | 2686031.8327 | 1244517.1002 | 2686005.767 | 1244516.2488
37 | 2686031.8327 | 1244517.1002 | 2686052.494 | 1244514.8694
38 | 2685988.6003 | 1244786.54 | 2685990.361 | 1244782.2987
39 | 2686001.8019 | 1244746.7492 | 2686000.4438 | 1244758.0112 | 2685990.361 | 1244782.2987
40 | 2686004.129 | 1244727.4532 | 2686001.8019 | 1244746.7492
41 | 2686004.129 | 1244727.4532 | 2686004.579 | 1244727.4655
42 | 2686004.129 | 1244727.4532 | 2685992.9243 | 1244726.757 | 2685983.6088 | 1244726.5885 | 2685978.4371 | 1244726.4228
43 | 2685972.8298 | 1244726.2432 | 2685978.4371 | 1244726.4228
44 | 2686091.3459 | 1244668.4405 | 2686088.1536 | 1244668.4639
45 | 2686107.0772 | 1244668.3251 | 2686091.3459 | 1244668.4405
46 | 2686066.084 | 1244668.6258 | 2686088.1536 | 1244668.4639
47 | 2686107.0772 | 1244668.3251 | 2686109.3816 | 1244657.3414
48 | 2686107.0772 | 1244668.3251 | 2686106.8317 | 1244671.0874
49 | 2686066.084 | 1244668.6258 | 2686062.5235 | 1244668.6519
50 | 2686109.3816 | 1244657.3414 | 2686113.0449 | 1244639.8797 | 2686117.0122 | 1244628.1052
51 | 2686104.3725 | 1244698.7517 | 2686106.8317 | 1244671.0874
52 | 2686044.9956 | 1244668.7804 | 2686062.5235 | 1244668.6519
53 | 2686120.7417 | 1244617.0365 | 2686117.0122 | 1244628.1052
54 | 2686104.3725 | 1244698.7517 | 2686104.2535 | 1244700.0907
55 | 2686044.9956 | 1244668.7804 | 2686054.4192 | 1244697.9961
56 | 2686120.7417 | 1244617.0365 | 2686126.3507 | 1244600.3895
57 | 2686104.2535 | 1244700.0907 | 2686103.2924 | 1244710.9015 | 2686103.1804 | 1244720.0878
58 | 2685823.6409 | 1244722.3026 | 2685825.3443 | 1244717.7049
59 | 2685823.6409 | 1244722.3026 | 2685851.1296 | 1244731.4626
60 | 2685815.7586 | 1244665.3874 | 2685820.4581 | 1244666.5299
61 | 2685851.1296 | 1244731.4626 | 2685855.303 | 1244717.5699
62 | 2685851.1296 | 1244731.4626 | 2685861.6989 | 1244744.7253 | 2685866.9741 | 1244747.3125
63 | 2685852.0295 | 1244610.3422 | 2685849.8534 | 1244621.1319
64 | 2685852.0295 | 1244610.3422 | 2685871.3636 | 1244612.4507
65 | 2685852.0295 | 1244610.3422 | 2685853.8119 | 1244596.3243 | 2685854.5466 | 1244587.6498
66 | 2685789.3812 | 1244658.9747 | 2685815.7586 | 1244665.3874
67 | 2685866.9741 | 1244747.3125 | 2685896.0757 | 1244761.5854
68 | 2685871.3636 | 1244612.4507 | 2685871.5612 | 1244612.4723
69 | 2685854.5466 | 1244587.6498 | 2685857.5746 | 1244551.8972
70 | 2686027.3338 | 1244459.9597 | 2686028.3373 | 1244472.7047
71 | 2685981.0105 | 1244515.4401 | 2686005.767 | 1244516.2488
72 | 2686055.4115 | 1244514.5544 | 2686052.494 | 1244514.8694
73 | 2686027.3338 | 1244459.9597 | 2686026.8945 | 1244449.0898 | 2686026.7169 | 1244444.6617 | 2686026.6453 | 1244442.2778
74 | 2686027.3338 | 1244459.9597 | 2686055.1782 | 1244457.0534
75 | 2685977.1012 | 1244507.7667 | 2685981.0105 | 1244515.4401
76 | 2685981.0105 | 1244515.4401 | 2685986.5035 | 1244526.9142
77 | 2686055.4115 | 1244514.5544 | 2686073.5924 | 1244512.5915 | 2686085.0176 | 1244514.7314
78 | 2685871.6983 | 1244456.572 | 2685872.2657 | 1244454.4761 | 2685883.3366 | 1244425.735
79 | 2685871.6983 | 1244456.572 | 2685868.481 | 1244468.4563
80 | 2685861.6071 | 1244507.3607 | 2685865.1354 | 1244480.8144 | 2685868.481 | 1244468.4563
81 | 2685861.6071 | 1244507.3607 | 2685881.6844 | 1244509.1413
82 | 2685861.6071 | 1244507.3607 | 2685860.886 | 1244512.7987
83 | 2685910.287 | 1244511.6781 | 2685881.6844 | 1244509.1413
84 | 2685860.886 | 1244512.7987 | 2685832.2889 | 1244509.5704
85 | 2685860.886 | 1244512.7987 | 2685857.8246 | 1244548.9458
86 | 2685942.1352 | 1244426.1602 | 2685941.7852 | 1244425.0253
87 | 2685945.0871 | 1244435.7325 | 2685942.1352 | 1244426.1602
88 | 2686098.5622 | 1244517.2683 | 2686087.8177 | 1244515.2559
89 | 2686085.0176 | 1244514.7314 | 2686087.8177 | 1244515.2559
90 | 2686098.5622 | 1244517.2683 | 2686098.5622 | 1244517.2683 | 2686101.1524 | 1244525.7343 | 2686110.8442 | 1244526.3839
91 | 2686110.8442 | 1244526.3839 | 2686120.8505 | 1244527.0545 | 2686121.5429 | 1244527.1434
92 | 2685785.3529 | 1244575.3976 | 2685779.3342 | 1244606.2397
93 | 2685785.3529 | 1244575.3976 | 2685790.1802 | 1244550.6606
94 | 2685806.1659 | 1244509.4491 | 2685799.0207 | 1244515.9505 | 2685795.6029 | 1244522.8728 | 2685790.1802 | 1244550.6606
95 | 2686132.0628 | 1244583.4365 | 2686126.3507 | 1244600.3895
96 | 2686132.0628 | 1244583.4365 | 2686134.5648 | 1244575.5914
97 | 2686132.0628 | 1244583.4365 | 2686151.1083 | 1244586.979
98 | 2686061.701 | 1244720.5719 | 2686054.4192 | 1244697.9961
99 | 2686061.701 | 1244720.5719 | 2686068.4049 | 1244741.9025
100 | 2685857.8246 | 1244548.9458 | 2685857.5746 | 1244551.8972
101 | 2686068.4411 | 1244824.4134 | 2686032.5839 | 1244829.2661
102 | 2686089.5185 | 1244821.5609 | 2686068.4411 | 1244824.4134
103 | 2686088.837 | 1244810.2093 | 2686089.5185 | 1244821.5609
104 | 2686089.5185 | 1244821.5609 | 2686107.8123 | 1244847.7011
105 | 2686088.837 | 1244810.2093 | 2686086.8846 | 1244800.5071 | 2686084.1514 | 1244792.0057
106 | 2686088.837 | 1244810.2093 | 2686098.5079 | 1244797.8628
107 | 2686107.8123 | 1244847.7011 | 2686117.3845 | 1244841.113 | 2686127.4598 | 1244832.1415 | 2686133.268 | 1244826.0548
108 | 2686084.1514 | 1244792.0057 | 2686068.2325 | 1244798.5293
109 | 2686098.5079 | 1244797.8628 | 2686098.5079 | 1244797.8628 | 2686102.2003 | 1244774.7123
110 | 2686138.8765 | 1244816.4912 | 2686134.3356 | 1244824.936 | 2686133.268 | 1244826.0548
111 | 2686150.8074 | 1244794.3031 | 2686138.8765 | 1244816.4912
112 | 2686042.8238 | 1244779.8973 | 2686048.3466 | 1244790.4073 | 2686056.4135 | 1244801.0989 | 2686065.6247 | 1244799.598 | 2686068.2325 | 1244798.5293
113 | 2686102.2003 | 1244774.7123 | 2686102.5403 | 1244772.5804 | 2686102.6597 | 1244762.7891
114 | 2685806.1659 | 1244509.4491 | 2685815.2382 | 1244507.6456 | 2685820.1649 | 1244508.2018
115 | 2685820.1649 | 1244508.2018 | 2685832.2889 | 1244509.5704
116 | 2685977.1012 | 1244507.7667 | 2685965.0979 | 1244513.6527 | 2685956.9351 | 1244518.9161
117 | 2685977.1012 | 1244507.7667 | 2685968.9621 | 1244491.2158
118 | 2685956.9351 | 1244518.9161 | 2685953.4514 | 1244523.5913 | 2685948.8464 | 1244532.6312 | 2685946.6894 | 1244544.1778
119 | 2685956.9351 | 1244518.9161 | 2685937.5403 | 1244512.3081 | 2685918.849 | 1244512.4375
120 | 2685968.9621 | 1244491.2158 | 2685965.0551 | 1244483.2708
121 | 2686013.781 | 1244584.0989 | 2686009.8591 | 1244575.8088
122 | 2686013.781 | 1244584.0989 | 2685998.6044 | 1244591.4094
123 | 2685980.3024 | 1244600.2255 | 2685998.6044 | 1244591.4094
124 | 2685980.3024 | 1244600.2255 | 2685979.0072 | 1244597.3046 | 2685971.4213 | 1244594.5815 | 2685964.0404 | 1244593.3626 | 2685958.0714 | 1244588.0611
125 | 2685946.1969 | 1244546.814 | 2685946.6894 | 1244544.1778
126 | 2685918.849 | 1244512.4375 | 2685914.968 | 1244530.9541
127 | 2685918.849 | 1244512.4375 | 2685910.287 | 1244511.6781
128 | 2685955.0258 | 1244462.8762 | 2685965.0551 | 1244483.2708
129 | 2685903.6644 | 1244584.885 | 2685900.5259 | 1244599.8594
130 | 2685905.348 | 1244576.8527 | 2685903.6644 | 1244584.885
131 | 2685905.348 | 1244576.8527 | 2685909.9822 | 1244554.7419
132 | 2686093.09 | 1244463.6189 | 2686077.6625 | 1244460.0179
133 | 2686061.9391 | 1244456.3478 | 2686077.6625 | 1244460.0179
134 | 2686061.9391 | 1244456.3478 | 2686055.1782 | 1244457.0534
135 | 2686061.9391 | 1244456.3478 | 2686065.1526 | 1244443.7797
136 | 2686070.8132 | 1244420.8579 | 2686067.9724 | 1244432.7513 | 2686065.1526 | 1244443.7797
137 | 2686103.0884 | 1244727.6345 | 2686103.1804 | 1244720.0878
138 | 2686103.0884 | 1244727.6345 | 2686103.0576 | 1244730.1626
139 | 2686181.0822 | 1244712.1986 | 2686176.3957 | 1244722.6946
140 | 2686181.0822 | 1244712.1986 | 2686189.5495 | 1244696.3861
141 | 2686171.8199 | 1244732.9429 | 2686176.3957 | 1244722.6946
142 | 2686102.7779 | 1244753.0971 | 2686103.0576 | 1244730.1626
143 | 2686164.9797 | 1244748.2625 | 2686171.8199 | 1244732.9429
144 | 2686102.7779 | 1244753.0971 | 2686102.7709 | 1244753.6663
145 | 2686025.874 | 1244416.6008 | 2686026.6453 | 1244442.2778
146 | 2685945.0871 | 1244435.7325 | 2685950.8204 | 1244454.3245 | 2685950.8204 | 1244454.3245
147 | 2685952.3731 | 1244457.482 | 2685950.8204 | 1244454.3245
148 | 2685955.0258 | 1244462.8762 | 2685952.3731 | 1244457.482
149 | 2685914.968 | 1244530.9541 | 2685909.9822 | 1244554.7419
150 | 2686102.7709 | 1244753.6663 | 2686102.6597 | 1244762.7891
151 | 2686158.4796 | 1244767.5988 | 2686153.362 | 1244789.174
152 | 2686158.4796 | 1244767.5988 | 2686160.8975 | 1244757.4053 | 2686164.9797 | 1244748.2625
153 | 2686150.8074 | 1244794.3031 | 2686153.2014 | 1244789.8508 | 2686153.362 | 1244789.174

## bus_geodata
| x | y | coords
0 | 2685920.2496 | 1244645.1091
1 | 2685929.8147 | 1244623.5112
2 | 2685933.4602 | 1244614.9688
3 | 2685955.0101 | 1244633.9727
4 | 2685949.6294 | 1244620.1016
5 | 2685949.3578 | 1244649.3022
6 | 2685976.0439 | 1244618.4452
7 | 2685935.2818 | 1244686.0095
8 | 2685980.5172 | 1244655.9853
9 | 2685969.5184 | 1244700.4093
10 | 2685897.2663 | 1244697.005
11 | 2685878.2904 | 1244685.8871
12 | 2685925.5293 | 1244715.3166
13 | 2685871.2015 | 1244682.4059
14 | 2685944.5136 | 1244721.5184
15 | 2685860.9123 | 1244702.7759
16 | 2685839.7517 | 1244671.2204
17 | 2685946.8889 | 1244745.7152
18 | 2685962.1524 | 1244725.1432
19 | 2686035.7983 | 1244585.5629
20 | 2686036.0217 | 1244589.3734
21 | 2686034.2886 | 1244559.8087
22 | 2686037.8508 | 1244620.5747
23 | 2686034.2727 | 1244559.5374
24 | 2686037.9743 | 1244621.6848
25 | 2686027.0302 | 1244617.3487
26 | 2686032.9624 | 1244537.1862
27 | 2686041.8664 | 1244654.8789
28 | 2686021.6094 | 1244603.7449
29 | 2686031.8327 | 1244517.1002
30 | 2685988.6003 | 1244786.54
31 | 2685990.361 | 1244782.2987
32 | 2686001.8019 | 1244746.7492
33 | 2686004.129 | 1244727.4532
34 | 2686004.579 | 1244727.4655
35 | 2685978.4371 | 1244726.4228
36 | 2686091.3459 | 1244668.4405
37 | 2686088.1536 | 1244668.4639
38 | 2686107.0772 | 1244668.3251
39 | 2686066.084 | 1244668.6258
40 | 2686109.3816 | 1244657.3414
41 | 2686106.8317 | 1244671.0874
42 | 2686062.5235 | 1244668.6519
43 | 2686117.0122 | 1244628.1052
44 | 2686104.3725 | 1244698.7517
45 | 2686044.9956 | 1244668.7804
46 | 2686120.7417 | 1244617.0365
47 | 2686104.2535 | 1244700.0907
48 | 2685825.3443 | 1244717.705
49 | 2685823.6409 | 1244722.3026
50 | 2685820.4581 | 1244666.5299
51 | 2685851.1296 | 1244731.4626
52 | 2685849.8534 | 1244621.1319
53 | 2685852.0295 | 1244610.3422
54 | 2685815.7586 | 1244665.3874
55 | 2685855.303 | 1244717.5699
56 | 2685866.9741 | 1244747.3125
57 | 2685871.3636 | 1244612.4507
58 | 2685854.5466 | 1244587.6498
59 | 2685789.3812 | 1244658.9747
60 | 2685896.0757 | 1244761.5854
61 | 2686028.3373 | 1244472.7047
62 | 2686005.767 | 1244516.2488
63 | 2686052.494 | 1244514.8694
64 | 2686027.3338 | 1244459.9597
65 | 2685981.0105 | 1244515.4401
66 | 2686055.4115 | 1244514.5544
67 | 2685883.3366 | 1244425.735
68 | 2685871.6983 | 1244456.572
69 | 2685868.481 | 1244468.4563
70 | 2685861.6071 | 1244507.3607
71 | 2685881.6844 | 1244509.1413
72 | 2685860.886 | 1244512.7987
73 | 2685941.7852 | 1244425.0253
74 | 2685942.1352 | 1244426.1602
75 | 2686087.8177 | 1244515.2559
76 | 2686098.5622 | 1244517.2683
77 | 2686085.0176 | 1244514.7314
78 | 2686110.8442 | 1244526.3839
79 | 2686121.5429 | 1244527.1434
80 | 2685779.3342 | 1244606.2397
81 | 2685785.3529 | 1244575.3976
82 | 2685790.1802 | 1244550.6606
83 | 2686126.3507 | 1244600.3895
84 | 2686132.0628 | 1244583.4365
85 | 2685972.8298 | 1244726.2432
86 | 2685941.2217 | 1244761.5276
87 | 2686054.4192 | 1244697.9961
88 | 2686061.701 | 1244720.5719
89 | 2685871.5612 | 1244612.4723
90 | 2685857.5746 | 1244551.8972
91 | 2685857.8245 | 1244548.9458
92 | 2686068.4411 | 1244824.4134
93 | 2686032.5839 | 1244829.2661
94 | 2686089.5185 | 1244821.5609
95 | 2686088.837 | 1244810.2093
96 | 2686107.8123 | 1244847.7011
97 | 2686084.1514 | 1244792.0057
98 | 2686098.5079 | 1244797.8628
99 | 2686133.268 | 1244826.0548
100 | 2686138.8765 | 1244816.4912
101 | 2686068.2325 | 1244798.5293
102 | 2686102.2003 | 1244774.7123
103 | 2685806.1659 | 1244509.4491
104 | 2685820.1649 | 1244508.2018
105 | 2685832.2889 | 1244509.5704
106 | 2686068.4049 | 1244741.9025
107 | 2685986.5035 | 1244526.9142
108 | 2685977.1013 | 1244507.7667
109 | 2685956.9351 | 1244518.9161
110 | 2685968.9621 | 1244491.2158
111 | 2686009.8591 | 1244575.8088
112 | 2686013.781 | 1244584.0989
113 | 2685998.6044 | 1244591.4094
114 | 2685980.3024 | 1244600.2255
115 | 2685946.6894 | 1244544.1778
116 | 2685918.849 | 1244512.4375
117 | 2685965.0551 | 1244483.2708
118 | 2685900.5259 | 1244599.8594
119 | 2685903.6644 | 1244584.885
120 | 2685905.348 | 1244576.8527
121 | 2686093.09 | 1244463.6189
122 | 2686077.6625 | 1244460.0179
123 | 2686061.9391 | 1244456.3478
124 | 2686055.1783 | 1244457.0534
125 | 2686065.1526 | 1244443.7797
126 | 2686070.8132 | 1244420.8579
127 | 2686042.8238 | 1244779.8973
128 | 2685910.287 | 1244511.6781
129 | 2686103.1804 | 1244720.0878
130 | 2686103.0884 | 1244727.6345
131 | 2686181.0822 | 1244712.1986
132 | 2686176.3957 | 1244722.6946
133 | 2686189.5495 | 1244696.3861
134 | 2686103.0576 | 1244730.1626
135 | 2686171.8199 | 1244732.9429
136 | 2686102.7779 | 1244753.0971
137 | 2686134.5648 | 1244575.5914
138 | 2686151.1083 | 1244586.979
139 | 2686026.6453 | 1244442.2778
140 | 2685945.0871 | 1244435.7325
141 | 2685950.8204 | 1244454.3245
142 | 2685952.3731 | 1244457.482
143 | 2685955.0258 | 1244462.8762
144 | 2685958.0714 | 1244588.0611
145 | 2685946.1969 | 1244546.814
146 | 2685914.968 | 1244530.9541
147 | 2685909.9822 | 1244554.7419
148 | 2686025.874 | 1244416.6008
149 | 2686102.7709 | 1244753.6663
150 | 2686102.6597 | 1244762.7891
151 | 2686158.4796 | 1244767.5988
152 | 2686153.362 | 1244789.174
153 | 2686164.9797 | 1244748.2625
154 | 2686150.8074 | 1244794.3031
155 | 2685980.3024 | 1244600.2255

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99428 | -0.10821 | 0.0069776 | 0.0017488
1 | 0.99443 | -0.10531 | 0 | 0
2 | 0.99561 | -0.082936 | 0 | 0
3 | 0.99099 | -0.17097 | 0 | 0
4 | 0.99777 | -0.042079 | 0.004064 | 0.0010185
5 | 0.98902 | -0.20873 | 0.0082478 | 0.0020671
6 | 1 | 0 | -0.5795 | -0.14899
7 | 0.9844 | -0.29802 | 0.008673 | 0.0021737
8 | 0.97832 | -0.41664 | 0.007829 | 0.0019621
9 | 0.97865 | -0.41011 | 0.0076109 | 0.0019075
10 | 0.97969 | -0.38966 | 0 | 0
11 | 0.97874 | -0.40843 | 0.0072473 | 0.0018163
12 | 0.98116 | -0.36105 | 0 | 0
13 | 0.97845 | -0.41414 | 0 | 0
14 | 0.97994 | -0.38489 | 0 | 0
15 | 0.97791 | -0.42463 | 0.004448 | 0.0011148
16 | 0.978 | -0.4229 | 0 | 0
17 | 0.97968 | -0.38996 | 0.0049682 | 0.0012451
18 | 0.97902 | -0.40286 | 0 | 0
19 | 0.98793 | -0.22938 | 0.0040551 | 0.0010163
20 | 0.98817 | -0.22492 | 0.0039711 | 0.00099525
21 | 0.98639 | -0.25912 | 0.0019933 | 0.00049958
22 | 0.99009 | -0.18791 | 0 | 0
23 | 0.98637 | -0.25943 | 0.0029599 | 0.00074181
24 | 0.98996 | -0.19041 | 0.008195 | 0.0020539
25 | 0.99116 | -0.16758 | 0.0030182 | 0.00075643
26 | 0.98506 | -0.28483 | 0.0057196 | 0.0014335
27 | 0.98631 | -0.26069 | 0.01245 | 0.0031203
28 | 0.9925 | -0.14197 | 0.0029189 | 0.00073154
29 | 0.9839 | -0.30718 | 0 | 0
30 | 0.97681 | -0.44636 | 0.006312 | 0.0015819
31 | 0.97683 | -0.44583 | 0.0077216 | 0.0019352
32 | 0.97732 | -0.43618 | 0.0057854 | 0.00145
33 | 0.97768 | -0.42916 | 0 | 0
34 | 0.97768 | -0.42925 | 0.011193 | 0.0028051
35 | 0.97842 | -0.41462 | 0.0086276 | 0.0021623
36 | 0.98098 | -0.36406 | 0.0021633 | 0.00054218
37 | 0.98123 | -0.35906 | 0.0022036 | 0.00055228
38 | 0.97974 | -0.38813 | 0 | 0
39 | 0.98305 | -0.32368 | 0.0024555 | 0.0006154
40 | 0.97951 | -0.39266 | 0.0020063 | 0.00050282
41 | 0.97958 | -0.39126 | 0.0039695 | 0.00099484
42 | 0.98336 | -0.31782 | 0.0045846 | 0.001149
43 | 0.97894 | -0.40377 | 0.0033638 | 0.00084304
44 | 0.97808 | -0.42066 | 0.0030099 | 0.00075435
45 | 0.98492 | -0.28761 | 0 | 0
46 | 0.97876 | -0.40735 | 0.0030082 | 0.00075393
47 | 0.97801 | -0.42201 | 0.0030752 | 0.00077073
48 | 0.97735 | -0.43566 | 0.0010981 | 0.00027521
49 | 0.97735 | -0.43556 | 0 | 0
50 | 0.97773 | -0.42813 | 0.0074356 | 0.0018635
51 | 0.97738 | -0.43498 | 0 | 0
52 | 0.9704 | -0.57153 | 0.0059743 | 0.0014973
53 | 0.97046 | -0.57032 | 0 | 0
54 | 0.9777 | -0.42874 | 0.0054501 | 0.0013659
55 | 0.9776 | -0.43065 | 0.0044092 | 0.001105
56 | 0.97706 | -0.44135 | 0.0075411 | 0.00189
57 | 0.97021 | -0.57539 | 0.0075724 | 0.0018978
58 | 0.97089 | -0.56184 | 0.0078977 | 0.0019794
59 | 0.97766 | -0.42951 | 0.0015412 | 0.00038627
60 | 0.97683 | -0.44594 | 0.0077415 | 0.0019402
61 | 0.98285 | -0.32786 | 0.0050714 | 0.001271
62 | 0.9827 | -0.3305 | 0.0062137 | 0.0015573
63 | 0.98346 | -0.31579 | 0.0043513 | 0.0010905
64 | 0.9826 | -0.33264 | 0 | 0
65 | 0.98159 | -0.352 | 0 | 0
66 | 0.98341 | -0.31678 | 0.0033564 | 0.00084118
67 | 0.97267 | -0.52672 | 0.0068612 | 0.0017196
68 | 0.97288 | -0.52255 | 0.0084446 | 0.0021164
69 | 0.97306 | -0.51908 | 0.0075855 | 0.0019011
70 | 0.9739 | -0.50242 | 0 | 0
71 | 0.97574 | -0.46637 | 0.0058935 | 0.0014771
72 | 0.97352 | -0.50994 | 0 | 0
73 | 0.98041 | -0.37509 | 0.0021507 | 0.00053902
74 | 0.98042 | -0.37504 | 0.0016042 | 0.00040205
75 | 0.98296 | -0.32558 | 0.0046412 | 0.0011632
76 | 0.9829 | -0.32678 | 0.0013321 | 0.00033386
77 | 0.98299 | -0.32503 | 0.0045695 | 0.0011452
78 | 0.98282 | -0.32837 | 0.0014151 | 0.00035465
79 | 0.98279 | -0.32902 | 0.0033379 | 0.00083656
80 | 0.97155 | -0.54885 | 0.0012047 | 0.00030193
81 | 0.97159 | -0.54815 | 0.0063721 | 0.001597
82 | 0.97176 | -0.54463 | 0.0064022 | 0.0016046
83 | 0.97854 | -0.41177 | 0.004532 | 0.0011358
84 | 0.97838 | -0.4148 | 0 | 0
85 | 0.97863 | -0.41058 | 0 | 0
86 | 0.97959 | -0.39178 | 0.0059725 | 0.0014969
87 | 0.98465 | -0.29288 | 0.0040032 | 0.0010033
88 | 0.98453 | -0.29524 | 0 | 0
89 | 0.97021 | -0.57541 | 0.0065124 | 0.0016322
90 | 0.97183 | -0.54331 | 0.0098639 | 0.0024721
91 | 0.97193 | -0.54124 | 0.0090182 | 0.0022602
92 | 0.97293 | -0.52169 | 0.0034006 | 0.00085228
93 | 0.9728 | -0.52431 | 0.0039265 | 0.00098409
94 | 0.97308 | -0.51882 | 0 | 0
95 | 0.97336 | -0.51321 | 0 | 0
96 | 0.9725 | -0.53027 | 0 | 0
97 | 0.97317 | -0.51697 | 0 | 0
98 | 0.97391 | -0.50235 | 0.0017522 | 0.00043914
99 | 0.97189 | -0.54231 | 0.0020457 | 0.0005127
100 | 0.97171 | -0.54589 | 0.0013859 | 0.00034733
101 | 0.973 | -0.5204 | 0.0055653 | 0.0013948
102 | 0.97477 | -0.48539 | 0.00099656 | 0.00024976
103 | 0.97236 | -0.53284 | 0 | 0
104 | 0.97255 | -0.52918 | 0.0061631 | 0.0015446
105 | 0.97277 | -0.52465 | 0.0076259 | 0.0019112
106 | 0.98441 | -0.29746 | 0.0055351 | 0.0013872
107 | 0.98148 | -0.35416 | 0.0093763 | 0.0023499
108 | 0.98123 | -0.35912 | 0 | 0
109 | 0.98033 | -0.37667 | 0 | 0
110 | 0.98098 | -0.36397 | 0.0013011 | 0.00032608
111 | 0.99443 | -0.10515 | 0.0019949 | 0.00049996
112 | 0.99445 | -0.10483 | 0 | 0
113 | 0.99601 | -0.075205 | 0.012786 | 0.0032045
114 | 0.99796 | -0.038464 | 0 | 0
115 | 0.9799 | -0.38495 | 0.0086 | 0.0021554
116 | 0.97895 | -0.4036 | 0 | 0
117 | 0.98087 | -0.36609 | 0.001539 | 0.00038572
118 | 0.97697 | -0.44244 | 0.00381 | 0.00095488
119 | 0.97702 | -0.44137 | 0.0085103 | 0.0021329
120 | 0.97712 | -0.43953 | 0.0083157 | 0.0020841
121 | 0.98205 | -0.34338 | 0.0029173 | 0.00073115
122 | 0.9821 | -0.34254 | 0.0012908 | 0.0003235
123 | 0.98216 | -0.34131 | 0 | 0
124 | 0.98222 | -0.34007 | 0.0045678 | 0.0011448
125 | 0.98209 | -0.3427 | 0.0044815 | 0.0011232
126 | 0.98206 | -0.34332 | 0.0014451 | 0.00036217
127 | 0.97281 | -0.52404 | 0.005278 | 0.0013228
128 | 0.97851 | -0.41216 | 0.0060769 | 0.001523
129 | 0.97703 | -0.44106 | 0.0028005 | 0.00070187
130 | 0.97669 | -0.44785 | 0.0012797 | 0.00032072
131 | 0.97045 | -0.57082 | 0 | 0
132 | 0.97049 | -0.56995 | 0.0027884 | 0.00069885
133 | 0.97038 | -0.5722 | 0.0041321 | 0.0010356
134 | 0.97657 | -0.45007 | 0.0027668 | 0.00069343
135 | 0.97056 | -0.56851 | 0.0039867 | 0.00099916
136 | 0.97561 | -0.46906 | 0.0017123 | 0.00042914
137 | 0.97833 | -0.41576 | 0.0064096 | 0.0016064
138 | 0.97833 | -0.41582 | 0.0028851 | 0.00072307
139 | 0.9825 | -0.33455 | 0.003688 | 0.00092429
140 | 0.98045 | -0.37436 | 0.0016253 | 0.00040734
141 | 0.98055 | -0.37246 | 0.0018046 | 0.00045226
142 | 0.98057 | -0.372 | 0.0029073 | 0.00072863
143 | 0.98063 | -0.3709 | 0.0015909 | 0.00039872
144 | 0.99763 | -0.044847 | 0.013645 | 0.0034198
145 | 0.97988 | -0.38534 | 0.0078652 | 0.0019712
146 | 0.9782 | -0.41817 | 0.013314 | 0.0033367
147 | 0.97755 | -0.43102 | 0.0083607 | 0.0020954
148 | 0.98245 | -0.33561 | 0.0022972 | 0.00057572
149 | 0.97558 | -0.46951 | 0.0014822 | 0.00037148
150 | 0.97522 | -0.47654 | 0.0016549 | 0.00041475
151 | 0.97097 | -0.56047 | 0.0013359 | 0.00033481
152 | 0.97125 | -0.5549 | 0.00096197 | 0.00024109
153 | 0.97073 | -0.56512 | 0.0013598 | 0.00034079
154 | 0.97133 | -0.55335 | 0.0014733 | 0.00036924
155 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0069776 | -0.0017488 | 0.0069786 | 0.0017491 | 9.6591e-07 | 3.1178e-07 | 0.010442 | 0.010442 | 0.010442 | 0.99428 | -0.10821 | 0.99443 | -0.10531 | 2.8688
1 | -0.1387 | -0.035482 | 0.13885 | 0.035578 | 0.00015035 | 9.6107e-05 | 0.2078 | 0.2078 | 0.2078 | 0.99443 | -0.10531 | 0.99561 | -0.082936 | 57.0888
2 | 0.13172 | 0.033733 | -0.13131 | -0.033466 | 0.00041758 | 0.00026688 | 0.19736 | 0.19736 | 0.19736 | 0.99443 | -0.10531 | 0.99099 | -0.17097 | 54.2201
3 | -0.13885 | -0.035578 | 0.13913 | 0.035754 | 0.00027554 | 0.00017612 | 0.2078 | 0.2078 | 0.2078 | 0.99561 | -0.082936 | 0.99777 | -0.042079 | 57.0888
4 | 0.13131 | 0.033466 | -0.13107 | -0.033314 | 0.00023882 | 0.00015263 | 0.19736 | 0.19736 | 0.19736 | 0.99099 | -0.17097 | 0.98902 | -0.20873 | 54.2201
5 | -0.14319 | -0.036773 | 0.14349 | 0.03696 | 0.00029319 | 0.00018675 | 0.21386 | 0.21386 | 0.21386 | 0.99777 | -0.042079 | 1 | 0 | 29.3769
6 | 0.12282 | 0.031247 | -0.12229 | -0.03091 | 0.00052604 | 0.00033614 | 0.18495 | 0.18495 | 0.18495 | 0.98902 | -0.20873 | 0.9844 | -0.29802 | 50.8111
7 | 0.43436 | 0.11203 | -0.43355 | -0.11151 | 0.0008123 | 0.00051879 | 0.64747 | 0.64747 | 0.64747 | 1 | 0 | 0.99796 | -0.038464 | 44.4688
8 | 0.11362 | 0.028737 | -0.11328 | -0.028518 | 0.00034242 | 0.00021876 | 0.17184 | 0.17184 | 0.17184 | 0.9844 | -0.29802 | 0.98116 | -0.36105 | 47.2094
9 | -0.007829 | -0.0019621 | 0.0078314 | 0.0019631 | 2.4358e-06 | 9.8351e-07 | 0.011908 | 0.011908 | 0.011908 | 0.97832 | -0.41664 | 0.97865 | -0.41011 | 3.2714
10 | -0.015442 | -0.0038706 | 0.015448 | 0.0038737 | 5.3353e-06 | 3.0902e-06 | 0.02348 | 0.02348 | 0.02348 | 0.97865 | -0.41011 | 0.97902 | -0.40286 | 6.4505
11 | 0.047003 | 0.011812 | -0.046961 | -0.011786 | 4.209e-05 | 2.6661e-05 | 0.071403 | 0.071403 | 0.071403 | 0.97969 | -0.38966 | 0.97874 | -0.40843 | 19.6161
12 | -0.047003 | -0.011812 | 0.047067 | 0.011853 | 6.4292e-05 | 4.0723e-05 | 0.071403 | 0.071403 | 0.071403 | 0.97969 | -0.38966 | 0.98116 | -0.36105 | 19.6161
13 | 0.039714 | 0.0099693 | -0.039703 | -0.0099625 | 1.0799e-05 | 6.812e-06 | 0.060384 | 0.060384 | 0.060384 | 0.97874 | -0.40843 | 0.97845 | -0.41414 | 16.5891
14 | 0.066211 | 0.016665 | -0.066135 | -0.016617 | 7.5351e-05 | 4.7973e-05 | 0.10044 | 0.10044 | 0.10044 | 0.98116 | -0.36105 | 0.97994 | -0.38489 | 27.5934
15 | 0.025266 | 0.0063416 | -0.025254 | -0.0063338 | 1.2638e-05 | 7.8016e-06 | 0.038428 | 0.038428 | 0.038428 | 0.97845 | -0.41414 | 0.97791 | -0.42463 | 10.5572
16 | 0.014437 | 0.003621 | -0.014431 | -0.0036175 | 6.0316e-06 | 3.4414e-06 | 0.021956 | 0.021957 | 0.021957 | 0.97845 | -0.41414 | 0.978 | -0.4229 | 6.032
17 | 0.010944 | 0.0027435 | -0.010941 | -0.0027421 | 2.6445e-06 | 1.3709e-06 | 0.016618 | 0.016618 | 0.016618 | 0.97994 | -0.38489 | 0.97968 | -0.38996 | 4.5655
18 | 0.055191 | 0.013873 | -0.055144 | -0.013843 | 4.731e-05 | 3.0052e-05 | 0.083822 | 0.083822 | 0.083822 | 0.97994 | -0.38489 | 0.97902 | -0.40286 | 23.0279
19 | 0.020806 | 0.005219 | -0.0208 | -0.0052154 | 5.9693e-06 | 3.6212e-06 | 0.03166 | 0.03166 | 0.03166 | 0.97791 | -0.42463 | 0.9776 | -0.43065 | 8.6978
20 | 0.014431 | 0.0036175 | -0.014427 | -0.0036155 | 3.5896e-06 | 2.0482e-06 | 0.021957 | 0.021957 | 0.021957 | 0.978 | -0.4229 | 0.97773 | -0.42813 | 6.032
21 | 0.0059731 | 0.001497 | -0.0059725 | -0.0014969 | 5.1904e-07 | 1.2047e-07 | 0.0090724 | 0.0090724 | 0.0090724 | 0.97968 | -0.38996 | 0.97959 | -0.39178 | 2.4924
22 | 0.039696 | 0.0099698 | -0.039682 | -0.0099605 | 1.4613e-05 | 9.2178e-06 | 0.060342 | 0.060342 | 0.060342 | 0.97902 | -0.40286 | 0.97863 | -0.41058 | 16.5775
23 | -0.26443 | -0.067259 | 0.26449 | 0.067295 | 5.6867e-05 | 3.6199e-05 | 0.39864 | 0.39864 | 0.39864 | 0.98793 | -0.22938 | 0.98817 | -0.22492 | 27.3792
24 | 0.26038 | 0.066243 | -0.26001 | -0.066006 | 0.00037267 | 0.00023719 | 0.39253 | 0.39253 | 0.39253 | 0.98793 | -0.22938 | 0.98639 | -0.25912 | 26.9598
25 | -0.26846 | -0.068291 | 0.26894 | 0.068596 | 0.00047972 | 0.00030541 | 0.40462 | 0.40462 | 0.40462 | 0.98817 | -0.22492 | 0.99009 | -0.18791 | 27.7899
26 | 0.25801 | 0.065506 | -0.25801 | -0.065504 | 3.8663e-06 | 2.4606e-06 | 0.38953 | 0.38953 | 0.38953 | 0.98639 | -0.25912 | 0.98637 | -0.25943 | 26.7533
27 | 0.1273 | 0.032424 | -0.12728 | -0.032414 | 1.536e-05 | 9.8162e-06 | 0.1915 | 0.1915 | 0.1915 | 0.99009 | -0.18791 | 0.98996 | -0.19041 | 52.61
28 | -0.39624 | -0.10102 | 0.39663 | 0.10127 | 0.00038915 | 0.00024845 | 0.59612 | 0.59612 | 0.59612 | 0.99009 | -0.18791 | 0.99116 | -0.16758 | 40.9424
29 | 0.25505 | 0.064762 | -0.25474 | -0.064564 | 0.00031123 | 0.00019805 | 0.38506 | 0.38506 | 0.38506 | 0.98637 | -0.25943 | 0.98506 | -0.28483 | 26.4466
30 | 0.11909 | 0.03036 | -0.11868 | -0.030103 | 0.0004025 | 0.00025717 | 0.17918 | 0.17918 | 0.17918 | 0.98996 | -0.19041 | 0.98631 | -0.26069 | 49.226
31 | -0.39965 | -0.10202 | 0.40014 | 0.10234 | 0.00049531 | 0.00031625 | 0.60065 | 0.60065 | 0.60065 | 0.99116 | -0.16758 | 0.9925 | -0.14197 | 41.2536
32 | 0.24902 | 0.06313 | -0.24875 | -0.06296 | 0.00026724 | 0.00017001 | 0.37642 | 0.37642 | 0.37642 | 0.98506 | -0.28483 | 0.9839 | -0.30718 | 25.8533
33 | 0.10623 | 0.026982 | -0.1061 | -0.026895 | 0.00013749 | 8.7812e-05 | 0.1604 | 0.1604 | 0.1604 | 0.98631 | -0.26069 | 0.98492 | -0.28761 | 44.0658
34 | -0.40306 | -0.10307 | 0.40379 | 0.10354 | 0.00072577 | 0.0004634 | 0.60503 | 0.60503 | 0.60503 | 0.9925 | -0.14197 | 0.99445 | -0.10483 | 41.5541
35 | 0.025796 | 0.0064771 | -0.025771 | -0.0064614 | 2.5423e-05 | 1.5706e-05 | 0.039018 | 0.039018 | 0.039018 | 0.9839 | -0.30718 | 0.98285 | -0.32786 | 10.7192
36 | 0.19993 | 0.050708 | -0.19971 | -0.050566 | 0.00022386 | 0.00014195 | 0.30259 | 0.30259 | 0.30259 | 0.9839 | -0.30718 | 0.9827 | -0.3305 | 20.7822
37 | 0.023021 | 0.0057752 | -0.023012 | -0.0057694 | 9.4474e-06 | 5.7825e-06 | 0.034818 | 0.034818 | 0.034818 | 0.9839 | -0.30718 | 0.98346 | -0.31579 | 9.5654
38 | -0.006312 | -0.0015819 | 0.0063122 | 0.001582 | 1.5922e-07 | 4.4413e-08 | 0.0096154 | 0.0096154 | 0.0096154 | 0.97681 | -0.44636 | 0.97683 | -0.44583 | 2.6416
39 | -0.014034 | -0.0035172 | 0.01404 | 0.0035209 | 6.4508e-06 | 3.6571e-06 | 0.021378 | 0.021378 | 0.021378 | 0.97683 | -0.44583 | 0.97732 | -0.43618 | 5.873
40 | -0.019826 | -0.0049708 | 0.019832 | 0.0049748 | 6.6413e-06 | 4.0068e-06 | 0.030186 | 0.030186 | 0.030186 | 0.97732 | -0.43618 | 0.97768 | -0.42916 | 8.2929
41 | 0.011193 | 0.0028052 | -0.011193 | -0.0028051 | 4.8984e-08 | 2.5705e-08 | 0.017035 | 0.017035 | 0.017035 | 0.97768 | -0.42916 | 0.97768 | -0.42925 | 4.68
42 | -0.031025 | -0.00778 | 0.031047 | 0.0077934 | 2.1505e-05 | 1.344e-05 | 0.047221 | 0.047221 | 0.047221 | 0.97768 | -0.42916 | 0.97842 | -0.41462 | 12.9728
43 | -0.039674 | -0.0099557 | 0.039682 | 0.0099605 | 7.6604e-06 | 4.8322e-06 | 0.060342 | 0.060342 | 0.060342 | 0.97842 | -0.41462 | 0.97863 | -0.41058 | 16.5775
44 | -0.086972 | -0.02197 | 0.086993 | 0.021983 | 2.0856e-05 | 1.3307e-05 | 0.13199 | 0.13199 | 0.13199 | 0.98098 | -0.36406 | 0.98123 | -0.35906 | 36.2604
45 | 0.084809 | 0.021428 | -0.084711 | -0.021366 | 9.7725e-05 | 6.2346e-05 | 0.12871 | 0.12871 | 0.12871 | 0.98098 | -0.36406 | 0.97974 | -0.38813 | 35.3589
46 | -0.089197 | -0.022536 | 0.089348 | 0.022632 | 0.00015157 | 9.6727e-05 | 0.13533 | 0.13533 | 0.13533 | 0.98123 | -0.35906 | 0.98305 | -0.32368 | 37.1784
47 | 0.022228 | 0.0055784 | -0.022223 | -0.0055755 | 4.7973e-06 | 2.929e-06 | 0.033762 | 0.033762 | 0.033762 | 0.97974 | -0.38813 | 0.97951 | -0.39266 | 9.2754
48 | 0.062483 | 0.015787 | -0.062474 | -0.015781 | 9.3741e-06 | 5.9645e-06 | 0.094944 | 0.094944 | 0.094944 | 0.97974 | -0.38813 | 0.97958 | -0.39126 | 26.0835
49 | -0.091804 | -0.023248 | 0.091829 | 0.023264 | 2.5815e-05 | 1.6477e-05 | 0.13905 | 0.13905 | 0.13905 | 0.98305 | -0.32368 | 0.98336 | -0.31782 | 38.1995
50 | 0.020217 | 0.0050726 | -0.020206 | -0.0050662 | 1.0707e-05 | 6.472e-06 | 0.030714 | 0.030715 | 0.030715 | 0.97951 | -0.39266 | 0.97894 | -0.40377 | 8.4381
51 | 0.058504 | 0.014786 | -0.058422 | -0.014734 | 8.2339e-05 | 5.2348e-05 | 0.088914 | 0.088914 | 0.088914 | 0.97958 | -0.39126 | 0.97808 | -0.42066 | 24.4271
52 | -0.096414 | -0.024413 | 0.096554 | 0.024503 | 0.00014008 | 8.9429e-05 | 0.14598 | 0.14598 | 0.14598 | 0.98336 | -0.31782 | 0.98492 | -0.28761 | 40.1054
53 | 0.016842 | 0.0042231 | -0.01684 | -0.0042214 | 2.8709e-06 | 1.6905e-06 | 0.025602 | 0.025602 | 0.025602 | 0.97894 | -0.40377 | 0.97876 | -0.40735 | 7.0334
54 | 0.055412 | 0.01398 | -0.055408 | -0.013977 | 3.5855e-06 | 2.2778e-06 | 0.084335 | 0.084335 | 0.084335 | 0.97808 | -0.42066 | 0.97801 | -0.42201 | 23.1691
55 | 0.0095419 | 0.0023919 | -0.0095396 | -0.0023907 | 2.3925e-06 | 1.1406e-06 | 0.014416 | 0.014416 | 0.014416 | 0.98492 | -0.28761 | 0.98465 | -0.29288 | 3.9605
56 | 0.013831 | 0.0034675 | -0.013828 | -0.0034659 | 2.9129e-06 | 1.6435e-06 | 0.021028 | 0.021028 | 0.021028 | 0.97876 | -0.40735 | 0.97854 | -0.41177 | 5.777
57 | 0.052333 | 0.013207 | -0.052285 | -0.013176 | 4.7685e-05 | 3.0267e-05 | 0.079656 | 0.079657 | 0.079657 | 0.97801 | -0.42201 | 0.97703 | -0.44106 | 21.8837
58 | -0.0010981 | -0.00027521 | 0.0010981 | 0.00027515 | 5.1391e-09 | -5.8155e-08 | 0.0016719 | 0.0016718 | 0.0016719 | 0.97735 | -0.43566 | 0.97735 | -0.43556 | 0.4593
59 | -0.0010981 | -0.00027515 | 0.0010981 | 0.00027481 | 3.0285e-08 | -3.4276e-07 | 0.0016718 | 0.0016717 | 0.0016718 | 0.97735 | -0.43556 | 0.97738 | -0.43498 | 0.45929
60 | 0.0069916 | 0.001752 | -0.0069914 | -0.0017519 | 2.0534e-07 | 7.0761e-08 | 0.01064 | 0.01064 | 0.01064 | 0.97773 | -0.42813 | 0.9777 | -0.42874 | 2.9232
61 | -0.016387 | -0.0041083 | 0.01639 | 0.0041103 | 3.3859e-06 | 1.9852e-06 | 0.024949 | 0.024949 | 0.024949 | 0.97738 | -0.43498 | 0.9776 | -0.43065 | 6.8541
62 | 0.015289 | 0.0038335 | -0.015284 | -0.0038308 | 4.6397e-06 | 2.6833e-06 | 0.023277 | 0.023277 | 0.023277 | 0.97738 | -0.43498 | 0.97706 | -0.44135 | 6.3949
63 | -0.0059743 | -0.0014973 | 0.0059747 | 0.0014974 | 3.4641e-07 | 8.5711e-08 | 0.0091611 | 0.009161 | 0.0091611 | 0.9704 | -0.57153 | 0.97046 | -0.57032 | 2.5168
64 | 0.014088 | 0.0035319 | -0.014085 | -0.00353 | 3.4034e-06 | 1.9379e-06 | 0.021602 | 0.021602 | 0.021602 | 0.97046 | -0.57032 | 0.97021 | -0.57539 | 5.9346
65 | -0.020063 | -0.0050293 | 0.020071 | 0.0050342 | 8.1043e-06 | 4.9044e-06 | 0.030763 | 0.030763 | 0.030763 | 0.97046 | -0.57032 | 0.97089 | -0.56184 | 8.4514
66 | 0.0015413 | 0.00038597 | -0.0015412 | -0.00038627 | 5.6013e-08 | -3.0457e-07 | 0.0023457 | 0.0023458 | 0.0023458 | 0.9777 | -0.42874 | 0.97766 | -0.42951 | 0.64445
67 | 0.0077432 | 0.0019409 | -0.0077415 | -0.0019402 | 1.6904e-06 | 6.7597e-07 | 0.011793 | 0.011793 | 0.011793 | 0.97706 | -0.44135 | 0.97683 | -0.44594 | 3.2398
68 | 0.0065125 | 0.0016322 | -0.0065124 | -0.0016322 | 7.4367e-09 | 2.3049e-09 | 0.0099882 | 0.0099882 | 0.0099882 | 0.97021 | -0.57539 | 0.97021 | -0.57541 | 2.744
69 | -0.027969 | -0.0070136 | 0.027993 | 0.007029 | 2.4725e-05 | 1.538e-05 | 0.042867 | 0.042867 | 0.042867 | 0.97089 | -0.56184 | 0.97183 | -0.54331 | 11.7767
70 | 0.0207 | 0.0051904 | -0.020695 | -0.0051876 | 4.7088e-06 | 2.8516e-06 | 0.03134 | 0.03134 | 0.03134 | 0.98285 | -0.32786 | 0.9826 | -0.33264 | 8.6098
71 | 0.1935 | 0.049009 | -0.1933 | -0.048882 | 0.0001996 | 0.00012649 | 0.29318 | 0.29318 | 0.29318 | 0.9827 | -0.3305 | 0.98159 | -0.352 | 20.136
72 | 0.01866 | 0.0046788 | -0.018659 | -0.0046783 | 8.7723e-07 | 5.2419e-07 | 0.028234 | 0.028234 | 0.028234 | 0.98346 | -0.31579 | 0.98341 | -0.31678 | 7.7567
73 | 0.0059858 | 0.0014999 | -0.0059852 | -0.0014998 | 5.4524e-07 | 1.2483e-07 | 0.0090645 | 0.0090646 | 0.0090646 | 0.9826 | -0.33264 | 0.9825 | -0.33455 | 2.4903
74 | 0.014709 | 0.0036877 | -0.014704 | -0.0036847 | 5.2092e-06 | 2.9794e-06 | 0.022275 | 0.022275 | 0.022275 | 0.9826 | -0.33264 | 0.98222 | -0.34007 | 6.1196
75 | 0.18392 | 0.046532 | -0.18386 | -0.046492 | 6.2795e-05 | 3.9753e-05 | 0.27896 | 0.27896 | 0.27896 | 0.98159 | -0.352 | 0.98123 | -0.35912 | 19.1597
76 | 0.0093773 | 0.0023504 | -0.0093763 | -0.0023499 | 9.6399e-07 | 4.5616e-07 | 0.014215 | 0.014215 | 0.014215 | 0.98159 | -0.352 | 0.98148 | -0.35416 | 3.9053
77 | 0.015303 | 0.0038371 | -0.015297 | -0.0038337 | 6.0142e-06 | 3.4697e-06 | 0.023156 | 0.023156 | 0.023156 | 0.98341 | -0.31678 | 0.98299 | -0.32503 | 6.3615
78 | -0.0068612 | -0.0017196 | 0.0068626 | 0.00172 | 1.3622e-06 | 4.6248e-07 | 0.010496 | 0.010496 | 0.010496 | 0.97267 | -0.52672 | 0.97288 | -0.52255 | 2.8836
79 | -0.015307 | -0.0038365 | 0.01531 | 0.0038379 | 2.5307e-06 | 1.4668e-06 | 0.023412 | 0.023412 | 0.023412 | 0.97288 | -0.52255 | 0.97306 | -0.51908 | 6.4319
80 | -0.022895 | -0.005739 | 0.022913 | 0.0057502 | 1.8196e-05 | 1.1153e-05 | 0.035012 | 0.035012 | 0.035012 | 0.97306 | -0.51908 | 0.9739 | -0.50242 | 9.6187
81 | -0.097693 | -0.024555 | 0.097862 | 0.024663 | 0.00016846 | 0.00010756 | 0.14929 | 0.14929 | 0.14929 | 0.9739 | -0.50242 | 0.97574 | -0.46637 | 41.0138
82 | 0.07478 | 0.018805 | -0.074753 | -0.018788 | 2.6867e-05 | 1.7127e-05 | 0.11428 | 0.11428 | 0.11428 | 0.9739 | -0.50242 | 0.97352 | -0.50994 | 31.3952
83 | -0.10376 | -0.02614 | 0.10402 | 0.026312 | 0.00026976 | 0.00017229 | 0.15828 | 0.15828 | 0.15828 | 0.97574 | -0.46637 | 0.97851 | -0.41216 | 43.4829
84 | 0.027804 | 0.0069801 | -0.027784 | -0.006968 | 1.9495e-05 | 1.2119e-05 | 0.042502 | 0.042502 | 0.042502 | 0.97352 | -0.50994 | 0.97277 | -0.52465 | 11.6764
85 | 0.046949 | 0.011808 | -0.046879 | -0.011764 | 7.0085e-05 | 4.4404e-05 | 0.071777 | 0.071777 | 0.071777 | 0.97352 | -0.50994 | 0.97193 | -0.54124 | 19.7189
86 | -0.0021507 | -0.00053902 | 0.0021507 | 0.000539 | 4.7452e-09 | -1.1939e-08 | 0.0032642 | 0.0032642 | 0.0032642 | 0.98041 | -0.37509 | 0.98042 | -0.37504 | 0.89676
87 | -0.0037549 | -0.00094106 | 0.003755 | 0.00094101 | 1.22e-07 | -4.8244e-08 | 0.005699 | 0.0056989 | 0.005699 | 0.98042 | -0.37504 | 0.98045 | -0.37436 | 1.5657
88 | 0.0060859 | 0.0015251 | -0.0060856 | -0.001525 | 3.4793e-07 | 8.4119e-08 | 0.0092129 | 0.0092129 | 0.0092129 | 0.98296 | -0.32558 | 0.9829 | -0.32678 | 2.531
89 | -0.010727 | -0.0026883 | 0.010727 | 0.0026884 | 2.8172e-07 | 1.4418e-07 | 0.016239 | 0.016239 | 0.016239 | 0.98296 | -0.32558 | 0.98299 | -0.32503 | 4.4612
90 | 0.0047535 | 0.0011911 | -0.0047531 | -0.0011911 | 3.6056e-07 | -4.5462e-09 | 0.0071962 | 0.0071963 | 0.0071963 | 0.9829 | -0.32678 | 0.98282 | -0.32837 | 1.977
91 | 0.003338 | 0.00083649 | -0.0033379 | -0.00083656 | 1.0274e-07 | -7.0176e-08 | 0.0050538 | 0.0050539 | 0.0050539 | 0.98282 | -0.32837 | 0.98279 | -0.32902 | 1.3884
92 | -0.0012047 | -0.00030193 | 0.0012048 | 0.00030157 | 4.0116e-08 | -3.6348e-07 | 0.0018451 | 0.001845 | 0.0018451 | 0.97155 | -0.54885 | 0.97159 | -0.54815 | 0.50691
93 | -0.0075769 | -0.0018986 | 0.0075781 | 0.0018991 | 1.2727e-06 | 5.0232e-07 | 0.011604 | 0.011604 | 0.011604 | 0.97159 | -0.54815 | 0.97176 | -0.54463 | 3.1879
94 | -0.01398 | -0.0035036 | 0.013988 | 0.0035081 | 7.8523e-06 | 4.4591e-06 | 0.021407 | 0.021407 | 0.021407 | 0.97176 | -0.54463 | 0.97236 | -0.53284 | 5.8812
95 | 0.0092965 | 0.00233 | -0.0092951 | -0.0023294 | 1.3407e-06 | 6.3336e-07 | 0.014137 | 0.014137 | 0.014137 | 0.97854 | -0.41177 | 0.97838 | -0.4148 | 3.8838
96 | 0.0064099 | 0.0016065 | -0.0064096 | -0.0016064 | 2.9348e-07 | 8.442e-08 | 0.0097488 | 0.0097489 | 0.0097489 | 0.97838 | -0.4148 | 0.97833 | -0.41576 | 2.6783
97 | 0.0028852 | 0.00072291 | -0.0028851 | -0.00072307 | 1.3988e-07 | -1.5374e-07 | 0.004388 | 0.0043881 | 0.0043881 | 0.97838 | -0.4148 | 0.97833 | -0.41582 | 1.2055
98 | 0.0055363 | 0.0013874 | -0.0055357 | -0.0013873 | 6.2268e-07 | 9.6834e-08 | 0.0083666 | 0.0083667 | 0.0083667 | 0.98465 | -0.29288 | 0.98453 | -0.29524 | 2.2985
99 | 0.0055357 | 0.0013873 | -0.0055351 | -0.0013872 | 5.8695e-07 | 9.1352e-08 | 0.0083667 | 0.0083668 | 0.0083668 | 0.98453 | -0.29524 | 0.98441 | -0.29746 | 2.2986
100 | -0.037857 | -0.0095011 | 0.037861 | 0.0095035 | 3.7327e-06 | 2.3522e-06 | 0.05797 | 0.05797 | 0.05797 | 0.97183 | -0.54331 | 0.97193 | -0.54124 | 15.9259
101 | 0.003927 | 0.00098395 | -0.0039265 | -0.00098409 | 4.8947e-07 | -1.3604e-07 | 0.006006 | 0.0060061 | 0.0060061 | 0.97293 | -0.52169 | 0.9728 | -0.52431 | 1.65
102 | -0.0073277 | -0.0018362 | 0.0073287 | 0.0018366 | 1.0018e-06 | 3.7694e-07 | 0.011207 | 0.011207 | 0.011207 | 0.97293 | -0.52169 | 0.97308 | -0.51882 | 3.0788
103 | -0.026839 | -0.0067396 | 0.026846 | 0.0067441 | 7.1856e-06 | 4.4574e-06 | 0.041047 | 0.041047 | 0.041047 | 0.97308 | -0.51882 | 0.97336 | -0.51321 | 11.2766
104 | 0.01951 | 0.004903 | -0.0195 | -0.0048966 | 1.0654e-05 | 6.4222e-06 | 0.02984 | 0.02984 | 0.02984 | 0.97308 | -0.51882 | 0.9725 | -0.53027 | 8.1978
105 | 0.010848 | 0.0027196 | -0.010846 | -0.0027186 | 1.9415e-06 | 1.0086e-06 | 0.016584 | 0.016584 | 0.016584 | 0.97336 | -0.51321 | 0.97317 | -0.51697 | 4.5561
106 | -0.037694 | -0.0094637 | 0.037714 | 0.009476 | 1.9533e-05 | 1.2306e-05 | 0.057631 | 0.05763 | 0.057631 | 0.97336 | -0.51321 | 0.97391 | -0.50235 | 15.8326
107 | 0.0195 | 0.0048966 | -0.019489 | -0.0048898 | 1.1194e-05 | 6.7485e-06 | 0.02984 | 0.02984 | 0.02984 | 0.9725 | -0.53027 | 0.97189 | -0.54231 | 8.1978
108 | 0.010846 | 0.0027186 | -0.010844 | -0.0027177 | 1.7743e-06 | 9.2187e-07 | 0.016584 | 0.016584 | 0.016584 | 0.97317 | -0.51697 | 0.973 | -0.5204 | 4.5561
109 | -0.039466 | -0.0099152 | 0.039498 | 0.0099353 | 3.1973e-05 | 2.0171e-05 | 0.060308 | 0.060308 | 0.060308 | 0.97391 | -0.50235 | 0.97477 | -0.48539 | 16.568
110 | 0.017443 | 0.0043772 | -0.01744 | -0.0043754 | 2.9785e-06 | 1.7683e-06 | 0.026708 | 0.026708 | 0.026708 | 0.97189 | -0.54231 | 0.97171 | -0.54589 | 7.3374
111 | 0.016054 | 0.004028 | -0.016048 | -0.0040247 | 5.7105e-06 | 3.3428e-06 | 0.024586 | 0.024586 | 0.024586 | 0.97171 | -0.54589 | 0.97133 | -0.55335 | 6.7544
112 | 0.0052789 | 0.0013229 | -0.005278 | -0.0013228 | 9.145e-07 | 1.2064e-07 | 0.008073 | 0.0080732 | 0.0080732 | 0.973 | -0.5204 | 0.97281 | -0.52404 | 2.2179
113 | -0.040494 | -0.010185 | 0.040512 | 0.010196 | 1.7132e-05 | 1.0816e-05 | 0.061829 | 0.061829 | 0.061829 | 0.97477 | -0.48539 | 0.97522 | -0.47654 | 16.9859
114 | -0.013988 | -0.0035081 | 0.013991 | 0.0035095 | 2.4416e-06 | 1.3864e-06 | 0.021407 | 0.021407 | 0.021407 | 0.97236 | -0.53284 | 0.97255 | -0.52918 | 5.8811
115 | -0.020154 | -0.0050541 | 0.020158 | 0.0050567 | 4.3508e-06 | 2.6331e-06 | 0.030837 | 0.030837 | 0.030837 | 0.97255 | -0.52918 | 0.97277 | -0.52465 | 8.4717
116 | 0.16933 | 0.042848 | -0.16918 | -0.042758 | 0.00014253 | 9.0056e-05 | 0.25693 | 0.25693 | 0.25693 | 0.98123 | -0.35912 | 0.98033 | -0.37667 | 17.6461
117 | 0.014532 | 0.0036442 | -0.014528 | -0.0036423 | 3.3592e-06 | 1.917e-06 | 0.022038 | 0.022038 | 0.022038 | 0.98123 | -0.35912 | 0.98098 | -0.36397 | 6.0544
118 | 0.016472 | 0.0041304 | -0.016465 | -0.0041266 | 6.499e-06 | 3.81e-06 | 0.025003 | 0.025003 | 0.025003 | 0.98033 | -0.37667 | 0.9799 | -0.38495 | 6.869
119 | 0.15271 | 0.038627 | -0.15251 | -0.038503 | 0.00019703 | 0.00012413 | 0.23192 | 0.23193 | 0.23193 | 0.98033 | -0.37667 | 0.97895 | -0.4036 | 15.9289
120 | 0.013227 | 0.0033162 | -0.013226 | -0.0033155 | 1.3366e-06 | 7.4368e-07 | 0.020064 | 0.020065 | 0.020065 | 0.98098 | -0.36397 | 0.98087 | -0.36609 | 5.5122
121 | -0.0019949 | -0.00049996 | 0.0019949 | 0.00049986 | 3.0643e-08 | -9.9372e-08 | 0.002985 | 0.002985 | 0.002985 | 0.99443 | -0.10515 | 0.99445 | -0.10483 | 0.82005
122 | -0.40578 | -0.10404 | 0.40637 | 0.10441 | 0.00058382 | 0.00037277 | 0.60801 | 0.60801 | 0.60801 | 0.99445 | -0.10483 | 0.99601 | -0.075205 | 41.7591
123 | -0.41915 | -0.10761 | 0.4199 | 0.10809 | 0.00074899 | 0.00047829 | 0.62711 | 0.62711 | 0.62711 | 0.99601 | -0.075205 | 0.99796 | -0.038464 | 43.071
124 | 0.013649 | 0.0034221 | -0.013645 | -0.0034198 | 4.1504e-06 | 2.3073e-06 | 0.020352 | 0.020353 | 0.020353 | 0.99796 | -0.038464 | 0.99763 | -0.044847 | 5.5914
125 | 0.0078653 | 0.0019713 | -0.0078652 | -0.0019712 | 1.4346e-07 | 5.8033e-08 | 0.011944 | 0.011944 | 0.011944 | 0.9799 | -0.38495 | 0.97988 | -0.38534 | 3.2813
126 | 0.042367 | 0.010639 | -0.042338 | -0.010621 | 2.943e-05 | 1.8597e-05 | 0.064406 | 0.064407 | 0.064407 | 0.97895 | -0.4036 | 0.9782 | -0.41817 | 17.6941
127 | 0.11015 | 0.027864 | -0.1101 | -0.027835 | 4.5227e-05 | 2.873e-05 | 0.16752 | 0.16752 | 0.16752 | 0.97895 | -0.4036 | 0.97851 | -0.41216 | 23.0108
128 | 0.011687 | 0.0029298 | -0.011684 | -0.0029284 | 2.6791e-06 | 1.4278e-06 | 0.01773 | 0.01773 | 0.01773 | 0.98087 | -0.36609 | 0.98063 | -0.3709 | 4.8708
129 | -0.00381 | -0.00095488 | 0.0038102 | 0.00095481 | 1.9321e-07 | -6.7942e-08 | 0.005803 | 0.0058029 | 0.005803 | 0.97697 | -0.44244 | 0.97702 | -0.44137 | 1.5942
130 | -0.012321 | -0.0030877 | 0.012322 | 0.0030883 | 1.0836e-06 | 5.9072e-07 | 0.018764 | 0.018764 | 0.018764 | 0.97702 | -0.44137 | 0.97712 | -0.43953 | 5.155
131 | -0.020637 | -0.0051724 | 0.020646 | 0.0051775 | 8.3676e-06 | 5.0721e-06 | 0.031428 | 0.031428 | 0.031428 | 0.97712 | -0.43953 | 0.97755 | -0.43102 | 8.634
132 | -0.0029173 | -0.00073115 | 0.0029174 | 0.00073102 | 1.1608e-07 | -1.2616e-07 | 0.0044203 | 0.0044203 | 0.0044203 | 0.98205 | -0.34338 | 0.9821 | -0.34254 | 1.2144
133 | -0.0042082 | -0.0010545 | 0.0042084 | 0.0010545 | 2.4614e-07 | -4.679e-08 | 0.006376 | 0.0063759 | 0.006376 | 0.9821 | -0.34254 | 0.98216 | -0.34131 | 1.7516
134 | -0.010135 | -0.0025396 | 0.010136 | 0.0025399 | 6.0104e-07 | 2.9864e-07 | 0.015355 | 0.015355 | 0.015355 | 0.98216 | -0.34131 | 0.98222 | -0.34007 | 4.2185
135 | 0.005927 | 0.0014852 | -0.0059266 | -0.0014851 | 3.9225e-07 | 8.6883e-08 | 0.0089796 | 0.0089796 | 0.0089796 | 0.98216 | -0.34131 | 0.98209 | -0.3427 | 2.4669
136 | 0.0014451 | 0.0003619 | -0.0014451 | -0.00036217 | 4.2447e-08 | -2.7159e-07 | 0.0021895 | 0.0021896 | 0.0021896 | 0.98209 | -0.3427 | 0.98206 | -0.34332 | 0.60153
137 | 0.049485 | 0.012475 | -0.049469 | -0.012464 | 1.6087e-05 | 1.0201e-05 | 0.075391 | 0.075391 | 0.075391 | 0.97703 | -0.44106 | 0.97669 | -0.44785 | 20.7119
138 | 0.048189 | 0.012144 | -0.048184 | -0.01214 | 5.1137e-06 | 3.2411e-06 | 0.073442 | 0.073442 | 0.073442 | 0.97669 | -0.44785 | 0.97657 | -0.45007 | 20.1763
139 | -0.0041324 | -0.0010356 | 0.0041326 | 0.0010355 | 1.7306e-07 | -3.1269e-08 | 0.0063363 | 0.0063362 | 0.0063363 | 0.97045 | -0.57082 | 0.97049 | -0.56995 | 1.7407
140 | 0.0041324 | 0.0010356 | -0.0041321 | -0.0010356 | 2.7006e-07 | -4.8764e-08 | 0.0063363 | 0.0063364 | 0.0063364 | 0.97045 | -0.57082 | 0.97038 | -0.5722 | 1.7408
141 | -0.006921 | -0.0017344 | 0.0069215 | 0.0017345 | 4.7394e-07 | 1.6463e-07 | 0.010612 | 0.010612 | 0.010612 | 0.97049 | -0.56995 | 0.97056 | -0.56851 | 2.9153
142 | 0.045417 | 0.011447 | -0.045376 | -0.011421 | 4.1218e-05 | 2.6093e-05 | 0.069226 | 0.069226 | 0.069226 | 0.97657 | -0.45007 | 0.97561 | -0.46906 | 19.0182
143 | -0.010908 | -0.0027337 | 0.01091 | 0.0027346 | 1.7596e-06 | 9.1878e-07 | 0.016724 | 0.016724 | 0.016724 | 0.97056 | -0.56851 | 0.97073 | -0.56512 | 4.5944
144 | 0.043664 | 0.010992 | -0.043663 | -0.010991 | 9.4738e-07 | 5.9922e-07 | 0.066614 | 0.066614 | 0.066614 | 0.97561 | -0.46906 | 0.97558 | -0.46951 | 18.3007
145 | 0.0022973 | 0.00057547 | -0.0022972 | -0.00057572 | 1.1661e-07 | -2.5068e-07 | 0.0034791 | 0.0034793 | 0.0034793 | 0.9825 | -0.33455 | 0.98245 | -0.33561 | 0.95584
146 | -0.0053804 | -0.0013484 | 0.0053808 | 0.0013484 | 4.8647e-07 | 6.5953e-08 | 0.0081656 | 0.0081656 | 0.0081656 | 0.98045 | -0.37436 | 0.98055 | -0.37246 | 2.2433
147 | -0.0071854 | -0.0018007 | 0.0071855 | 0.0018007 | 1.5688e-07 | 5.6021e-08 | 0.010904 | 0.010904 | 0.010904 | 0.98055 | -0.37246 | 0.98057 | -0.372 | 2.9956
148 | -0.010093 | -0.0025294 | 0.010093 | 0.0025296 | 5.2878e-07 | 2.6259e-07 | 0.015316 | 0.015316 | 0.015316 | 0.98057 | -0.372 | 0.98063 | -0.3709 | 4.2076
149 | 0.029024 | 0.0072839 | -0.029006 | -0.0072728 | 1.7769e-05 | 1.1067e-05 | 0.044154 | 0.044154 | 0.044154 | 0.9782 | -0.41817 | 0.97755 | -0.43102 | 12.1303
150 | 0.042181 | 0.01062 | -0.042166 | -0.010611 | 1.4169e-05 | 8.9542e-06 | 0.064354 | 0.064354 | 0.064354 | 0.97558 | -0.46951 | 0.97522 | -0.47654 | 17.6796
151 | -0.013608 | -0.0034117 | 0.013612 | 0.0034138 | 3.6166e-06 | 2.0403e-06 | 0.020855 | 0.020855 | 0.020855 | 0.97097 | -0.56047 | 0.97125 | -0.5549 | 5.7295
152 | 0.012272 | 0.0030769 | -0.01227 | -0.0030754 | 2.7179e-06 | 1.4861e-06 | 0.018808 | 0.018808 | 0.018808 | 0.97097 | -0.56047 | 0.97073 | -0.56512 | 5.1671
153 | -0.014574 | -0.0036548 | 0.014575 | 0.0036555 | 1.0752e-06 | 6.1696e-07 | 0.022329 | 0.022329 | 0.022329 | 0.97125 | -0.5549 | 0.97133 | -0.55335 | 6.1343

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58399 | 0.15012

## res_load
| p_mw | q_mvar
0 | 0.0069776 | 0.0017488
1 | 0.004064 | 0.0010185
2 | 0.0082478 | 0.0020671
3 | 0.0044939 | 0.0011263
4 | 0.008673 | 0.0021737
5 | 0.007829 | 0.0019621
6 | 0.0076109 | 0.0019075
7 | 0.0072473 | 0.0018163
8 | 0.004448 | 0.0011148
9 | 0.0049682 | 0.0012451
10 | 0.0040551 | 0.0010163
11 | 0.0039711 | 0.00099525
12 | 0.0019933 | 0.00049958
13 | 0.0029599 | 0.00074181
14 | 0.008195 | 0.0020539
15 | 0.0030182 | 0.00075643
16 | 0.0057196 | 0.0014335
17 | 0.01245 | 0.0031203
18 | 0.0029189 | 0.00073154
19 | 0.006312 | 0.0015819
20 | 0.0077216 | 0.0019352
21 | 0.0057854 | 0.00145
22 | 0.011193 | 0.0028051
23 | 0.0086276 | 0.0021623
24 | 0.0021633 | 0.00054218
25 | 0.0022036 | 0.00055228
26 | 0.0024555 | 0.0006154
27 | 0.0020063 | 0.00050282
28 | 0.0039695 | 0.00099484
29 | 0.0045846 | 0.001149
30 | 0.0033638 | 0.00084304
31 | 0.0030099 | 0.00075435
32 | 0.0030082 | 0.00075393
33 | 0.0030752 | 0.00077073
34 | 0.0010981 | 0.00027521
35 | 0.0074356 | 0.0018635
36 | 0.0059743 | 0.0014973
37 | 0.0054501 | 0.0013659
38 | 0.0044092 | 0.001105
39 | 0.0075411 | 0.00189
40 | 0.0075724 | 0.0018978
41 | 0.0078977 | 0.0019794
42 | 0.0015412 | 0.00038627
43 | 0.0077415 | 0.0019402
44 | 0.0050714 | 0.001271
45 | 0.0062137 | 0.0015573
46 | 0.0043513 | 0.0010905
47 | 0.0033564 | 0.00084118
48 | 0.0068612 | 0.0017196
49 | 0.0084446 | 0.0021164
50 | 0.0075855 | 0.0019011
51 | 0.0058935 | 0.0014771
52 | 0.0021507 | 0.00053902
53 | 0.0016042 | 0.00040205
54 | 0.0046412 | 0.0011632
55 | 0.0013321 | 0.00033386
56 | 0.0045695 | 0.0011452
57 | 0.0014151 | 0.00035465
58 | 0.0033379 | 0.00083656
59 | 0.0012047 | 0.00030193
60 | 0.0063721 | 0.001597
61 | 0.0064022 | 0.0016046
62 | 0.004532 | 0.0011358
63 | 0.0059725 | 0.0014969
64 | 0.0040032 | 0.0010033
65 | 0.0065124 | 0.0016322
66 | 0.0098639 | 0.0024721
67 | 0.0090182 | 0.0022602
68 | 0.0034006 | 0.00085228
69 | 0.0039265 | 0.00098409
70 | 0.0017522 | 0.00043914
71 | 0.0020457 | 0.0005127
72 | 0.0013859 | 0.00034733
73 | 0.0055653 | 0.0013948
74 | 0.00099656 | 0.00024976
75 | 0.0061631 | 0.0015446
76 | 0.0076259 | 0.0019112
77 | 0.0055351 | 0.0013872
78 | 0.0093763 | 0.0023499
79 | 0.0013011 | 0.00032608
80 | 0.0019949 | 0.00049996
81 | 0.012786 | 0.0032045
82 | 0.0086 | 0.0021554
83 | 0.001539 | 0.00038572
84 | 0.00381 | 0.00095488
85 | 0.0085103 | 0.0021329
86 | 0.0083157 | 0.0020841
87 | 0.0029173 | 0.00073115
88 | 0.0012908 | 0.0003235
89 | 0.0045678 | 0.0011448
90 | 0.0044815 | 0.0011232
91 | 0.0014451 | 0.00036217
92 | 0.005278 | 0.0013228
93 | 0.0060769 | 0.001523
94 | 0.0028005 | 0.00070187
95 | 0.0012797 | 0.00032072
96 | 0.0027884 | 0.00069885
97 | 0.0041321 | 0.0010356
98 | 0.0027668 | 0.00069343
99 | 0.0039867 | 0.00099916
100 | 0.0017123 | 0.00042914
101 | 0.0064096 | 0.0016064
102 | 0.0028851 | 0.00072307
103 | 0.003688 | 0.00092429
104 | 0.0016253 | 0.00040734
105 | 0.0018046 | 0.00045226
106 | 0.0029073 | 0.00072863
107 | 0.0015909 | 0.00039872
108 | 0.013645 | 0.0034198
109 | 0.0078652 | 0.0019712
110 | 0.013314 | 0.0033367
111 | 0.0083607 | 0.0020954
112 | 0.0022972 | 0.00057572
113 | 0.0014822 | 0.00037148
114 | 0.0016549 | 0.00041475
115 | 0.0013359 | 0.00033481
116 | 0.00096197 | 0.00024109
117 | 0.0013598 | 0.00034079
118 | 0.0014733 | 0.00036924

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1