## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-24_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-24_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-24_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_161-24_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_161-24_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_161-24_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_161-24_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_161-24_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_161-24_0_4_node_182 | 0.4 | n |  | TRUE
9 | bus_LV_161-24_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_161-24_0_4_node_183 | 0.4 | n |  | TRUE
11 | bus_LV_161-24_0_4_node_193 | 0.4 | n |  | TRUE
12 | bus_LV_161-24_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_161-24_0_4_node_186 | 0.4 | n |  | TRUE
14 | bus_LV_161-24_0_4_node_185 | 0.4 | n |  | TRUE
15 | bus_LV_161-24_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_161-24_0_4_node_189 | 0.4 | n |  | TRUE
17 | bus_LV_161-24_0_4_node_192 | 0.4 | n |  | TRUE
18 | bus_LV_161-24_0_4_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_161-24_0_4_node_188 | 0.4 | n |  | TRUE
20 | bus_LV_161-24_0_4_node_194 | 0.4 | n |  | TRUE
21 | bus_LV_161-24_0_4_node_190 | 0.4 | n |  | TRUE
22 | bus_LV_161-24_0_4_node_187 | 0.4 | n |  | TRUE
23 | bus_LV_161-24_0_4_node_184 | 0.4 | n |  | TRUE
24 | bus_LV_161-24_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_161-24_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_161-24_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_161-24_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_161-24_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_161-24_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_161-24_0_4_node_49 | 0.4 | n |  | TRUE
31 | bus_LV_161-24_0_4_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_161-24_0_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_161-24_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_161-24_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_161-24_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_161-24_0_4_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_161-24_0_4_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_161-24_0_4_node_68 | 0.4 | n |  | TRUE
39 | bus_LV_161-24_0_4_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_161-24_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_161-24_0_4_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_161-24_0_4_node_178 | 0.4 | n |  | TRUE
43 | bus_LV_161-24_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_161-24_0_4_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_161-24_0_4_node_179 | 0.4 | n |  | TRUE
46 | bus_LV_161-24_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_161-24_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_161-24_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_161-24_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_161-24_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_161-24_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_161-24_0_4_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_161-24_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_161-24_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_161-24_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_161-24_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_161-24_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_161-24_0_4_node_78 | 0.4 | n |  | TRUE
59 | bus_LV_161-24_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_161-24_0_4_node_138 | 0.4 | n |  | TRUE
61 | bus_LV_161-24_0_4_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_161-24_0_4_node_139 | 0.4 | n |  | TRUE
63 | bus_LV_161-24_0_4_node_137 | 0.4 | n |  | TRUE
64 | bus_LV_161-24_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_161-24_0_4_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_161-24_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_161-24_0_4_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_161-24_0_4_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_161-24_0_4_node_80 | 0.4 | n |  | TRUE
70 | bus_LV_161-24_0_4_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_161-24_0_4_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_161-24_0_4_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_161-24_0_4_node_169 | 0.4 | n |  | TRUE
74 | bus_LV_161-24_0_4_node_144 | 0.4 | n |  | TRUE
75 | bus_LV_161-24_0_4_node_121 | 0.4 | n |  | TRUE
76 | bus_LV_161-24_0_4_node_123 | 0.4 | n |  | TRUE
77 | bus_LV_161-24_0_4_node_124 | 0.4 | n |  | TRUE
78 | bus_LV_161-24_0_4_node_133 | 0.4 | n |  | TRUE
79 | bus_LV_161-24_0_4_node_154 | 0.4 | n |  | TRUE
80 | bus_LV_161-24_0_4_node_132 | 0.4 | n |  | TRUE
81 | bus_LV_161-24_0_4_node_155 | 0.4 | n |  | TRUE
82 | bus_LV_161-24_0_4_node_125 | 0.4 | n |  | TRUE
83 | bus_LV_161-24_0_4_node_126 | 0.4 | n |  | TRUE
84 | bus_LV_161-24_0_4_node_127 | 0.4 | n |  | TRUE
85 | bus_LV_161-24_0_4_node_128 | 0.4 | n |  | TRUE
86 | bus_LV_161-24_0_4_node_129 | 0.4 | n |  | TRUE
87 | bus_LV_161-24_0_4_node_130 | 0.4 | n |  | TRUE
88 | bus_LV_161-24_0_4_node_131 | 0.4 | n |  | TRUE
89 | bus_LV_161-24_0_4_node_147 | 0.4 | n |  | TRUE
90 | bus_LV_161-24_0_4_node_148 | 0.4 | n |  | TRUE
91 | bus_LV_161-24_0_4_node_163 | 0.4 | n |  | TRUE
92 | bus_LV_161-24_0_4_node_161 | 0.4 | n |  | TRUE
93 | bus_LV_161-24_0_4_node_140 | 0.4 | n |  | TRUE
94 | bus_LV_161-24_0_4_node_141 | 0.4 | n |  | TRUE
95 | bus_LV_161-24_0_4_node_142 | 0.4 | n |  | TRUE
96 | bus_LV_161-24_0_4_node_143 | 0.4 | n |  | TRUE
97 | bus_LV_161-24_0_4_node_145 | 0.4 | n |  | TRUE
98 | bus_LV_161-24_0_4_node_164 | 0.4 | n |  | TRUE
99 | bus_LV_161-24_0_4_node_146 | 0.4 | n |  | TRUE
100 | bus_LV_161-24_0_4_node_151 | 0.4 | n |  | TRUE
101 | bus_LV_161-24_0_4_node_165 | 0.4 | n |  | TRUE
102 | bus_LV_161-24_0_4_node_153 | 0.4 | n |  | TRUE
103 | bus_LV_161-24_0_4_node_149 | 0.4 | n |  | TRUE
104 | bus_LV_161-24_0_4_node_150 | 0.4 | n |  | TRUE
105 | bus_LV_161-24_0_4_node_152 | 0.4 | n |  | TRUE
106 | bus_LV_161-24_0_4_node_158 | 0.4 | n |  | TRUE
107 | bus_LV_161-24_0_4_node_171 | 0.4 | n |  | TRUE
108 | bus_LV_161-24_0_4_node_159 | 0.4 | n |  | TRUE
109 | bus_LV_161-24_0_4_node_160 | 0.4 | n |  | TRUE
110 | bus_LV_161-24_0_4_node_172 | 0.4 | n |  | TRUE
111 | bus_LV_161-24_0_4_node_175 | 0.4 | n |  | TRUE
112 | bus_LV_161-24_0_4_node_174 | 0.4 | n |  | TRUE
113 | bus_LV_161-24_0_4_node_162 | 0.4 | n |  | TRUE
114 | bus_LV_161-24_0_4_node_176 | 0.4 | n |  | TRUE
115 | bus_LV_161-24_0_4_node_167 | 0.4 | n |  | TRUE
116 | bus_LV_161-24_0_4_node_177 | 0.4 | n |  | TRUE
117 | bus_LV_161-24_0_4_node_191 | 0.4 | n |  | TRUE
118 | bus_LV_161-24_0_4_node_195 | 0.4 | n |  | TRUE
119 | bus_MV_493_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-24_0_4_load_0 | 0 | 0.0077554 | 0.0019437 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-24_0_4_load_1 | 1 | 0.0084556 | 0.0021192 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-24_0_4_load_3 | 2 | 0.0068215 | 0.0017096 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-24_0_4_load_2 | 3 | 0.0015622 | 0.00039154 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-24_0_4_load_5 | 4 | 0.0052791 | 0.0013231 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-24_0_4_load_6 | 5 | 0.0028366 | 0.00071092 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-24_0_4_load_15 | 7 | 0.0075255 | 0.0018861 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-24_0_4_load_182 | 8 | 0.0029355 | 0.00073572 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-24_0_4_load_183 | 10 | 0.0016075 | 0.00040288 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-24_0_4_load_193 | 11 | 0.0018199 | 0.00045611 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-24_0_4_load_186 | 13 | 0.0018128 | 0.00045434 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-24_0_4_load_185 | 14 | 0.0026709 | 0.0006694 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-24_0_4_load_192 | 17 | 0.0012206 | 0.00030592 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-24_0_4_load_188 | 19 | 0.0012172 | 0.00030505 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-24_0_4_load_194 | 20 | 0.0018445 | 0.00046226 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-24_0_4_load_187 | 22 | 0.0011892 | 0.00029804 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-24_0_4_load_184 | 23 | 0.0028045 | 0.00070287 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-24_0_4_load_19 | 24 | 0.0027154 | 0.00068055 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-24_0_4_load_20 | 25 | 0.0015136 | 0.00037935 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-24_0_4_load_22 | 27 | 0.0012349 | 0.00030949 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-24_0_4_load_23 | 28 | 0.0025368 | 0.00063579 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-24_0_4_load_24 | 29 | 0.0020606 | 0.00051644 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-24_0_4_load_67 | 31 | 0.0020439 | 0.00051225 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-24_0_4_load_42 | 32 | 0.003417 | 0.00085638 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-24_0_4_load_31 | 35 | 0.016333 | 0.0040936 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-24_0_4_load_48 | 36 | 0.0017469 | 0.00043782 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-24_0_4_load_47 | 37 | 0.0023156 | 0.00058033 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-24_0_4_load_68 | 38 | 0.0016316 | 0.00040892 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-24_0_4_load_40 | 39 | 0.0014854 | 0.00037229 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-24_0_4_load_54 | 41 | 0.0011706 | 0.00029339 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-24_0_4_load_178 | 42 | 0.0011122 | 0.00027875 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-24_0_4_load_32 | 43 | 0.0079563 | 0.001994 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-24_0_4_load_51 | 44 | 0.0016718 | 0.000419 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-24_0_4_load_35 | 46 | 0.0064956 | 0.0016279 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-24_0_4_load_36 | 47 | 0.003296 | 0.00082607 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-24_0_4_load_37 | 48 | 0.0011231 | 0.00028149 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-24_0_4_load_38 | 49 | 0.002804 | 0.00070274 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-24_0_4_load_39 | 50 | 0.0017716 | 0.00044402 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-24_0_4_load_50 | 51 | 0.0022199 | 0.00055637 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-24_0_4_load_53 | 52 | 0.0014212 | 0.00035618 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-24_0_4_load_52 | 53 | 0.0080134 | 0.0020083 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-24_0_4_load_41 | 54 | 0.00195 | 0.00048872 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-24_0_4_load_44 | 56 | 0.0020943 | 0.00052489 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-24_0_4_load_45 | 57 | 0.0033958 | 0.00085108 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-24_0_4_load_78 | 58 | 0.003705 | 0.00092857 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-24_0_4_load_46 | 59 | 0.0012134 | 0.00030412 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-24_0_4_load_77 | 61 | 0.0017269 | 0.0004328 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-24_0_4_load_139 | 62 | 0.00169 | 0.00042357 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-24_0_4_load_137 | 63 | 0.0020278 | 0.00050823 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-24_0_4_load_60 | 64 | 0.0012168 | 0.00030495 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-24_0_4_load_61 | 65 | 0.0022437 | 0.00056231 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-24_0_4_load_62 | 66 | 0.0078842 | 0.001976 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-24_0_4_load_63 | 67 | 0.0019835 | 0.00049712 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-24_0_4_load_64 | 68 | 0.0028377 | 0.00071119 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-24_0_4_load_80 | 69 | 0.001071 | 0.00026841 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-24_0_4_load_79 | 70 | 0.0023632 | 0.00059228 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-24_0_4_load_81 | 71 | 0.00086454 | 0.00021667 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-24_0_4_load_70 | 72 | 0.0016042 | 0.00040205 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-24_0_4_load_169 | 73 | 0.0022361 | 0.00056041 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-24_0_4_load_144 | 74 | 0.0027842 | 0.00069779 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-24_0_4_load_123 | 76 | 0.0024565 | 0.00061566 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-24_0_4_load_124 | 77 | 0.0030757 | 0.00077083 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-24_0_4_load_133 | 78 | 0.002915 | 0.00073056 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_161-24_0_4_load_154 | 79 | 0.002263 | 0.00056717 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_161-24_0_4_load_132 | 80 | 0.0033018 | 0.00082751 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_161-24_0_4_load_155 | 81 | 0.0038005 | 0.00095249 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_161-24_0_4_load_125 | 82 | 0.0041744 | 0.0010462 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_161-24_0_4_load_126 | 83 | 0.0034805 | 0.0008723 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_161-24_0_4_load_128 | 85 | 0.0032485 | 0.00081416 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_161-24_0_4_load_129 | 86 | 0.0025285 | 0.00063369 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_161-24_0_4_load_130 | 87 | 0.0056396 | 0.0014134 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_161-24_0_4_load_131 | 88 | 0.002446 | 0.00061302 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_161-24_0_4_load_147 | 89 | 0.0020351 | 0.00051004 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_161-24_0_4_load_148 | 90 | 0.0045413 | 0.0011382 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_161-24_0_4_load_163 | 91 | 0.0016874 | 0.00042291 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_161-24_0_4_load_161 | 92 | 0.0036372 | 0.00091157 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_161-24_0_4_load_140 | 93 | 0.0041891 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_161-24_0_4_load_143 | 96 | 0.0015402 | 0.000386 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_161-24_0_4_load_145 | 97 | 0.0042943 | 0.0010763 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_161-24_0_4_load_164 | 98 | 0.0024319 | 0.00060949 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_161-24_0_4_load_165 | 101 | 0.0042212 | 0.0010579 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_161-24_0_4_load_153 | 102 | 0.0020479 | 0.00051325 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_161-24_0_4_load_149 | 103 | 0.0022564 | 0.00056551 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_161-24_0_4_load_150 | 104 | 0.0022703 | 0.00056898 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_161-24_0_4_load_152 | 105 | 0.0015776 | 0.00039539 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_161-24_0_4_load_171 | 107 | 0.0023901 | 0.00059902 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_161-24_0_4_load_160 | 109 | 0.0014904 | 0.00037352 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_161-24_0_4_load_172 | 110 | 0.0019594 | 0.00049106 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_161-24_0_4_load_175 | 111 | 0.0029186 | 0.00073147 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_161-24_0_4_load_174 | 112 | 0.001206 | 0.00030226 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_161-24_0_4_load_162 | 113 | 0.0055258 | 0.0013849 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_161-24_0_4_load_176 | 114 | 0.0022871 | 0.0005732 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_161-24_0_4_load_167 | 115 | 0.0037358 | 0.00093628 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_161-24_0_4_load_177 | 116 | 0.0024188 | 0.00060621 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_161-24_0_4_load_191 | 117 | 0.001857 | 0.00046542 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_161-24_0_4_load_195 | 118 | 0.0018286 | 0.00045829 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 55 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-24_0_4_line_0 |  | 0 | 1 | 0.023544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-24_0_4_line_1 |  | 1 | 2 | 0.044113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-24_0_4_line_2 |  | 2 | 6 | 0.020931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_161-24_0_4_line_3 |  | 3 | 4 | 0.020907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-24_0_4_line_4 |  | 3 | 5 | 0.013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_161-24_0_4_line_5 |  | 4 | 7 | 0.0084173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_161-24_0_4_line_6 |  | 5 | 8 | 0.016134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-24_0_4_line_7 |  | 6 | 9 | 0.040579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_161-24_0_4_line_8 |  | 8 | 10 | 0.013859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_161-24_0_4_line_9 |  | 9 | 11 | 0.019001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-24_0_4_line_10 |  | 10 | 23 | 0.023377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-24_0_4_line_11 |  | 11 | 20 | 0.0087561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_161-24_0_4_line_12 |  | 12 | 13 | 0.014438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_161-24_0_4_line_13 |  | 12 | 14 | 0.025736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-24_0_4_line_14 |  | 13 | 21 | 0.02529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-24_0_4_line_15 |  | 14 | 23 | 0.0096392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-24_0_4_line_16 |  | 15 | 16 | 0.038931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_161-24_0_4_line_17 |  | 15 | 17 | 0.046415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_161-24_0_4_line_18 |  | 15 | 18 | 0.053148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-24_0_4_line_19 |  | 16 | 19 | 0.032087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-24_0_4_line_20 |  | 17 | 22 | 0.024763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-24_0_4_line_21 |  | 18 | 36 | 0.013408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-24_0_4_line_22 |  | 18 | 37 | 0.0015041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-24_0_4_line_23 |  | 19 | 21 | 0.00285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_161-24_0_4_line_24 |  | 20 | 118 | 0.00875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_161-24_0_4_line_25 |  | 21 | 117 | 0.0099527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_161-24_0_4_line_26 |  | 24 | 25 | 0.017928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_161-24_0_4_line_27 |  | 24 | 26 | 0.026162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_161-24_0_4_line_28 |  | 25 | 27 | 0.0097877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_161-24_0_4_line_29 |  | 26 | 28 | 0.014631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_161-24_0_4_line_30 |  | 26 | 29 | 0.01927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_161-24_0_4_line_31 |  | 27 | 30 | 0.015052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_161-24_0_4_line_32 |  | 28 | 31 | 0.03277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_161-24_0_4_line_33 |  | 29 | 32 | 0.020591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-24_0_4_line_34 |  | 30 | 36 | 0.0066752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_161-24_0_4_line_35 |  | 31 | 38 | 0.021908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_161-24_0_4_line_36 |  | 32 | 39 | 0.00037516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_161-24_0_4_line_37 |  | 33 | 34 | 0.008927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_161-24_0_4_line_38 |  | 33 | 35 | 0.01751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_161-24_0_4_line_39 |  | 34 | 37 | 0.015254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-24_0_4_line_40 |  | 35 | 43 | 0.021404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_161-24_0_4_line_41 |  | 38 | 72 | 0.022648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_161-24_0_4_line_42 |  | 39 | 54 | 0.0086212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_161-24_0_4_line_43 |  | 40 | 41 | 0.019676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_161-24_0_4_line_44 |  | 40 | 42 | 0.011856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_161-24_0_4_line_45 |  | 41 | 44 | 0.013881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_161-24_0_4_line_46 |  | 42 | 45 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_161-24_0_4_line_47 |  | 44 | 51 | 0.0010948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-24_0_4_line_48 |  | 45 | 116 | 0.010378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-24_0_4_line_49 |  | 46 | 47 | 0.0043008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-24_0_4_line_50 |  | 46 | 48 | 0.0022201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-24_0_4_line_51 |  | 47 | 49 | 0.019954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-24_0_4_line_52 |  | 48 | 50 | 0.010678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-24_0_4_line_53 |  | 49 | 51 | 0.0069068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-24_0_4_line_54 |  | 50 | 52 | 0.023028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_161-24_0_4_line_55 |  | 52 | 53 | 0.0052176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_161-24_0_4_line_56 |  | 53 | 56 | 0.02393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_161-24_0_4_line_57 |  | 54 | 55 | 0.016211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-24_0_4_line_58 |  | 55 | 56 | 0.018262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_161-24_0_4_line_59 |  | 55 | 57 | 0.017534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-24_0_4_line_60 |  | 57 | 58 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-24_0_4_line_61 |  | 58 | 61 | 0.0060825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-24_0_4_line_62 |  | 59 | 60 | 0.015472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-24_0_4_line_63 |  | 60 | 62 | 0.0076726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-24_0_4_line_64 |  | 60 | 63 | 0.015048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_161-24_0_4_line_65 |  | 61 | 70 | 0.0045715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_161-24_0_4_line_66 |  | 62 | 91 | 0.009681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_161-24_0_4_line_67 |  | 63 | 85 | 0.0018162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-24_0_4_line_68 |  | 64 | 65 | 0.017991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-24_0_4_line_69 |  | 64 | 66 | 0.0025339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-24_0_4_line_70 |  | 65 | 67 | 0.0076543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_161-24_0_4_line_71 |  | 66 | 68 | 0.016792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_161-24_0_4_line_72 |  | 67 | 69 | 0.0010605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-24_0_4_line_73 |  | 68 | 70 | 0.0036277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-24_0_4_line_74 |  | 69 | 71 | 0.0077231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-24_0_4_line_75 |  | 73 | 74 | 0.002224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_161-24_0_4_line_76 |  | 74 | 94 | 0.02322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_161-24_0_4_line_77 |  | 75 | 76 | 0.0066824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_161-24_0_4_line_78 |  | 75 | 77 | 0.016972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_161-24_0_4_line_79 |  | 76 | 78 | 0.0090244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_161-24_0_4_line_80 |  | 77 | 79 | 0.01822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_161-24_0_4_line_81 |  | 78 | 80 | 0.0016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_161-24_0_4_line_82 |  | 79 | 81 | 0.0080494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_161-24_0_4_line_83 |  | 80 | 88 | 0.020221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_161-24_0_4_line_84 |  | 82 | 83 | 0.00095895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_161-24_0_4_line_85 |  | 82 | 84 | 0.016675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_161-24_0_4_line_86 |  | 83 | 85 | 0.024658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_161-24_0_4_line_87 |  | 84 | 86 | 0.0071261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_161-24_0_4_line_88 |  | 84 | 87 | 0.016839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_161-24_0_4_line_89 |  | 86 | 88 | 0.0088463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_161-24_0_4_line_90 |  | 87 | 89 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_161-24_0_4_line_91 |  | 89 | 90 | 0.020668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_161-24_0_4_line_92 |  | 91 | 92 | 0.01865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_161-24_0_4_line_93 |  | 92 | 113 | 0.023715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_161-24_0_4_line_94 |  | 93 | 94 | 0.01885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_161-24_0_4_line_95 |  | 93 | 95 | 0.017327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_161-24_0_4_line_96 |  | 94 | 96 | 0.0082725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_161-24_0_4_line_97 |  | 95 | 97 | 0.0022313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_161-24_0_4_line_98 |  | 96 | 98 | 0.00083273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_161-24_0_4_line_99 |  | 97 | 99 | 0.0038416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_161-24_0_4_line_100 |  | 98 | 101 | 0.007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_161-24_0_4_line_101 |  | 99 | 100 | 0.019273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_161-24_0_4_line_102 |  | 100 | 102 | 0.014952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_161-24_0_4_line_103 |  | 100 | 103 | 0.017002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_161-24_0_4_line_104 |  | 101 | 115 | 0.021127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_161-24_0_4_line_105 |  | 102 | 107 | 0.01005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_161-24_0_4_line_106 |  | 103 | 104 | 0.014117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_161-24_0_4_line_107 |  | 104 | 105 | 0.0089231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_161-24_0_4_line_108 |  | 105 | 106 | 0.027246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_161-24_0_4_line_109 |  | 106 | 108 | 0.004204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_161-24_0_4_line_110 |  | 106 | 109 | 0.017033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_161-24_0_4_line_111 |  | 107 | 110 | 0.028862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_161-24_0_4_line_112 |  | 108 | 111 | 0.017284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_161-24_0_4_line_113 |  | 108 | 112 | 0.0098919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_161-24_0_4_line_114 |  | 109 | 113 | 0.0022227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_161-24_0_4_line_115 |  | 111 | 114 | 0.027802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_161-24_0_4_line_116 |  | 114 | 116 | 0.00059448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_161-24_0_4_line_117 |  | 117 | 118 | 0.0087838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-24_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 119 | 55 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2687335.9333 | 1244615.5848 | 2687346.6353 | 1244636.5555
1 | 2687346.6353 | 1244636.5555 | 2687361.0941 | 1244664.8876 | 2687350.245 | 1244670.6928
2 | 2687331.7903 | 1244680.5678 | 2687350.245 | 1244670.6928
3 | 2687315.634 | 1244575.8082 | 2687300.6485 | 1244589.609 | 2687300.2521 | 1244589.9687
4 | 2687315.634 | 1244575.8082 | 2687324.3107 | 1244585.6694
5 | 2687294.0187 | 1244595.6252 | 2687300.2521 | 1244589.9687
6 | 2687334.9683 | 1244597.782 | 2687324.3107 | 1244585.6694
7 | 2687331.7903 | 1244680.5678 | 2687335.9793 | 1244689.1358 | 2687349.0465 | 1244717.2934
8 | 2687334.9683 | 1244597.782 | 2687344.123 | 1244608.1865
9 | 2687349.0465 | 1244717.2934 | 2687365.6213 | 1244708.0033
10 | 2687358.9365 | 1244626.2664 | 2687347.0158 | 1244611.4742 | 2687344.123 | 1244608.1865
11 | 2687365.6213 | 1244708.0033 | 2687373.2594 | 1244703.7221
12 | 2687379.1392 | 1244655.2574 | 2687383.8879 | 1244668.8924
13 | 2687379.1392 | 1244655.2574 | 2687365.8965 | 1244634.9029 | 2687364.9849 | 1244633.7718
14 | 2687397.2365 | 1244690.2831 | 2687384.7873 | 1244671.4747 | 2687383.8879 | 1244668.8924
15 | 2687358.9365 | 1244626.2664 | 2687364.9849 | 1244633.7718
16 | 2687450.168 | 1244708.1763 | 2687445.9256 | 1244709.3924 | 2687413.3257 | 1244721.0429
17 | 2687450.168 | 1244708.1763 | 2687449.5749 | 1244689.4648 | 2687443.7604 | 1244678.3931 | 2687432.174 | 1244668.573
18 | 2687450.168 | 1244708.1763 | 2687466.1349 | 1244703.1524 | 2687468.1013 | 1244693.83 | 2687469.5545 | 1244688.0472 | 2687473.9598 | 1244667.597
19 | 2687413.3257 | 1244721.0429 | 2687409.9938 | 1244710.7417 | 2687398.7445 | 1244692.7015
20 | 2687414.0109 | 1244651.8047 | 2687419.6741 | 1244657.9787 | 2687432.174 | 1244668.573
21 | 2687473.9598 | 1244667.597 | 2687462.4129 | 1244660.7813
22 | 2687473.9598 | 1244667.597 | 2687475.329 | 1244668.2195
23 | 2687397.2365 | 1244690.2831 | 2687398.7445 | 1244692.7015
24 | 2687380.8922 | 1244699.444 | 2687373.2594 | 1244703.7221
25 | 2687397.2365 | 1244690.2831 | 2687388.5545 | 1244695.1493
26 | 2687437.7522 | 1244644.1606 | 2687428.225 | 1244634.6764 | 2687425.1711 | 1244631.3914
27 | 2687407.3576 | 1244612.2301 | 2687425.1711 | 1244631.3914
28 | 2687437.7522 | 1244644.1606 | 2687442.4878 | 1244648.8748 | 2687444.9164 | 1244650.8105
29 | 2687407.3576 | 1244612.2301 | 2687397.6137 | 1244601.3157
30 | 2687407.3576 | 1244612.2301 | 2687411.287 | 1244608.6743 | 2687422.7769 | 1244600.7267
31 | 2687456.6873 | 1244660.1925 | 2687444.9164 | 1244650.8105
32 | 2687397.6137 | 1244601.3157 | 2687375.7898 | 1244576.8701
33 | 2687439.7115 | 1244589.0132 | 2687422.7769 | 1244600.7267
34 | 2687456.6873 | 1244660.1925 | 2687459.2097 | 1244658.773 | 2687462.0774 | 1244660.5833 | 2687462.4129 | 1244660.7813
35 | 2687375.7898 | 1244576.8701 | 2687361.1999 | 1244560.5275
36 | 2687440.02 | 1244588.7998 | 2687439.7115 | 1244589.0132
37 | 2687494.4615 | 1244678.941 | 2687486.0422 | 1244675.9035
38 | 2687494.4615 | 1244678.941 | 2687498.7874 | 1244674.6349 | 2687501.4992 | 1244674.7194 | 2687510.1863 | 1244675.0352
39 | 2687486.0422 | 1244675.9035 | 2687486.3419 | 1244672.4943 | 2687484.9596 | 1244671.9402 | 2687480.153 | 1244670.4126 | 2687475.329 | 1244668.2195
40 | 2687531.5763 | 1244675.8126 | 2687510.1863 | 1244675.0352
41 | 2687344.7574 | 1244544.9615 | 2687360.17 | 1244559.3739 | 2687361.1999 | 1244560.5275
42 | 2687440.02 | 1244588.7998 | 2687447.1103 | 1244583.8955
43 | 2687598.1809 | 1244607.6076 | 2687580.2062 | 1244611.9232 | 2687579.0367 | 1244612.1464
44 | 2687598.1809 | 1244607.6076 | 2687595.6054 | 1244596.0351
45 | 2687565.2976 | 1244613.9143 | 2687571.8241 | 1244613.5229 | 2687579.0367 | 1244612.1464
46 | 2687593.0712 | 1244584.6485 | 2687595.6054 | 1244596.0351
47 | 2687565.2976 | 1244613.9143 | 2687564.2047 | 1244613.9799
48 | 2687593.0712 | 1244584.6485 | 2687591.2955 | 1244575.4266 | 2687591.2612 | 1244574.4406
49 | 2687537.4498 | 1244612.8579 | 2687533.2092 | 1244612.141
50 | 2687531.0337 | 1244611.7061 | 2687531.8394 | 1244611.9095 | 2687533.2092 | 1244612.141
51 | 2687537.4498 | 1244612.8579 | 2687543.803 | 1244613.9319 | 2687557.3087 | 1244614.2955
52 | 2687520.6802 | 1244609.0931 | 2687531.0337 | 1244611.7061
53 | 2687557.3087 | 1244614.2955 | 2687558.4358 | 1244614.3259 | 2687564.2047 | 1244613.9799
54 | 2687498.8499 | 1244601.7891 | 2687518.1285 | 1244608.4491 | 2687520.6802 | 1244609.0931
55 | 2687498.8499 | 1244601.7891 | 2687493.9183 | 1244600.0854
56 | 2687474.0675 | 1244586.8333 | 2687477.4944 | 1244589.8917 | 2687493.6842 | 1244600.0046 | 2687493.9183 | 1244600.0854
57 | 2687460.4427 | 1244574.6735 | 2687447.1103 | 1244583.8955
58 | 2687460.4427 | 1244574.6735 | 2687474.0675 | 1244586.8333
59 | 2687460.4427 | 1244574.6735 | 2687448.617 | 1244561.7284
60 | 2687437.0685 | 1244549.0867 | 2687448.617 | 1244561.7284
61 | 2687432.9661 | 1244544.5959 | 2687437.0685 | 1244549.0867
62 | 2687507.4224 | 1244543.7545 | 2687494.4986 | 1244552.2601
63 | 2687507.4224 | 1244543.7545 | 2687514.6082 | 1244541.0651
64 | 2687507.4224 | 1244543.7545 | 2687500.3074 | 1244530.4947
65 | 2687432.9661 | 1244544.5959 | 2687429.8828 | 1244541.2207
66 | 2687523.675 | 1244537.6718 | 2687514.6082 | 1244541.0651
67 | 2687499.4487 | 1244528.8944 | 2687500.3074 | 1244530.4947
68 | 2687414.4016 | 1244524.2741 | 2687402.2676 | 1244510.9915
69 | 2687414.4016 | 1244524.2741 | 2687416.1106 | 1244526.1448
70 | 2687402.2676 | 1244510.9915 | 2687402.2676 | 1244510.9915 | 2687396.3265 | 1244506.1652
71 | 2687427.4361 | 1244538.5424 | 2687416.1106 | 1244526.1448
72 | 2687395.5034 | 1244505.4966 | 2687396.3265 | 1244506.1652
73 | 2687427.4361 | 1244538.5424 | 2687429.8828 | 1244541.2207
74 | 2687395.5034 | 1244505.4966 | 2687389.509 | 1244500.6269
75 | 2687562.3426 | 1244399.6172 | 2687560.4845 | 1244400.8394
76 | 2687541.0853 | 1244413.5994 | 2687560.4845 | 1244400.8394
77 | 2687437.413 | 1244456.9694 | 2687442.5524 | 1244461.2403
78 | 2687437.413 | 1244456.9694 | 2687448.3384 | 1244443.9817
79 | 2687442.5524 | 1244461.2403 | 2687443.3933 | 1244461.939 | 2687449.1529 | 1244467.3915
80 | 2687460.0672 | 1244430.039 | 2687448.3384 | 1244443.9817
81 | 2687450.3747 | 1244468.5482 | 2687449.1529 | 1244467.3915
82 | 2687460.0672 | 1244430.039 | 2687460.0672 | 1244430.039 | 2687466.4213 | 1244434.9805
83 | 2687465.0589 | 1244482.4496 | 2687450.3747 | 1244468.5482
84 | 2687486.7915 | 1244506.6736 | 2687487.3742 | 1244507.4352
85 | 2687476.6579 | 1244493.4304 | 2687486.7915 | 1244506.6736
86 | 2687499.4487 | 1244528.8944 | 2687489.2478 | 1244509.8837 | 2687487.3742 | 1244507.4352
87 | 2687476.6579 | 1244493.4304 | 2687471.483 | 1244488.5313
88 | 2687476.6579 | 1244493.4304 | 2687489.3027 | 1244482.3102
89 | 2687465.0589 | 1244482.4496 | 2687471.483 | 1244488.5313
90 | 2687489.3027 | 1244482.3102 | 2687502.6224 | 1244470.5964
91 | 2687517.2038 | 1244485.2444 | 2687502.6224 | 1244470.5964
92 | 2687523.675 | 1244537.6718 | 2687525.9726 | 1244536.8119 | 2687542.0423 | 1244534.7845
93 | 2687565.5705 | 1244531.8162 | 2687542.0423 | 1244534.7845
94 | 2687541.0853 | 1244413.5994 | 2687555.2206 | 1244426.0701
95 | 2687566.4656 | 1244439.0594 | 2687561.5044 | 1244431.614 | 2687555.2206 | 1244426.0701
96 | 2687541.0853 | 1244413.5994 | 2687534.953 | 1244408.047
97 | 2687566.4656 | 1244439.0594 | 2687567.5841 | 1244440.9901
98 | 2687534.953 | 1244408.047 | 2687534.3357 | 1244407.4881
99 | 2687569.4026 | 1244444.3733 | 2687568.0575 | 1244441.8071 | 2687567.5841 | 1244440.9901
100 | 2687534.3357 | 1244407.4881 | 2687529.1467 | 1244402.7897
101 | 2687574.7449 | 1244462.8547 | 2687571.8622 | 1244450.7921 | 2687569.4026 | 1244444.3733
102 | 2687574.7449 | 1244462.8547 | 2687589.4415 | 1244460.1051
103 | 2687574.7449 | 1244462.8547 | 2687577.254 | 1244479.6707
104 | 2687513.4856 | 1244388.6096 | 2687529.1467 | 1244402.7897
105 | 2687599.3198 | 1244458.2569 | 2687589.4415 | 1244460.1051
106 | 2687579.3373 | 1244493.6332 | 2687577.254 | 1244479.6707
107 | 2687579.3373 | 1244493.6332 | 2687580.6541 | 1244502.4586
108 | 2687584.6748 | 1244529.406 | 2687580.6541 | 1244502.4586
109 | 2687584.6748 | 1244529.406 | 2687588.8547 | 1244528.8562
110 | 2687584.6748 | 1244529.406 | 2687567.7757 | 1244531.538
111 | 2687599.3198 | 1244458.2569 | 2687627.6893 | 1244452.9492
112 | 2687588.8547 | 1244528.8562 | 2687589.9644 | 1244537.1231 | 2687590.275 | 1244546.061
113 | 2687588.8547 | 1244528.8562 | 2687598.6659 | 1244527.5953
114 | 2687565.5705 | 1244531.8162 | 2687567.7757 | 1244531.538
115 | 2687590.275 | 1244546.061 | 2687591.2405 | 1244573.8465
116 | 2687591.2612 | 1244574.4406 | 2687591.2405 | 1244573.8465
117 | 2687388.5545 | 1244695.1493 | 2687380.8922 | 1244699.444

## bus_geodata
| x | y | coords
0 | 2687335.9333 | 1244615.5848
1 | 2687346.6353 | 1244636.5555
2 | 2687350.245 | 1244670.6928
3 | 2687315.634 | 1244575.8082
4 | 2687300.2521 | 1244589.9687
5 | 2687324.3107 | 1244585.6694
6 | 2687331.7903 | 1244680.5678
7 | 2687294.0187 | 1244595.6252
8 | 2687334.9683 | 1244597.782
9 | 2687349.0465 | 1244717.2934
10 | 2687344.123 | 1244608.1865
11 | 2687365.6213 | 1244708.0033
12 | 2687379.1392 | 1244655.2574
13 | 2687383.8879 | 1244668.8924
14 | 2687364.9849 | 1244633.7718
15 | 2687450.168 | 1244708.1763
16 | 2687413.3257 | 1244721.0429
17 | 2687432.174 | 1244668.573
18 | 2687473.9598 | 1244667.597
19 | 2687398.7445 | 1244692.7015
20 | 2687373.2594 | 1244703.7221
21 | 2687397.2365 | 1244690.2831
22 | 2687414.0109 | 1244651.8047
23 | 2687358.9365 | 1244626.2664
24 | 2687425.1711 | 1244631.3914
25 | 2687437.7522 | 1244644.1606
26 | 2687407.3576 | 1244612.2301
27 | 2687444.9164 | 1244650.8105
28 | 2687397.6137 | 1244601.3157
29 | 2687422.7769 | 1244600.7267
30 | 2687456.6873 | 1244660.1925
31 | 2687375.7898 | 1244576.8701
32 | 2687439.7115 | 1244589.0132
33 | 2687494.4615 | 1244678.941
34 | 2687486.0422 | 1244675.9035
35 | 2687510.1863 | 1244675.0352
36 | 2687462.4129 | 1244660.7813
37 | 2687475.329 | 1244668.2195
38 | 2687361.1999 | 1244560.5275
39 | 2687440.02 | 1244588.7998
40 | 2687598.1809 | 1244607.6076
41 | 2687579.0367 | 1244612.1464
42 | 2687595.6054 | 1244596.0351
43 | 2687531.5763 | 1244675.8126
44 | 2687565.2976 | 1244613.9143
45 | 2687593.0712 | 1244584.6485
46 | 2687533.2092 | 1244612.141
47 | 2687537.4498 | 1244612.8579
48 | 2687531.0337 | 1244611.7061
49 | 2687557.3087 | 1244614.2955
50 | 2687520.6802 | 1244609.0931
51 | 2687564.2047 | 1244613.9799
52 | 2687498.8499 | 1244601.7891
53 | 2687493.9183 | 1244600.0854
54 | 2687447.1103 | 1244583.8955
55 | 2687460.4427 | 1244574.6735
56 | 2687474.0675 | 1244586.8333
57 | 2687448.617 | 1244561.7284
58 | 2687437.0685 | 1244549.0867
59 | 2687494.4986 | 1244552.2601
60 | 2687507.4224 | 1244543.7545
61 | 2687432.9661 | 1244544.5959
62 | 2687514.6082 | 1244541.0651
63 | 2687500.3074 | 1244530.4947
64 | 2687414.4016 | 1244524.2741
65 | 2687402.2676 | 1244510.9915
66 | 2687416.1106 | 1244526.1448
67 | 2687396.3265 | 1244506.1652
68 | 2687427.436 | 1244538.5424
69 | 2687395.5034 | 1244505.4966
70 | 2687429.8828 | 1244541.2207
71 | 2687389.509 | 1244500.6269
72 | 2687344.7574 | 1244544.9615
73 | 2687562.3426 | 1244399.6172
74 | 2687560.4845 | 1244400.8394
75 | 2687437.413 | 1244456.9694
76 | 2687442.5524 | 1244461.2403
77 | 2687448.3384 | 1244443.9817
78 | 2687449.1529 | 1244467.3915
79 | 2687460.0672 | 1244430.039
80 | 2687450.3747 | 1244468.5482
81 | 2687466.4213 | 1244434.9805
82 | 2687486.7915 | 1244506.6736
83 | 2687487.3742 | 1244507.4352
84 | 2687476.6579 | 1244493.4304
85 | 2687499.4487 | 1244528.8944
86 | 2687471.483 | 1244488.5313
87 | 2687489.3027 | 1244482.3102
88 | 2687465.0589 | 1244482.4496
89 | 2687502.6224 | 1244470.5964
90 | 2687517.2038 | 1244485.2444
91 | 2687523.675 | 1244537.6718
92 | 2687542.0423 | 1244534.7845
93 | 2687555.2206 | 1244426.0701
94 | 2687541.0853 | 1244413.5994
95 | 2687566.4656 | 1244439.0594
96 | 2687534.953 | 1244408.047
97 | 2687567.5841 | 1244440.9901
98 | 2687534.3357 | 1244407.4881
99 | 2687569.4026 | 1244444.3733
100 | 2687574.7449 | 1244462.8547
101 | 2687529.1467 | 1244402.7897
102 | 2687589.4415 | 1244460.1051
103 | 2687577.254 | 1244479.6707
104 | 2687579.3373 | 1244493.6332
105 | 2687580.6541 | 1244502.4586
106 | 2687584.6748 | 1244529.406
107 | 2687599.3198 | 1244458.2569
108 | 2687588.8547 | 1244528.8562
109 | 2687567.7757 | 1244531.538
110 | 2687627.6893 | 1244452.9492
111 | 2687590.275 | 1244546.061
112 | 2687598.6659 | 1244527.5953
113 | 2687565.5705 | 1244531.8162
114 | 2687591.2405 | 1244573.8465
115 | 2687513.4856 | 1244388.6096
116 | 2687591.2612 | 1244574.4406
117 | 2687388.5545 | 1244695.1493
118 | 2687380.8922 | 1244699.444
119 | 2687507.4224 | 1244543.7545

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97499 | -0.48203 | 0.0077554 | 0.0019437
1 | 0.97516 | -0.47868 | 0.0084556 | 0.0021192
2 | 0.97582 | -0.46558 | 0.0068215 | 0.0017096
3 | 0.9754 | -0.474 | 0.0015622 | 0.00039154
4 | 0.97515 | -0.47891 | 0.0052791 | 0.0013231
5 | 0.97557 | -0.47054 | 0.0028366 | 0.00071092
6 | 0.97627 | -0.45676 | 0 | 0
7 | 0.97509 | -0.48007 | 0.0075255 | 0.0018861
8 | 0.97583 | -0.46546 | 0.0029355 | 0.00073572
9 | 0.97714 | -0.43968 | 0 | 0
10 | 0.97609 | -0.46035 | 0.0016075 | 0.00040288
11 | 0.97755 | -0.4317 | 0.0018199 | 0.00045611
12 | 0.97743 | -0.43394 | 0 | 0
13 | 0.9778 | -0.42677 | 0.0018128 | 0.00045434
14 | 0.97678 | -0.44673 | 0.0026709 | 0.0006694
15 | 0.98264 | -0.33225 | 0 | 0
16 | 0.98045 | -0.37496 | 0 | 0
17 | 0.98254 | -0.33427 | 0.0012206 | 0.00030592
18 | 0.98576 | -0.27194 | 0 | 0
19 | 0.97864 | -0.41031 | 0.0012172 | 0.00030505
20 | 0.97775 | -0.42773 | 0.0018445 | 0.00046226
21 | 0.97848 | -0.41339 | 0 | 0
22 | 0.98251 | -0.3348 | 0.0011892 | 0.00029804
23 | 0.97656 | -0.45106 | 0.0028045 | 0.00070287
24 | 0.99112 | -0.16876 | 0.0027154 | 0.00068055
25 | 0.98955 | -0.19876 | 0.0015136 | 0.00037935
26 | 0.99346 | -0.12389 | 0 | 0
27 | 0.98871 | -0.21492 | 0.0012349 | 0.00030949
28 | 0.99336 | -0.12592 | 0.0025368 | 0.00063579
29 | 0.99533 | -0.088331 | 0.0020606 | 0.00051644
30 | 0.98744 | -0.23949 | 0 | 0
31 | 0.9932 | -0.12897 | 0.0020439 | 0.00051225
32 | 0.99737 | -0.049733 | 0.003417 | 0.00085638
33 | 0.98518 | -0.2832 | 0 | 0
34 | 0.98538 | -0.27931 | 0 | 0
35 | 0.98479 | -0.29084 | 0.016333 | 0.0040936
36 | 0.98687 | -0.2504 | 0.0017469 | 0.00043782
37 | 0.98572 | -0.27266 | 0.0023156 | 0.00058033
38 | 0.99314 | -0.13023 | 0.0016316 | 0.00040892
39 | 0.99741 | -0.049009 | 0.0014854 | 0.00037229
40 | 0.98689 | -0.24902 | 0 | 0
41 | 0.98892 | -0.20999 | 0.0011706 | 0.00029339
42 | 0.98566 | -0.27261 | 0.0011122 | 0.00027875
43 | 0.98463 | -0.2939 | 0.0079563 | 0.001994
44 | 0.99038 | -0.18226 | 0.0016718 | 0.000419
45 | 0.98447 | -0.29565 | 0 | 0
46 | 0.99394 | -0.11451 | 0.0064956 | 0.0016279
47 | 0.99345 | -0.12379 | 0.003296 | 0.00082607
48 | 0.9942 | -0.10947 | 0.0011231 | 0.00028149
49 | 0.99124 | -0.1658 | 0.002804 | 0.00070274
50 | 0.99549 | -0.085053 | 0.0017716 | 0.00044402
51 | 0.99049 | -0.18004 | 0.0022199 | 0.00055637
52 | 0.9969 | -0.058434 | 0.0014212 | 0.00035618
53 | 0.99722 | -0.052348 | 0.0080134 | 0.0020083
54 | 0.9983 | -0.032157 | 0.00195 | 0.00048872
55 | 1 | 0 | -0.29242 | -0.074701
56 | 0.99879 | -0.022812 | 0.0020943 | 0.00052489
57 | 0.99953 | -0.0089568 | 0.0033958 | 0.00085108
58 | 0.99913 | -0.016696 | 0.003705 | 0.00092857
59 | 0.97447 | -0.49076 | 0.0012134 | 0.00030412
60 | 0.97448 | -0.49041 | 0 | 0
61 | 0.99901 | -0.019054 | 0.0017269 | 0.0004328
62 | 0.97483 | -0.48349 | 0.00169 | 0.00042357
63 | 0.97381 | -0.50366 | 0.0020278 | 0.00050823
64 | 0.99861 | -0.026641 | 0.0012168 | 0.00030495
65 | 0.99851 | -0.028579 | 0.0022437 | 0.00056231
66 | 0.99863 | -0.026314 | 0.0078842 | 0.001976
67 | 0.99849 | -0.029103 | 0.0019835 | 0.00049712
68 | 0.99886 | -0.021835 | 0.0028377 | 0.00071119
69 | 0.99848 | -0.029139 | 0.001071 | 0.00026841
70 | 0.99892 | -0.020688 | 0.0023632 | 0.00059228
71 | 0.99848 | -0.029256 | 0.00086454 | 0.00021667
72 | 0.9931 | -0.13087 | 0.0016042 | 0.00040205
73 | 0.97503 | -0.47993 | 0.0022361 | 0.00056041
74 | 0.97503 | -0.47984 | 0.0027842 | 0.00069779
75 | 0.97134 | -0.55247 | 0 | 0
76 | 0.9714 | -0.55134 | 0.0024565 | 0.00061566
77 | 0.97119 | -0.55534 | 0.0030757 | 0.00077083
78 | 0.97149 | -0.54941 | 0.002915 | 0.00073056
79 | 0.97109 | -0.55738 | 0.002263 | 0.00056717
80 | 0.97152 | -0.54896 | 0.0033018 | 0.00082751
81 | 0.97106 | -0.55794 | 0.0038005 | 0.00095249
82 | 0.97272 | -0.52525 | 0.0041744 | 0.0010462
83 | 0.97275 | -0.52456 | 0.0034805 | 0.0008723
84 | 0.97217 | -0.53601 | 0 | 0
85 | 0.97373 | -0.5052 | 0.0032485 | 0.00081416
86 | 0.97202 | -0.539 | 0.0025285 | 0.00063369
87 | 0.97198 | -0.5398 | 0.0056396 | 0.0014134
88 | 0.97185 | -0.54231 | 0.002446 | 0.00061302
89 | 0.97187 | -0.54195 | 0.0020351 | 0.00051004
90 | 0.97178 | -0.54369 | 0.0045413 | 0.0011382
91 | 0.97529 | -0.47447 | 0.0016874 | 0.00042291
92 | 0.97621 | -0.45654 | 0.0036372 | 0.00091157
93 | 0.97544 | -0.47185 | 0.0041891 | 0.0010499
94 | 0.97514 | -0.47771 | 0 | 0
95 | 0.97578 | -0.46514 | 0 | 0
96 | 0.97505 | -0.47951 | 0.0015402 | 0.000386
97 | 0.97582 | -0.46428 | 0.0042943 | 0.0010763
98 | 0.97504 | -0.47967 | 0.0024319 | 0.00060949
99 | 0.97591 | -0.46249 | 0 | 0
100 | 0.97637 | -0.45352 | 0 | 0
101 | 0.97499 | -0.48069 | 0.0042212 | 0.0010579
102 | 0.97628 | -0.45527 | 0.0020479 | 0.00051325
103 | 0.97687 | -0.44363 | 0.0022564 | 0.00056551
104 | 0.97732 | -0.43485 | 0.0022703 | 0.00056898
105 | 0.97762 | -0.42893 | 0.0015776 | 0.00039539
106 | 0.97858 | -0.41009 | 0 | 0
107 | 0.97624 | -0.45607 | 0.0023901 | 0.00059902
108 | 0.97898 | -0.40236 | 0 | 0
109 | 0.97758 | -0.4297 | 0.0014904 | 0.00037352
110 | 0.97619 | -0.45711 | 0.0019594 | 0.00049106
111 | 0.98062 | -0.37024 | 0.0029186 | 0.00073147
112 | 0.97896 | -0.40257 | 0.001206 | 0.00030226
113 | 0.97745 | -0.4322 | 0.0055258 | 0.0013849
114 | 0.98335 | -0.31735 | 0.0022871 | 0.0005732
115 | 0.97491 | -0.48214 | 0.0037358 | 0.00093628
116 | 0.98341 | -0.3162 | 0.0024188 | 0.00060621
117 | 0.9782 | -0.4189 | 0.001857 | 0.00046542
118 | 0.97797 | -0.42347 | 0.0018286 | 0.00045829
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0077554 | -0.0019437 | 0.0077567 | 0.0019442 | 1.2369e-06 | 4.9793e-07 | 0.011836 | 0.011836 | 0.011836 | 0.97499 | -0.48203 | 0.97516 | -0.47868 | 3.2517
1 | -0.016212 | -0.0040634 | 0.016222 | 0.0040693 | 1.0124e-05 | 5.9286e-06 | 0.024739 | 0.024739 | 0.024739 | 0.97516 | -0.47868 | 0.97582 | -0.46558 | 6.7964
2 | -0.023044 | -0.0057789 | 0.023054 | 0.0057849 | 9.6924e-06 | 5.9415e-06 | 0.035141 | 0.03514 | 0.035141 | 0.97582 | -0.46558 | 0.97627 | -0.45676 | 9.654
3 | 0.012808 | 0.0032109 | -0.012805 | -0.0032093 | 2.9934e-06 | 1.6549e-06 | 0.019539 | 0.01954 | 0.01954 | 0.9754 | -0.474 | 0.97515 | -0.47891 | 5.368
4 | -0.01437 | -0.0036025 | 0.014373 | 0.0036038 | 2.3673e-06 | 1.3511e-06 | 0.021923 | 0.021923 | 0.021923 | 0.9754 | -0.474 | 0.97557 | -0.47054 | 6.0227
5 | 0.0075259 | 0.0018862 | -0.0075255 | -0.0018861 | 4.1629e-07 | 1.6142e-07 | 0.011484 | 0.011484 | 0.011484 | 0.97515 | -0.47891 | 0.97509 | -0.48007 | 3.155
6 | -0.017209 | -0.0043147 | 0.017213 | 0.0043172 | 4.1687e-06 | 2.4665e-06 | 0.026249 | 0.026249 | 0.026249 | 0.97557 | -0.47054 | 0.97583 | -0.46546 | 7.2113
7 | -0.023054 | -0.0057849 | 0.023072 | 0.0057964 | 1.8791e-05 | 1.1518e-05 | 0.03514 | 0.03514 | 0.03514 | 0.97627 | -0.45676 | 0.97714 | -0.43968 | 9.654
8 | -0.020149 | -0.0050529 | 0.020154 | 0.0050559 | 4.9062e-06 | 2.9668e-06 | 0.030726 | 0.030725 | 0.030726 | 0.97583 | -0.46546 | 0.97609 | -0.46035 | 8.4411
9 | -0.023072 | -0.0057964 | 0.023081 | 0.0058018 | 8.7986e-06 | 5.393e-06 | 0.03514 | 0.03514 | 0.03514 | 0.97714 | -0.43968 | 0.97755 | -0.4317 | 9.6539
10 | -0.021761 | -0.0054588 | 0.021771 | 0.0054646 | 9.6486e-06 | 5.8828e-06 | 0.033176 | 0.033176 | 0.033176 | 0.97609 | -0.46035 | 0.97656 | -0.45106 | 9.1143
11 | -0.024901 | -0.0062579 | 0.024906 | 0.0062608 | 4.7191e-06 | 2.9104e-06 | 0.03791 | 0.03791 | 0.03791 | 0.97755 | -0.4317 | 0.97775 | -0.42773 | 10.4149
12 | -0.027268 | -0.0068504 | 0.027277 | 0.0068562 | 9.3329e-06 | 5.792e-06 | 0.041518 | 0.041518 | 0.041518 | 0.97743 | -0.43394 | 0.9778 | -0.42677 | 11.406
13 | 0.027268 | 0.0068504 | -0.027251 | -0.00684 | 1.6636e-05 | 1.0325e-05 | 0.041518 | 0.041518 | 0.041518 | 0.97743 | -0.43394 | 0.97678 | -0.44673 | 11.4061
14 | -0.02909 | -0.0073105 | 0.029109 | 0.0073221 | 1.8592e-05 | 1.1581e-05 | 0.044277 | 0.044276 | 0.044277 | 0.9778 | -0.42677 | 0.97848 | -0.41339 | 12.1639
15 | 0.02458 | 0.0061706 | -0.024575 | -0.0061675 | 5.0694e-06 | 3.1238e-06 | 0.037449 | 0.037449 | 0.037449 | 0.97678 | -0.44673 | 0.97656 | -0.45106 | 10.2882
16 | 0.061018 | 0.015437 | -0.060893 | -0.015357 | 0.00012478 | 7.9369e-05 | 0.092451 | 0.092451 | 0.092451 | 0.98264 | -0.33225 | 0.98045 | -0.37496 | 25.3988
17 | 0.0024101 | 0.00060323 | -0.0024099 | -0.00060367 | 2.3181e-07 | -4.3955e-07 | 0.0036493 | 0.0036495 | 0.0036495 | 0.98264 | -0.33225 | 0.98254 | -0.33427 | 1.0026
18 | -0.063428 | -0.01604 | 0.063612 | 0.016157 | 0.00018406 | 0.00011713 | 0.096101 | 0.0961 | 0.096101 | 0.98264 | -0.33225 | 0.98576 | -0.27194 | 26.4013
19 | 0.060893 | 0.015357 | -0.06079 | -0.015292 | 0.00010285 | 6.5417e-05 | 0.092451 | 0.092452 | 0.092452 | 0.98045 | -0.37496 | 0.97864 | -0.41031 | 25.3988
20 | 0.0011892 | 0.00029775 | -0.0011892 | -0.00029804 | 3.0121e-08 | -2.9435e-07 | 0.0018009 | 0.001801 | 0.001801 | 0.98254 | -0.33427 | 0.98251 | -0.3348 | 0.49479
21 | -0.090241 | -0.022839 | 0.090334 | 0.022898 | 9.341e-05 | 5.9612e-05 | 0.1363 | 0.1363 | 0.1363 | 0.98576 | -0.27194 | 0.98687 | -0.2504 | 37.4449
22 | 0.026629 | 0.0066819 | -0.026628 | -0.0066814 | 9.1147e-07 | 5.6417e-07 | 0.040199 | 0.040199 | 0.040199 | 0.98576 | -0.27194 | 0.98572 | -0.27266 | 11.0437
23 | 0.059573 | 0.014987 | -0.059564 | -0.014981 | 8.773e-06 | 5.5789e-06 | 0.090601 | 0.090601 | 0.090601 | 0.97864 | -0.41031 | 0.97848 | -0.41339 | 24.8904
24 | -0.02675 | -0.0067231 | 0.026756 | 0.0067264 | 5.44e-06 | 3.3718e-06 | 0.040717 | 0.040717 | 0.040717 | 0.97775 | -0.42773 | 0.97797 | -0.42347 | 11.1861
25 | 0.030456 | 0.007659 | -0.030448 | -0.007654 | 8.0093e-06 | 5.0009e-06 | 0.046324 | 0.046325 | 0.046325 | 0.97848 | -0.41339 | 0.9782 | -0.4189 | 12.7265
26 | 0.095197 | 0.02426 | -0.09506 | -0.024172 | 0.00013761 | 8.7841e-05 | 0.14307 | 0.14307 | 0.14307 | 0.99112 | -0.16876 | 0.98955 | -0.19876 | 39.3043
27 | -0.097913 | -0.02494 | 0.098125 | 0.025076 | 0.00021242 | 0.00013561 | 0.14714 | 0.14714 | 0.14714 | 0.99112 | -0.16876 | 0.99346 | -0.12389 | 40.4243
28 | 0.093546 | 0.023793 | -0.093473 | -0.023746 | 7.2756e-05 | 4.6438e-05 | 0.14079 | 0.14079 | 0.14079 | 0.98955 | -0.19876 | 0.98871 | -0.21492 | 38.6791
29 | 0.0078183 | 0.001959 | -0.0078176 | -0.0019587 | 7.5237e-07 | 2.9209e-07 | 0.01171 | 0.01171 | 0.01171 | 0.99346 | -0.12389 | 0.99336 | -0.12592 | 3.2171
30 | -0.10594 | -0.027035 | 0.10613 | 0.027151 | 0.00018235 | 0.00011646 | 0.15885 | 0.15885 | 0.15885 | 0.99346 | -0.12389 | 0.99533 | -0.088331 | 43.6413
31 | 0.092238 | 0.023437 | -0.092129 | -0.023367 | 0.00010896 | 6.9539e-05 | 0.13893 | 0.13893 | 0.13893 | 0.98871 | -0.21492 | 0.98744 | -0.23949 | 38.1685
32 | 0.0052807 | 0.0013229 | -0.00528 | -0.0013228 | 7.6892e-07 | 6.7947e-08 | 0.0079101 | 0.0079103 | 0.0079103 | 0.99336 | -0.12592 | 0.9932 | -0.12897 | 2.1732
33 | -0.10819 | -0.027668 | 0.10839 | 0.027797 | 0.00020248 | 0.00012932 | 0.16193 | 0.16193 | 0.16193 | 0.99533 | -0.088331 | 0.99737 | -0.049733 | 44.4876
34 | 0.092129 | 0.023367 | -0.092081 | -0.023336 | 4.8318e-05 | 3.0838e-05 | 0.13893 | 0.13893 | 0.13893 | 0.98744 | -0.23949 | 0.98687 | -0.2504 | 38.1685
35 | 0.003236 | 0.00081055 | -0.0032358 | -0.00081071 | 1.931e-07 | -1.5992e-07 | 0.0048481 | 0.0048482 | 0.0048482 | 0.9932 | -0.12897 | 0.99314 | -0.13023 | 1.3319
36 | -0.11181 | -0.028653 | 0.11181 | 0.028656 | 3.9251e-06 | 2.5072e-06 | 0.16703 | 0.16703 | 0.16703 | 0.99737 | -0.049733 | 0.99741 | -0.049009 | 45.8881
37 | -0.0243 | -0.0060935 | 0.024304 | 0.0060963 | 4.5098e-06 | 2.7726e-06 | 0.036704 | 0.036704 | 0.036704 | 0.98518 | -0.2832 | 0.98538 | -0.27931 | 10.0835
38 | 0.0243 | 0.0060935 | -0.024291 | -0.0060881 | 8.8457e-06 | 5.4384e-06 | 0.036704 | 0.036704 | 0.036704 | 0.98518 | -0.2832 | 0.98479 | -0.29084 | 10.0835
39 | -0.024304 | -0.0060963 | 0.024312 | 0.006101 | 7.7062e-06 | 4.7376e-06 | 0.036704 | 0.036704 | 0.036704 | 0.98538 | -0.27931 | 0.98572 | -0.27266 | 10.0834
40 | 0.0079575 | 0.0019945 | -0.0079563 | -0.001994 | 1.1604e-06 | 4.7039e-07 | 0.012024 | 0.012024 | 0.012024 | 0.98479 | -0.29084 | 0.98463 | -0.2939 | 3.3033
41 | 0.0016042 | 0.00040179 | -0.0016042 | -0.00040205 | 4.9065e-08 | -2.6165e-07 | 0.0024035 | 0.0024036 | 0.0024036 | 0.99314 | -0.13023 | 0.9931 | -0.13087 | 0.66034
42 | -0.1133 | -0.029028 | 0.11339 | 0.029087 | 9.2608e-05 | 5.9156e-05 | 0.16925 | 0.16925 | 0.16925 | 0.99741 | -0.049009 | 0.9983 | -0.032157 | 46.4969
43 | -0.11232 | -0.028633 | 0.11253 | 0.028768 | 0.00021205 | 0.00013546 | 0.16952 | 0.16952 | 0.16952 | 0.98689 | -0.24902 | 0.98892 | -0.20999 | 46.5725
44 | 0.11232 | 0.028633 | -0.11219 | -0.028551 | 0.00012777 | 8.162e-05 | 0.16952 | 0.16952 | 0.16952 | 0.98689 | -0.24902 | 0.98566 | -0.27261 | 46.5726
45 | -0.1137 | -0.029062 | 0.11385 | 0.029159 | 0.00015272 | 9.7562e-05 | 0.17129 | 0.17129 | 0.17129 | 0.98892 | -0.20999 | 0.99038 | -0.18226 | 47.0564
46 | 0.11108 | 0.028272 | -0.11095 | -0.028194 | 0.00012324 | 7.8723e-05 | 0.16785 | 0.16785 | 0.16785 | 0.98566 | -0.27261 | 0.98447 | -0.29565 | 46.1113
47 | -0.11552 | -0.029578 | 0.11554 | 0.029586 | 1.2401e-05 | 7.9228e-06 | 0.1738 | 0.1738 | 0.1738 | 0.99038 | -0.18226 | 0.99049 | -0.18004 | 47.7465
48 | 0.11095 | 0.028194 | -0.11084 | -0.028124 | 0.00010964 | 7.0036e-05 | 0.16785 | 0.16785 | 0.16785 | 0.98447 | -0.29565 | 0.98341 | -0.3162 | 46.1113
49 | 0.12424 | 0.031916 | -0.12418 | -0.03188 | 5.5964e-05 | 3.5761e-05 | 0.18628 | 0.18628 | 0.18628 | 0.99394 | -0.11451 | 0.99345 | -0.12379 | 51.1753
50 | -0.13074 | -0.033544 | 0.13077 | 0.033565 | 3.1984e-05 | 2.0441e-05 | 0.196 | 0.196 | 0.196 | 0.99394 | -0.11451 | 0.9942 | -0.10947 | 53.8468
51 | 0.12089 | 0.031054 | -0.12064 | -0.030897 | 0.00024607 | 0.00015722 | 0.18134 | 0.18134 | 0.18134 | 0.99345 | -0.12379 | 0.99124 | -0.1658 | 49.819
52 | -0.13189 | -0.033846 | 0.13205 | 0.033946 | 0.00015648 | 0.00010001 | 0.19768 | 0.19768 | 0.19768 | 0.9942 | -0.10947 | 0.99549 | -0.085053 | 54.3086
53 | 0.11784 | 0.030194 | -0.11776 | -0.030143 | 8.1265e-05 | 5.1921e-05 | 0.17713 | 0.17713 | 0.17713 | 0.99124 | -0.1658 | 0.99049 | -0.18004 | 48.6627
54 | -0.13382 | -0.03439 | 0.13399 | 0.0345 | 0.00017328 | 0.0001103 | 0.20033 | 0.20033 | 0.20033 | 0.99549 | -0.085053 | 0.9969 | -0.058434 | 27.518
55 | -0.13541 | -0.034857 | 0.13545 | 0.034882 | 4.0098e-05 | 2.5526e-05 | 0.20245 | 0.20245 | 0.20245 | 0.9969 | -0.058434 | 0.99722 | -0.052348 | 27.8094
56 | -0.14347 | -0.036891 | 0.14367 | 0.037022 | 0.00020626 | 0.00013138 | 0.21441 | 0.21441 | 0.21441 | 0.99722 | -0.052348 | 0.99879 | -0.022812 | 29.4518
57 | -0.11534 | -0.029576 | 0.11552 | 0.029691 | 0.00018017 | 0.0001151 | 0.17216 | 0.17216 | 0.17216 | 0.9983 | -0.032157 | 1 | 0 | 47.2954
58 | 0.14593 | 0.03765 | -0.14577 | -0.037547 | 0.00016202 | 0.00010322 | 0.21753 | 0.21753 | 0.21753 | 1 | 0 | 0.99879 | -0.022812 | 29.8804
59 | 0.029324 | 0.00736 | -0.029311 | -0.0073522 | 1.2521e-05 | 7.7833e-06 | 0.043638 | 0.043638 | 0.043638 | 1 | 0 | 0.99953 | -0.0089568 | 11.9884
60 | 0.025915 | 0.0065011 | -0.025906 | -0.0064952 | 9.5582e-06 | 5.8929e-06 | 0.038582 | 0.038582 | 0.038582 | 0.99953 | -0.0089568 | 0.99913 | -0.016696 | 10.5996
61 | 0.022201 | 0.0055667 | -0.022198 | -0.0055651 | 2.4937e-06 | 1.5163e-06 | 0.033064 | 0.033065 | 0.033065 | 0.99913 | -0.016696 | 0.99901 | -0.019054 | 9.0837
62 | -0.0012134 | -0.00030412 | 0.0012135 | 0.00030394 | 1.9919e-08 | -1.8e-07 | 0.0018529 | 0.0018529 | 0.0018529 | 0.97447 | -0.49076 | 0.97448 | -0.49041 | 0.50905
63 | -0.049259 | -0.012386 | 0.049275 | 0.012397 | 1.6285e-05 | 1.0327e-05 | 0.075233 | 0.075233 | 0.075233 | 0.97448 | -0.49041 | 0.97483 | -0.48349 | 20.6683
64 | 0.048046 | 0.012082 | -0.048015 | -0.012063 | 3.0385e-05 | 1.9259e-05 | 0.07338 | 0.07338 | 0.07338 | 0.97448 | -0.49041 | 0.97381 | -0.50366 | 20.1593
65 | 0.020471 | 0.0051323 | -0.02047 | -0.0051314 | 1.5939e-06 | 9.6027e-07 | 0.030492 | 0.030492 | 0.030492 | 0.99901 | -0.019054 | 0.99892 | -0.020688 | 8.377
66 | -0.050966 | -0.01282 | 0.050988 | 0.012834 | 2.1981e-05 | 1.3947e-05 | 0.077812 | 0.077812 | 0.077812 | 0.97483 | -0.48349 | 0.97529 | -0.47447 | 21.377
67 | 0.045988 | 0.011555 | -0.045984 | -0.011553 | 3.364e-06 | 2.1304e-06 | 0.070281 | 0.070281 | 0.070281 | 0.97381 | -0.50366 | 0.97373 | -0.5052 | 19.308
68 | 0.0061634 | 0.0015445 | -0.0061628 | -0.0015444 | 5.6902e-07 | 1.2883e-07 | 0.0091839 | 0.0091839 | 0.0091839 | 0.99861 | -0.026641 | 0.99851 | -0.028579 | 2.5231
69 | -0.0073801 | -0.0018494 | 0.0073803 | 0.0018495 | 1.1491e-07 | 4.0392e-08 | 0.010997 | 0.010997 | 0.010997 | 0.99861 | -0.026641 | 0.99863 | -0.026314 | 3.0211
70 | 0.0039191 | 0.00098206 | -0.0039191 | -0.00098209 | 9.7909e-08 | -3.7457e-08 | 0.0058404 | 0.0058404 | 0.0058404 | 0.99851 | -0.028579 | 0.99849 | -0.029103 | 1.6045
71 | -0.015264 | -0.0038254 | 0.015268 | 0.0038273 | 3.2576e-06 | 1.8651e-06 | 0.022745 | 0.022745 | 0.022745 | 0.99863 | -0.026314 | 0.99886 | -0.021835 | 6.2486
72 | 0.0019355 | 0.00048497 | -0.0019355 | -0.00048498 | 3.3085e-09 | -1.1753e-08 | 0.0028844 | 0.0028844 | 0.0028844 | 0.99849 | -0.029103 | 0.99848 | -0.029139 | 0.79241
73 | -0.018105 | -0.0045385 | 0.018106 | 0.0045391 | 9.8966e-07 | 5.859e-07 | 0.026972 | 0.026972 | 0.026972 | 0.99886 | -0.021835 | 0.99892 | -0.020688 | 7.4099
74 | 0.00086454 | 0.00021658 | -0.00086454 | -0.00021667 | 4.8075e-09 | -9.7938e-08 | 0.0012884 | 0.0012884 | 0.0012884 | 0.99848 | -0.029139 | 0.99848 | -0.029256 | 0.35396
75 | -0.0022361 | -0.00056041 | 0.0022361 | 0.00056039 | 9.7121e-09 | -2.1522e-08 | 0.0034125 | 0.0034125 | 0.0034125 | 0.97503 | -0.47993 | 0.97503 | -0.47984 | 0.93751
76 | -0.0050203 | -0.0012582 | 0.0050208 | 0.0012582 | 5.1111e-07 | 3.7478e-08 | 0.0076616 | 0.0076615 | 0.0076616 | 0.97503 | -0.47984 | 0.97514 | -0.47771 | 2.1048
77 | -0.0091411 | -0.0022912 | 0.0091416 | 0.0022914 | 4.914e-07 | 2.3178e-07 | 0.014004 | 0.014004 | 0.014004 | 0.97134 | -0.55247 | 0.9714 | -0.55134 | 3.8471
78 | 0.0091411 | 0.0022912 | -0.0091399 | -0.0022906 | 1.2481e-06 | 5.8872e-07 | 0.014004 | 0.014004 | 0.014004 | 0.97134 | -0.55247 | 0.97119 | -0.55534 | 3.8472
79 | -0.011598 | -0.0029071 | 0.011599 | 0.0029077 | 1.0682e-06 | 5.7192e-07 | 0.017767 | 0.017766 | 0.017767 | 0.9714 | -0.55134 | 0.97149 | -0.54941 | 4.8809
80 | 0.0060642 | 0.0015198 | -0.0060636 | -0.0015196 | 5.8984e-07 | 1.5206e-07 | 0.0092913 | 0.0092913 | 0.0092913 | 0.97119 | -0.55534 | 0.97109 | -0.55738 | 2.5526
81 | -0.014514 | -0.0036382 | 0.014514 | 0.0036384 | 3.1182e-07 | 1.7873e-07 | 0.022231 | 0.022231 | 0.022231 | 0.97149 | -0.54941 | 0.97152 | -0.54896 | 6.1075
82 | 0.0038006 | 0.00095246 | -0.0038005 | -0.00095249 | 1.0237e-07 | -3.4062e-08 | 0.0058237 | 0.0058237 | 0.0058237 | 0.97109 | -0.55738 | 0.97106 | -0.55794 | 1.5999
83 | -0.017816 | -0.0044659 | 0.017822 | 0.0044693 | 5.6465e-06 | 3.3633e-06 | 0.027288 | 0.027288 | 0.027288 | 0.97152 | -0.54896 | 0.97185 | -0.54231 | 7.4968
84 | -0.039214 | -0.0098404 | 0.039216 | 0.0098412 | 1.2943e-06 | 8.1643e-07 | 0.059993 | 0.059993 | 0.059993 | 0.97272 | -0.52525 | 0.97275 | -0.52456 | 16.4815
85 | 0.03504 | 0.0087942 | -0.035022 | -0.0087829 | 1.797e-05 | 1.1294e-05 | 0.053607 | 0.053607 | 0.053607 | 0.97272 | -0.52525 | 0.97217 | -0.53601 | 14.7272
86 | -0.042696 | -0.010714 | 0.042736 | 0.010738 | 3.9449e-05 | 2.4941e-05 | 0.065317 | 0.065317 | 0.065317 | 0.97275 | -0.52456 | 0.97373 | -0.5052 | 17.9442
87 | 0.022803 | 0.0057199 | -0.0228 | -0.0057179 | 3.2556e-06 | 1.9952e-06 | 0.034904 | 0.034904 | 0.034904 | 0.97217 | -0.53601 | 0.97202 | -0.539 | 9.589
88 | 0.012219 | 0.003063 | -0.012217 | -0.0030618 | 2.2089e-06 | 1.2049e-06 | 0.018703 | 0.018703 | 0.018703 | 0.97217 | -0.53601 | 0.97198 | -0.5398 | 5.1383
89 | 0.020271 | 0.0050842 | -0.020268 | -0.0050823 | 3.1948e-06 | 1.9351e-06 | 0.031033 | 0.031033 | 0.031033 | 0.97202 | -0.539 | 0.97185 | -0.54231 | 8.5257
90 | 0.0065775 | 0.0016484 | -0.0065768 | -0.0016482 | 6.7445e-07 | 2.1183e-07 | 0.01007 | 0.01007 | 0.01007 | 0.97198 | -0.5398 | 0.97187 | -0.54195 | 2.7664
91 | 0.0045417 | 0.0011381 | -0.0045413 | -0.0011382 | 3.7478e-07 | -1.6233e-08 | 0.0069537 | 0.0069538 | 0.0069538 | 0.97187 | -0.54195 | 0.97178 | -0.54369 | 1.9104
92 | -0.052675 | -0.013257 | 0.05272 | 0.013286 | 4.5195e-05 | 2.8692e-05 | 0.080387 | 0.080387 | 0.080387 | 0.97529 | -0.47447 | 0.97621 | -0.45654 | 22.0843
93 | -0.056357 | -0.014197 | 0.056423 | 0.014239 | 6.5667e-05 | 4.173e-05 | 0.085931 | 0.085931 | 0.085931 | 0.97621 | -0.45654 | 0.97745 | -0.4322 | 23.6074
94 | 0.016956 | 0.0042514 | -0.016952 | -0.0042486 | 4.7299e-06 | 2.7919e-06 | 0.025867 | 0.025867 | 0.025867 | 0.97544 | -0.47185 | 0.97514 | -0.47771 | 7.1064
95 | -0.021145 | -0.0053013 | 0.021152 | 0.0053054 | 6.761e-06 | 4.1107e-06 | 0.032258 | 0.032258 | 0.032258 | 0.97544 | -0.47185 | 0.97578 | -0.46514 | 8.862
96 | 0.011931 | 0.0029904 | -0.01193 | -0.0029898 | 1.0282e-06 | 5.5489e-07 | 0.018206 | 0.018206 | 0.018206 | 0.97514 | -0.47771 | 0.97505 | -0.47951 | 5.0016
97 | -0.021152 | -0.0053054 | 0.021153 | 0.0053059 | 8.7067e-07 | 5.2935e-07 | 0.032258 | 0.032258 | 0.032258 | 0.97578 | -0.46514 | 0.97582 | -0.46428 | 8.862
98 | 0.01039 | 0.0026038 | -0.01039 | -0.0026038 | 7.8505e-08 | 3.9857e-08 | 0.015856 | 0.015856 | 0.015856 | 0.97505 | -0.47951 | 0.97504 | -0.47967 | 4.3559
99 | -0.025447 | -0.0063822 | 0.02545 | 0.0063835 | 2.1694e-06 | 1.3404e-06 | 0.038806 | 0.038806 | 0.038806 | 0.97582 | -0.46428 | 0.97591 | -0.46249 | 10.661
100 | 0.0079576 | 0.0019943 | -0.0079573 | -0.0019941 | 3.8714e-07 | 1.6047e-07 | 0.012144 | 0.012144 | 0.012144 | 0.97504 | -0.47967 | 0.97499 | -0.48069 | 3.3363
101 | -0.02545 | -0.0063835 | 0.02546 | 0.0063902 | 1.0884e-05 | 6.7246e-06 | 0.038806 | 0.038806 | 0.038806 | 0.97591 | -0.46249 | 0.97637 | -0.45352 | 10.661
102 | 0.0063982 | 0.0016032 | -0.0063976 | -0.001603 | 5.331e-07 | 1.5421e-07 | 0.0097509 | 0.0097509 | 0.0097509 | 0.97637 | -0.45352 | 0.97628 | -0.45527 | 2.6788
103 | -0.031859 | -0.0079934 | 0.031874 | 0.0080028 | 1.5033e-05 | 9.4081e-06 | 0.048557 | 0.048557 | 0.048557 | 0.97637 | -0.45352 | 0.97687 | -0.44363 | 13.3398
104 | 0.0037361 | 0.00093618 | -0.0037358 | -0.00093628 | 2.5758e-07 | -9.8609e-08 | 0.0057019 | 0.005702 | 0.005702 | 0.97499 | -0.48069 | 0.97491 | -0.48214 | 1.5665
105 | 0.0043497 | 0.0010898 | -0.0043496 | -0.0010898 | 1.6564e-07 | -1.9649e-08 | 0.0066296 | 0.0066297 | 0.0066297 | 0.97628 | -0.45527 | 0.97624 | -0.45607 | 1.8213
106 | -0.03413 | -0.0085683 | 0.034144 | 0.0085773 | 1.4311e-05 | 8.9823e-06 | 0.051994 | 0.051994 | 0.051994 | 0.97687 | -0.44363 | 0.97732 | -0.43485 | 14.284
107 | -0.036415 | -0.0091463 | 0.036425 | 0.0091527 | 1.0289e-05 | 6.4728e-06 | 0.05545 | 0.05545 | 0.05545 | 0.97732 | -0.43485 | 0.97762 | -0.42893 | 15.2336
108 | -0.038003 | -0.0095481 | 0.038037 | 0.0095697 | 3.4195e-05 | 2.1543e-05 | 0.057851 | 0.057851 | 0.057851 | 0.97762 | -0.42893 | 0.97858 | -0.41009 | 15.8933
109 | -0.10154 | -0.02561 | 0.10158 | 0.025634 | 3.7613e-05 | 2.402e-05 | 0.15446 | 0.15446 | 0.15446 | 0.97858 | -0.41009 | 0.97898 | -0.40236 | 42.4348
110 | 0.063506 | 0.01604 | -0.063447 | -0.016002 | 5.9619e-05 | 3.7942e-05 | 0.096611 | 0.096611 | 0.096611 | 0.97858 | -0.41009 | 0.97758 | -0.4297 | 26.5416
111 | 0.0019595 | 0.00049076 | -0.0019594 | -0.00049106 | 9.6541e-08 | -2.9906e-07 | 0.0029865 | 0.0029867 | 0.0029867 | 0.97624 | -0.45607 | 0.97619 | -0.45711 | 0.82051
112 | -0.10279 | -0.025936 | 0.10294 | 0.026037 | 0.00015834 | 0.00010112 | 0.1563 | 0.1563 | 0.1563 | 0.97898 | -0.40236 | 0.98062 | -0.37024 | 42.9384
113 | 0.001206 | 0.00030214 | -0.001206 | -0.00030226 | 1.2465e-08 | -1.164e-07 | 0.0018331 | 0.0018332 | 0.0018332 | 0.97898 | -0.40236 | 0.97896 | -0.40257 | 0.50361
114 | 0.061956 | 0.015629 | -0.061949 | -0.015624 | 7.4188e-06 | 4.7202e-06 | 0.094343 | 0.094343 | 0.094343 | 0.97758 | -0.4297 | 0.97745 | -0.4322 | 25.9184
115 | -0.10586 | -0.026768 | 0.10613 | 0.02694 | 0.00026932 | 0.00017202 | 0.16072 | 0.16072 | 0.16072 | 0.98062 | -0.37024 | 0.98335 | -0.31735 | 44.1551
116 | -0.10842 | -0.027514 | 0.10843 | 0.027518 | 6.0095e-06 | 3.8386e-06 | 0.16419 | 0.16419 | 0.16419 | 0.98335 | -0.31735 | 0.98341 | -0.3162 | 45.1058
117 | 0.028591 | 0.0071886 | -0.028584 | -0.0071847 | 6.2329e-06 | 3.8788e-06 | 0.0435 | 0.0435 | 0.0435 | 0.9782 | -0.4189 | 0.97797 | -0.42347 | 11.9505

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29242 | 0.074701

## res_load
| p_mw | q_mvar
0 | 0.0077554 | 0.0019437
1 | 0.0084556 | 0.0021192
2 | 0.0068215 | 0.0017096
3 | 0.0015622 | 0.00039154
4 | 0.0052791 | 0.0013231
5 | 0.0028366 | 0.00071092
6 | 0.0075255 | 0.0018861
7 | 0.0029355 | 0.00073572
8 | 0.0016075 | 0.00040288
9 | 0.0018199 | 0.00045611
10 | 0.0018128 | 0.00045434
11 | 0.0026709 | 0.0006694
12 | 0.0012206 | 0.00030592
13 | 0.0012172 | 0.00030505
14 | 0.0018445 | 0.00046226
15 | 0.0011892 | 0.00029804
16 | 0.0028045 | 0.00070287
17 | 0.0027154 | 0.00068055
18 | 0.0015136 | 0.00037935
19 | 0.0012349 | 0.00030949
20 | 0.0025368 | 0.00063579
21 | 0.0020606 | 0.00051644
22 | 0.0020439 | 0.00051225
23 | 0.003417 | 0.00085638
24 | 0.016333 | 0.0040936
25 | 0.0017469 | 0.00043782
26 | 0.0023156 | 0.00058033
27 | 0.0016316 | 0.00040892
28 | 0.0014854 | 0.00037229
29 | 0.0011706 | 0.00029339
30 | 0.0011122 | 0.00027875
31 | 0.0079563 | 0.001994
32 | 0.0016718 | 0.000419
33 | 0.0064956 | 0.0016279
34 | 0.003296 | 0.00082607
35 | 0.0011231 | 0.00028149
36 | 0.002804 | 0.00070274
37 | 0.0017716 | 0.00044402
38 | 0.0022199 | 0.00055637
39 | 0.0014212 | 0.00035618
40 | 0.0080134 | 0.0020083
41 | 0.00195 | 0.00048872
42 | 0.0020943 | 0.00052489
43 | 0.0033958 | 0.00085108
44 | 0.003705 | 0.00092857
45 | 0.0012134 | 0.00030412
46 | 0.0017269 | 0.0004328
47 | 0.00169 | 0.00042357
48 | 0.0020278 | 0.00050823
49 | 0.0012168 | 0.00030495
50 | 0.0022437 | 0.00056231
51 | 0.0078842 | 0.001976
52 | 0.0019835 | 0.00049712
53 | 0.0028377 | 0.00071119
54 | 0.001071 | 0.00026841
55 | 0.0023632 | 0.00059228
56 | 0.00086454 | 0.00021667
57 | 0.0016042 | 0.00040205
58 | 0.0022361 | 0.00056041
59 | 0.0027842 | 0.00069779
60 | 0.0024565 | 0.00061566
61 | 0.0030757 | 0.00077083
62 | 0.002915 | 0.00073056
63 | 0.002263 | 0.00056717
64 | 0.0033018 | 0.00082751
65 | 0.0038005 | 0.00095249
66 | 0.0041744 | 0.0010462
67 | 0.0034805 | 0.0008723
68 | 0.0032485 | 0.00081416
69 | 0.0025285 | 0.00063369
70 | 0.0056396 | 0.0014134
71 | 0.002446 | 0.00061302
72 | 0.0020351 | 0.00051004
73 | 0.0045413 | 0.0011382
74 | 0.0016874 | 0.00042291
75 | 0.0036372 | 0.00091157
76 | 0.0041891 | 0.0010499
77 | 0.0015402 | 0.000386
78 | 0.0042943 | 0.0010763
79 | 0.0024319 | 0.00060949
80 | 0.0042212 | 0.0010579
81 | 0.0020479 | 0.00051325
82 | 0.0022564 | 0.00056551
83 | 0.0022703 | 0.00056898
84 | 0.0015776 | 0.00039539
85 | 0.0023901 | 0.00059902
86 | 0.0014904 | 0.00037352
87 | 0.0019594 | 0.00049106
88 | 0.0029186 | 0.00073147
89 | 0.001206 | 0.00030226
90 | 0.0055258 | 0.0013849
91 | 0.0022871 | 0.0005732
92 | 0.0037358 | 0.00093628
93 | 0.0024188 | 0.00060621
94 | 0.001857 | 0.00046542
95 | 0.0018286 | 0.00045829

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1