## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_161-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_161-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_161-6_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_161-6_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_161-6_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_161-6_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_161-6_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_161-6_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_161-6_0_5_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_161-6_0_5_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_161-6_0_5_node_86 | 0.4 | n |  | TRUE
11 | bus_LV_161-6_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_161-6_0_5_node_131 | 0.4 | n |  | TRUE
13 | bus_LV_161-6_0_5_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_161-6_0_5_node_78 | 0.4 | n |  | TRUE
15 | bus_LV_161-6_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_161-6_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_161-6_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_161-6_0_5_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_161-6_0_5_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_161-6_0_5_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_161-6_0_5_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_161-6_0_5_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_161-6_0_5_node_135 | 0.4 | n |  | TRUE
24 | bus_LV_161-6_0_5_node_130 | 0.4 | n |  | TRUE
25 | bus_LV_161-6_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_161-6_0_5_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_161-6_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_161-6_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_161-6_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_161-6_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_161-6_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_161-6_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_161-6_0_5_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_161-6_0_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_161-6_0_5_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_161-6_0_5_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_161-6_0_5_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_161-6_0_5_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_161-6_0_5_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_161-6_0_5_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_161-6_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_161-6_0_5_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_161-6_0_5_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_161-6_0_5_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_161-6_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_161-6_0_5_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_161-6_0_5_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_161-6_0_5_node_138 | 0.4 | n |  | TRUE
49 | bus_LV_161-6_0_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_161-6_0_5_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_161-6_0_5_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_161-6_0_5_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_161-6_0_5_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_161-6_0_5_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_161-6_0_5_node_107 | 0.4 | n |  | TRUE
56 | bus_LV_161-6_0_5_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_161-6_0_5_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_161-6_0_5_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_161-6_0_5_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_161-6_0_5_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_161-6_0_5_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_161-6_0_5_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_161-6_0_5_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_161-6_0_5_node_72 | 0.4 | n |  | TRUE
65 | bus_LV_161-6_0_5_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_161-6_0_5_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_161-6_0_5_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_161-6_0_5_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_161-6_0_5_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_161-6_0_5_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_161-6_0_5_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_161-6_0_5_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_161-6_0_5_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_161-6_0_5_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_161-6_0_5_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_161-6_0_5_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_161-6_0_5_node_84 | 0.4 | n |  | TRUE
78 | bus_LV_161-6_0_5_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_161-6_0_5_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_161-6_0_5_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_161-6_0_5_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_161-6_0_5_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_161-6_0_5_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_161-6_0_5_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_161-6_0_5_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_161-6_0_5_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_161-6_0_5_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_161-6_0_5_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_161-6_0_5_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_161-6_0_5_node_92 | 0.4 | n |  | TRUE
91 | bus_LV_161-6_0_5_node_99 | 0.4 | n |  | TRUE
92 | bus_LV_161-6_0_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_161-6_0_5_node_91 | 0.4 | n |  | TRUE
94 | bus_LV_161-6_0_5_node_100 | 0.4 | n |  | TRUE
95 | bus_LV_161-6_0_5_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_161-6_0_5_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_161-6_0_5_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_161-6_0_5_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_161-6_0_5_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_161-6_0_5_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_161-6_0_5_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_161-6_0_5_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_161-6_0_5_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_161-6_0_5_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_161-6_0_5_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_161-6_0_5_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_161-6_0_5_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_161-6_0_5_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_161-6_0_5_node_132 | 0.4 | n |  | TRUE
110 | bus_LV_161-6_0_5_node_136 | 0.4 | n |  | TRUE
111 | bus_LV_161-6_0_5_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_161-6_0_5_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_161-6_0_5_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_161-6_0_5_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_161-6_0_5_node_133 | 0.4 | n |  | TRUE
116 | bus_LV_161-6_0_5_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_161-6_0_5_node_134 | 0.4 | n |  | TRUE
118 | bus_LV_161-6_0_5_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_161-6_0_5_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_161-6_0_5_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_161-6_0_5_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_161-6_0_5_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_161-6_0_5_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_161-6_0_5_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_161-6_0_5_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_161-6_0_5_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_161-6_0_5_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_161-6_0_5_node_126 | 0.4 | n |  | TRUE
129 | bus_LV_161-6_0_5_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_161-6_0_5_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_161-6_0_5_node_129 | 0.4 | n |  | TRUE
132 | bus_MV_494_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_161-6_0_5_load_0 | 0 | 0.0064666 | 0.0016207 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_161-6_0_5_load_1 | 1 | 0.013891 | 0.0034814 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_161-6_0_5_load_2 | 2 | 0.012073 | 0.0030257 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_161-6_0_5_load_4 | 4 | 0.0058103 | 0.0014562 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_161-6_0_5_load_6 | 6 | 0.003007 | 0.00075363 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_161-6_0_5_load_7 | 7 | 0.013414 | 0.0033619 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_161-6_0_5_load_16 | 8 | 0.0051959 | 0.0013022 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_161-6_0_5_load_13 | 9 | 0.0056936 | 0.0014269 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_161-6_0_5_load_86 | 10 | 0.0090941 | 0.0022792 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_161-6_0_5_load_8 | 11 | 0.0063407 | 0.0015891 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_161-6_0_5_load_14 | 13 | 0.0057109 | 0.0014313 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_161-6_0_5_load_78 | 14 | 0.004639 | 0.0011626 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_161-6_0_5_load_9 | 15 | 0.0073726 | 0.0018477 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_161-6_0_5_load_10 | 16 | 0.0085523 | 0.0021434 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_161-6_0_5_load_12 | 17 | 0.0067534 | 0.0016926 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_161-6_0_5_load_48 | 18 | 0.0050204 | 0.0012582 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_161-6_0_5_load_49 | 19 | 0.0041879 | 0.0010496 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_161-6_0_5_load_15 | 20 | 0.0023279 | 0.00058342 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_161-6_0_5_load_28 | 21 | 0.0019584 | 0.00049082 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_161-6_0_5_load_29 | 22 | 0.001816 | 0.00045514 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_161-6_0_5_load_135 | 23 | 0.0012714 | 0.00031864 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_161-6_0_5_load_130 | 24 | 0.0014787 | 0.00037059 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_161-6_0_5_load_17 | 25 | 0.0078254 | 0.0019612 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_161-6_0_5_load_18 | 26 | 0.015262 | 0.0038249 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_161-6_0_5_load_20 | 28 | 0.0036 | 0.00090223 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_161-6_0_5_load_21 | 29 | 0.0055682 | 0.0013955 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_161-6_0_5_load_22 | 30 | 0.0089092 | 0.0022329 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_161-6_0_5_load_30 | 31 | 0.0037314 | 0.00093518 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_161-6_0_5_load_26 | 32 | 0.0070927 | 0.0017776 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_161-6_0_5_load_31 | 33 | 0.0035817 | 0.00089767 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_161-6_0_5_load_23 | 35 | 0.0085636 | 0.0021462 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_161-6_0_5_load_24 | 36 | 0.014113 | 0.003537 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_161-6_0_5_load_27 | 37 | 0.0051776 | 0.0012976 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_161-6_0_5_load_40 | 39 | 0.0045856 | 0.0011493 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_161-6_0_5_load_36 | 40 | 0.0061669 | 0.0015456 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_161-6_0_5_load_32 | 41 | 0.0025586 | 0.00064125 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_161-6_0_5_load_33 | 42 | 0.0042133 | 0.0010559 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_161-6_0_5_load_34 | 43 | 0.0049287 | 0.0012353 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_161-6_0_5_load_35 | 44 | 0.032723 | 0.0082012 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_161-6_0_5_load_37 | 45 | 0.01609 | 0.0040324 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_161-6_0_5_load_138 | 48 | 0.010027 | 0.002513 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_161-6_0_5_load_41 | 49 | 0.0055667 | 0.0013951 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_161-6_0_5_load_42 | 50 | 0.0055857 | 0.0013999 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_161-6_0_5_load_43 | 51 | 0.0034772 | 0.00087147 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_161-6_0_5_load_45 | 52 | 0.0040202 | 0.0010075 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_161-6_0_5_load_46 | 53 | 0.003409 | 0.00085439 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_161-6_0_5_load_47 | 54 | 0.0027072 | 0.0006785 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_161-6_0_5_load_107 | 55 | 0.0042473 | 0.0010645 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_161-6_0_5_load_108 | 56 | 0.0032146 | 0.00080566 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_161-6_0_5_load_53 | 57 | 0.0072642 | 0.0018206 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_161-6_0_5_load_51 | 58 | 0.0026412 | 0.00066194 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_161-6_0_5_load_50 | 59 | 0.0056923 | 0.0014266 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_161-6_0_5_load_54 | 61 | 0.0021607 | 0.00054152 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_161-6_0_5_load_55 | 62 | 0.0017658 | 0.00044255 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_161-6_0_5_load_62 | 63 | 0.0021556 | 0.00054024 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_161-6_0_5_load_72 | 64 | 0.0025564 | 0.00064071 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_161-6_0_5_load_59 | 65 | 0.0010945 | 0.0002743 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_161-6_0_5_load_63 | 66 | 0.0014274 | 0.00035775 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_161-6_0_5_load_69 | 67 | 0.0058425 | 0.0014643 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_161-6_0_5_load_57 | 68 | 0.001231 | 0.00030852 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_161-6_0_5_load_56 | 69 | 0.0033663 | 0.00084367 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_161-6_0_5_load_60 | 71 | 0.0014563 | 0.00036498 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_161-6_0_5_load_67 | 72 | 0.0024671 | 0.00061832 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_161-6_0_5_load_65 | 73 | 0.0037492 | 0.00093963 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_161-6_0_5_load_66 | 74 | 0.0055791 | 0.0013982 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_161-6_0_5_load_68 | 75 | 0.0015358 | 0.0003849 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_161-6_0_5_load_64 | 76 | 0.001345 | 0.00033708 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_161-6_0_5_load_84 | 77 | 0.001475 | 0.00036966 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_161-6_0_5_load_70 | 79 | 0.0039109 | 0.00098016 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_161-6_0_5_load_71 | 80 | 0.0010554 | 0.00026451 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_161-6_0_5_load_74 | 81 | 0.015879 | 0.0039796 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_161-6_0_5_load_75 | 82 | 0.012727 | 0.0031896 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_161-6_0_5_load_76 | 83 | 0.010516 | 0.0026356 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_161-6_0_5_load_77 | 84 | 0.013836 | 0.0034677 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_161-6_0_5_load_79 | 85 | 0.0037587 | 0.00094201 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_161-6_0_5_load_83 | 88 | 0.0034882 | 0.00087423 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_161-6_0_5_load_85 | 89 | 0.015472 | 0.0038777 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_161-6_0_5_load_99 | 91 | 0.002142 | 0.00053684 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_161-6_0_5_load_94 | 92 | 0.00088548 | 0.00022192 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_161-6_0_5_load_91 | 93 | 0.0022301 | 0.00055892 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_161-6_0_5_load_87 | 95 | 0.0030487 | 0.00076408 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_161-6_0_5_load_88 | 96 | 0.0017996 | 0.00045101 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_161-6_0_5_load_89 | 97 | 0.0038786 | 0.00097207 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_161-6_0_5_load_97 | 99 | 0.0027738 | 0.00069517 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_161-6_0_5_load_95 | 100 | 0.0030941 | 0.00077545 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_161-6_0_5_load_93 | 101 | 0.0044915 | 0.0011257 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_161-6_0_5_load_96 | 102 | 0.0037929 | 0.00095059 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_161-6_0_5_load_101 | 103 | 0.0018853 | 0.0004725 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_161-6_0_5_load_102 | 104 | 0.0016542 | 0.00041458 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_161-6_0_5_load_103 | 105 | 0.0016181 | 0.00040554 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_161-6_0_5_load_104 | 106 | 0.0048133 | 0.0012063 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_161-6_0_5_load_105 | 107 | 0.0029457 | 0.00073827 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_161-6_0_5_load_106 | 108 | 0.0049911 | 0.0012509 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_161-6_0_5_load_132 | 109 | 0.0024131 | 0.00060478 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_161-6_0_5_load_136 | 110 | 0.0019373 | 0.00048554 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_161-6_0_5_load_109 | 111 | 0.0040283 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_161-6_0_5_load_110 | 112 | 0.0068893 | 0.0017266 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_161-6_0_5_load_113 | 114 | 0.0036424 | 0.00091286 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_161-6_0_5_load_133 | 115 | 0.0019189 | 0.00048091 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_161-6_0_5_load_112 | 116 | 0.0039939 | 0.001001 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_161-6_0_5_load_134 | 117 | 0.0021222 | 0.00053187 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_161-6_0_5_load_114 | 118 | 0.0036018 | 0.00090271 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_161-6_0_5_load_115 | 119 | 0.0046065 | 0.0011545 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_161-6_0_5_load_118 | 121 | 0.0027843 | 0.00069781 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_161-6_0_5_load_116 | 122 | 0.0049599 | 0.0012431 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_161-6_0_5_load_117 | 123 | 0.0042091 | 0.0010549 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_161-6_0_5_load_119 | 124 | 0.0043104 | 0.0010803 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_161-6_0_5_load_121 | 125 | 0.0035489 | 0.00088944 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_161-6_0_5_load_123 | 126 | 0.010256 | 0.0025704 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_161-6_0_5_load_124 | 127 | 0.0041293 | 0.0010349 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_161-6_0_5_load_127 | 129 | 0.0025247 | 0.00063275 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_161-6_0_5_load_128 | 130 | 0.0078221 | 0.0019604 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_161-6_0_5_load_129 | 131 | 0.0033097 | 0.0008295 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_161-6_0_5_line_0 |  | 0 | 1 | 0.0042858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_161-6_0_5_line_1 |  | 0 | 2 | 0.023699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_161-6_0_5_line_2 |  | 1 | 3 | 0.024271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_161-6_0_5_line_3 |  | 2 | 4 | 0.0031155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_161-6_0_5_line_4 |  | 3 | 5 | 0.023637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_161-6_0_5_line_5 |  | 3 | 6 | 0.038196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_161-6_0_5_line_6 |  | 4 | 7 | 0.023438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_161-6_0_5_line_7 |  | 5 | 8 | 0.015806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_161-6_0_5_line_8 |  | 5 | 9 | 0.025672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_161-6_0_5_line_9 |  | 6 | 10 | 0.031026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_161-6_0_5_line_10 |  | 7 | 11 | 0.019855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_161-6_0_5_line_11 |  | 8 | 12 | 0.01339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_161-6_0_5_line_12 |  | 9 | 13 | 0.0065885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_161-6_0_5_line_13 |  | 10 | 14 | 0.017891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_161-6_0_5_line_14 |  | 11 | 15 | 0.0052881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_161-6_0_5_line_15 |  | 12 | 23 | 0.036938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_161-6_0_5_line_16 |  | 12 | 24 | 0.04339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_161-6_0_5_line_17 |  | 13 | 20 | 0.015102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_161-6_0_5_line_18 |  | 14 | 83 | 0.0012461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_161-6_0_5_line_19 |  | 15 | 16 | 0.002635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_161-6_0_5_line_20 |  | 17 | 18 | 0.032933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_161-6_0_5_line_21 |  | 18 | 19 | 0.03251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_161-6_0_5_line_22 |  | 19 | 57 | 0.0059982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_161-6_0_5_line_23 |  | 20 | 21 | 2.3101e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_161-6_0_5_line_24 |  | 21 | 22 | 0.00015525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_161-6_0_5_line_25 |  | 22 | 29 | 0.012374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_161-6_0_5_line_26 |  | 23 | 117 | 3.6659e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_161-6_0_5_line_27 |  | 24 | 131 | 0.0025961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_161-6_0_5_line_28 |  | 25 | 26 | 0.028272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_161-6_0_5_line_29 |  | 25 | 27 | 0.026295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_161-6_0_5_line_30 |  | 26 | 28 | 0.0052189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_161-6_0_5_line_31 |  | 27 | 29 | 0.027684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_161-6_0_5_line_32 |  | 27 | 30 | 0.0020079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_161-6_0_5_line_33 |  | 28 | 31 | 0.022021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_161-6_0_5_line_34 |  | 30 | 32 | 0.02726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_161-6_0_5_line_35 |  | 31 | 33 | 0.0055979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_161-6_0_5_line_36 |  | 32 | 34 | 0.0043856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_161-6_0_5_line_37 |  | 33 | 41 | 0.0054306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_161-6_0_5_line_38 |  | 34 | 37 | 0.021278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_161-6_0_5_line_39 |  | 34 | 35 | 0.019383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_161-6_0_5_line_40 |  | 35 | 36 | 0.0028619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_161-6_0_5_line_41 |  | 37 | 38 | 0.017624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_161-6_0_5_line_42 |  | 38 | 39 | 0.031218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_161-6_0_5_line_43 |  | 38 | 40 | 0.01915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_161-6_0_5_line_44 |  | 40 | 45 | 0.032112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_161-6_0_5_line_45 |  | 41 | 42 | 0.0053072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_161-6_0_5_line_46 |  | 42 | 43 | 0.0056765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_161-6_0_5_line_47 |  | 43 | 44 | 0.0011345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_161-6_0_5_line_48 |  | 45 | 46 | 0.023667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_161-6_0_5_line_49 |  | 46 | 47 | 0.046549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_161-6_0_5_line_50 |  | 47 | 48 | 0.027838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_161-6_0_5_line_51 |  | 49 | 50 | 0.0046812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_161-6_0_5_line_52 |  | 49 | 51 | 0.0057991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_161-6_0_5_line_53 |  | 51 | 52 | 0.01961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_161-6_0_5_line_54 |  | 52 | 53 | 0.0046281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_161-6_0_5_line_55 |  | 53 | 54 | 0.020892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_161-6_0_5_line_56 |  | 54 | 55 | 0.0094291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_161-6_0_5_line_57 |  | 55 | 56 | 0.013107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_161-6_0_5_line_58 |  | 56 | 111 | 0.017147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_161-6_0_5_line_59 |  | 57 | 58 | 0.023716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_161-6_0_5_line_60 |  | 58 | 59 | 0.0077137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_161-6_0_5_line_61 |  | 59 | 60 | 0.008694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_161-6_0_5_line_62 |  | 60 | 61 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_161-6_0_5_line_63 |  | 60 | 62 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_161-6_0_5_line_64 |  | 61 | 63 | 0.027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_161-6_0_5_line_65 |  | 62 | 64 | 0.010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_161-6_0_5_line_66 |  | 62 | 65 | 0.080163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_161-6_0_5_line_67 |  | 63 | 66 | 0.0035918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_161-6_0_5_line_68 |  | 64 | 67 | 0.018411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_161-6_0_5_line_69 |  | 65 | 68 | 0.00058915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_161-6_0_5_line_70 |  | 66 | 76 | 0.0085193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_161-6_0_5_line_71 |  | 67 | 72 | 0.00445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_161-6_0_5_line_72 |  | 68 | 69 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_161-6_0_5_line_73 |  | 69 | 70 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_161-6_0_5_line_74 |  | 70 | 71 | 0.021966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_161-6_0_5_line_75 |  | 72 | 73 | 0.027603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_161-6_0_5_line_76 |  | 73 | 74 | 0.023568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_161-6_0_5_line_77 |  | 74 | 75 | 0.0036345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_161-6_0_5_line_78 |  | 75 | 79 | 0.018477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_161-6_0_5_line_79 |  | 76 | 77 | 0.0083153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_161-6_0_5_line_80 |  | 77 | 78 | 0.025353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_161-6_0_5_line_81 |  | 78 | 89 | 0.016906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_161-6_0_5_line_82 |  | 78 | 85 | 0.00050811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_161-6_0_5_line_83 |  | 79 | 80 | 0.016104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_161-6_0_5_line_84 |  | 81 | 82 | 0.00066907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_161-6_0_5_line_85 |  | 81 | 83 | 0.029785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_161-6_0_5_line_86 |  | 82 | 84 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_161-6_0_5_line_87 |  | 85 | 86 | 0.021001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_161-6_0_5_line_88 |  | 86 | 87 | 0.008813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_161-6_0_5_line_89 |  | 86 | 88 | 0.011507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_161-6_0_5_line_90 |  | 87 | 90 | 0.023139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_161-6_0_5_line_91 |  | 87 | 91 | 0.016809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_161-6_0_5_line_92 |  | 90 | 92 | 0.018794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_161-6_0_5_line_93 |  | 90 | 93 | 0.024692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_161-6_0_5_line_94 |  | 91 | 94 | 0.019136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_161-6_0_5_line_95 |  | 92 | 98 | 0.022076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_161-6_0_5_line_96 |  | 93 | 101 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_161-6_0_5_line_97 |  | 94 | 103 | 0.01256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_161-6_0_5_line_98 |  | 94 | 104 | 0.018602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_161-6_0_5_line_99 |  | 95 | 96 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_161-6_0_5_line_100 |  | 95 | 97 | 0.0034304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_161-6_0_5_line_101 |  | 96 | 98 | 0.020203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_161-6_0_5_line_102 |  | 98 | 99 | 0.0070979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_161-6_0_5_line_103 |  | 99 | 100 | 0.0082458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_161-6_0_5_line_104 |  | 100 | 102 | 0.041705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_161-6_0_5_line_105 |  | 104 | 105 | 0.011823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_161-6_0_5_line_106 |  | 105 | 106 | 0.004189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_161-6_0_5_line_107 |  | 106 | 107 | 0.026985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_161-6_0_5_line_108 |  | 107 | 108 | 0.003045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_161-6_0_5_line_109 |  | 108 | 109 | 0.019011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_161-6_0_5_line_110 |  | 109 | 110 | 0.012806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_161-6_0_5_line_111 |  | 110 | 130 | 0.00092453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_161-6_0_5_line_112 |  | 111 | 112 | 0.0089505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_161-6_0_5_line_113 |  | 112 | 113 | 0.03949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_161-6_0_5_line_114 |  | 113 | 114 | 0.0078557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_161-6_0_5_line_115 |  | 113 | 115 | 0.020197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_161-6_0_5_line_116 |  | 114 | 116 | 0.01319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_161-6_0_5_line_117 |  | 115 | 117 | 0.0021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_161-6_0_5_line_118 |  | 116 | 118 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_161-6_0_5_line_119 |  | 118 | 119 | 0.024855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_161-6_0_5_line_120 |  | 119 | 120 | 0.0055676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_161-6_0_5_line_121 |  | 120 | 121 | 0.017922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_161-6_0_5_line_122 |  | 121 | 122 | 0.02349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_161-6_0_5_line_123 |  | 122 | 123 | 0.025798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_161-6_0_5_line_124 |  | 123 | 124 | 0.026457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_161-6_0_5_line_125 |  | 124 | 125 | 0.024727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_161-6_0_5_line_126 |  | 126 | 127 | 0.05657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_161-6_0_5_line_127 |  | 127 | 128 | 0.026795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_161-6_0_5_line_128 |  | 128 | 129 | 0.0078803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_161-6_0_5_line_129 |  | 128 | 130 | 0.015906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_161-6_0_5_line_130 |  | 129 | 131 | 0.033159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_161-6_0_5_trafo_1 | 0.63 MVA 20/0.4 kV | 132 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2686103.1736 | 1243318.724 | 2686099.8359 | 1243316.0356
1 | 2686103.1736 | 1243318.724 | 2686121.6298 | 1243333.5903
2 | 2686080.7879 | 1243300.9962 | 2686089.2127 | 1243307.4787 | 2686099.8359 | 1243316.0356
3 | 2686124.0562 | 1243335.5447 | 2686121.6298 | 1243333.5903
4 | 2686066.5376 | 1243319.8589 | 2686072.715 | 1243310.8863 | 2686080.7879 | 1243300.9962
5 | 2686080.7879 | 1243300.9962 | 2686084.3497 | 1243296.7225 | 2686095.7698 | 1243283.2894 | 2686104.8076 | 1243271.3168
6 | 2686124.0562 | 1243335.5447 | 2686142.3089 | 1243350.2471
7 | 2686066.5376 | 1243319.8589 | 2686059.2438 | 1243313.5707 | 2686057.6336 | 1243307.609
8 | 2686066.5376 | 1243319.8589 | 2686058.3413 | 1243338.2535 | 2686056.3178 | 1243343.404
9 | 2686123.5006 | 1243246.5538 | 2686104.8076 | 1243271.3168
10 | 2686157.7716 | 1243362.7022 | 2686142.3089 | 1243350.2471
11 | 2686057.3324 | 1243294.2288 | 2686057.5795 | 1243307.4087 | 2686057.6336 | 1243307.609
12 | 2686053.9085 | 1243349.5362 | 2686056.3178 | 1243343.404
13 | 2686123.5006 | 1243246.5538 | 2686137.8414 | 1243257.2515
14 | 2686157.7716 | 1243362.7022 | 2686161.8899 | 1243366.0194
15 | 2686057.3324 | 1243294.2288 | 2686031.3056 | 1243285.4562 | 2686022.3947 | 1243282.2427
16 | 2686057.3324 | 1243294.2288 | 2686056.6167 | 1243282.5988 | 2686052.3178 | 1243265.7798 | 2686046.8943 | 1243252.4632
17 | 2686053.9085 | 1243349.5362 | 2686048.3861 | 1243363.5923
18 | 2686138.8402 | 1243257.9966 | 2686137.8414 | 1243257.2515
19 | 2686163.942 | 1243367.6723 | 2686161.8899 | 1243366.0194
20 | 2686204.4775 | 1243330.4619 | 2686213.2933 | 1243314.7408 | 2686221.0026 | 1243301.9796
21 | 2686237.8131 | 1243274.1532 | 2686221.0026 | 1243301.9796
22 | 2686237.8131 | 1243274.1532 | 2686238.4039 | 1243273.1752 | 2686240.6582 | 1243268.8747
23 | 2686048.3861 | 1243363.5923 | 2686048.3776 | 1243363.6138
24 | 2686048.3776 | 1243363.6138 | 2686048.3209 | 1243363.7583
25 | 2686043.796 | 1243375.2754 | 2686048.3209 | 1243363.7583
26 | 2686022.3602 | 1243282.2303 | 2686022.3947 | 1243282.2427
27 | 2686046.8943 | 1243252.4632 | 2686045.915 | 1243250.0588
28 | 2686058.2834 | 1243410.3016 | 2686084.7259 | 1243420.3077
29 | 2686033.6728 | 1243401.0417 | 2686041.2437 | 1243403.8536 | 2686058.2834 | 1243410.3016
30 | 2686084.7259 | 1243420.3077 | 2686089.6071 | 1243422.1548
31 | 2686033.6728 | 1243401.0417 | 2686043.796 | 1243375.2754
32 | 2686033.6728 | 1243401.0417 | 2686032.9954 | 1243402.932
33 | 2686089.6071 | 1243422.1548 | 2686098.4446 | 1243425.499 | 2686103.3774 | 1243413.9355
34 | 2686023.8003 | 1243428.594 | 2686032.9954 | 1243402.932
35 | 2686103.3774 | 1243413.9355 | 2686105.5738 | 1243408.7865
36 | 2686022.3209 | 1243432.7226 | 2686023.8003 | 1243428.594
37 | 2686105.5738 | 1243408.7865 | 2686107.7046 | 1243403.7914
38 | 2686022.3209 | 1243432.7226 | 2686015.1439 | 1243452.7531
39 | 2686022.3209 | 1243432.7226 | 2686039.7993 | 1243441.101
40 | 2686039.7993 | 1243441.101 | 2686042.38 | 1243442.3381
41 | 2686009.3096 | 1243469.3831 | 2686013.4427 | 1243457.5009 | 2686015.1439 | 1243452.7531
42 | 2686009.3096 | 1243469.3831 | 2686003.5 | 1243467.6087 | 2685996.4783 | 1243466.5395 | 2685978.6349 | 1243463.8771
43 | 2686009.3096 | 1243469.3831 | 2686016.1195 | 1243472.0281 | 2686027.2748 | 1243476.0085
44 | 2686057.5191 | 1243486.8001 | 2686027.2748 | 1243476.0085
45 | 2686107.7046 | 1243403.7914 | 2686109.787 | 1243398.9098
46 | 2686109.787 | 1243398.9098 | 2686112.0143 | 1243393.6885
47 | 2686112.4595 | 1243392.645 | 2686112.0143 | 1243393.6885
48 | 2686079.8202 | 1243494.724 | 2686077.481 | 1243493.9228 | 2686057.5191 | 1243486.8001
49 | 2686079.8202 | 1243494.724 | 2686055.2593 | 1243518.8632 | 2686044.0639 | 1243514.2419
50 | 2686018.5481 | 1243508.3455 | 2686022.8599 | 1243507.0737 | 2686026.9912 | 1243505.7437 | 2686039.4411 | 1243511.9399 | 2686044.0639 | 1243514.2419
51 | 2685945.1016 | 1243401.8222 | 2685943.2638 | 1243406.1276
52 | 2685945.1016 | 1243401.8222 | 2685947.3783 | 1243396.4887
53 | 2685955.2506 | 1243378.529 | 2685949.789 | 1243390.841 | 2685947.3783 | 1243396.4887
54 | 2685955.2506 | 1243378.529 | 2685957.1273 | 1243374.2985
55 | 2685957.1273 | 1243374.2985 | 2685965.5988 | 1243355.201
56 | 2685969.4223 | 1243346.5819 | 2685965.5988 | 1243355.201
57 | 2685974.7369 | 1243334.6011 | 2685969.4223 | 1243346.5819
58 | 2685974.7369 | 1243334.6011 | 2685981.6899 | 1243318.9269
59 | 2686240.6582 | 1243268.8747 | 2686250.9911 | 1243249.1628 | 2686251.48 | 1243247.7871
60 | 2686254.0625 | 1243240.5185 | 2686251.48 | 1243247.7871
61 | 2686256.9733 | 1243232.3263 | 2686254.0625 | 1243240.5185
62 | 2686256.9733 | 1243232.3263 | 2686243.2727 | 1243227.1222
63 | 2686256.9733 | 1243232.3263 | 2686262.3917 | 1243214.7589 | 2686262.7545 | 1243213.0504
64 | 2686217.7377 | 1243217.423 | 2686243.2727 | 1243227.1222
65 | 2686265.0014 | 1243202.4697 | 2686262.7545 | 1243213.0504
66 | 2686262.7545 | 1243213.0504 | 2686340.3653 | 1243233.1168
67 | 2686217.7377 | 1243217.423 | 2686214.38 | 1243216.1476
68 | 2686265.0014 | 1243202.4697 | 2686268.0884 | 1243187.9331 | 2686268.8369 | 1243184.4628
69 | 2686340.5243 | 1243232.5495 | 2686340.3653 | 1243233.1168
70 | 2686214.38 | 1243216.1476 | 2686206.4158 | 1243213.1225
71 | 2686268.8369 | 1243184.4628 | 2686269.7751 | 1243180.1129
72 | 2686350.162 | 1243198.1545 | 2686340.5243 | 1243232.5495
73 | 2686354.2823 | 1243183.4501 | 2686350.162 | 1243198.1545
74 | 2686354.2823 | 1243183.4501 | 2686357.9007 | 1243170.6378 | 2686357.7825 | 1243161.9862
75 | 2686275.5948 | 1243153.1306 | 2686269.7751 | 1243180.1129
76 | 2686275.5948 | 1243153.1306 | 2686278.8611 | 1243137.9865 | 2686281.0125 | 1243130.2024
77 | 2686281.9806 | 1243126.6993 | 2686281.0125 | 1243130.2024
78 | 2686281.9806 | 1243126.6993 | 2686285.5398 | 1243113.8215 | 2686287.654 | 1243109.1629
79 | 2686198.6424 | 1243210.1698 | 2686206.4158 | 1243213.1225
80 | 2686174.9417 | 1243201.1673 | 2686198.6424 | 1243210.1698
81 | 2686166.9243 | 1243216.0618 | 2686174.9417 | 1243201.1673
82 | 2686174.9417 | 1243201.1673 | 2686174.4677 | 1243200.9843
83 | 2686297.2658 | 1243097.1265 | 2686295.5837 | 1243102.0256 | 2686288.648 | 1243106.9728 | 2686287.654 | 1243109.1629
84 | 2686163.4073 | 1243268.7387 | 2686162.8252 | 1243268.4088
85 | 2686162.8252 | 1243268.4088 | 2686152.8363 | 1243262.747 | 2686149.8456 | 1243266.2061 | 2686138.8402 | 1243257.9966
86 | 2686173.8961 | 1243274.6837 | 2686163.4073 | 1243268.7387
87 | 2686154.9183 | 1243193.3153 | 2686160.3739 | 1243195.5406 | 2686174.4677 | 1243200.9843
88 | 2686154.9183 | 1243193.3153 | 2686158.505 | 1243185.2615
89 | 2686154.9183 | 1243193.3153 | 2686149.9708 | 1243203.7039
90 | 2686158.505 | 1243185.2615 | 2686168.1012 | 1243164.1965
91 | 2686158.505 | 1243185.2615 | 2686152.257 | 1243182.4243 | 2686143.1902 | 1243178.3337
92 | 2686168.1012 | 1243164.1965 | 2686175.8928 | 1243147.0937
93 | 2686168.1012 | 1243164.1965 | 2686192.7102 | 1243166.221
94 | 2686125.747 | 1243170.4641 | 2686143.1902 | 1243178.3337
95 | 2686185.045 | 1243127.0042 | 2686175.8928 | 1243147.0937
96 | 2686203.8887 | 1243167.1406 | 2686192.7102 | 1243166.221
97 | 2686125.747 | 1243170.4641 | 2686130.5043 | 1243158.8357
98 | 2686125.747 | 1243170.4641 | 2686120.7384 | 1243168.6901 | 2686113.4869 | 1243167.2838 | 2686107.5908 | 1243167.5533
99 | 2686218.4295 | 1243140.3094 | 2686203.8123 | 1243134.4838
100 | 2686221.6161 | 1243141.5794 | 2686218.4295 | 1243140.3094
101 | 2686185.045 | 1243127.0042 | 2686203.8123 | 1243134.4838
102 | 2686185.045 | 1243127.0042 | 2686187.9112 | 1243120.5108
103 | 2686191.241 | 1243112.9672 | 2686187.9112 | 1243120.5108
104 | 2686191.241 | 1243112.9672 | 2686203.7814 | 1243084.5564 | 2686207.4818 | 1243074.5699
105 | 2686096.0961 | 1243169.9558 | 2686103.5174 | 1243167.7395 | 2686107.5908 | 1243167.5533
106 | 2686096.0961 | 1243169.9558 | 2686093.0783 | 1243170.857 | 2686092.2059 | 1243171.4221
107 | 2686092.2059 | 1243171.4221 | 2686069.5569 | 1243186.0931
108 | 2686067.0012 | 1243187.7485 | 2686069.5569 | 1243186.0931
109 | 2686067.0012 | 1243187.7485 | 2686051.0451 | 1243198.0841
110 | 2686040.2971 | 1243205.0461 | 2686051.0451 | 1243198.0841
111 | 2686040.2971 | 1243205.0461 | 2686039.5212 | 1243205.5488
112 | 2685985.3193 | 1243310.7452 | 2685981.6899 | 1243318.9269
113 | 2686001.3322 | 1243274.6472 | 2685985.3193 | 1243310.7452
114 | 2686001.3322 | 1243274.6472 | 2685994.1459 | 1243271.474
115 | 2686001.3322 | 1243274.6472 | 2686020.332 | 1243281.4989
116 | 2685994.1459 | 1243271.474 | 2685982.0802 | 1243266.1462
117 | 2686022.3602 | 1243282.2303 | 2686020.332 | 1243281.4989
118 | 2685965.4774 | 1243258.8151 | 2685982.0802 | 1243266.1462
119 | 2685965.4774 | 1243258.8151 | 2685942.7402 | 1243248.7752
120 | 2685937.647 | 1243246.5263 | 2685942.7402 | 1243248.7752
121 | 2685937.647 | 1243246.5263 | 2685930.3291 | 1243262.8858
122 | 2685930.3291 | 1243262.8858 | 2685920.7374 | 1243284.3282
123 | 2685920.7374 | 1243284.3282 | 2685919.6637 | 1243286.7286 | 2685910.9911 | 1243308.2121
124 | 2685910.9911 | 1243308.2121 | 2685901.0873 | 1243332.7453
125 | 2685901.0873 | 1243332.7453 | 2685891.8311 | 1243355.6745
126 | 2685961.5516 | 1243161.7819 | 2686006.5633 | 1243196.0468
127 | 2686026.1712 | 1243214.1963 | 2686014.7036 | 1243202.2435 | 2686006.5633 | 1243196.0468
128 | 2686026.1712 | 1243214.1963 | 2686030.2602 | 1243220.9327
129 | 2686026.1712 | 1243214.1963 | 2686039.5212 | 1243205.5488
130 | 2686030.2602 | 1243220.9327 | 2686041.7854 | 1243239.9192 | 2686045.915 | 1243250.0588

## bus_geodata
| x | y | coords
0 | 2686103.1736 | 1243318.724
1 | 2686099.8359 | 1243316.0356
2 | 2686121.6298 | 1243333.5903
3 | 2686080.7879 | 1243300.9962
4 | 2686124.0562 | 1243335.5447
5 | 2686066.5376 | 1243319.8589
6 | 2686104.8076 | 1243271.3168
7 | 2686142.3089 | 1243350.2471
8 | 2686057.6336 | 1243307.609
9 | 2686056.3178 | 1243343.404
10 | 2686123.5006 | 1243246.5538
11 | 2686157.7716 | 1243362.7022
12 | 2686057.3324 | 1243294.2288
13 | 2686053.9085 | 1243349.5362
14 | 2686137.8414 | 1243257.2515
15 | 2686161.8899 | 1243366.0194
16 | 2686163.942 | 1243367.6723
17 | 2686204.4775 | 1243330.4619
18 | 2686221.0026 | 1243301.9796
19 | 2686237.8131 | 1243274.1532
20 | 2686048.3861 | 1243363.5923
21 | 2686048.3776 | 1243363.6138
22 | 2686048.3209 | 1243363.7583
23 | 2686022.3947 | 1243282.2427
24 | 2686046.8943 | 1243252.4632
25 | 2686058.2834 | 1243410.3016
26 | 2686084.7259 | 1243420.3077
27 | 2686033.6728 | 1243401.0417
28 | 2686089.6071 | 1243422.1548
29 | 2686043.796 | 1243375.2754
30 | 2686032.9954 | 1243402.932
31 | 2686103.3774 | 1243413.9355
32 | 2686023.8003 | 1243428.594
33 | 2686105.5738 | 1243408.7865
34 | 2686022.3209 | 1243432.7226
35 | 2686039.7993 | 1243441.101
36 | 2686042.38 | 1243442.3381
37 | 2686015.1439 | 1243452.7531
38 | 2686009.3096 | 1243469.3831
39 | 2685978.6349 | 1243463.8771
40 | 2686027.2748 | 1243476.0085
41 | 2686107.7046 | 1243403.7914
42 | 2686109.787 | 1243398.9098
43 | 2686112.0143 | 1243393.6885
44 | 2686112.4595 | 1243392.645
45 | 2686057.5191 | 1243486.8001
46 | 2686079.8202 | 1243494.724
47 | 2686044.0639 | 1243514.2419
48 | 2686018.5481 | 1243508.3455
49 | 2685945.1016 | 1243401.8222
50 | 2685943.2638 | 1243406.1276
51 | 2685947.3783 | 1243396.4887
52 | 2685955.2506 | 1243378.529
53 | 2685957.1273 | 1243374.2985
54 | 2685965.5988 | 1243355.201
55 | 2685969.4223 | 1243346.5819
56 | 2685974.7369 | 1243334.6011
57 | 2686240.6582 | 1243268.8747
58 | 2686251.48 | 1243247.7871
59 | 2686254.0625 | 1243240.5185
60 | 2686256.9733 | 1243232.3263
61 | 2686243.2727 | 1243227.1222
62 | 2686262.7545 | 1243213.0504
63 | 2686217.7377 | 1243217.423
64 | 2686265.0014 | 1243202.4697
65 | 2686340.3653 | 1243233.1168
66 | 2686214.38 | 1243216.1476
67 | 2686268.8369 | 1243184.4628
68 | 2686340.5243 | 1243232.5495
69 | 2686350.162 | 1243198.1545
70 | 2686354.2823 | 1243183.4501
71 | 2686357.7825 | 1243161.9862
72 | 2686269.7751 | 1243180.1129
73 | 2686275.5948 | 1243153.1306
74 | 2686281.0125 | 1243130.2024
75 | 2686281.9806 | 1243126.6993
76 | 2686206.4158 | 1243213.1225
77 | 2686198.6424 | 1243210.1698
78 | 2686174.9417 | 1243201.1673
79 | 2686287.654 | 1243109.1629
80 | 2686297.2658 | 1243097.1265
81 | 2686162.8252 | 1243268.4088
82 | 2686163.4073 | 1243268.7387
83 | 2686138.8402 | 1243257.9966
84 | 2686173.8961 | 1243274.6837
85 | 2686174.4677 | 1243200.9843
86 | 2686154.9183 | 1243193.3153
87 | 2686158.505 | 1243185.2615
88 | 2686149.9708 | 1243203.7039
89 | 2686166.9243 | 1243216.0618
90 | 2686168.1012 | 1243164.1965
91 | 2686143.1902 | 1243178.3337
92 | 2686175.8928 | 1243147.0937
93 | 2686192.7102 | 1243166.221
94 | 2686125.747 | 1243170.4641
95 | 2686218.4295 | 1243140.3094
96 | 2686203.8123 | 1243134.4838
97 | 2686221.6161 | 1243141.5794
98 | 2686185.045 | 1243127.0042
99 | 2686187.9112 | 1243120.5108
100 | 2686191.241 | 1243112.9672
101 | 2686203.8887 | 1243167.1406
102 | 2686207.4818 | 1243074.5699
103 | 2686130.5043 | 1243158.8357
104 | 2686107.5908 | 1243167.5533
105 | 2686096.0961 | 1243169.9558
106 | 2686092.2059 | 1243171.4221
107 | 2686069.5569 | 1243186.0931
108 | 2686067.0012 | 1243187.7485
109 | 2686051.0451 | 1243198.0841
110 | 2686040.2971 | 1243205.0461
111 | 2685981.6899 | 1243318.9269
112 | 2685985.3193 | 1243310.7452
113 | 2686001.3322 | 1243274.6472
114 | 2685994.1459 | 1243271.474
115 | 2686020.332 | 1243281.4989
116 | 2685982.0802 | 1243266.1462
117 | 2686022.3602 | 1243282.2303
118 | 2685965.4774 | 1243258.8151
119 | 2685942.7402 | 1243248.7752
120 | 2685937.647 | 1243246.5263
121 | 2685930.3291 | 1243262.8858
122 | 2685920.7374 | 1243284.3282
123 | 2685910.9911 | 1243308.2121
124 | 2685901.0873 | 1243332.7453
125 | 2685891.8311 | 1243355.6745
126 | 2685961.5516 | 1243161.7819
127 | 2686006.5633 | 1243196.0468
128 | 2686026.1712 | 1243214.1963
129 | 2686030.2602 | 1243220.9327
130 | 2686039.5212 | 1243205.5488
131 | 2686045.915 | 1243250.0588
132 | 2686080.7879 | 1243300.9962

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99977 | -0.0044854 | 0.0064666 | 0.0016207
1 | 1 | 0 | -0.58887 | -0.15008
2 | 0.99861 | -0.026647 | 0.012073 | 0.0030257
3 | 0.99709 | -0.055123 | 0 | 0
4 | 0.9985 | -0.028906 | 0.0058103 | 0.0014562
5 | 0.99464 | -0.10186 | 0 | 0
6 | 0.99466 | -0.10191 | 0.003007 | 0.00075363
7 | 0.99774 | -0.043537 | 0.013414 | 0.0033619
8 | 0.99366 | -0.12051 | 0.0051959 | 0.0013022
9 | 0.99356 | -0.12248 | 0.0056936 | 0.0014269
10 | 0.99276 | -0.13843 | 0.0090941 | 0.0022792
11 | 0.99733 | -0.051281 | 0.0063407 | 0.0015891
12 | 0.99285 | -0.13604 | 0 | 0
13 | 0.9933 | -0.12762 | 0.0057109 | 0.0014313
14 | 0.99182 | -0.15668 | 0.004639 | 0.0011626
15 | 0.99726 | -0.052757 | 0.0073726 | 0.0018477
16 | 0.99724 | -0.053152 | 0.0085523 | 0.0021434
17 | 0.97065 | -0.56705 | 0.0067534 | 0.0016926
18 | 0.97086 | -0.56293 | 0.0050204 | 0.0012582
19 | 0.97121 | -0.55586 | 0.0041879 | 0.0010496
20 | 0.9927 | -0.13902 | 0.0023279 | 0.00058342
21 | 0.9927 | -0.13904 | 0.0019584 | 0.00049082
22 | 0.9927 | -0.13915 | 0.001816 | 0.00045514
23 | 0.98999 | -0.19114 | 0.0012714 | 0.00031864
24 | 0.99105 | -0.17032 | 0.0014787 | 0.00037059
25 | 0.9883 | -0.22398 | 0.0078254 | 0.0019612
26 | 0.98646 | -0.25967 | 0.015262 | 0.0038249
27 | 0.9902 | -0.18725 | 0 | 0
28 | 0.9862 | -0.26484 | 0.0036 | 0.00090223
29 | 0.99223 | -0.14817 | 0.0055682 | 0.0013955
30 | 0.99005 | -0.19013 | 0.0089092 | 0.0022329
31 | 0.98515 | -0.28528 | 0.0037314 | 0.00093518
32 | 0.98825 | -0.22501 | 0.0070927 | 0.0017776
33 | 0.9849 | -0.29011 | 0.0035817 | 0.00089767
34 | 0.98799 | -0.23008 | 0 | 0
35 | 0.98759 | -0.23793 | 0.0085636 | 0.0021462
36 | 0.98755 | -0.23865 | 0.014113 | 0.003537
37 | 0.98717 | -0.24607 | 0.0051776 | 0.0012976
38 | 0.98657 | -0.2577 | 0 | 0
39 | 0.98644 | -0.26026 | 0.0045856 | 0.0011493
40 | 0.986 | -0.26878 | 0.0061669 | 0.0015456
41 | 0.98468 | -0.29444 | 0.0025586 | 0.00064125
42 | 0.98448 | -0.29844 | 0.0042133 | 0.0010559
43 | 0.98428 | -0.30228 | 0.0049287 | 0.0012353
44 | 0.98424 | -0.30295 | 0.032723 | 0.0082012
45 | 0.98523 | -0.28383 | 0.01609 | 0.0040324
46 | 0.98501 | -0.28809 | 0 | 0
47 | 0.98458 | -0.29648 | 0 | 0
48 | 0.98432 | -0.3015 | 0.010027 | 0.002513
49 | 0.98459 | -0.29598 | 0.0055667 | 0.0013951
50 | 0.98457 | -0.29645 | 0.0055857 | 0.0013999
51 | 0.98465 | -0.29481 | 0.0034772 | 0.00087147
52 | 0.98492 | -0.28966 | 0.0040202 | 0.0010075
53 | 0.985 | -0.28811 | 0.003409 | 0.00085439
54 | 0.98542 | -0.27983 | 0.0027072 | 0.0006785
55 | 0.98564 | -0.27564 | 0.0042473 | 0.0010645
56 | 0.98599 | -0.26882 | 0.0032146 | 0.00080566
57 | 0.9713 | -0.55409 | 0.0072642 | 0.0018206
58 | 0.97182 | -0.54392 | 0.0026412 | 0.00066194
59 | 0.972 | -0.54023 | 0.0056923 | 0.0014266
60 | 0.97226 | -0.53517 | 0 | 0
61 | 0.97318 | -0.51704 | 0.0021607 | 0.00054152
62 | 0.97159 | -0.5484 | 0.0017658 | 0.00044255
63 | 0.97495 | -0.48224 | 0.0021556 | 0.00054024
64 | 0.97132 | -0.55374 | 0.0025564 | 0.00064071
65 | 0.97106 | -0.55899 | 0.0010945 | 0.0002743
66 | 0.97519 | -0.47753 | 0.0014274 | 0.00035775
67 | 0.97091 | -0.56195 | 0.0058425 | 0.0014643
68 | 0.97105 | -0.55906 | 0.001231 | 0.00030852
69 | 0.97089 | -0.56225 | 0.0033663 | 0.00084367
70 | 0.97087 | -0.56266 | 0 | 0
71 | 0.97084 | -0.56325 | 0.0014563 | 0.00036498
72 | 0.97083 | -0.56346 | 0.0024671 | 0.00061832
73 | 0.97042 | -0.57154 | 0.0037492 | 0.00093963
74 | 0.97016 | -0.57681 | 0.0055791 | 0.0013982
75 | 0.97013 | -0.57725 | 0.0015358 | 0.0003849
76 | 0.97577 | -0.46615 | 0.001345 | 0.00033708
77 | 0.97634 | -0.45485 | 0.001475 | 0.00036966
78 | 0.97814 | -0.4198 | 0 | 0
79 | 0.97005 | -0.57895 | 0.0039109 | 0.00098016
80 | 0.97003 | -0.57927 | 0.0010554 | 0.00026451
81 | 0.9906 | -0.18027 | 0.015879 | 0.0039796
82 | 0.99059 | -0.18059 | 0.012727 | 0.0031896
83 | 0.99176 | -0.15784 | 0.010516 | 0.0026356
84 | 0.99043 | -0.18355 | 0.013836 | 0.0034677
85 | 0.97818 | -0.41896 | 0.0037587 | 0.00094201
86 | 0.98004 | -0.38269 | 0 | 0
87 | 0.98085 | -0.36696 | 0 | 0
88 | 0.98 | -0.38342 | 0.0034882 | 0.00087423
89 | 0.9779 | -0.42457 | 0.015472 | 0.0038777
90 | 0.98029 | -0.37787 | 0 | 0
91 | 0.9828 | -0.32913 | 0.002142 | 0.00053684
92 | 0.97996 | -0.38444 | 0.00088548 | 0.00022192
93 | 0.98014 | -0.38088 | 0.0022301 | 0.00055892
94 | 0.98505 | -0.28551 | 0 | 0
95 | 0.97932 | -0.39699 | 0.0030487 | 0.00076408
96 | 0.97942 | -0.39501 | 0.0017996 | 0.00045101
97 | 0.97931 | -0.39724 | 0.0038786 | 0.00097207
98 | 0.97958 | -0.39181 | 0 | 0
99 | 0.97952 | -0.39306 | 0.0027738 | 0.00069517
100 | 0.97947 | -0.39409 | 0.0030941 | 0.00077545
101 | 0.98009 | -0.38179 | 0.0044915 | 0.0011257
102 | 0.97932 | -0.39696 | 0.0037929 | 0.00095059
103 | 0.98503 | -0.28594 | 0.0018853 | 0.0004725
104 | 0.98617 | -0.26407 | 0.0016542 | 0.00041458
105 | 0.98652 | -0.25717 | 0.0016181 | 0.00040554
106 | 0.98665 | -0.2547 | 0.0048133 | 0.0012063
107 | 0.98751 | -0.23822 | 0.0029457 | 0.00073827
108 | 0.98761 | -0.23632 | 0.0049911 | 0.0012509
109 | 0.98825 | -0.22405 | 0.0024131 | 0.00060478
110 | 0.98869 | -0.21566 | 0.0019373 | 0.00048554
111 | 0.9865 | -0.25892 | 0.0040283 | 0.0010096
112 | 0.98679 | -0.25311 | 0.0068893 | 0.0017266
113 | 0.98836 | -0.22265 | 0 | 0
114 | 0.9881 | -0.22765 | 0.0036424 | 0.00091286
115 | 0.98983 | -0.19429 | 0.0019189 | 0.00048091
116 | 0.98772 | -0.2352 | 0.0039939 | 0.001001
117 | 0.98999 | -0.1912 | 0.0021222 | 0.00053187
118 | 0.98725 | -0.24429 | 0.0036018 | 0.00090271
119 | 0.98669 | -0.25515 | 0.0046065 | 0.0011545
120 | 0.98659 | -0.25713 | 0 | 0
121 | 0.98626 | -0.26349 | 0.0027843 | 0.00069781
122 | 0.98589 | -0.27066 | 0.0049599 | 0.0012431
123 | 0.98561 | -0.27624 | 0.0042091 | 0.0010549
124 | 0.98542 | -0.27997 | 0.0043104 | 0.0010803
125 | 0.98534 | -0.28155 | 0.0035489 | 0.00088944
126 | 0.98841 | -0.22116 | 0.010256 | 0.0025704
127 | 0.98894 | -0.21081 | 0.0041293 | 0.0010349
128 | 0.9893 | -0.20394 | 0 | 0
129 | 0.98961 | -0.19794 | 0.0025247 | 0.00063275
130 | 0.98872 | -0.21505 | 0.0078221 | 0.0019604
131 | 0.99094 | -0.17236 | 0.0033097 | 0.0008295
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.060125 | -0.015105 | 0.060138 | 0.015113 | 1.2874e-05 | 8.1831e-06 | 0.089501 | 0.089501 | 0.089501 | 0.99977 | -0.0044854 | 1 | 0 | 24.5881
1 | 0.053658 | 0.013484 | -0.053602 | -0.013448 | 5.6701e-05 | 3.5978e-05 | 0.079876 | 0.079876 | 0.079876 | 0.99977 | -0.0044854 | 0.99861 | -0.026647 | 21.944
2 | 0.52708 | 0.13497 | -0.52568 | -0.13407 | 0.0014033 | 0.00089685 | 0.78532 | 0.78532 | 0.78532 | 1 | 0 | 0.99709 | -0.055123 | 53.9368
3 | 0.041529 | 0.010423 | -0.041525 | -0.01042 | 4.4746e-06 | 2.823e-06 | 0.061887 | 0.061887 | 0.061887 | 0.99861 | -0.026647 | 0.9985 | -0.028906 | 17.0019
4 | 0.4556 | 0.11637 | -0.45458 | -0.11571 | 0.0010268 | 0.0006559 | 0.6807 | 0.6807 | 0.6807 | 0.99709 | -0.055123 | 0.99464 | -0.10186 | 46.7512
5 | 0.070072 | 0.017706 | -0.069915 | -0.017606 | 0.00015679 | 9.9846e-05 | 0.10462 | 0.10462 | 0.10462 | 0.99709 | -0.055123 | 0.99466 | -0.10191 | 28.7428
6 | 0.035714 | 0.0089636 | -0.035689 | -0.0089479 | 2.4902e-05 | 1.5631e-05 | 0.053228 | 0.053228 | 0.053228 | 0.9985 | -0.028906 | 0.99774 | -0.043537 | 14.6231
7 | 0.27105 | 0.069216 | -0.2708 | -0.06906 | 0.0002442 | 0.00015547 | 0.40596 | 0.40596 | 0.40596 | 0.99464 | -0.10186 | 0.99366 | -0.12051 | 27.8816
8 | 0.18353 | 0.046496 | -0.18335 | -0.046381 | 0.00018167 | 0.00011494 | 0.27474 | 0.27474 | 0.27474 | 0.99464 | -0.10186 | 0.99356 | -0.12248 | 18.8697
9 | 0.066908 | 0.016852 | -0.066792 | -0.016778 | 0.00011664 | 7.4248e-05 | 0.10013 | 0.10013 | 0.10013 | 0.99466 | -0.10191 | 0.99276 | -0.13843 | 27.507
10 | 0.022275 | 0.005586 | -0.022267 | -0.005581 | 8.2179e-06 | 5.0002e-06 | 0.033222 | 0.033222 | 0.033222 | 0.99774 | -0.043537 | 0.99733 | -0.051281 | 9.127
11 | 0.26561 | 0.067758 | -0.26541 | -0.067632 | 0.00019902 | 0.00012668 | 0.39818 | 0.39818 | 0.39818 | 0.99366 | -0.12051 | 0.99285 | -0.13604 | 27.3472
12 | 0.17765 | 0.044954 | -0.17761 | -0.044926 | 4.3774e-05 | 2.7674e-05 | 0.26622 | 0.26622 | 0.26622 | 0.99356 | -0.12248 | 0.9933 | -0.12762 | 18.284
13 | 0.057698 | 0.014499 | -0.057648 | -0.014467 | 5.0194e-05 | 3.1893e-05 | 0.086495 | 0.086495 | 0.086495 | 0.99276 | -0.13843 | 0.99182 | -0.15668 | 23.7623
14 | 0.015926 | 0.0039919 | -0.015925 | -0.0039912 | 1.1197e-06 | 6.4759e-07 | 0.023762 | 0.023762 | 0.023762 | 0.99733 | -0.051281 | 0.99726 | -0.052757 | 6.528
15 | 0.084638 | 0.021411 | -0.084415 | -0.021269 | 0.00022314 | 0.00014233 | 0.12692 | 0.12692 | 0.12692 | 0.99285 | -0.13604 | 0.98999 | -0.19114 | 34.8683
16 | 0.18077 | 0.046221 | -0.18047 | -0.046031 | 0.00029931 | 0.00018932 | 0.27126 | 0.27126 | 0.27126 | 0.99285 | -0.13604 | 0.99105 | -0.17032 | 18.6302
17 | 0.1719 | 0.043495 | -0.1718 | -0.043435 | 9.3994e-05 | 5.9375e-05 | 0.25766 | 0.25766 | 0.25766 | 0.9933 | -0.12762 | 0.9927 | -0.13902 | 17.6965
18 | 0.053009 | 0.013304 | -0.053006 | -0.013303 | 2.956e-06 | 1.8757e-06 | 0.079535 | 0.079535 | 0.079535 | 0.99182 | -0.15668 | 0.99176 | -0.15784 | 21.8503
19 | 0.0085525 | 0.0021435 | -0.0085523 | -0.0021434 | 1.6092e-07 | 6.8607e-08 | 0.012761 | 0.012761 | 0.012761 | 0.99726 | -0.052757 | 0.99724 | -0.053152 | 3.5058
20 | -0.0067534 | -0.0016926 | 0.0067548 | 0.001693 | 1.3237e-06 | 4.4003e-07 | 0.010353 | 0.010353 | 0.010353 | 0.97065 | -0.56705 | 0.97086 | -0.56293 | 2.8443
21 | -0.011775 | -0.0029512 | 0.011779 | 0.0029534 | 3.9709e-06 | 2.1392e-06 | 0.018048 | 0.018047 | 0.018048 | 0.97086 | -0.56293 | 0.97121 | -0.55586 | 4.9581
22 | -0.015967 | -0.004003 | 0.015968 | 0.0040037 | 1.3462e-06 | 7.8731e-07 | 0.024464 | 0.024464 | 0.024464 | 0.97121 | -0.55586 | 0.9713 | -0.55409 | 6.7208
23 | 0.16948 | 0.042852 | -0.16948 | -0.042852 | 1.3991e-07 | 8.8329e-08 | 0.25417 | 0.25417 | 0.25417 | 0.9927 | -0.13902 | 0.9927 | -0.13904 | 17.4568
24 | 0.16752 | 0.042361 | -0.16752 | -0.04236 | 9.1867e-07 | 5.7992e-07 | 0.25124 | 0.25124 | 0.25124 | 0.9927 | -0.13904 | 0.9927 | -0.13915 | 17.2552
25 | 0.1657 | 0.041905 | -0.16563 | -0.04186 | 7.1645e-05 | 4.5213e-05 | 0.24851 | 0.24851 | 0.24851 | 0.9927 | -0.13915 | 0.99223 | -0.14817 | 17.0682
26 | 0.083143 | 0.02095 | -0.083143 | -0.02095 | 2.1483e-07 | 1.3702e-07 | 0.12501 | 0.12501 | 0.12501 | 0.98999 | -0.19114 | 0.98999 | -0.1912 | 34.3433
27 | 0.17899 | 0.045661 | -0.17898 | -0.04565 | 1.7617e-05 | 1.1141e-05 | 0.26904 | 0.26904 | 0.26904 | 0.99105 | -0.17032 | 0.99094 | -0.17236 | 18.4778
28 | 0.070819 | 0.017834 | -0.070699 | -0.017757 | 0.00012061 | 7.6828e-05 | 0.10666 | 0.10666 | 0.10666 | 0.9883 | -0.22398 | 0.98646 | -0.25967 | 29.3017
29 | -0.078645 | -0.019795 | 0.078783 | 0.019883 | 0.00013833 | 8.8191e-05 | 0.11844 | 0.11844 | 0.11844 | 0.9883 | -0.22398 | 0.9902 | -0.18725 | 32.5385
30 | 0.055437 | 0.013932 | -0.055423 | -0.013924 | 1.369e-05 | 8.6951e-06 | 0.083637 | 0.083637 | 0.083637 | 0.98646 | -0.25967 | 0.9862 | -0.26484 | 22.9772
31 | -0.15976 | -0.040274 | 0.16006 | 0.040465 | 0.00029939 | 0.0001909 | 0.24016 | 0.24016 | 0.24016 | 0.9902 | -0.18725 | 0.99223 | -0.14817 | 32.9895
32 | 0.080978 | 0.02039 | -0.080967 | -0.020383 | 1.1157e-05 | 7.1144e-06 | 0.12172 | 0.12172 | 0.12172 | 0.9902 | -0.18725 | 0.99005 | -0.19013 | 33.4405
33 | 0.051824 | 0.013021 | -0.051773 | -0.012989 | 5.0505e-05 | 3.2043e-05 | 0.078205 | 0.078205 | 0.078205 | 0.9862 | -0.26484 | 0.98515 | -0.28528 | 21.485
34 | 0.072058 | 0.01815 | -0.071938 | -0.018074 | 0.00011997 | 7.6431e-05 | 0.10833 | 0.10833 | 0.10833 | 0.99005 | -0.19013 | 0.98825 | -0.22501 | 29.7619
35 | 0.048042 | 0.012054 | -0.048031 | -0.012047 | 1.1055e-05 | 7.0039e-06 | 0.072569 | 0.072569 | 0.072569 | 0.98515 | -0.28528 | 0.9849 | -0.29011 | 19.9366
36 | 0.064845 | 0.016296 | -0.06483 | -0.016286 | 1.5683e-05 | 9.9812e-06 | 0.097654 | 0.097654 | 0.097654 | 0.98825 | -0.22501 | 0.98799 | -0.23008 | 26.828
37 | 0.044449 | 0.011149 | -0.04444 | -0.011144 | 9.1849e-06 | 5.8092e-06 | 0.067158 | 0.067158 | 0.067158 | 0.9849 | -0.29011 | 0.98468 | -0.29444 | 18.45
38 | 0.042144 | 0.010597 | -0.042112 | -0.010577 | 3.2159e-05 | 2.031e-05 | 0.063486 | 0.063486 | 0.063486 | 0.98799 | -0.23008 | 0.98717 | -0.24607 | 17.4412
39 | 0.022686 | 0.0056887 | -0.022677 | -0.0056836 | 8.4856e-06 | 5.1827e-06 | 0.034168 | 0.034168 | 0.034168 | 0.98799 | -0.23008 | 0.98759 | -0.23793 | 9.3868
40 | 0.014113 | 0.0035373 | -0.014113 | -0.003537 | 4.8531e-07 | 2.7398e-07 | 0.021265 | 0.021265 | 0.021265 | 0.98759 | -0.23793 | 0.98755 | -0.23865 | 5.8421
41 | 0.036934 | 0.0092795 | -0.036914 | -0.0092666 | 2.049e-05 | 1.2889e-05 | 0.055681 | 0.055682 | 0.055682 | 0.98717 | -0.24607 | 0.98657 | -0.2577 | 15.2971
42 | 0.0045861 | 0.0011492 | -0.0045856 | -0.0011493 | 5.6013e-07 | -4.0095e-08 | 0.0069171 | 0.0069172 | 0.0069172 | 0.98657 | -0.2577 | 0.98644 | -0.26026 | 1.9003
43 | 0.032328 | 0.0081174 | -0.032311 | -0.0081067 | 1.7077e-05 | 1.0685e-05 | 0.048764 | 0.048765 | 0.048765 | 0.98657 | -0.2577 | 0.986 | -0.26878 | 13.3969
44 | 0.026144 | 0.0065612 | -0.026125 | -0.0065496 | 1.8748e-05 | 1.159e-05 | 0.039458 | 0.039458 | 0.039458 | 0.986 | -0.26878 | 0.98523 | -0.28383 | 10.8401
45 | 0.041881 | 0.010502 | -0.041873 | -0.010497 | 7.9723e-06 | 5.0348e-06 | 0.063291 | 0.063291 | 0.063291 | 0.98468 | -0.29444 | 0.98448 | -0.29844 | 17.3878
46 | 0.03766 | 0.0094414 | -0.037653 | -0.0094371 | 6.8975e-06 | 4.3423e-06 | 0.056923 | 0.056923 | 0.056923 | 0.98448 | -0.29844 | 0.98428 | -0.30228 | 15.6383
47 | 0.032724 | 0.0082019 | -0.032723 | -0.0082012 | 1.0413e-06 | 6.5199e-07 | 0.049472 | 0.049472 | 0.049472 | 0.98428 | -0.30228 | 0.98424 | -0.30295 | 13.5912
48 | 0.010035 | 0.0025172 | -0.010033 | -0.0025162 | 2.0391e-06 | 1.0037e-06 | 0.015158 | 0.015158 | 0.015158 | 0.98523 | -0.28383 | 0.98501 | -0.28809 | 4.1642
49 | 0.010033 | 0.0025162 | -0.010029 | -0.0025142 | 4.0106e-06 | 1.9745e-06 | 0.015158 | 0.015158 | 0.015158 | 0.98501 | -0.28809 | 0.98458 | -0.29648 | 4.1642
50 | 0.010029 | 0.0025142 | -0.010027 | -0.002513 | 2.3985e-06 | 1.1811e-06 | 0.015158 | 0.015158 | 0.015158 | 0.98458 | -0.29648 | 0.98432 | -0.3015 | 4.1643
51 | 0.0055858 | 0.0013999 | -0.0055857 | -0.0013999 | 1.251e-07 | 2.0529e-08 | 0.0084418 | 0.0084418 | 0.0084418 | 0.98459 | -0.29598 | 0.98457 | -0.29645 | 2.3192
52 | -0.011152 | -0.0027951 | 0.011153 | 0.0027954 | 6.1778e-07 | 3.2162e-07 | 0.016855 | 0.016855 | 0.016855 | 0.98459 | -0.29598 | 0.98465 | -0.29481 | 4.6304
53 | -0.01463 | -0.0036668 | 0.014634 | 0.0036689 | 3.5946e-06 | 2.0511e-06 | 0.022109 | 0.022109 | 0.022109 | 0.98465 | -0.29481 | 0.98492 | -0.28966 | 6.074
54 | -0.018654 | -0.0046764 | 0.018655 | 0.0046773 | 1.3785e-06 | 8.2333e-07 | 0.028183 | 0.028183 | 0.028183 | 0.98492 | -0.28966 | 0.985 | -0.28811 | 7.7426
55 | -0.022064 | -0.0055317 | 0.022073 | 0.005537 | 8.7048e-06 | 5.3051e-06 | 0.033333 | 0.033333 | 0.033333 | 0.985 | -0.28811 | 0.98542 | -0.27983 | 9.1574
56 | -0.02478 | -0.0062155 | 0.024785 | 0.0062185 | 4.9514e-06 | 3.0488e-06 | 0.037421 | 0.037421 | 0.037421 | 0.98542 | -0.27983 | 0.98564 | -0.27564 | 10.2805
57 | -0.029033 | -0.007283 | 0.029042 | 0.0072889 | 9.4433e-06 | 5.8766e-06 | 0.043833 | 0.043833 | 0.043833 | 0.98564 | -0.27564 | 0.98599 | -0.26882 | 12.042
58 | -0.032257 | -0.0080945 | 0.032272 | 0.0081041 | 1.5241e-05 | 9.5351e-06 | 0.048684 | 0.048684 | 0.048684 | 0.98599 | -0.26882 | 0.9865 | -0.25892 | 13.3748
59 | -0.023233 | -0.0058243 | 0.023244 | 0.0058313 | 1.1266e-05 | 6.9168e-06 | 0.035592 | 0.035592 | 0.035592 | 0.9713 | -0.55409 | 0.97182 | -0.54392 | 9.7781
60 | -0.025885 | -0.0064932 | 0.02589 | 0.006496 | 4.5445e-06 | 2.8129e-06 | 0.039636 | 0.039636 | 0.039636 | 0.97182 | -0.54392 | 0.972 | -0.54023 | 10.8891
61 | -0.031582 | -0.0079226 | 0.031589 | 0.0079274 | 7.6217e-06 | 4.7701e-06 | 0.048351 | 0.048351 | 0.048351 | 0.972 | -0.54023 | 0.97226 | -0.53517 | 13.2831
62 | -0.067254 | -0.016883 | 0.067312 | 0.01692 | 5.8238e-05 | 3.7091e-05 | 0.10294 | 0.10294 | 0.10294 | 0.97226 | -0.53517 | 0.97318 | -0.51704 | 28.2803
63 | 0.035664 | 0.0089558 | -0.035642 | -0.0089416 | 2.2496e-05 | 1.4148e-05 | 0.05459 | 0.05459 | 0.05459 | 0.97226 | -0.53517 | 0.97159 | -0.5484 | 14.9972
64 | -0.069473 | -0.017462 | 0.069588 | 0.017535 | 0.00011562 | 7.3658e-05 | 0.10624 | 0.10624 | 0.10624 | 0.97318 | -0.51704 | 0.97495 | -0.48224 | 29.1879
65 | 0.026724 | 0.0067067 | -0.026717 | -0.0067024 | 6.7957e-06 | 4.2153e-06 | 0.040931 | 0.040931 | 0.040931 | 0.97159 | -0.5484 | 0.97132 | -0.55374 | 11.2448
66 | 0.0071525 | 0.0017924 | -0.0071489 | -0.0017911 | 3.6073e-06 | 1.3164e-06 | 0.010954 | 0.010955 | 0.010955 | 0.97159 | -0.5484 | 0.97106 | -0.55899 | 3.0095
67 | -0.071744 | -0.018076 | 0.07176 | 0.018086 | 1.616e-05 | 1.0297e-05 | 0.10953 | 0.10953 | 0.10953 | 0.97495 | -0.48224 | 0.97519 | -0.47753 | 30.0916
68 | 0.02416 | 0.0060617 | -0.024151 | -0.0060559 | 9.4593e-06 | 5.8262e-06 | 0.037015 | 0.037015 | 0.037015 | 0.97132 | -0.55374 | 0.97091 | -0.56195 | 10.1689
69 | 0.0060544 | 0.0015168 | -0.0060544 | -0.0015168 | 1.9015e-08 | 4.8815e-09 | 0.0092774 | 0.0092774 | 0.0092774 | 0.97106 | -0.55899 | 0.97105 | -0.55906 | 2.5487
70 | -0.073188 | -0.018444 | 0.073227 | 0.018469 | 3.9869e-05 | 2.541e-05 | 0.11171 | 0.11171 | 0.11171 | 0.97519 | -0.47753 | 0.97577 | -0.46615 | 30.69
71 | 0.018308 | 0.0045916 | -0.018307 | -0.0045909 | 1.314e-06 | 7.8592e-07 | 0.028061 | 0.028061 | 0.028061 | 0.97091 | -0.56195 | 0.97083 | -0.56346 | 7.709
72 | 0.0048234 | 0.0012083 | -0.0048226 | -0.0012082 | 7.3174e-07 | 2.6508e-08 | 0.007391 | 0.0073912 | 0.0073912 | 0.97105 | -0.55906 | 0.97089 | -0.56225 | 2.0305
73 | 0.0014564 | 0.00036456 | -0.0014563 | -0.00036474 | 2.8527e-08 | -1.7059e-07 | 0.0022319 | 0.002232 | 0.002232 | 0.97089 | -0.56225 | 0.97087 | -0.56266 | 0.61318
74 | 0.0014563 | 0.00036474 | -0.0014563 | -0.00036498 | 4.1037e-08 | -2.4536e-07 | 0.002232 | 0.0022321 | 0.0022321 | 0.97087 | -0.56266 | 0.97084 | -0.56325 | 0.61321
75 | 0.01584 | 0.0039725 | -0.015834 | -0.003969 | 6.1018e-06 | 3.564e-06 | 0.024279 | 0.024279 | 0.024279 | 0.97083 | -0.56346 | 0.97042 | -0.57154 | 6.6702
76 | 0.012085 | 0.0030293 | -0.012082 | -0.0030277 | 3.0349e-06 | 1.6512e-06 | 0.018531 | 0.018531 | 0.018531 | 0.97042 | -0.57154 | 0.97016 | -0.57681 | 5.0908
77 | 0.0065026 | 0.0016294 | -0.0065025 | -0.0016294 | 1.3557e-07 | 4.189e-08 | 0.0099735 | 0.0099736 | 0.0099736 | 0.97016 | -0.57681 | 0.97013 | -0.57725 | 2.74
78 | 0.0049667 | 0.0012445 | -0.0049663 | -0.0012445 | 4.021e-07 | 2.9228e-08 | 0.007618 | 0.007618 | 0.007618 | 0.97013 | -0.57725 | 0.97005 | -0.57895 | 2.0929
79 | -0.074572 | -0.018806 | 0.074613 | 0.018832 | 4.0356e-05 | 2.5724e-05 | 0.11376 | 0.11376 | 0.11376 | 0.97577 | -0.46615 | 0.97634 | -0.45485 | 31.2535
80 | -0.076088 | -0.019202 | 0.076216 | 0.019283 | 0.00012795 | 8.1573e-05 | 0.11601 | 0.11601 | 0.11601 | 0.97634 | -0.45485 | 0.97814 | -0.4198 | 31.871
81 | 0.015476 | 0.0038798 | -0.015472 | -0.0038777 | 3.5141e-06 | 2.0369e-06 | 0.023544 | 0.023544 | 0.023544 | 0.97814 | -0.4198 | 0.9779 | -0.42457 | 6.468
82 | -0.091692 | -0.023163 | 0.091695 | 0.023165 | 3.7108e-06 | 2.3685e-06 | 0.13955 | 0.13955 | 0.13955 | 0.97814 | -0.4198 | 0.97818 | -0.41896 | 38.339
83 | 0.0010554 | 0.00026432 | -0.0010554 | -0.00026451 | 1.5828e-08 | -1.8868e-07 | 0.0016189 | 0.001619 | 0.001619 | 0.97005 | -0.57895 | 0.97003 | -0.57927 | 0.44477
84 | 0.026565 | 0.0066586 | -0.026565 | -0.0066584 | 3.9954e-07 | 2.4709e-07 | 0.039905 | 0.039905 | 0.039905 | 0.9906 | -0.18027 | 0.99059 | -0.18059 | 10.9629
85 | -0.042444 | -0.010638 | 0.04249 | 0.010667 | 4.5402e-05 | 2.8674e-05 | 0.063757 | 0.063757 | 0.063757 | 0.9906 | -0.18027 | 0.99176 | -0.15784 | 17.5156
86 | 0.013838 | 0.0034688 | -0.013836 | -0.0034677 | 1.9537e-06 | 1.0952e-06 | 0.020787 | 0.020787 | 0.020787 | 0.99059 | -0.18059 | 0.99043 | -0.18355 | 5.7108
87 | -0.095454 | -0.024107 | 0.09562 | 0.024213 | 0.0001662 | 0.0001061 | 0.14527 | 0.14527 | 0.14527 | 0.97818 | -0.41896 | 0.98004 | -0.38269 | 39.9098
88 | -0.099108 | -0.025088 | 0.099183 | 0.025135 | 7.4924e-05 | 4.784e-05 | 0.15057 | 0.15057 | 0.15057 | 0.98004 | -0.38269 | 0.98085 | -0.36696 | 41.3648
89 | 0.0034883 | 0.00087416 | -0.0034882 | -0.00087423 | 1.2104e-07 | -6.7519e-08 | 0.0052964 | 0.0052964 | 0.0052964 | 0.98004 | -0.38269 | 0.98 | -0.38342 | 1.4551
90 | 0.026025 | 0.006532 | -0.026012 | -0.0065237 | 1.3529e-05 | 8.3665e-06 | 0.039486 | 0.039486 | 0.039486 | 0.98085 | -0.36696 | 0.98029 | -0.37787 | 10.8478
91 | -0.12521 | -0.031667 | 0.12544 | 0.031813 | 0.00022768 | 0.0001455 | 0.19005 | 0.19005 | 0.19005 | 0.98085 | -0.36696 | 0.9828 | -0.32913 | 52.2125
92 | 0.019289 | 0.0048388 | -0.019283 | -0.0048352 | 6.0426e-06 | 3.6304e-06 | 0.029281 | 0.029281 | 0.029281 | 0.98029 | -0.37787 | 0.97996 | -0.38444 | 8.0443
93 | 0.0067228 | 0.0016849 | -0.0067219 | -0.0016846 | 9.6428e-07 | 3.0588e-07 | 0.010205 | 0.010205 | 0.010205 | 0.98029 | -0.37787 | 0.98014 | -0.38088 | 2.8035
94 | -0.12758 | -0.03235 | 0.12785 | 0.032521 | 0.00026812 | 0.00017136 | 0.1933 | 0.1933 | 0.1933 | 0.9828 | -0.32913 | 0.98505 | -0.28551 | 53.1035
95 | 0.018398 | 0.0046132 | -0.018391 | -0.0046094 | 6.461e-06 | 3.857e-06 | 0.027937 | 0.027937 | 0.027937 | 0.97996 | -0.38444 | 0.97958 | -0.39181 | 7.6749
96 | 0.0044917 | 0.0011257 | -0.0044915 | -0.0011257 | 1.9559e-07 | -1.6178e-08 | 0.0068192 | 0.0068192 | 0.0068192 | 0.98014 | -0.38088 | 0.98009 | -0.38179 | 1.8734
97 | 0.0018853 | 0.00047236 | -0.0018853 | -0.0004725 | 3.8202e-08 | -1.3544e-07 | 0.0028479 | 0.002848 | 0.002848 | 0.98505 | -0.28551 | 0.98503 | -0.28594 | 0.78241
98 | -0.12973 | -0.032994 | 0.12987 | 0.033079 | 0.00013419 | 8.5407e-05 | 0.19614 | 0.19614 | 0.19614 | 0.98505 | -0.28551 | 0.98617 | -0.26407 | 26.9429
99 | -0.0069274 | -0.0017361 | 0.006928 | 0.0017364 | 6.5374e-07 | 2.2039e-07 | 0.010526 | 0.010526 | 0.010526 | 0.97932 | -0.39699 | 0.97942 | -0.39501 | 2.8917
100 | 0.0038787 | 0.00097206 | -0.0038786 | -0.00097207 | 4.468e-08 | -1.4567e-08 | 0.0058934 | 0.0058934 | 0.0058934 | 0.97932 | -0.39699 | 0.97931 | -0.39724 | 1.6191
101 | -0.0087276 | -0.0021874 | 0.0087289 | 0.002188 | 1.332e-06 | 5.9819e-07 | 0.01326 | 0.01326 | 0.01326 | 0.97942 | -0.39501 | 0.97958 | -0.39181 | 3.6428
102 | 0.0096622 | 0.0024214 | -0.0096616 | -0.0024211 | 5.7338e-07 | 2.7761e-07 | 0.014677 | 0.014677 | 0.014677 | 0.97958 | -0.39181 | 0.97952 | -0.39306 | 4.0322
103 | 0.0068878 | 0.001726 | -0.0068875 | -0.0017259 | 3.3854e-07 | 1.1288e-07 | 0.010463 | 0.010463 | 0.010463 | 0.97952 | -0.39306 | 0.97947 | -0.39409 | 2.8746
104 | 0.0037934 | 0.0009504 | -0.0037929 | -0.00095059 | 5.1942e-07 | -1.924e-07 | 0.0057629 | 0.0057631 | 0.0057631 | 0.97947 | -0.39409 | 0.97932 | -0.39696 | 1.5833
105 | -0.13152 | -0.033494 | 0.13156 | 0.033521 | 4.3735e-05 | 2.7386e-05 | 0.19864 | 0.19864 | 0.19864 | 0.98617 | -0.26407 | 0.98652 | -0.25717 | 13.6429
106 | -0.13318 | -0.033926 | 0.1332 | 0.033936 | 1.5879e-05 | 9.9485e-06 | 0.20108 | 0.20108 | 0.20108 | 0.98652 | -0.25717 | 0.98665 | -0.2547 | 13.8105
107 | -0.13801 | -0.035143 | 0.13812 | 0.035212 | 0.00010981 | 6.8899e-05 | 0.20834 | 0.20834 | 0.20834 | 0.98665 | -0.2547 | 0.98751 | -0.23822 | 14.309
108 | -0.14107 | -0.03595 | 0.14108 | 0.035958 | 1.2924e-05 | 8.1158e-06 | 0.21278 | 0.21278 | 0.21278 | 0.98751 | -0.23822 | 0.98761 | -0.23632 | 14.6139
109 | -0.14607 | -0.037209 | 0.14616 | 0.037263 | 8.6496e-05 | 5.4384e-05 | 0.2203 | 0.2203 | 0.2203 | 0.98761 | -0.23632 | 0.98825 | -0.22405 | 15.1303
110 | -0.14857 | -0.037868 | 0.14863 | 0.037906 | 6.0201e-05 | 3.7872e-05 | 0.22393 | 0.22393 | 0.22393 | 0.98825 | -0.22405 | 0.98869 | -0.21566 | 15.3799
111 | -0.15057 | -0.038391 | 0.15057 | 0.038394 | 4.4602e-06 | 2.8071e-06 | 0.22685 | 0.22685 | 0.22685 | 0.98869 | -0.21566 | 0.98872 | -0.21505 | 15.5801
112 | -0.0363 | -0.0091136 | 0.03631 | 0.00912 | 1.0065e-05 | 6.3273e-06 | 0.05476 | 0.05476 | 0.05476 | 0.9865 | -0.25892 | 0.98679 | -0.25311 | 15.0441
113 | -0.0432 | -0.010847 | 0.043262 | 0.010886 | 6.2854e-05 | 3.9721e-05 | 0.065149 | 0.065149 | 0.065149 | 0.98679 | -0.25311 | 0.98836 | -0.22265 | 17.8981
114 | 0.035721 | 0.0089747 | -0.035712 | -0.0089694 | 8.5225e-06 | 5.3537e-06 | 0.053787 | 0.053787 | 0.053787 | 0.98836 | -0.22265 | 0.9881 | -0.22765 | 14.7766
115 | -0.078983 | -0.019861 | 0.07909 | 0.019929 | 0.00010714 | 6.831e-05 | 0.11894 | 0.11894 | 0.11894 | 0.98836 | -0.22265 | 0.98983 | -0.19429 | 32.6746
116 | 0.03207 | 0.0080565 | -0.032058 | -0.0080493 | 1.154e-05 | 7.2164e-06 | 0.048302 | 0.048302 | 0.048302 | 0.9881 | -0.22765 | 0.98772 | -0.2352 | 13.2697
117 | -0.081009 | -0.02041 | 0.081021 | 0.020418 | 1.1999e-05 | 7.6514e-06 | 0.12182 | 0.12182 | 0.12182 | 0.98983 | -0.19429 | 0.98999 | -0.1912 | 33.467
118 | 0.028064 | 0.0070483 | -0.028052 | -0.0070408 | 1.2169e-05 | 7.556e-06 | 0.042285 | 0.042285 | 0.042285 | 0.98772 | -0.2352 | 0.98725 | -0.24429 | 11.6167
119 | 0.02445 | 0.0061381 | -0.024438 | -0.0061303 | 1.2661e-05 | 7.7853e-06 | 0.036856 | 0.036856 | 0.036856 | 0.98725 | -0.24429 | 0.98669 | -0.25515 | 10.1253
120 | 0.019831 | 0.0049758 | -0.019829 | -0.0049747 | 1.8677e-06 | 1.1242e-06 | 0.029909 | 0.029909 | 0.029909 | 0.98669 | -0.25515 | 0.98659 | -0.25713 | 8.2168
121 | 0.019829 | 0.0049747 | -0.019823 | -0.0049711 | 6.012e-06 | 3.6189e-06 | 0.029909 | 0.029909 | 0.029909 | 0.98659 | -0.25713 | 0.98626 | -0.26349 | 8.2168
122 | 0.017039 | 0.0042733 | -0.017033 | -0.0042698 | 5.8219e-06 | 3.4264e-06 | 0.025708 | 0.025709 | 0.025709 | 0.98626 | -0.26349 | 0.98589 | -0.27066 | 7.0628
123 | 0.012073 | 0.0030267 | -0.01207 | -0.003025 | 3.2124e-06 | 1.7271e-06 | 0.018222 | 0.018223 | 0.018223 | 0.98589 | -0.27066 | 0.98561 | -0.27624 | 5.0062
124 | 0.0078609 | 0.0019701 | -0.0078595 | -0.0019696 | 1.3974e-06 | 5.5724e-07 | 0.011868 | 0.011868 | 0.011868 | 0.98561 | -0.27624 | 0.98542 | -0.27997 | 3.2605
125 | 0.0035492 | 0.00088929 | -0.0035489 | -0.00088944 | 2.6633e-07 | -1.4453e-07 | 0.0053593 | 0.0053594 | 0.0053594 | 0.98542 | -0.27997 | 0.98534 | -0.28155 | 1.4724
126 | -0.010256 | -0.0025704 | 0.010261 | 0.0025729 | 5.0571e-06 | 2.5111e-06 | 0.01544 | 0.01544 | 0.01544 | 0.98841 | -0.22116 | 0.98894 | -0.21081 | 4.2418
127 | -0.01439 | -0.0036078 | 0.014395 | 0.0036105 | 4.711e-06 | 2.6711e-06 | 0.021653 | 0.021653 | 0.021653 | 0.98894 | -0.21081 | 0.9893 | -0.20394 | 5.9486
128 | -0.17287 | -0.044019 | 0.17292 | 0.04405 | 5.0046e-05 | 3.1624e-05 | 0.26027 | 0.26027 | 0.26027 | 0.9893 | -0.20394 | 0.98961 | -0.19794 | 17.8757
129 | 0.15848 | 0.040408 | -0.15839 | -0.040355 | 8.4907e-05 | 5.3524e-05 | 0.23862 | 0.23862 | 0.23862 | 0.9893 | -0.20394 | 0.98872 | -0.21505 | 16.3886
130 | -0.17545 | -0.044683 | 0.17567 | 0.04482 | 0.00021677 | 0.00013703 | 0.26407 | 0.26407 | 0.26407 | 0.98961 | -0.19794 | 0.99094 | -0.17236 | 18.1365

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60276 | 0.15356

## res_load
| p_mw | q_mvar
0 | 0.0064666 | 0.0016207
1 | 0.013891 | 0.0034814
2 | 0.012073 | 0.0030257
3 | 0.0058103 | 0.0014562
4 | 0.003007 | 0.00075363
5 | 0.013414 | 0.0033619
6 | 0.0051959 | 0.0013022
7 | 0.0056936 | 0.0014269
8 | 0.0090941 | 0.0022792
9 | 0.0063407 | 0.0015891
10 | 0.0057109 | 0.0014313
11 | 0.004639 | 0.0011626
12 | 0.0073726 | 0.0018477
13 | 0.0085523 | 0.0021434
14 | 0.0067534 | 0.0016926
15 | 0.0050204 | 0.0012582
16 | 0.0041879 | 0.0010496
17 | 0.0023279 | 0.00058342
18 | 0.0019584 | 0.00049082
19 | 0.001816 | 0.00045514
20 | 0.0012714 | 0.00031864
21 | 0.0014787 | 0.00037059
22 | 0.0078254 | 0.0019612
23 | 0.015262 | 0.0038249
24 | 0.0036 | 0.00090223
25 | 0.0055682 | 0.0013955
26 | 0.0089092 | 0.0022329
27 | 0.0037314 | 0.00093518
28 | 0.0070927 | 0.0017776
29 | 0.0035817 | 0.00089767
30 | 0.0085636 | 0.0021462
31 | 0.014113 | 0.003537
32 | 0.0051776 | 0.0012976
33 | 0.0045856 | 0.0011493
34 | 0.0061669 | 0.0015456
35 | 0.0025586 | 0.00064125
36 | 0.0042133 | 0.0010559
37 | 0.0049287 | 0.0012353
38 | 0.032723 | 0.0082012
39 | 0.01609 | 0.0040324
40 | 0.010027 | 0.002513
41 | 0.0055667 | 0.0013951
42 | 0.0055857 | 0.0013999
43 | 0.0034772 | 0.00087147
44 | 0.0040202 | 0.0010075
45 | 0.003409 | 0.00085439
46 | 0.0027072 | 0.0006785
47 | 0.0042473 | 0.0010645
48 | 0.0032146 | 0.00080566
49 | 0.0072642 | 0.0018206
50 | 0.0026412 | 0.00066194
51 | 0.0056923 | 0.0014266
52 | 0.0021607 | 0.00054152
53 | 0.0017658 | 0.00044255
54 | 0.0021556 | 0.00054024
55 | 0.0025564 | 0.00064071
56 | 0.0010945 | 0.0002743
57 | 0.0014274 | 0.00035775
58 | 0.0058425 | 0.0014643
59 | 0.001231 | 0.00030852
60 | 0.0033663 | 0.00084367
61 | 0.0014563 | 0.00036498
62 | 0.0024671 | 0.00061832
63 | 0.0037492 | 0.00093963
64 | 0.0055791 | 0.0013982
65 | 0.0015358 | 0.0003849
66 | 0.001345 | 0.00033708
67 | 0.001475 | 0.00036966
68 | 0.0039109 | 0.00098016
69 | 0.0010554 | 0.00026451
70 | 0.015879 | 0.0039796
71 | 0.012727 | 0.0031896
72 | 0.010516 | 0.0026356
73 | 0.013836 | 0.0034677
74 | 0.0037587 | 0.00094201
75 | 0.0034882 | 0.00087423
76 | 0.015472 | 0.0038777
77 | 0.002142 | 0.00053684
78 | 0.00088548 | 0.00022192
79 | 0.0022301 | 0.00055892
80 | 0.0030487 | 0.00076408
81 | 0.0017996 | 0.00045101
82 | 0.0038786 | 0.00097207
83 | 0.0027738 | 0.00069517
84 | 0.0030941 | 0.00077545
85 | 0.0044915 | 0.0011257
86 | 0.0037929 | 0.00095059
87 | 0.0018853 | 0.0004725
88 | 0.0016542 | 0.00041458
89 | 0.0016181 | 0.00040554
90 | 0.0048133 | 0.0012063
91 | 0.0029457 | 0.00073827
92 | 0.0049911 | 0.0012509
93 | 0.0024131 | 0.00060478
94 | 0.0019373 | 0.00048554
95 | 0.0040283 | 0.0010096
96 | 0.0068893 | 0.0017266
97 | 0.0036424 | 0.00091286
98 | 0.0019189 | 0.00048091
99 | 0.0039939 | 0.001001
100 | 0.0021222 | 0.00053187
101 | 0.0036018 | 0.00090271
102 | 0.0046065 | 0.0011545
103 | 0.0027843 | 0.00069781
104 | 0.0049599 | 0.0012431
105 | 0.0042091 | 0.0010549
106 | 0.0043104 | 0.0010803
107 | 0.0035489 | 0.00088944
108 | 0.010256 | 0.0025704
109 | 0.0041293 | 0.0010349
110 | 0.0025247 | 0.00063275
111 | 0.0078221 | 0.0019604
112 | 0.0033097 | 0.0008295

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1