## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-14_1_2_node_14 | 0.4 | n |  | TRUE
1 | bus_LV_1701-14_1_2_node_15 | 0.4 | n |  | TRUE
2 | bus_LV_1701-14_1_2_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_1701-14_1_2_node_50 | 0.4 | n |  | TRUE
4 | bus_LV_1701-14_1_2_node_47 | 0.4 | n |  | TRUE
5 | bus_LV_1701-14_1_2_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_1701-14_1_2_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1701-14_1_2_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_1701-14_1_2_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_1701-14_1_2_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1701-14_1_2_node_58 | 0.4 | n |  | TRUE
11 | bus_LV_1701-14_1_2_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_1701-14_1_2_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_1701-14_1_2_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1701-14_1_2_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_1701-14_1_2_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_1701-14_1_2_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_1701-14_1_2_node_70 | 0.4 | n |  | TRUE
18 | bus_LV_1701-14_1_2_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_1701-14_1_2_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_1701-14_1_2_node_55 | 0.4 | n |  | TRUE
21 | bus_LV_1701-14_1_2_node_77 | 0.4 | n |  | TRUE
22 | bus_LV_1701-14_1_2_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_1701-14_1_2_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_1701-14_1_2_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_1701-14_1_2_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_1701-14_1_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1701-14_1_2_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_1701-14_1_2_node_68 | 0.4 | n |  | TRUE
29 | bus_LV_1701-14_1_2_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_1701-14_1_2_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_1701-14_1_2_node_76 | 0.4 | n |  | TRUE
32 | bus_MV_230_0_node_124 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-14_1_2_load_14 | 0 | 0.0060892 | 0.0015261 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-14_1_2_load_49 | 5 | 0.037604 | 0.0094245 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-14_1_2_load_56 | 7 | 0.0031092 | 0.00077923 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-14_1_2_load_54 | 8 | 0.011557 | 0.0028964 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-14_1_2_load_58 | 10 | 0.0031082 | 0.000779 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-14_1_2_load_42 | 11 | 0.0093099 | 0.0023333 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-14_1_2_load_43 | 12 | 0.012415 | 0.0031114 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-14_1_2_load_46 | 14 | 0.014978 | 0.0037538 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-14_1_2_load_51 | 15 | 0.011487 | 0.002879 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-14_1_2_load_70 | 17 | 0.013427 | 0.0033652 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-14_1_2_load_52 | 18 | 0.0030807 | 0.0007721 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-14_1_2_load_55 | 20 | 0.0030807 | 0.0007721 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-14_1_2_load_77 | 21 | 0.0030821 | 0.00077245 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-14_1_2_load_59 | 22 | 0.010761 | 0.002697 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-14_1_2_load_60 | 23 | 0.0030799 | 0.00077191 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-14_1_2_load_72 | 24 | 0.0030799 | 0.00077191 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-14_1_2_load_65 | 25 | 0.0164 | 0.0041102 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1701-14_1_2_load_66 | 26 | 0.023082 | 0.0057849 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1701-14_1_2_load_67 | 27 | 0.0078788 | 0.0019746 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1701-14_1_2_load_68 | 28 | 0.0075456 | 0.0018911 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1701-14_1_2_load_69 | 29 | 0.037258 | 0.0093379 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1701-14_1_2_load_78 | 30 | 0.021542 | 0.005399 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1701-14_1_2_load_76 | 31 | 0.0030799 | 0.00077191 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-14_1_2_line_0 |  | 0 | 1 | 0.022248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-14_1_2_line_1 |  | 1 | 2 | 0.069842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-14_1_2_line_2 |  | 2 | 3 | 0.058845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-14_1_2_line_3 |  | 2 | 4 | 0.048491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1701-14_1_2_line_4 |  | 2 | 5 | 0.03145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1701-14_1_2_line_5 |  | 3 | 16 | 0.083748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1701-14_1_2_line_6 |  | 3 | 17 | 0.048761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1701-14_1_2_line_7 |  | 4 | 15 | 0.017833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1701-14_1_2_line_8 |  | 4 | 13 | 0.10974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-14_1_2_line_9 |  | 6 | 7 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1701-14_1_2_line_10 |  | 6 | 8 | 0.010342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1701-14_1_2_line_11 |  | 7 | 9 | 0.016234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-14_1_2_line_12 |  | 9 | 10 | 0.01134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1701-14_1_2_line_13 |  | 10 | 22 | 0.016319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1701-14_1_2_line_14 |  | 11 | 12 | 0.0014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1701-14_1_2_line_15 |  | 12 | 13 | 0.02351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1701-14_1_2_line_16 |  | 13 | 14 | 0.044766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-14_1_2_line_17 |  | 15 | 18 | 0.0015166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-14_1_2_line_18 |  | 16 | 30 | 0.014814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1701-14_1_2_line_19 |  | 17 | 28 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1701-14_1_2_line_20 |  | 18 | 19 | 0.008288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1701-14_1_2_line_21 |  | 19 | 20 | 0.01014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1701-14_1_2_line_22 |  | 20 | 21 | 0.0060706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1701-14_1_2_line_23 |  | 21 | 31 | 0.0060708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1701-14_1_2_line_24 |  | 22 | 23 | 0.0098078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1701-14_1_2_line_25 |  | 23 | 24 | 0.0060689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1701-14_1_2_line_26 |  | 24 | 31 | 0.0060689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1701-14_1_2_line_27 |  | 25 | 26 | 0.0848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1701-14_1_2_line_28 |  | 25 | 27 | 0.02316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1701-14_1_2_line_29 |  | 26 | 28 | 0.021534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1701-14_1_2_line_30 |  | 27 | 29 | 0.011616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-14_1_2_trafo_78 | 0.63 MVA 20/0.4 kV | 32 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2682477.8511 | 1226247.954 | 2682478.0099 | 1226243.064 | 2682476.9467 | 1226236.1 | 2682472.9122 | 1226226.6114
1 | 2682477.8511 | 1226247.954 | 2682480.7144 | 1226249.7504 | 2682483.6526 | 1226252.7043 | 2682490.456 | 1226249.1628 | 2682495.2511 | 1226247.228 | 2682507.1517 | 1226243.4682 | 2682543.155 | 1226235.0505
2 | 2682543.155 | 1226235.0505 | 2682546.4118 | 1226234.7066 | 2682546.466 | 1226231.3495 | 2682547.4215 | 1226228.0494 | 2682548.9029 | 1226222.8997 | 2682553.9434 | 1226205.4689 | 2682557.7121 | 1226200.4733 | 2682566.3665 | 1226199.0257 | 2682573.3525 | 1226199.2672 | 2682576.552 | 1226198.689
3 | 2682543.155 | 1226235.0505 | 2682546.4118 | 1226234.7066 | 2682558.8597 | 1226235.2129 | 2682579.1995 | 1226235.6843 | 2682591.5456 | 1226236.9676
4 | 2682543.155 | 1226235.0505 | 2682547.001 | 1226240.3186 | 2682548.6854 | 1226243.4885 | 2682551.4077 | 1226255.9904 | 2682552.1639 | 1226264.4993
5 | 2682576.552 | 1226198.689 | 2682585.2563 | 1226204.0245 | 2682637.8205 | 1226218.7531 | 2682652.4884 | 1226222.6149 | 2682653.4565 | 1226218.9592
6 | 2682576.552 | 1226198.689 | 2682580.3231 | 1226195.1612 | 2682594.0601 | 1226165.6205 | 2682598.0657 | 1226155.3559
7 | 2682591.5456 | 1226236.9676 | 2682593.1185 | 1226254.7315
8 | 2682698.4181 | 1226260.3231 | 2682689.3898 | 1226255.4054 | 2682674.1794 | 1226250.7687 | 2682631.9754 | 1226244.4339 | 2682605.8371 | 1226238.4558 | 2682591.5456 | 1226236.9676
9 | 2682596.696 | 1226295.1454 | 2682609.8292 | 1226300.3601
10 | 2682596.696 | 1226295.1454 | 2682595.7842 | 1226284.844
11 | 2682624.7187 | 1226306.7867 | 2682620.5191 | 1226304.6047 | 2682609.8292 | 1226300.3601
12 | 2682624.7187 | 1226306.7867 | 2682628.924 | 1226296.2557
13 | 2682628.924 | 1226296.2557 | 2682634.9757 | 1226281.1005 | 2682634.9757 | 1226281.1005
14 | 2682689.4667 | 1226283.6084 | 2682689.982 | 1226282.2679
15 | 2682698.4181 | 1226260.3231 | 2682689.982 | 1226282.2679
16 | 2682698.4181 | 1226260.3231 | 2682728.4265 | 1226275.2615 | 2682738.7133 | 1226279.8044
17 | 2682593.1185 | 1226254.7315 | 2682593.2523 | 1226256.2422
18 | 2682657.0976 | 1226204.6 | 2682653.4565 | 1226218.9592
19 | 2682604.2265 | 1226135.0823 | 2682602.4599 | 1226141.5763 | 2682598.4619 | 1226154.3406 | 2682598.0657 | 1226155.3559
20 | 2682593.9833 | 1226264.498 | 2682593.2523 | 1226256.2422
21 | 2682593.9833 | 1226264.498 | 2682603.3817 | 1226268.3045
22 | 2682609.0083 | 1226270.5833 | 2682603.3817 | 1226268.3045
23 | 2682614.6351 | 1226272.8623 | 2682609.0083 | 1226270.5833
24 | 2682634.9757 | 1226281.1005 | 2682625.8853 | 1226277.4187
25 | 2682625.8853 | 1226277.4187 | 2682620.2602 | 1226275.1405
26 | 2682620.2602 | 1226275.1405 | 2682614.6351 | 1226272.8623
27 | 2682677.5744 | 1226106.9422 | 2682659.7995 | 1226101.823 | 2682652.1783 | 1226101.4614 | 2682619.8633 | 1226092.5956 | 2682615.0097 | 1226095.4635 | 2682609.8803 | 1226114.3039
28 | 2682677.5744 | 1226106.9422 | 2682699.8296 | 1226113.3517
29 | 2682604.2265 | 1226135.0823 | 2682608.2756 | 1226120.198 | 2682609.8803 | 1226114.3039
30 | 2682710.9921 | 1226116.5665 | 2682699.8296 | 1226113.3517

## bus_geodata
| x | y | coords
0 | 2682472.9122 | 1226226.6114
1 | 2682477.8511 | 1226247.954
2 | 2682543.155 | 1226235.0505
3 | 2682576.552 | 1226198.689
4 | 2682591.5456 | 1226236.9676
5 | 2682552.1639 | 1226264.4993
6 | 2682596.696 | 1226295.1454
7 | 2682609.8292 | 1226300.3601
8 | 2682595.7842 | 1226284.844
9 | 2682624.7187 | 1226306.7867
10 | 2682628.924 | 1226296.2557
11 | 2682689.4667 | 1226283.6084
12 | 2682689.982 | 1226282.2679
13 | 2682698.4181 | 1226260.3231
14 | 2682738.7133 | 1226279.8044
15 | 2682593.1185 | 1226254.7315
16 | 2682653.4565 | 1226218.9592
17 | 2682598.0657 | 1226155.3559
18 | 2682593.2523 | 1226256.2422
19 | 2682593.9833 | 1226264.498
20 | 2682603.3817 | 1226268.3045
21 | 2682609.0083 | 1226270.5833
22 | 2682634.9757 | 1226281.1005
23 | 2682625.8853 | 1226277.4187
24 | 2682620.2602 | 1226275.1405
25 | 2682677.5744 | 1226106.9422
26 | 2682609.8803 | 1226114.3039
27 | 2682699.8296 | 1226113.3517
28 | 2682604.2265 | 1226135.0823
29 | 2682710.9921 | 1226116.5665
30 | 2682657.0976 | 1226204.6
31 | 2682614.6351 | 1226272.8623
32 | 2682653.4565 | 1226218.9592

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98067 | -0.36943 | 0.0060892 | 0.0015261
1 | 0.9808 | -0.36697 | 0 | 0
2 | 0.98119 | -0.35927 | 0 | 0
3 | 0.98879 | -0.21241 | 0 | 0
4 | 0.97689 | -0.44323 | 0 | 0
5 | 0.9801 | -0.3807 | 0.037604 | 0.0094245
6 | 0.97322 | -0.51549 | 0 | 0
7 | 0.97337 | -0.51249 | 0.0031092 | 0.00077923
8 | 0.97311 | -0.51769 | 0.011557 | 0.0028964
9 | 0.97359 | -0.50811 | 0 | 0
10 | 0.97375 | -0.50505 | 0.0031082 | 0.000779
11 | 0.97265 | -0.52673 | 0.0093099 | 0.0023333
12 | 0.97266 | -0.52648 | 0.012415 | 0.0031114
13 | 0.97314 | -0.51708 | 0 | 0
14 | 0.97251 | -0.52943 | 0.014978 | 0.0037538
15 | 0.97592 | -0.4623 | 0.011487 | 0.002879
16 | 0.99831 | -0.031621 | 0 | 0
17 | 0.98401 | -0.30465 | 0.013427 | 0.0033652
18 | 0.97585 | -0.46361 | 0.0030807 | 0.0007721
19 | 0.97551 | -0.47028 | 0 | 0
20 | 0.9751 | -0.47844 | 0.0030807 | 0.0007721
21 | 0.97487 | -0.48299 | 0.0030821 | 0.00077245
22 | 0.97402 | -0.49972 | 0.010761 | 0.002697
23 | 0.97428 | -0.49458 | 0.0030799 | 0.00077191
24 | 0.97446 | -0.49106 | 0.0030799 | 0.00077191
25 | 0.97565 | -0.46793 | 0.0164 | 0.0041102
26 | 0.98051 | -0.37285 | 0.023082 | 0.0057849
27 | 0.97468 | -0.48709 | 0.0078788 | 0.0019746
28 | 0.9822 | -0.33988 | 0.0075456 | 0.0018911
29 | 0.97428 | -0.49504 | 0.037258 | 0.0093379
30 | 1 | 0 | -0.25151 | -0.064697
31 | 0.97465 | -0.48719 | 0.0030799 | 0.00077191
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0060892 | -0.0015261 | 0.00609 | 0.0015263 | 7.1221e-07 | 1.7508e-07 | 0.0092395 | 0.0092394 | 0.0092395 | 0.98067 | -0.36943 | 0.9808 | -0.36697 | 2.5383
1 | -0.00609 | -0.0015263 | 0.0060922 | 0.0015268 | 2.2357e-06 | 5.4908e-07 | 0.0092394 | 0.009239 | 0.0092394 | 0.9808 | -0.36697 | 0.98119 | -0.35927 | 2.5383
2 | -0.13961 | -0.03526 | 0.1406 | 0.035893 | 0.00099013 | 0.00063294 | 0.21182 | 0.21182 | 0.21182 | 0.98119 | -0.35927 | 0.98879 | -0.21241 | 58.1934
3 | 0.095877 | 0.024285 | -0.095492 | -0.024039 | 0.00038493 | 0.00024574 | 0.14549 | 0.14549 | 0.14549 | 0.98119 | -0.35927 | 0.97689 | -0.44323 | 39.9707
4 | 0.037643 | 0.0094487 | -0.037604 | -0.0094245 | 3.8441e-05 | 2.4206e-05 | 0.057092 | 0.057092 | 0.057092 | 0.98119 | -0.35927 | 0.9801 | -0.3807 | 15.6846
5 | -0.24729 | -0.063058 | 0.24947 | 0.06445 | 0.0021792 | 0.0013925 | 0.37253 | 0.37253 | 0.37253 | 0.98879 | -0.21241 | 0.99831 | -0.031621 | 51.1721
6 | 0.10669 | 0.027165 | -0.10622 | -0.026863 | 0.00047227 | 0.00030163 | 0.16071 | 0.16071 | 0.16071 | 0.98879 | -0.21241 | 0.98401 | -0.30465 | 44.151
7 | 0.058641 | 0.014748 | -0.058588 | -0.014714 | 5.3379e-05 | 3.394e-05 | 0.089341 | 0.089341 | 0.089341 | 0.97689 | -0.44323 | 0.97592 | -0.4623 | 24.5444
8 | 0.036851 | 0.0092912 | -0.036721 | -0.0092096 | 0.00012975 | 8.1672e-05 | 0.056152 | 0.056152 | 0.056152 | 0.97689 | -0.44323 | 0.97314 | -0.51708 | 15.4265
9 | -0.011558 | -0.002897 | 0.01156 | 0.0028979 | 1.6548e-06 | 8.8346e-07 | 0.017672 | 0.017672 | 0.017672 | 0.97322 | -0.51549 | 0.97337 | -0.51249 | 4.8549
10 | 0.011558 | 0.002897 | -0.011557 | -0.0028964 | 1.2111e-06 | 6.4661e-07 | 0.017672 | 0.017672 | 0.017672 | 0.97322 | -0.51549 | 0.97311 | -0.51769 | 4.8549
11 | -0.014669 | -0.0036771 | 0.014672 | 0.0036789 | 3.0614e-06 | 1.7575e-06 | 0.022425 | 0.022425 | 0.022425 | 0.97337 | -0.51249 | 0.97359 | -0.50811 | 6.1606
12 | -0.014672 | -0.0036789 | 0.014674 | 0.0036801 | 2.1384e-06 | 1.2275e-06 | 0.022425 | 0.022425 | 0.022425 | 0.97359 | -0.50811 | 0.97375 | -0.50505 | 6.1606
13 | -0.017782 | -0.0044591 | 0.017787 | 0.0044618 | 4.519e-06 | 2.6891e-06 | 0.027174 | 0.027174 | 0.027174 | 0.97375 | -0.50505 | 0.97402 | -0.49972 | 7.4655
14 | -0.0093099 | -0.0023333 | 0.00931 | 0.0023333 | 1.0925e-07 | 5.2097e-08 | 0.014243 | 0.014243 | 0.014243 | 0.97265 | -0.52673 | 0.97266 | -0.52648 | 3.9129
15 | -0.021725 | -0.0054447 | 0.021734 | 0.0054507 | 9.7385e-06 | 5.9407e-06 | 0.033235 | 0.033235 | 0.033235 | 0.97266 | -0.52648 | 0.97314 | -0.51708 | 9.1306
16 | 0.014987 | 0.0037589 | -0.014978 | -0.0037538 | 8.8167e-06 | 5.0869e-06 | 0.022917 | 0.022917 | 0.022917 | 0.97314 | -0.51708 | 0.97251 | -0.52943 | 6.296
17 | 0.0471 | 0.011835 | -0.047097 | -0.011833 | 2.9341e-06 | 1.8589e-06 | 0.071827 | 0.071827 | 0.071827 | 0.97592 | -0.4623 | 0.97585 | -0.46361 | 19.7326
18 | -0.24947 | -0.06445 | 0.24986 | 0.064697 | 0.00038548 | 0.00024632 | 0.37253 | 0.37253 | 0.37253 | 0.99831 | -0.031621 | 1 | 0 | 51.172
19 | 0.092792 | 0.023498 | -0.092635 | -0.023398 | 0.00015669 | 0.00010001 | 0.14041 | 0.14041 | 0.14041 | 0.98401 | -0.30465 | 0.9822 | -0.33988 | 38.5729
20 | 0.044017 | 0.011061 | -0.044003 | -0.011052 | 1.4006e-05 | 8.8601e-06 | 0.067129 | 0.067129 | 0.067129 | 0.97585 | -0.46361 | 0.97551 | -0.47028 | 18.442
21 | 0.044003 | 0.011052 | -0.043986 | -0.011041 | 1.7135e-05 | 1.084e-05 | 0.067129 | 0.067129 | 0.067129 | 0.97551 | -0.47028 | 0.9751 | -0.47844 | 18.442
22 | 0.040905 | 0.010269 | -0.040896 | -0.010263 | 8.8719e-06 | 5.6023e-06 | 0.062428 | 0.062428 | 0.062428 | 0.9751 | -0.47844 | 0.97487 | -0.48299 | 17.1505
23 | 0.037814 | 0.009491 | -0.037806 | -0.0094862 | 7.5855e-06 | 4.779e-06 | 0.057723 | 0.057723 | 0.057723 | 0.97487 | -0.48299 | 0.97465 | -0.48719 | 15.8581
24 | -0.028548 | -0.0071588 | 0.028555 | 0.0071632 | 6.9961e-06 | 4.3554e-06 | 0.043614 | 0.043614 | 0.043614 | 0.97402 | -0.49972 | 0.97428 | -0.49458 | 11.9819
25 | -0.031635 | -0.0079351 | 0.03164 | 0.0079384 | 5.3133e-06 | 3.3249e-06 | 0.048318 | 0.048318 | 0.048318 | 0.97428 | -0.49458 | 0.97446 | -0.49106 | 13.2742
26 | -0.03472 | -0.0087103 | 0.034726 | 0.0087143 | 6.398e-06 | 4.0191e-06 | 0.053021 | 0.053021 | 0.053021 | 0.97446 | -0.49106 | 0.97465 | -0.48719 | 14.5663
27 | -0.061592 | -0.015458 | 0.061873 | 0.015636 | 0.00028066 | 0.00017856 | 0.093945 | 0.093945 | 0.093945 | 0.97565 | -0.46793 | 0.98051 | -0.37285 | 25.8091
28 | 0.045193 | 0.011347 | -0.045151 | -0.011321 | 4.1269e-05 | 2.6123e-05 | 0.068933 | 0.068933 | 0.068933 | 0.97565 | -0.46793 | 0.97468 | -0.48709 | 18.9377
29 | -0.084955 | -0.021421 | 0.085089 | 0.021507 | 0.00013433 | 8.5696e-05 | 0.12897 | 0.12897 | 0.12897 | 0.98051 | -0.37285 | 0.9822 | -0.33988 | 35.4325
30 | 0.037273 | 0.0093467 | -0.037258 | -0.0093379 | 1.4106e-05 | 8.883e-06 | 0.056905 | 0.056905 | 0.056905 | 0.97468 | -0.48709 | 0.97428 | -0.49504 | 15.6333

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27305 | 0.070096

## res_load
| p_mw | q_mvar
0 | 0.0060892 | 0.0015261
1 | 0.037604 | 0.0094245
2 | 0.0031092 | 0.00077923
3 | 0.011557 | 0.0028964
4 | 0.0031082 | 0.000779
5 | 0.0093099 | 0.0023333
6 | 0.012415 | 0.0031114
7 | 0.014978 | 0.0037538
8 | 0.011487 | 0.002879
9 | 0.013427 | 0.0033652
10 | 0.0030807 | 0.0007721
11 | 0.0030807 | 0.0007721
12 | 0.0030821 | 0.00077245
13 | 0.010761 | 0.002697
14 | 0.0030799 | 0.00077191
15 | 0.0030799 | 0.00077191
16 | 0.0164 | 0.0041102
17 | 0.023082 | 0.0057849
18 | 0.0078788 | 0.0019746
19 | 0.0075456 | 0.0018911
20 | 0.037258 | 0.0093379
21 | 0.021542 | 0.005399
22 | 0.0030799 | 0.00077191

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1