## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-15_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1701-15_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1701-15_0_5_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_1701-15_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1701-15_0_5_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1701-15_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1701-15_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1701-15_0_5_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1701-15_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1701-15_0_5_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1701-15_0_5_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1701-15_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1701-15_0_5_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1701-15_0_5_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_1701-15_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1701-15_0_5_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1701-15_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1701-15_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1701-15_0_5_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1701-15_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1701-15_0_5_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1701-15_0_5_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1701-15_0_5_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1701-15_0_5_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_1701-15_0_5_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1701-15_0_5_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1701-15_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1701-15_0_5_node_28 | 0.4 | n |  | TRUE
28 | bus_MV_230_0_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-15_0_5_load_0 | 0 | 0.038969 | 0.0097666 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-15_0_5_load_3 | 3 | 0.01925 | 0.0048245 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-15_0_5_load_12 | 4 | 0.02583 | 0.0064737 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-15_0_5_load_17 | 7 | 0.027463 | 0.0068829 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-15_0_5_load_16 | 10 | 0.027463 | 0.0068828 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-15_0_5_load_30 | 13 | 0.01968 | 0.0049324 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-15_0_5_load_11 | 14 | 0.029305 | 0.0073445 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-15_0_5_load_18 | 15 | 0.088142 | 0.02209 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-15_0_5_load_22 | 17 | 0.020424 | 0.0051188 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-15_0_5_load_19 | 18 | 0.046856 | 0.011743 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-15_0_5_load_24 | 21 | 0.015031 | 0.003767 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-15_0_5_load_23 | 22 | 0.010878 | 0.0027263 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-15_0_5_load_29 | 23 | 0.013877 | 0.0034779 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-15_0_5_load_26 | 24 | 0.015456 | 0.0038736 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-15_0_5_load_27 | 25 | 0.015474 | 0.0038782 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-15_0_5_load_21 | 26 | 0.012996 | 0.0032572 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-15_0_5_load_28 | 27 | 0.014949 | 0.0037466 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-15_0_5_line_0 |  | 0 | 1 | 0.065227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-15_0_5_line_1 |  | 1 | 2 | 0.11848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-15_0_5_line_2 |  | 2 | 14 | 0.11213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-15_0_5_line_3 |  | 2 | 11 | 0.064744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1701-15_0_5_line_4 |  | 3 | 4 | 0.069526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1701-15_0_5_line_5 |  | 4 | 14 | 0.020952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1701-15_0_5_line_6 |  | 5 | 6 | 0.074441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1701-15_0_5_line_7 |  | 5 | 7 | 0.023189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1701-15_0_5_line_8 |  | 6 | 10 | 0.022005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-15_0_5_line_9 |  | 7 | 8 | 0.0019109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1701-15_0_5_line_10 |  | 8 | 9 | 0.097891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1701-15_0_5_line_11 |  | 9 | 15 | 0.020532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-15_0_5_line_12 |  | 9 | 11 | 0.082737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1701-15_0_5_line_13 |  | 11 | 12 | 0.037725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1701-15_0_5_line_14 |  | 11 | 13 | 0.027013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1701-15_0_5_line_15 |  | 12 | 26 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1701-15_0_5_line_16 |  | 12 | 18 | 0.03413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-15_0_5_line_17 |  | 13 | 23 | 0.0068182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-15_0_5_line_18 |  | 16 | 17 | 0.028151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1701-15_0_5_line_19 |  | 16 | 18 | 0.0043471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1701-15_0_5_line_20 |  | 17 | 19 | 0.0036406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1701-15_0_5_line_21 |  | 19 | 20 | 0.029263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1701-15_0_5_line_22 |  | 20 | 22 | 0.042562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1701-15_0_5_line_23 |  | 21 | 22 | 0.046207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1701-15_0_5_line_24 |  | 24 | 25 | 0.016681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1701-15_0_5_line_25 |  | 25 | 27 | 0.016541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1701-15_0_5_line_26 |  | 26 | 27 | 0.0091926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-15_0_5_trafo_13 | 0.63 MVA 20/0.4 kV | 28 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2682850.3777 | 1226592.8413 | 2682886.5271 | 1226602.1176 | 2682904.7952 | 1226604.8406 | 2682914.1603 | 1226606.0014
1 | 2682850.3777 | 1226592.8413 | 2682852.357 | 1226575.368 | 2682858.1266 | 1226575.8375 | 2682860.3039 | 1226571.8985 | 2682862.0058 | 1226552.5757 | 2682863.7148 | 1226538.7233 | 2682867.6819 | 1226534.1866 | 2682876.9454 | 1226499.881 | 2682881.8831 | 1226484.9841
2 | 2682881.8831 | 1226484.9841 | 2682893.1848 | 1226505.689 | 2682896.9877 | 1226509.122 | 2682902.3378 | 1226511.9541 | 2682935.2134 | 1226519.0169 | 2682945.7886 | 1226523.3117 | 2682954.9285 | 1226530.5107 | 2682964.9621 | 1226540.4796 | 2682970.6164 | 1226543.7829
3 | 2682881.8831 | 1226484.9841 | 2682882.7615 | 1226482.3278 | 2682894.3069 | 1226447.476 | 2682900.7774 | 1226430.8436 | 2682893.3977 | 1226431.1299
4 | 2682991.4326 | 1226545.8193 | 2682994.6228 | 1226545.9635 | 2683003.7195 | 1226545.9348 | 2683031.6381 | 1226543.7116 | 2683033.8622 | 1226572.8555
5 | 2682970.6164 | 1226543.7829 | 2682979.684 | 1226545.2881 | 2682991.4326 | 1226545.8193
6 | 2683021.8645 | 1226470.0583 | 2683027.2547 | 1226471.1009 | 2683029.7974 | 1226471.948 | 2683039.4529 | 1226471.538 | 2683056.9624 | 1226469.9813 | 2683054.1337 | 1226440.7552 | 2683053.1992 | 1226431.1356
7 | 2683053.1992 | 1226431.1356 | 2683052.11 | 1226422.8258 | 2683049.5812 | 1226408.2353
8 | 2683021.8645 | 1226470.0583 | 2683023.6438 | 1226485.9495 | 2683024.1981 | 1226491.9381
9 | 2683049.2548 | 1226406.3525 | 2683049.5812 | 1226408.2353
10 | 2682956.9227 | 1226408.1883 | 2682962.0984 | 1226407.7712 | 2683003.4275 | 1226404.4563 | 2683012.3748 | 1226403.7362 | 2683013.1484 | 1226409.6844 | 2683018.3087 | 1226409.2783 | 2683039.3286 | 1226407.1479 | 2683049.2548 | 1226406.3525
11 | 2682956.9227 | 1226408.1883 | 2682955.5222 | 1226408.6024 | 2682955.2524 | 1226405.6633 | 2682953.772 | 1226389.6117
12 | 2682893.3977 | 1226431.1299 | 2682900.7774 | 1226430.8436 | 2682916.4015 | 1226430.2275 | 2682930.7832 | 1226429.5608 | 2682947.3253 | 1226428.346 | 2682947.3353 | 1226421.6527 | 2682950.1915 | 1226421.2256 | 2682955.8235 | 1226420.6926 | 2682957.0566 | 1226420.3318 | 2682957.4656 | 1226418.7252 | 2682956.9227 | 1226408.1883
13 | 2682904.8675 | 1226395.1874 | 2682898.0312 | 1226416.8514 | 2682893.3977 | 1226431.1299
14 | 2682893.3977 | 1226431.1299 | 2682881.2201 | 1226427.5801 | 2682866.9554 | 1226428.9279
15 | 2682904.8675 | 1226395.1874 | 2682890.7278 | 1226390.7415
16 | 2682904.8675 | 1226395.1874 | 2682917.0186 | 1226363.2937
17 | 2682860.1674 | 1226429.5693 | 2682866.9554 | 1226428.9279
18 | 2682918.5663 | 1226359.2314 | 2682928.5922 | 1226332.9263
19 | 2682918.5663 | 1226359.2314 | 2682917.0186 | 1226363.2937
20 | 2682929.8888 | 1226329.5245 | 2682928.5922 | 1226332.9263
21 | 2682929.8888 | 1226329.5245 | 2682934.9474 | 1226310.3263 | 2682925.5382 | 1226310.4508
22 | 2682925.5382 | 1226310.4508 | 2682922.3538 | 1226310.4954 | 2682884.1565 | 1226320.0644
23 | 2682839.1792 | 1226322.4904 | 2682843.0321 | 1226323.4996 | 2682855.4751 | 1226326.5193 | 2682863.8707 | 1226325.1464 | 2682884.1565 | 1226320.0644
24 | 2682865.4807 | 1226387.1517 | 2682859.6842 | 1226387.8642 | 2682849.1712 | 1226390.5086 | 2682849.1712 | 1226390.5086
25 | 2682865.4807 | 1226387.1517 | 2682870.7326 | 1226386.506 | 2682881.7464 | 1226388.7981
26 | 2682881.7464 | 1226388.7981 | 2682890.0295 | 1226390.5219 | 2682890.7278 | 1226390.7415

## bus_geodata
| x | y | coords
0 | 2682914.1603 | 1226606.0014
1 | 2682850.3777 | 1226592.8413
2 | 2682881.8831 | 1226484.9841
3 | 2683033.8622 | 1226572.8555
4 | 2682991.4326 | 1226545.8193
5 | 2683053.1992 | 1226431.1356
6 | 2683021.8645 | 1226470.0583
7 | 2683049.5812 | 1226408.2353
8 | 2683049.2548 | 1226406.3525
9 | 2682956.9228 | 1226408.1883
10 | 2683024.1981 | 1226491.9381
11 | 2682893.3977 | 1226431.1299
12 | 2682904.8675 | 1226395.1874
13 | 2682866.9554 | 1226428.9279
14 | 2682970.6164 | 1226543.7829
15 | 2682953.772 | 1226389.6117
16 | 2682918.5663 | 1226359.2314
17 | 2682928.5922 | 1226332.9263
18 | 2682917.0186 | 1226363.2937
19 | 2682929.8888 | 1226329.5245
20 | 2682925.5382 | 1226310.4508
21 | 2682839.1792 | 1226322.4904
22 | 2682884.1565 | 1226320.0644
23 | 2682860.1674 | 1226429.5693
24 | 2682849.1712 | 1226390.5086
25 | 2682865.4807 | 1226387.1517
26 | 2682890.7278 | 1226390.7415
27 | 2682881.7464 | 1226388.7981
28 | 2682947.3353 | 1226421.6527

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97895 | -0.40496 | 0.038969 | 0.0097666
1 | 0.9813 | -0.35885 | 0 | 0
2 | 0.98558 | -0.27563 | 0 | 0
3 | 0.97571 | -0.46819 | 0.01925 | 0.0048245
4 | 0.97696 | -0.44372 | 0.02583 | 0.0064737
5 | 0.99441 | -0.10725 | 0 | 0
6 | 0.99255 | -0.14336 | 0 | 0
7 | 0.995 | -0.096033 | 0.027463 | 0.0068829
8 | 0.99509 | -0.094185 | 0 | 0
9 | 1 | 0 | -0.44868 | -0.11396
10 | 0.99199 | -0.15405 | 0.027463 | 0.0068828
11 | 0.99239 | -0.14483 | 0 | 0
12 | 0.98975 | -0.19573 | 0 | 0
13 | 0.99156 | -0.16089 | 0.01968 | 0.0049324
14 | 0.97783 | -0.42649 | 0.029305 | 0.0073445
15 | 0.99836 | -0.031594 | 0.088142 | 0.02209
16 | 0.98664 | -0.2561 | 0 | 0
17 | 0.98544 | -0.27948 | 0.020424 | 0.0051188
18 | 0.98683 | -0.25249 | 0.046856 | 0.011743
19 | 0.98535 | -0.28117 | 0 | 0
20 | 0.98465 | -0.2948 | 0 | 0
21 | 0.983 | -0.32716 | 0.015031 | 0.003767
22 | 0.98364 | -0.31464 | 0.010878 | 0.0027263
23 | 0.99148 | -0.16256 | 0.013877 | 0.0034779
24 | 0.98786 | -0.23252 | 0.015456 | 0.0038736
25 | 0.9881 | -0.22792 | 0.015474 | 0.0038782
26 | 0.98895 | -0.21127 | 0.012996 | 0.0032572
27 | 0.98857 | -0.21879 | 0.014949 | 0.0037466
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.038969 | -0.0097666 | 0.039055 | 0.0098207 | 8.5822e-05 | 5.4104e-05 | 0.059234 | 0.059234 | 0.059234 | 0.97895 | -0.40496 | 0.9813 | -0.35885 | 16.273
1 | -0.039055 | -0.0098207 | 0.039211 | 0.009919 | 0.00015589 | 9.8267e-05 | 0.059234 | 0.059233 | 0.059234 | 0.9813 | -0.35885 | 0.98558 | -0.27563 | 16.2729
2 | 0.074984 | 0.019024 | -0.074445 | -0.01868 | 0.00053972 | 0.00034401 | 0.11329 | 0.11329 | 0.11329 | 0.98558 | -0.27563 | 0.97783 | -0.42649 | 31.1247
3 | -0.1142 | -0.028943 | 0.11492 | 0.029404 | 0.00072267 | 0.00046168 | 0.17253 | 0.17253 | 0.17253 | 0.98558 | -0.27563 | 0.99239 | -0.14483 | 47.3974
4 | -0.01925 | -0.0048245 | 0.019272 | 0.004838 | 2.247e-05 | 1.3511e-05 | 0.029357 | 0.029357 | 0.029357 | 0.97571 | -0.46819 | 0.97696 | -0.44372 | 8.0652
5 | -0.045103 | -0.011312 | 0.04514 | 0.011335 | 3.7083e-05 | 2.347e-05 | 0.0687 | 0.068699 | 0.0687 | 0.97696 | -0.44372 | 0.97783 | -0.42649 | 18.8735
6 | 0.027524 | 0.0069209 | -0.027477 | -0.0068915 | 4.7372e-05 | 2.9354e-05 | 0.041194 | 0.041195 | 0.041195 | 0.99441 | -0.10725 | 0.99255 | -0.14336 | 11.3173
7 | -0.027524 | -0.0069209 | 0.027539 | 0.00693 | 1.4757e-05 | 9.1433e-06 | 0.041194 | 0.041194 | 0.041194 | 0.99441 | -0.10725 | 0.995 | -0.096033 | 11.3172
8 | 0.027477 | 0.0068915 | -0.027463 | -0.0068828 | 1.4003e-05 | 8.6779e-06 | 0.041195 | 0.041195 | 0.041195 | 0.99255 | -0.14336 | 0.99199 | -0.15405 | 11.3173
9 | -0.055002 | -0.013813 | 0.055007 | 0.013816 | 4.8496e-06 | 3.0789e-06 | 0.082265 | 0.082265 | 0.082265 | 0.995 | -0.096033 | 0.99509 | -0.094185 | 22.6004
10 | -0.055007 | -0.013816 | 0.055255 | 0.013974 | 0.00024843 | 0.00015772 | 0.082265 | 0.082265 | 0.082265 | 0.99509 | -0.094185 | 1 | 0 | 22.6004
11 | 0.088274 | 0.022175 | -0.088142 | -0.02209 | 0.00013288 | 8.4774e-05 | 0.13137 | 0.13137 | 0.13137 | 1 | 0 | 0.99836 | -0.031594 | 36.0912
12 | 0.3035 | 0.07781 | -0.30138 | -0.076459 | 0.0021151 | 0.0013504 | 0.45223 | 0.45223 | 0.45223 | 1 | 0 | 0.99239 | -0.14483 | 41.4128
13 | 0.15288 | 0.038628 | -0.15251 | -0.038391 | 0.00037205 | 0.00023714 | 0.22934 | 0.22934 | 0.22934 | 0.99239 | -0.14483 | 0.98975 | -0.19573 | 31.5031
14 | 0.033584 | 0.008427 | -0.033558 | -0.0084109 | 2.5691e-05 | 1.6093e-05 | 0.05036 | 0.05036 | 0.05036 | 0.99239 | -0.14483 | 0.99156 | -0.16089 | 13.8353
15 | 0.058952 | 0.014804 | -0.058909 | -0.014776 | 4.3673e-05 | 2.776e-05 | 0.088641 | 0.088641 | 0.088641 | 0.98975 | -0.19573 | 0.98895 | -0.21127 | 24.3518
16 | 0.093555 | 0.023587 | -0.093301 | -0.023425 | 0.00025338 | 0.00016172 | 0.1407 | 0.1407 | 0.1407 | 0.98975 | -0.19573 | 0.98683 | -0.25249 | 38.6543
17 | 0.013878 | 0.0034785 | -0.013877 | -0.0034779 | 1.109e-06 | 6.2182e-07 | 0.020826 | 0.020827 | 0.020827 | 0.99156 | -0.16089 | 0.99148 | -0.16256 | 5.7216
18 | 0.046437 | 0.011677 | -0.046385 | -0.011644 | 5.1799e-05 | 3.2792e-05 | 0.070048 | 0.070048 | 0.070048 | 0.98664 | -0.2561 | 0.98544 | -0.27948 | 19.244
19 | -0.046437 | -0.011677 | 0.046445 | 0.011682 | 7.9988e-06 | 5.0637e-06 | 0.070048 | 0.070048 | 0.070048 | 0.98664 | -0.2561 | 0.98683 | -0.25249 | 19.244
20 | 0.025961 | 0.0065253 | -0.025959 | -0.006524 | 2.0987e-06 | 1.2968e-06 | 0.039208 | 0.039208 | 0.039208 | 0.98544 | -0.27948 | 0.98535 | -0.28117 | 10.7714
21 | 0.025959 | 0.006524 | -0.025942 | -0.0065136 | 1.687e-05 | 1.0424e-05 | 0.039208 | 0.039208 | 0.039208 | 0.98535 | -0.28117 | 0.98465 | -0.2948 | 10.7715
22 | 0.025942 | 0.0065136 | -0.025918 | -0.0064985 | 2.4536e-05 | 1.5163e-05 | 0.039208 | 0.039208 | 0.039208 | 0.98465 | -0.2948 | 0.98364 | -0.31464 | 10.7715
23 | -0.015031 | -0.003767 | 0.01504 | 0.0037722 | 8.97e-06 | 5.1547e-06 | 0.022753 | 0.022752 | 0.022753 | 0.983 | -0.32716 | 0.98364 | -0.31464 | 6.2507
24 | -0.015456 | -0.0038736 | 0.015459 | 0.0038756 | 3.3904e-06 | 1.9563e-06 | 0.023281 | 0.023281 | 0.023281 | 0.98786 | -0.23252 | 0.9881 | -0.22792 | 6.396
25 | -0.030934 | -0.0077538 | 0.030947 | 0.0077622 | 1.3461e-05 | 8.4031e-06 | 0.046584 | 0.046584 | 0.046584 | 0.9881 | -0.22792 | 0.98857 | -0.21879 | 12.7979
26 | 0.045912 | 0.011519 | -0.045896 | -0.011509 | 1.6453e-05 | 1.0412e-05 | 0.069086 | 0.069086 | 0.069086 | 0.98895 | -0.21127 | 0.98857 | -0.21879 | 18.9797

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44868 | 0.11396

## res_load
| p_mw | q_mvar
0 | 0.038969 | 0.0097666
1 | 0.01925 | 0.0048245
2 | 0.02583 | 0.0064737
3 | 0.027463 | 0.0068829
4 | 0.027463 | 0.0068828
5 | 0.01968 | 0.0049324
6 | 0.029305 | 0.0073445
7 | 0.088142 | 0.02209
8 | 0.020424 | 0.0051188
9 | 0.046856 | 0.011743
10 | 0.015031 | 0.003767
11 | 0.010878 | 0.0027263
12 | 0.013877 | 0.0034779
13 | 0.015456 | 0.0038736
14 | 0.015474 | 0.0038782
15 | 0.012996 | 0.0032572
16 | 0.014949 | 0.0037466

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1