## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-23_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1701-23_0_3_node_15 | 0.4 | n |  | TRUE
2 | bus_LV_1701-23_0_3_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_1701-23_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1701-23_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1701-23_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1701-23_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1701-23_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1701-23_0_3_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1701-23_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1701-23_0_3_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_1701-23_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1701-23_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1701-23_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1701-23_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1701-23_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1701-23_0_3_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1701-23_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1701-23_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1701-23_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1701-23_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1701-23_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1701-23_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1701-23_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1701-23_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1701-23_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1701-23_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1701-23_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1701-23_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1701-23_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1701-23_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1701-23_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1701-23_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1701-23_0_3_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1701-23_0_3_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_1701-23_0_3_node_36 | 0.4 | n |  | TRUE
36 | bus_MV_0_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-23_0_3_load_0 | 0 | 0.00056414 | 0.00014139 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-23_0_3_load_15 | 1 | 0.00067166 | 0.00016833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-23_0_3_load_2 | 3 | 0.0006164 | 0.00015448 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-23_0_3_load_3 | 4 | 0.00017427 | 4.3677e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-23_0_3_load_5 | 6 | 0.00020772 | 5.2059e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-23_0_3_load_6 | 7 | 0.00022552 | 5.6521e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-23_0_3_load_34 | 10 | 0.0015096 | 0.00037834 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-23_0_3_load_7 | 11 | 0.00039719 | 9.9545e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-23_0_3_load_8 | 12 | 0.00065043 | 0.00016301 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-23_0_3_load_11 | 14 | 0.00031342 | 7.855e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-23_0_3_load_16 | 15 | 0.00081459 | 0.00020415 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-23_0_3_load_17 | 16 | 0.0053547 | 0.001342 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-23_0_3_load_12 | 17 | 0.0023649 | 0.00059271 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-23_0_3_load_13 | 18 | 0.00015387 | 3.8565e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-23_0_3_load_18 | 19 | 0.00056174 | 0.00014078 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-23_0_3_load_23 | 21 | 0.00023003 | 5.7652e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-23_0_3_load_24 | 22 | 0.00052144 | 0.00013069 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1701-23_0_3_load_20 | 23 | 0.00031433 | 7.8777e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1701-23_0_3_load_21 | 24 | 0.00034316 | 8.6004e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1701-23_0_3_load_22 | 25 | 0.00030627 | 7.6758e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1701-23_0_3_load_31 | 26 | 0.0015481 | 0.00038798 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1701-23_0_3_load_25 | 27 | 0.0018462 | 0.0004627 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1701-23_0_3_load_26 | 28 | 0.00066568 | 0.00016683 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1701-23_0_3_load_28 | 30 | 0.0024076 | 0.00060341 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1701-23_0_3_load_29 | 31 | 0.0014268 | 0.00035759 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1701-23_0_3_load_36 | 35 | 0.002953 | 0.0007401 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-23_0_3_line_0 |  | 0 | 1 | 0.46281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-23_0_3_line_1 |  | 1 | 2 | 0.09294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-23_0_3_line_2 |  | 2 | 15 | 0.022661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-23_0_3_line_3 |  | 2 | 17 | 0.033152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1701-23_0_3_line_4 |  | 3 | 4 | 0.012005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1701-23_0_3_line_5 |  | 3 | 5 | 0.013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1701-23_0_3_line_6 |  | 4 | 6 | 0.028962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1701-23_0_3_line_7 |  | 5 | 7 | 0.015171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1701-23_0_3_line_8 |  | 6 | 8 | 0.026104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-23_0_3_line_9 |  | 7 | 9 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1701-23_0_3_line_10 |  | 8 | 10 | 0.040267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1701-23_0_3_line_11 |  | 9 | 11 | 0.04426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-23_0_3_line_12 |  | 11 | 12 | 0.024918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1701-23_0_3_line_13 |  | 12 | 13 | 0.021548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1701-23_0_3_line_14 |  | 13 | 14 | 0.0073639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1701-23_0_3_line_15 |  | 14 | 15 | 0.065583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1701-23_0_3_line_16 |  | 15 | 16 | 0.16945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-23_0_3_line_17 |  | 16 | 19 | 0.050936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-23_0_3_line_18 |  | 17 | 18 | 0.0068565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1701-23_0_3_line_19 |  | 19 | 20 | 0.018397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1701-23_0_3_line_20 |  | 20 | 23 | 0.0078177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1701-23_0_3_line_21 |  | 21 | 22 | 0.042881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1701-23_0_3_line_22 |  | 22 | 26 | 0.45719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1701-23_0_3_line_23 |  | 22 | 25 | 0.029193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1701-23_0_3_line_24 |  | 23 | 24 | 0.012289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1701-23_0_3_line_25 |  | 24 | 25 | 0.0016337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1701-23_0_3_line_26 |  | 26 | 33 | 0.015397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1701-23_0_3_line_27 |  | 27 | 28 | 0.0098817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1701-23_0_3_line_28 |  | 27 | 29 | 0.021446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1701-23_0_3_line_29 |  | 28 | 30 | 0.0097505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1701-23_0_3_line_30 |  | 29 | 31 | 0.010495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1701-23_0_3_line_31 |  | 29 | 32 | 0.03371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1701-23_0_3_line_32 |  | 31 | 33 | 0.0042527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1701-23_0_3_line_33 |  | 32 | 34 | 0.003703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1701-23_0_3_line_34 |  | 34 | 35 | 0.031695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-23_0_3_trafo_24 | 0.63 MVA 20/0.4 kV | 36 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2683339.5862 | 1230101.7962 | 2683659.5946 | 1229767.4439
1 | 2683275.5349 | 1230156.4603 | 2683288.6451 | 1230153.9866 | 2683306.6885 | 1230146.5452 | 2683312.9531 | 1230141.1737 | 2683317.4756 | 1230133.6207 | 2683322.6726 | 1230111.456 | 2683326.4947 | 1230106.306 | 2683339.5862 | 1230101.7962
2 | 2683275.5349 | 1230156.4603 | 2683259.7556 | 1230172.7253
3 | 2683275.5349 | 1230156.4603 | 2683283.2588 | 1230146.417 | 2683285.919 | 1230137.1479 | 2683284.0003 | 1230126.4803
4 | 2683119.0467 | 1230291.5552 | 2683107.427 | 1230294.5716
5 | 2683132.3021 | 1230288.1143 | 2683119.0467 | 1230291.5552
6 | 2683085.1158 | 1230312.9763 | 2683107.022 | 1230294.6767 | 2683107.427 | 1230294.5716
7 | 2683132.3021 | 1230288.1143 | 2683147.0042 | 1230284.3719
8 | 2683062.2425 | 1230320.2244 | 2683065.9181 | 1230322.2883 | 2683077.397 | 1230319.4244 | 2683085.1158 | 1230312.9763
9 | 2683160.7888 | 1230280.8631 | 2683147.0042 | 1230284.3719
10 | 2683062.2425 | 1230320.2244 | 2683057.9614 | 1230313.7935 | 2683058.7494 | 1230281.2598
11 | 2683160.7888 | 1230280.8631 | 2683164.8511 | 1230256.9033 | 2683167.2495 | 1230237.0898
12 | 2683167.2495 | 1230237.0898 | 2683173.2193 | 1230224.0754 | 2683182.6608 | 1230219.2584
13 | 2683201.8548 | 1230209.4658 | 2683182.6608 | 1230219.2584
14 | 2683201.8548 | 1230209.4658 | 2683201.5446 | 1230202.401 | 2683201.8113 | 1230202.2812
15 | 2683259.7556 | 1230172.7253 | 2683253.6973 | 1230178.9701 | 2683201.8113 | 1230202.2812
16 | 2683259.7556 | 1230172.7253 | 2683383.2155 | 1230288.7955
17 | 2683431.0551 | 1230276.0931 | 2683411.9577 | 1230275.1541 | 2683383.2155 | 1230288.7955
18 | 2683279.6578 | 1230121.1742 | 2683284.0003 | 1230126.4803 | 2683284.0003 | 1230126.4803
19 | 2683449.4114 | 1230275.1128 | 2683433.4799 | 1230276.2123 | 2683431.0551 | 1230276.0931
20 | 2683449.4114 | 1230275.1128 | 2683453.3009 | 1230281.8943
21 | 2683491.3695 | 1230298.6328 | 2683492.5826 | 1230303.7941 | 2683466.278 | 1230330.6321
22 | 2683491.3695 | 1230298.6328 | 2683923.2074 | 1230448.7634
23 | 2683466.9513 | 1230284.6363 | 2683473.3572 | 1230285.923 | 2683490.8599 | 1230296.4649 | 2683491.3695 | 1230298.6328
24 | 2683465.3496 | 1230284.3145 | 2683453.3009 | 1230281.8943 | 2683453.3009 | 1230281.8943
25 | 2683466.9513 | 1230284.6363 | 2683465.3496 | 1230284.3145
26 | 2683937.3577 | 1230454.6926 | 2683925.5344 | 1230450.2783 | 2683923.2074 | 1230448.7634
27 | 2683968.2711 | 1230465.1396 | 2683970.4712 | 1230465.2674 | 2683977.6167 | 1230468.0765
28 | 2683946.8672 | 1230464.7005 | 2683953.017 | 1230464.2536 | 2683968.2711 | 1230465.1396
29 | 2683985.6307 | 1230473.2092 | 2683982.6754 | 1230470.0653 | 2683977.6167 | 1230468.0765
30 | 2683946.8672 | 1230464.7005 | 2683945.7142 | 1230459.9809 | 2683940.9512 | 1230456.9667
31 | 2683949.5372 | 1230498.2392 | 2683947.8557 | 1230468.7283 | 2683946.8672 | 1230464.7005
32 | 2683937.3577 | 1230454.6926 | 2683940.9512 | 1230456.9667
33 | 2683949.5372 | 1230498.2392 | 2683949.8942 | 1230501.9246
34 | 2683949.8942 | 1230501.9246 | 2683935.0079 | 1230503.0708 | 2683919.7196 | 1230510.1489

## bus_geodata
| x | y | coords
0 | 2683659.5946 | 1229767.4439
1 | 2683339.5862 | 1230101.7962
2 | 2683275.5349 | 1230156.4603
3 | 2683119.0467 | 1230291.5553
4 | 2683107.427 | 1230294.5716
5 | 2683132.3021 | 1230288.1143
6 | 2683085.1158 | 1230312.9763
7 | 2683147.0042 | 1230284.3719
8 | 2683062.2425 | 1230320.2244
9 | 2683160.7888 | 1230280.8631
10 | 2683058.7494 | 1230281.2598
11 | 2683167.2495 | 1230237.0898
12 | 2683182.6608 | 1230219.2584
13 | 2683201.8548 | 1230209.4658
14 | 2683201.8113 | 1230202.2812
15 | 2683259.7556 | 1230172.7253
16 | 2683383.2155 | 1230288.7955
17 | 2683284.0003 | 1230126.4803
18 | 2683279.6578 | 1230121.1742
19 | 2683431.0551 | 1230276.0931
20 | 2683449.4114 | 1230275.1128
21 | 2683466.278 | 1230330.6321
22 | 2683491.3695 | 1230298.6328
23 | 2683453.3009 | 1230281.8943
24 | 2683465.3496 | 1230284.3145
25 | 2683466.9513 | 1230284.6363
26 | 2683923.2074 | 1230448.7634
27 | 2683968.2711 | 1230465.1396
28 | 2683977.6167 | 1230468.0765
29 | 2683946.8672 | 1230464.7005
30 | 2683985.6307 | 1230473.2092
31 | 2683940.9512 | 1230456.9667
32 | 2683949.5372 | 1230498.2392
33 | 2683937.3577 | 1230454.6926
34 | 2683949.8942 | 1230501.9246
35 | 2683919.7196 | 1230510.1489
36 | 2683491.3695 | 1230298.6328

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99665 | -0.064761 | 0.00056414 | 0.00014139
1 | 0.99689 | -0.060118 | 0.00067166 | 0.00016833
2 | 0.99699 | -0.058076 | 0 | 0
3 | 0.99644 | -0.068674 | 0.0006164 | 0.00015448
4 | 0.99642 | -0.069073 | 0.00017427 | 4.3677e-05
5 | 0.99647 | -0.06807 | 0 | 0
6 | 0.99638 | -0.069948 | 0.00020772 | 5.2059e-05
7 | 0.99651 | -0.067401 | 0.00022552 | 5.6521e-05
8 | 0.99634 | -0.07064 | 0 | 0
9 | 0.99654 | -0.066717 | 0 | 0
10 | 0.99629 | -0.071708 | 0.0015096 | 0.00037834
11 | 0.99665 | -0.06459 | 0.00039719 | 9.9545e-05
12 | 0.99672 | -0.063218 | 0.00065043 | 0.00016301
13 | 0.9968 | -0.061786 | 0 | 0
14 | 0.99682 | -0.061296 | 0.00031342 | 7.855e-05
15 | 0.99707 | -0.056576 | 0.00081459 | 0.00020415
16 | 0.9984 | -0.030771 | 0.0053547 | 0.001342
17 | 0.99692 | -0.059541 | 0.0023649 | 0.00059271
18 | 0.99691 | -0.05956 | 0.00015387 | 3.8565e-05
19 | 0.99905 | -0.01826 | 0.00056174 | 0.00014078
20 | 0.9993 | -0.013565 | 0 | 0
21 | 0.99999 | -0.00017247 | 0.00023003 | 5.7652e-05
22 | 1 | 0 | -0.028354 | -0.006701
23 | 0.9994 | -0.01157 | 0.00031433 | 7.8777e-05
24 | 0.99957 | -0.0083682 | 0.00034316 | 8.6004e-05
25 | 0.99959 | -0.0079329 | 0.00030627 | 7.6758e-05
26 | 0.99548 | -0.086929 | 0.0015481 | 0.00038798
27 | 0.99514 | -0.093456 | 0.0018462 | 0.0004627
28 | 0.99512 | -0.093991 | 0.00066568 | 0.00016683
29 | 0.99524 | -0.091599 | 0 | 0
30 | 0.9951 | -0.094404 | 0.0024076 | 0.00060341
31 | 0.99532 | -0.090145 | 0.0014268 | 0.00035759
32 | 0.99515 | -0.093352 | 0 | 0
33 | 0.99535 | -0.089449 | 0 | 0
34 | 0.99514 | -0.093545 | 0 | 0
35 | 0.99505 | -0.095192 | 0.002953 | 0.0007401
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00056414 | -0.00014139 | 0.00056426 | 0.00013543 | 1.2281e-07 | -5.954e-06 | 0.00084227 | 0.00084018 | 0.00084227 | 0.99665 | -0.064761 | 0.99689 | -0.060118 | 0.23139
1 | -0.0012359 | -0.00030377 | 0.001236 | 0.00030263 | 1.1832e-07 | -1.1361e-06 | 0.0018427 | 0.0018423 | 0.0018427 | 0.99689 | -0.060118 | 0.99699 | -0.058076 | 0.50624
2 | -0.003755 | -0.0009335 | 0.0037553 | 0.00093337 | 2.6666e-07 | -1.2488e-07 | 0.0056017 | 0.0056016 | 0.0056017 | 0.99699 | -0.058076 | 0.99707 | -0.056576 | 1.5389
3 | 0.002519 | 0.00063087 | -0.0025188 | -0.00063119 | 1.7571e-07 | -3.1983e-07 | 0.0037595 | 0.0037596 | 0.0037596 | 0.99699 | -0.058076 | 0.99692 | -0.059541 | 1.0329
4 | 0.0018918 | 0.00047283 | -0.0018918 | -0.00047296 | 3.5919e-08 | -1.3338e-07 | 0.0028246 | 0.0028247 | 0.0028247 | 0.99644 | -0.068674 | 0.99642 | -0.069073 | 0.77602
5 | -0.0025082 | -0.00062731 | 0.0025083 | 0.00062718 | 7.203e-08 | -1.323e-07 | 0.0037451 | 0.0037451 | 0.0037451 | 0.99644 | -0.068674 | 0.99647 | -0.06807 | 1.0289
6 | 0.0017175 | 0.00042928 | -0.0017174 | -0.00042962 | 7.1429e-08 | -3.3152e-07 | 0.0025645 | 0.0025646 | 0.0025646 | 0.99642 | -0.069073 | 0.99638 | -0.069948 | 0.70456
7 | -0.0025083 | -0.00062718 | 0.0025084 | 0.00062703 | 7.9792e-08 | -1.4657e-07 | 0.0037451 | 0.003745 | 0.0037451 | 0.99647 | -0.06807 | 0.99651 | -0.067401 | 1.0289
8 | 0.0015097 | 0.00037756 | -0.0015097 | -0.00037786 | 4.9752e-08 | -3.0813e-07 | 0.0022544 | 0.0022545 | 0.0022545 | 0.99638 | -0.069948 | 0.99634 | -0.07064 | 0.61937
9 | -0.0027339 | -0.00068355 | 0.002734 | 0.00068343 | 8.8868e-08 | -1.2844e-07 | 0.0040818 | 0.0040817 | 0.0040818 | 0.99651 | -0.067401 | 0.99654 | -0.066717 | 1.1214
10 | 0.0015097 | 0.00037786 | -0.0015096 | -0.00037834 | 7.6756e-08 | -4.7526e-07 | 0.0022545 | 0.0022547 | 0.0022547 | 0.99634 | -0.07064 | 0.99629 | -0.071708 | 0.61942
11 | -0.002734 | -0.00068343 | 0.0027343 | 0.00068303 | 2.765e-07 | -3.9975e-07 | 0.0040817 | 0.0040815 | 0.0040817 | 0.99654 | -0.066717 | 0.99665 | -0.06459 | 1.1213
12 | -0.0031314 | -0.00078257 | 0.0031316 | 0.00078238 | 2.0417e-07 | -1.9407e-07 | 0.0046745 | 0.0046744 | 0.0046745 | 0.99665 | -0.06459 | 0.99672 | -0.063218 | 1.2842
13 | -0.0037821 | -0.00094539 | 0.0037823 | 0.00094527 | 2.5752e-07 | -1.1605e-07 | 0.0056454 | 0.0056453 | 0.0056454 | 0.99672 | -0.063218 | 0.9968 | -0.061786 | 1.5509
14 | -0.0037823 | -0.00094527 | 0.0037824 | 0.00094523 | 8.8006e-08 | -3.967e-08 | 0.0056453 | 0.0056453 | 0.0056453 | 0.9968 | -0.061786 | 0.99682 | -0.061296 | 1.5509
15 | -0.0040958 | -0.0010238 | 0.0040968 | 0.0010235 | 9.1902e-07 | -2.6698e-07 | 0.0061131 | 0.0061128 | 0.0061131 | 0.99682 | -0.061296 | 0.99707 | -0.056576 | 1.6794
16 | -0.0086666 | -0.002161 | 0.0086773 | 0.0021656 | 1.0623e-05 | 4.5859e-06 | 0.01293 | 0.012929 | 0.01293 | 0.99707 | -0.056576 | 0.9984 | -0.030771 | 3.5522
17 | -0.014032 | -0.0035076 | 0.01404 | 0.0035123 | 8.3513e-06 | 4.6783e-06 | 0.02091 | 0.02091 | 0.02091 | 0.9984 | -0.030771 | 0.99905 | -0.01826 | 5.7445
18 | 0.00015387 | 3.8475e-05 | -0.00015387 | -3.8565e-05 | 1.3563e-10 | -8.9312e-08 | 0.00022965 | 0.00022968 | 0.00022968 | 0.99692 | -0.059541 | 0.99691 | -0.05956 | 0.063098
19 | -0.014602 | -0.0036531 | 0.014605 | 0.0036549 | 3.2625e-06 | 1.8471e-06 | 0.021746 | 0.021746 | 0.021746 | 0.99905 | -0.01826 | 0.9993 | -0.013565 | 5.9743
20 | -0.014605 | -0.0036549 | 0.014607 | 0.0036557 | 1.3864e-06 | 7.8485e-07 | 0.021746 | 0.021746 | 0.021746 | 0.9993 | -0.013565 | 0.9994 | -0.01157 | 5.9743
21 | -0.00023003 | -5.7652e-05 | 0.00023004 | 5.7091e-05 | 1.883e-09 | -5.6136e-07 | 0.0003423 | 0.0003421 | 0.0003423 | 0.99999 | -0.00017247 | 1 | 0 | 0.094038
22 | 0.010896 | 0.0027416 | -0.01085 | -0.0027187 | 4.5092e-05 | 2.2888e-05 | 0.016217 | 0.016219 | 0.016219 | 1 | 0 | 0.99548 | -0.086929 | 4.4557
23 | 0.015579 | 0.0039021 | -0.015573 | -0.0038987 | 5.8826e-06 | 3.3821e-06 | 0.023181 | 0.023181 | 0.023181 | 1 | 0 | 0.99959 | -0.0079329 | 6.3684
24 | -0.014921 | -0.0037345 | 0.014923 | 0.0037358 | 2.2742e-06 | 1.2944e-06 | 0.022214 | 0.022214 | 0.022214 | 0.9994 | -0.01157 | 0.99957 | -0.0083682 | 6.1028
25 | -0.015266 | -0.0038218 | 0.015267 | 0.003822 | 3.1638e-07 | 1.8107e-07 | 0.022725 | 0.022725 | 0.022725 | 0.99957 | -0.0083682 | 0.99959 | -0.0079329 | 6.2432
26 | 0.0093023 | 0.0023307 | -0.0093012 | -0.0023302 | 1.1163e-06 | 5.143e-07 | 0.013905 | 0.013905 | 0.013905 | 0.99548 | -0.086929 | 0.99535 | -0.089449 | 3.82
27 | 0.0030734 | 0.00077006 | -0.0030733 | -0.00077014 | 7.826e-08 | -7.8295e-08 | 0.0045955 | 0.0045956 | 0.0045956 | 0.99514 | -0.093456 | 0.99512 | -0.093991 | 1.2625
28 | -0.0049196 | -0.0012328 | 0.00492 | 0.0012328 | 4.3518e-07 | -1.4253e-10 | 0.0073561 | 0.007356 | 0.0073561 | 0.99514 | -0.093456 | 0.99524 | -0.091599 | 2.0209
29 | 0.0024077 | 0.00060331 | -0.0024076 | -0.0006034 | 4.7393e-08 | -9.6339e-08 | 0.0036002 | 0.0036002 | 0.0036002 | 0.99512 | -0.093991 | 0.9951 | -0.094404 | 0.98907
30 | -0.0078736 | -0.0019723 | 0.0078741 | 0.0019725 | 5.4537e-07 | 2.1264e-07 | 0.011772 | 0.011772 | 0.011772 | 0.99524 | -0.091599 | 0.99532 | -0.090145 | 3.234
31 | 0.0029535 | 0.00073952 | -0.0029533 | -0.0007398 | 2.4649e-07 | -2.8026e-07 | 0.0044157 | 0.0044158 | 0.0044158 | 0.99524 | -0.091599 | 0.99515 | -0.093352 | 1.2131
32 | -0.0093009 | -0.0023301 | 0.0093012 | 0.0023302 | 3.0833e-07 | 1.4206e-07 | 0.013905 | 0.013905 | 0.013905 | 0.99532 | -0.090145 | 0.99535 | -0.089449 | 3.82
33 | 0.0029533 | 0.0007398 | -0.0029532 | -0.00073983 | 2.7077e-08 | -3.0781e-08 | 0.0044158 | 0.0044158 | 0.0044158 | 0.99515 | -0.093352 | 0.99514 | -0.093545 | 1.2131
34 | 0.0029532 | 0.00073983 | -0.002953 | -0.0007401 | 2.3177e-07 | -2.6341e-07 | 0.0044158 | 0.004416 | 0.004416 | 0.99514 | -0.093545 | 0.99505 | -0.095192 | 1.2132

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.028876 | 0.0068316

## res_load
| p_mw | q_mvar
0 | 0.00056414 | 0.00014139
1 | 0.00067166 | 0.00016833
2 | 0.0006164 | 0.00015448
3 | 0.00017427 | 4.3677e-05
4 | 0.00020772 | 5.2059e-05
5 | 0.00022552 | 5.6521e-05
6 | 0.0015096 | 0.00037834
7 | 0.00039719 | 9.9545e-05
8 | 0.00065043 | 0.00016301
9 | 0.00031342 | 7.855e-05
10 | 0.00081459 | 0.00020415
11 | 0.0053547 | 0.001342
12 | 0.0023649 | 0.00059271
13 | 0.00015387 | 3.8565e-05
14 | 0.00056174 | 0.00014078
15 | 0.00023003 | 5.7652e-05
16 | 0.00052144 | 0.00013069
17 | 0.00031433 | 7.8777e-05
18 | 0.00034316 | 8.6004e-05
19 | 0.00030627 | 7.6758e-05
20 | 0.0015481 | 0.00038798
21 | 0.0018462 | 0.0004627
22 | 0.00066568 | 0.00016683
23 | 0.0024076 | 0.00060341
24 | 0.0014268 | 0.00035759
25 | 0.002953 | 0.0007401

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1