## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-33_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1701-33_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1701-33_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1701-33_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1701-33_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1701-33_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1701-33_0_6_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1701-33_0_6_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1701-33_0_6_node_53 | 0.4 | n |  | TRUE
9 | bus_LV_1701-33_0_6_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1701-33_0_6_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1701-33_0_6_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1701-33_0_6_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_1701-33_0_6_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_1701-33_0_6_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1701-33_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1701-33_0_6_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1701-33_0_6_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1701-33_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1701-33_0_6_node_94 | 0.4 | n |  | TRUE
20 | bus_LV_1701-33_0_6_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1701-33_0_6_node_95 | 0.4 | n |  | TRUE
22 | bus_LV_1701-33_0_6_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1701-33_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1701-33_0_6_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1701-33_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1701-33_0_6_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1701-33_0_6_node_87 | 0.4 | n |  | TRUE
28 | bus_LV_1701-33_0_6_node_85 | 0.4 | n |  | TRUE
29 | bus_LV_1701-33_0_6_node_96 | 0.4 | n |  | TRUE
30 | bus_LV_1701-33_0_6_node_84 | 0.4 | n |  | TRUE
31 | bus_LV_1701-33_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1701-33_0_6_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1701-33_0_6_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1701-33_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1701-33_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1701-33_0_6_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_1701-33_0_6_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1701-33_0_6_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_1701-33_0_6_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_1701-33_0_6_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_1701-33_0_6_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1701-33_0_6_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_1701-33_0_6_node_82 | 0.4 | n |  | TRUE
44 | bus_LV_1701-33_0_6_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_1701-33_0_6_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_1701-33_0_6_node_92 | 0.4 | n |  | TRUE
47 | bus_LV_1701-33_0_6_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1701-33_0_6_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1701-33_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1701-33_0_6_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_1701-33_0_6_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1701-33_0_6_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1701-33_0_6_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1701-33_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_1701-33_0_6_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_1701-33_0_6_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1701-33_0_6_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_1701-33_0_6_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_1701-33_0_6_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1701-33_0_6_node_67 | 0.4 | n |  | TRUE
61 | bus_LV_1701-33_0_6_node_65 | 0.4 | n |  | TRUE
62 | bus_LV_1701-33_0_6_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_1701-33_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1701-33_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1701-33_0_6_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_1701-33_0_6_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_1701-33_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_1701-33_0_6_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_1701-33_0_6_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_1701-33_0_6_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_1701-33_0_6_node_118 | 0.4 | n |  | TRUE
72 | bus_LV_1701-33_0_6_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_1701-33_0_6_node_119 | 0.4 | n |  | TRUE
74 | bus_LV_1701-33_0_6_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_1701-33_0_6_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_1701-33_0_6_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1701-33_0_6_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_1701-33_0_6_node_116 | 0.4 | n |  | TRUE
79 | bus_LV_1701-33_0_6_node_115 | 0.4 | n |  | TRUE
80 | bus_LV_1701-33_0_6_node_124 | 0.4 | n |  | TRUE
81 | bus_LV_1701-33_0_6_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_1701-33_0_6_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_1701-33_0_6_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1701-33_0_6_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_1701-33_0_6_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_1701-33_0_6_node_75 | 0.4 | n |  | TRUE
87 | bus_LV_1701-33_0_6_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_1701-33_0_6_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_1701-33_0_6_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_1701-33_0_6_node_117 | 0.4 | n |  | TRUE
91 | bus_LV_1701-33_0_6_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_1701-33_0_6_node_125 | 0.4 | n |  | TRUE
93 | bus_LV_1701-33_0_6_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_1701-33_0_6_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_1701-33_0_6_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_1701-33_0_6_node_126 | 0.4 | n |  | TRUE
97 | bus_LV_1701-33_0_6_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_1701-33_0_6_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_1701-33_0_6_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_1701-33_0_6_node_86 | 0.4 | n |  | TRUE
101 | bus_LV_1701-33_0_6_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_1701-33_0_6_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_1701-33_0_6_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_1701-33_0_6_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_1701-33_0_6_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_1701-33_0_6_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_1701-33_0_6_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_1701-33_0_6_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_1701-33_0_6_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1701-33_0_6_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1701-33_0_6_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1701-33_0_6_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_1701-33_0_6_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_1701-33_0_6_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1701-33_0_6_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_1701-33_0_6_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_1701-33_0_6_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_1701-33_0_6_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_1701-33_0_6_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_1701-33_0_6_node_127 | 0.4 | n |  | TRUE
121 | bus_MV_497_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-33_0_6_load_0 | 0 | 0.012559 | 0.0031476 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-33_0_6_load_1 | 1 | 0.0013498 | 0.00033829 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-33_0_6_load_3 | 3 | 0.002893 | 0.00072504 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-33_0_6_load_4 | 4 | 0.0025653 | 0.00064292 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-33_0_6_load_5 | 5 | 0.00646 | 0.001619 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-33_0_6_load_11 | 6 | 0.0020911 | 0.00052409 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-33_0_6_load_12 | 9 | 0.0019038 | 0.00047713 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-33_0_6_load_32 | 10 | 0.0030892 | 0.00077423 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-33_0_6_load_33 | 11 | 0.0045935 | 0.0011512 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-33_0_6_load_55 | 12 | 0.0065938 | 0.0016526 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-33_0_6_load_51 | 13 | 0.0019496 | 0.00048863 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-33_0_6_load_6 | 14 | 0.013163 | 0.0032991 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-33_0_6_load_8 | 15 | 0.0088193 | 0.0022103 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-33_0_6_load_7 | 16 | 0.01237 | 0.0031002 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-33_0_6_load_9 | 17 | 0.015038 | 0.0037689 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-33_0_6_load_94 | 19 | 0.01861 | 0.0046641 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-33_0_6_load_95 | 21 | 0.012784 | 0.003204 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1701-33_0_6_load_20 | 22 | 0.010647 | 0.0026684 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1701-33_0_6_load_13 | 24 | 0.019947 | 0.0049991 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1701-33_0_6_load_19 | 25 | 0.015026 | 0.003766 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1701-33_0_6_load_85 | 28 | 0.0050089 | 0.0012553 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1701-33_0_6_load_96 | 29 | 0.010991 | 0.0027547 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1701-33_0_6_load_84 | 30 | 0.015707 | 0.0039365 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1701-33_0_6_load_21 | 31 | 0.014773 | 0.0037026 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1701-33_0_6_load_23 | 32 | 0.0056188 | 0.0014082 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1701-33_0_6_load_24 | 33 | 0.0045495 | 0.0011402 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1701-33_0_6_load_25 | 34 | 0.0019384 | 0.00048581 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1701-33_0_6_load_26 | 35 | 0.0053105 | 0.0013309 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1701-33_0_6_load_27 | 36 | 0.0051245 | 0.0012843 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1701-33_0_6_load_28 | 37 | 0.0043048 | 0.0010789 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1701-33_0_6_load_58 | 38 | 0.0022669 | 0.00056814 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1701-33_0_6_load_29 | 39 | 0.003714 | 0.00093082 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1701-33_0_6_load_56 | 40 | 0.0016053 | 0.00040232 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1701-33_0_6_load_30 | 41 | 0.0046627 | 0.0011686 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1701-33_0_6_load_83 | 42 | 0.0033618 | 0.00084256 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1701-33_0_6_load_82 | 43 | 0.0029383 | 0.0007364 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1701-33_0_6_load_57 | 44 | 0.006099 | 0.0015286 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1701-33_0_6_load_91 | 45 | 0.0046071 | 0.0011547 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1701-33_0_6_load_92 | 46 | 0.0032665 | 0.00081866 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1701-33_0_6_load_34 | 47 | 0.005402 | 0.0013539 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1701-33_0_6_load_35 | 48 | 0.0048682 | 0.0012201 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1701-33_0_6_load_37 | 50 | 0.0027451 | 0.00068799 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1701-33_0_6_load_38 | 51 | 0.00069206 | 0.00017345 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1701-33_0_6_load_43 | 52 | 0.0044957 | 0.0011267 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1701-33_0_6_load_40 | 53 | 0.0090815 | 0.002276 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1701-33_0_6_load_39 | 54 | 0.0061319 | 0.0015368 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1701-33_0_6_load_61 | 55 | 0.0064233 | 0.0016098 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1701-33_0_6_load_44 | 56 | 0.007212 | 0.0018075 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1701-33_0_6_load_41 | 57 | 0.00053571 | 0.00013426 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1701-33_0_6_load_60 | 58 | 0.0017051 | 0.00042734 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1701-33_0_6_load_42 | 59 | 0.0032896 | 0.00082444 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1701-33_0_6_load_67 | 60 | 0.00072042 | 0.00018055 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1701-33_0_6_load_65 | 61 | 0.0030339 | 0.00076038 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1701-33_0_6_load_45 | 62 | 0.0041168 | 0.0010318 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1701-33_0_6_load_46 | 63 | 0.004184 | 0.0010486 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1701-33_0_6_load_47 | 64 | 0.0029589 | 0.00074157 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1701-33_0_6_load_48 | 65 | 0.0082808 | 0.0020754 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1701-33_0_6_load_49 | 66 | 0.0048517 | 0.001216 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1701-33_0_6_load_52 | 67 | 0.0024268 | 0.00060821 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1701-33_0_6_load_59 | 70 | 0.0026527 | 0.00066483 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1701-33_0_6_load_118 | 71 | 0.011833 | 0.0029656 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1701-33_0_6_load_63 | 72 | 0.0036002 | 0.00090229 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1701-33_0_6_load_119 | 73 | 0.0066354 | 0.001663 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1701-33_0_6_load_64 | 74 | 0.010143 | 0.002542 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1701-33_0_6_load_68 | 75 | 0.019879 | 0.0049821 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1701-33_0_6_load_69 | 76 | 0.002044 | 0.00051228 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1701-33_0_6_load_116 | 78 | 0.0028961 | 0.00072584 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1701-33_0_6_load_115 | 79 | 0.001944 | 0.00048721 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1701-33_0_6_load_113 | 81 | 0.0038138 | 0.00095583 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1701-33_0_6_load_71 | 82 | 0.0084013 | 0.0021056 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1701-33_0_6_load_72 | 84 | 0.0052582 | 0.0013178 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1701-33_0_6_load_75 | 86 | 0.017385 | 0.004357 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1701-33_0_6_load_76 | 87 | 0.0041293 | 0.0010349 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1701-33_0_6_load_77 | 88 | 0.0029799 | 0.00074683 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1701-33_0_6_load_117 | 90 | 0.0049536 | 0.0012415 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1701-33_0_6_load_88 | 91 | 0.0042468 | 0.0010644 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1701-33_0_6_load_125 | 92 | 0.0035212 | 0.00088249 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1701-33_0_6_load_106 | 93 | 0.0033984 | 0.00085173 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1701-33_0_6_load_81 | 94 | 0.0023825 | 0.00059711 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1701-33_0_6_load_89 | 95 | 0.004395 | 0.0011015 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1701-33_0_6_load_126 | 96 | 0.003512 | 0.0008802 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1701-33_0_6_load_78 | 97 | 0.0032507 | 0.00081471 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1701-33_0_6_load_79 | 98 | 0.0015617 | 0.0003914 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1701-33_0_6_load_80 | 99 | 0.00091895 | 0.00023031 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1701-33_0_6_load_86 | 100 | 0.0025908 | 0.00064931 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1701-33_0_6_load_90 | 101 | 0.0037923 | 0.00095045 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1701-33_0_6_load_102 | 102 | 0.0072749 | 0.0018233 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1701-33_0_6_load_100 | 103 | 0.0030696 | 0.00076931 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1701-33_0_6_load_93 | 104 | 0.0046852 | 0.0011742 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1701-33_0_6_load_101 | 105 | 0.0026493 | 0.00066398 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1701-33_0_6_load_99 | 106 | 0.0031432 | 0.00078775 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1701-33_0_6_load_97 | 107 | 0.0066485 | 0.0016663 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1701-33_0_6_load_98 | 108 | 0.003284 | 0.00082304 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1701-33_0_6_load_103 | 109 | 0.0050518 | 0.0012661 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1701-33_0_6_load_104 | 110 | 0.0037549 | 0.00094108 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1701-33_0_6_load_107 | 112 | 0.0040223 | 0.0010081 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1701-33_0_6_load_108 | 113 | 0.0016138 | 0.00040446 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1701-33_0_6_load_109 | 114 | 0.0020917 | 0.00052422 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1701-33_0_6_load_110 | 115 | 0.0014343 | 0.00035946 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1701-33_0_6_load_111 | 116 | 0.0037109 | 0.00093004 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1701-33_0_6_load_112 | 117 | 0.0028967 | 0.00072599 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1701-33_0_6_load_121 | 119 | 0.024209 | 0.0060674 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1701-33_0_6_load_127 | 120 | 0.0033442 | 0.00083813 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-33_0_6_line_0 |  | 0 | 1 | 0.00053599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-33_0_6_line_1 |  | 0 | 2 | 0.035398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-33_0_6_line_2 |  | 1 | 3 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-33_0_6_line_3 |  | 2 | 4 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1701-33_0_6_line_4 |  | 2 | 5 | 0.014384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1701-33_0_6_line_5 |  | 3 | 6 | 0.020591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1701-33_0_6_line_6 |  | 4 | 7 | 0.0052574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1701-33_0_6_line_7 |  | 5 | 8 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1701-33_0_6_line_8 |  | 6 | 9 | 0.00622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-33_0_6_line_9 |  | 7 | 10 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1701-33_0_6_line_10 |  | 7 | 11 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1701-33_0_6_line_11 |  | 8 | 12 | 0.049297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-33_0_6_line_12 |  | 8 | 13 | 0.024026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1701-33_0_6_line_13 |  | 9 | 18 | 0.021483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1701-33_0_6_line_14 |  | 10 | 44 | 0.0050108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1701-33_0_6_line_15 |  | 11 | 45 | 0.012822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1701-33_0_6_line_16 |  | 12 | 71 | 0.061664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-33_0_6_line_17 |  | 13 | 67 | 0.0096914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-33_0_6_line_18 |  | 14 | 15 | 0.007413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1701-33_0_6_line_19 |  | 15 | 18 | 0.023522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1701-33_0_6_line_20 |  | 16 | 17 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1701-33_0_6_line_21 |  | 17 | 19 | 0.039458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1701-33_0_6_line_22 |  | 18 | 20 | 0.008351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1701-33_0_6_line_23 |  | 19 | 21 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1701-33_0_6_line_24 |  | 20 | 22 | 0.0092833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1701-33_0_6_line_25 |  | 20 | 23 | 0.054962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1701-33_0_6_line_26 |  | 21 | 27 | 0.037513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1701-33_0_6_line_27 |  | 22 | 31 | 0.013598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1701-33_0_6_line_28 |  | 23 | 25 | 0.060916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1701-33_0_6_line_29 |  | 23 | 24 | 0.038006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1701-33_0_6_line_30 |  | 26 | 27 | 0.022074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1701-33_0_6_line_31 |  | 26 | 28 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1701-33_0_6_line_32 |  | 27 | 29 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1701-33_0_6_line_33 |  | 28 | 30 | 0.02377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1701-33_0_6_line_34 |  | 29 | 87 | 0.027039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1701-33_0_6_line_35 |  | 30 | 100 | 0.015651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1701-33_0_6_line_36 |  | 32 | 33 | 0.014975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1701-33_0_6_line_37 |  | 32 | 34 | 0.0045004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1701-33_0_6_line_38 |  | 33 | 35 | 0.0035493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1701-33_0_6_line_39 |  | 34 | 36 | 0.013744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1701-33_0_6_line_40 |  | 35 | 37 | 0.017198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1701-33_0_6_line_41 |  | 36 | 38 | 0.0082652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1701-33_0_6_line_42 |  | 37 | 39 | 0.0014392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1701-33_0_6_line_43 |  | 38 | 40 | 0.031216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1701-33_0_6_line_44 |  | 39 | 41 | 0.017333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1701-33_0_6_line_45 |  | 40 | 44 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1701-33_0_6_line_46 |  | 41 | 42 | 0.0035631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1701-33_0_6_line_47 |  | 42 | 43 | 0.016812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1701-33_0_6_line_48 |  | 43 | 99 | 0.0019008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1701-33_0_6_line_49 |  | 45 | 46 | 0.0051738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_1701-33_0_6_line_50 |  | 46 | 104 | 0.013168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_1701-33_0_6_line_51 |  | 47 | 48 | 0.012138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1701-33_0_6_line_52 |  | 47 | 49 | 0.006071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1701-33_0_6_line_53 |  | 48 | 50 | 0.0099014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1701-33_0_6_line_54 |  | 49 | 51 | 0.023758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1701-33_0_6_line_55 |  | 50 | 52 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1701-33_0_6_line_56 |  | 51 | 53 | 0.018374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1701-33_0_6_line_57 |  | 52 | 56 | 0.007987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1701-33_0_6_line_58 |  | 53 | 57 | 0.030541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1701-33_0_6_line_59 |  | 54 | 55 | 0.025246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1701-33_0_6_line_60 |  | 55 | 58 | 0.024734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1701-33_0_6_line_61 |  | 56 | 62 | 0.004044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1701-33_0_6_line_62 |  | 57 | 59 | 0.027755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1701-33_0_6_line_63 |  | 58 | 70 | 0.030181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1701-33_0_6_line_64 |  | 59 | 60 | 0.0025352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1701-33_0_6_line_65 |  | 60 | 61 | 0.022035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1701-33_0_6_line_66 |  | 61 | 74 | 0.016537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1701-33_0_6_line_67 |  | 62 | 63 | 0.017854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1701-33_0_6_line_68 |  | 63 | 64 | 0.0079495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1701-33_0_6_line_69 |  | 64 | 65 | 0.016941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1701-33_0_6_line_70 |  | 65 | 66 | 0.007863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1701-33_0_6_line_71 |  | 67 | 68 | 0.025048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1701-33_0_6_line_72 |  | 68 | 69 | 0.02619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1701-33_0_6_line_73 |  | 68 | 70 | 0.030069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1701-33_0_6_line_74 |  | 69 | 72 | 0.026014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1701-33_0_6_line_75 |  | 71 | 73 | 0.014823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1701-33_0_6_line_76 |  | 72 | 74 | 0.0073742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1701-33_0_6_line_77 |  | 73 | 118 | 0.099106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1701-33_0_6_line_78 |  | 75 | 76 | 0.031577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1701-33_0_6_line_79 |  | 75 | 77 | 0.052664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1701-33_0_6_line_80 |  | 77 | 80 | 0.10677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1701-33_0_6_line_81 |  | 78 | 79 | 0.044073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1701-33_0_6_line_82 |  | 79 | 113 | 0.03303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1701-33_0_6_line_83 |  | 80 | 81 | 0.043151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1701-33_0_6_line_84 |  | 81 | 117 | 0.018008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1701-33_0_6_line_85 |  | 82 | 83 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1701-33_0_6_line_86 |  | 83 | 86 | 0.032577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1701-33_0_6_line_87 |  | 83 | 87 | 0.024622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1701-33_0_6_line_88 |  | 83 | 88 | 0.028674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1701-33_0_6_line_89 |  | 84 | 85 | 0.014769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1701-33_0_6_line_90 |  | 85 | 89 | 0.039852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1701-33_0_6_line_91 |  | 85 | 90 | 0.024672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1701-33_0_6_line_92 |  | 86 | 91 | 0.0066094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1701-33_0_6_line_93 |  | 88 | 92 | 0.0085414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1701-33_0_6_line_94 |  | 89 | 93 | 0.018329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1701-33_0_6_line_95 |  | 90 | 94 | 0.012327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1701-33_0_6_line_96 |  | 91 | 95 | 0.019566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1701-33_0_6_line_97 |  | 92 | 96 | 0.0084193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1701-33_0_6_line_98 |  | 93 | 110 | 0.00097192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1701-33_0_6_line_99 |  | 94 | 98 | 0.0078446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1701-33_0_6_line_100 |  | 95 | 101 | 0.012744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1701-33_0_6_line_101 |  | 96 | 120 | 0.0068125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1701-33_0_6_line_102 |  | 97 | 98 | 0.011108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1701-33_0_6_line_103 |  | 97 | 99 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1701-33_0_6_line_104 |  | 101 | 102 | 0.0070657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1701-33_0_6_line_105 |  | 102 | 103 | 0.0090118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1701-33_0_6_line_106 |  | 103 | 108 | 0.011888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1701-33_0_6_line_107 |  | 104 | 105 | 0.0064276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1701-33_0_6_line_108 |  | 105 | 106 | 0.013233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1701-33_0_6_line_109 |  | 106 | 107 | 0.0091818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1701-33_0_6_line_110 |  | 107 | 108 | 0.010271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1701-33_0_6_line_111 |  | 109 | 110 | 0.021039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1701-33_0_6_line_112 |  | 109 | 111 | 0.017404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1701-33_0_6_line_113 |  | 111 | 112 | 0.0056625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1701-33_0_6_line_114 |  | 111 | 113 | 0.015623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1701-33_0_6_line_115 |  | 112 | 114 | 0.0011809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1701-33_0_6_line_116 |  | 114 | 115 | 0.0065254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1701-33_0_6_line_117 |  | 115 | 116 | 0.01653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1701-33_0_6_line_118 |  | 116 | 117 | 0.016227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1701-33_0_6_line_119 |  | 118 | 119 | 0.0023498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-33_0_6_trafo_91 | 0.63 MVA 20/0.4 kV | 121 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2681927.5355 | 1227947.1675 | 2681927.9401 | 1227946.816
1 | 2681903.6598 | 1227973.3011 | 2681927.5355 | 1227947.1675
2 | 2681935.6681 | 1227940.1018 | 2681927.9401 | 1227946.816
3 | 2681903.6598 | 1227973.3011 | 2681919.5314 | 1227981.5725
4 | 2681903.6598 | 1227973.3011 | 2681893.4605 | 1227983.4441
5 | 2681951.9626 | 1227927.5917 | 2681944.341 | 1227932.5667 | 2681935.6681 | 1227940.1018
6 | 2681924.1936 | 1227984.0022 | 2681919.5314 | 1227981.5725
7 | 2681882.1172 | 1227992.3621 | 2681890.3825 | 1227986.5052 | 2681893.4605 | 1227983.4441
8 | 2681951.9626 | 1227927.5917 | 2681957.1711 | 1227924.1918
9 | 2681924.1936 | 1227984.0022 | 2681918.3142 | 1227985.5557 | 2681913.8787 | 1227992.6855
10 | 2681924.1936 | 1227984.0022 | 2681936.267 | 1227990.9131
11 | 2681882.1172 | 1227992.3621 | 2681863.8326 | 1227983.9714 | 2681856.6596 | 1227991.956 | 2681839.191 | 1227986.032
12 | 2681882.1172 | 1227992.3621 | 2681873.2552 | 1227998.6333 | 2681866.7034 | 1228010.0571
13 | 2681977.9699 | 1227920.2215 | 2681966.6651 | 1227920.6105 | 2681957.953 | 1227923.6815 | 2681957.1711 | 1227924.1918
14 | 2681911.2318 | 1227996.9402 | 2681913.8787 | 1227992.6855
15 | 2681947.3951 | 1227997.2829 | 2681936.267 | 1227990.9131
16 | 2681839.191 | 1227986.032 | 2681794.9416 | 1227971.0262 | 2681799.4894 | 1227956.7961
17 | 2681866.7034 | 1228010.0571 | 2681863.689 | 1228015.3131 | 2681862.42 | 1228018.7166
18 | 2681995.9272 | 1227940.6639 | 2681989.6548 | 1227936.713
19 | 2681977.9699 | 1227920.2215 | 2681976.3899 | 1227924.8807 | 2681977.7849 | 1227929.2362 | 2681989.6548 | 1227936.713
20 | 2682042.1493 | 1227969.5129 | 2682029.6858 | 1227961.8019
21 | 2682042.1493 | 1227969.5129 | 2682075.7044 | 1227990.2732
22 | 2681977.9699 | 1227920.2215 | 2681982.207 | 1227913.0194
23 | 2682075.7044 | 1227990.2732 | 2682085.9873 | 1227996.6352
24 | 2681982.207 | 1227913.0194 | 2681982.2971 | 1227903.7365
25 | 2682011.5707 | 1227866.5145 | 2681982.207 | 1227913.0194
26 | 2682117.8887 | 1228016.3723 | 2682085.9873 | 1227996.6352
27 | 2681989.2666 | 1227892.0608 | 2681982.2971 | 1227903.7365
28 | 2682011.5707 | 1227866.5145 | 2681965.5009 | 1227839.5835 | 2681958.597 | 1227836.5215
29 | 2682011.5707 | 1227866.5145 | 2682029.2367 | 1227877.4655 | 2682043.8699 | 1227886.5444
30 | 2682128.1847 | 1227996.8343 | 2682117.8887 | 1228016.3723
31 | 2682128.1847 | 1227996.8343 | 2682141.5255 | 1228005.5943
32 | 2682117.8887 | 1228016.3723 | 2682106.54 | 1228035.5909
33 | 2682161.3948 | 1228018.6411 | 2682161.3948 | 1228018.6411 | 2682141.5255 | 1228005.5943
34 | 2682106.54 | 1228035.5909 | 2682101.8027 | 1228043.6134 | 2682092.6633 | 1228058.7967
35 | 2682175.7822 | 1228024.7862 | 2682170.3267 | 1228022.6894 | 2682161.3948 | 1228018.6411
36 | 2681928.0811 | 1228057.8892 | 2681915.3265 | 1228050.0426
37 | 2681911.4933 | 1228047.6845 | 2681915.3265 | 1228050.0426
38 | 2681928.0811 | 1228057.8892 | 2681931.1042 | 1228059.749
39 | 2681899.787 | 1228040.4828 | 2681911.4933 | 1228047.6845
40 | 2681945.7647 | 1228068.7408 | 2681933.9702 | 1228061.5121 | 2681931.1042 | 1228059.749
41 | 2681899.787 | 1228040.4828 | 2681892.7472 | 1228036.152
42 | 2681945.7647 | 1228068.7408 | 2681946.9918 | 1228069.4928
43 | 2681903.2593 | 1228009.754 | 2681890.3681 | 1228030.4684 | 2681890.7463 | 1228034.9211 | 2681892.7472 | 1228036.152
44 | 2681961.77 | 1228078.5501 | 2681946.9918 | 1228069.4928
45 | 2681903.2593 | 1228009.754 | 2681905.9763 | 1228005.3883 | 2681911.2318 | 1227996.9402
46 | 2681961.77 | 1228078.5501 | 2681964.8079 | 1228080.412
47 | 2681979.1418 | 1228089.197 | 2681964.8079 | 1228080.412
48 | 2681979.1418 | 1228089.197 | 2681980.7625 | 1228090.1903
49 | 2681947.3951 | 1227997.2829 | 2681951.8853 | 1227999.8531
50 | 2681951.8853 | 1227999.8531 | 2681963.3132 | 1228006.3945
51 | 2681706.018 | 1227971.8777 | 2681717.4827 | 1227975.863
52 | 2681723.2171 | 1227977.8564 | 2681717.4827 | 1227975.863
53 | 2681706.018 | 1227971.8777 | 2681696.6656 | 1227968.6267
54 | 2681723.2171 | 1227977.8564 | 2681716.3116 | 1228000.5882
55 | 2681685.109 | 1227964.6094 | 2681696.6656 | 1227968.6267
56 | 2681716.3116 | 1228000.5882 | 2681717.7259 | 1228002.9982 | 2681732.4908 | 1228007.9708
57 | 2681685.109 | 1227964.6094 | 2681677.5648 | 1227961.987
58 | 2681760.0638 | 1228020.9559 | 2681739.3754 | 1228010.2894 | 2681732.4908 | 1228007.9708
59 | 2681779.6511 | 1228000.4728 | 2681775.4415 | 1227998.6548 | 2681756.2468 | 1227991.0106
60 | 2681802.3582 | 1228010.2788 | 2681779.6511 | 1228000.4728
61 | 2681677.5648 | 1227961.987 | 2681673.7451 | 1227960.6591
62 | 2681760.0638 | 1228020.9559 | 2681784.7327 | 1228033.6746
63 | 2681830.066 | 1228022.2444 | 2681802.3582 | 1228010.2788
64 | 2681786.986 | 1228034.8363 | 2681784.7327 | 1228033.6746
65 | 2681806.5644 | 1228044.9473 | 2681796.7831 | 1228039.8875 | 2681786.986 | 1228034.8363
66 | 2681806.5644 | 1228044.9473 | 2681821.2523 | 1228052.5453
67 | 2681656.8809 | 1227954.7969 | 2681673.7451 | 1227960.6591
68 | 2681656.8809 | 1227954.7969 | 2681649.3721 | 1227952.1867
69 | 2681633.3705 | 1227946.6243 | 2681649.3721 | 1227952.1867
70 | 2681633.3705 | 1227946.6243 | 2681625.9434 | 1227944.0425
71 | 2681850.9937 | 1228040.7558 | 2681857.63 | 1228031.5631 | 2681862.42 | 1228018.7166
72 | 2681851.2989 | 1228065.9328 | 2681848.703 | 1228058.5254 | 2681847.8622 | 1228049.6855 | 2681850.9937 | 1228040.7558
73 | 2681850.9937 | 1228040.7558 | 2681849.517 | 1228034.0754 | 2681844.3734 | 1228028.423 | 2681830.066 | 1228022.2444
74 | 2681851.2989 | 1228065.9328 | 2681847.7027 | 1228066.228 | 2681827.802 | 1228055.9334
75 | 2681804.0019 | 1227942.6763 | 2681799.4894 | 1227956.7961
76 | 2681827.802 | 1228055.9334 | 2681821.2523 | 1228052.5453
77 | 2681798.4527 | 1227871.1507 | 2681780.0487 | 1227903.909 | 2681777.966 | 1227910.9741 | 2681779.6503 | 1227914.1438 | 2681809.6874 | 1227924.8863 | 2681804.0019 | 1227942.6763
78 | 2681766.4915 | 1228146.8574 | 2681764.7396 | 1228144.7855 | 2681759.1768 | 1228142.6075 | 2681751.4191 | 1228138.5871 | 2681739.0054 | 1228131.791
79 | 2681800.4949 | 1228187.0725 | 2681766.4915 | 1228146.8574
80 | 2681877.2543 | 1228261.2903 | 2681800.4949 | 1228187.0725
81 | 2681899.869 | 1228123.8944 | 2681928.7365 | 1228157.1979
82 | 2681928.7365 | 1228157.1979 | 2681943.2574 | 1228173.9503 | 2681950.4135 | 1228182.1192
83 | 2681877.2543 | 1228261.2903 | 2681910.8425 | 1228234.2015
84 | 2681910.8425 | 1228234.2015 | 2681923.4631 | 1228224.0231 | 2681924.8601 | 1228222.897
85 | 2682080.4953 | 1228080.2 | 2682071.6246 | 1228094.7765 | 2682069.6053 | 1228097.7033
86 | 2682080.4953 | 1228080.2 | 2682053.463 | 1228062.0207
87 | 2682080.4953 | 1228080.2 | 2682089.928 | 1228063.3408 | 2682092.6633 | 1228058.7967
88 | 2682080.4953 | 1228080.2 | 2682091.5737 | 1228087.4022 | 2682104.3285 | 1228096.1397
89 | 2682036.7583 | 1228132.5993 | 2682047.7111 | 1228122.6915
90 | 2682036.7583 | 1228132.5993 | 2682005.728 | 1228157.711
91 | 2682036.7583 | 1228132.5993 | 2682022.3079 | 1228121.5258 | 2682017.2331 | 1228117.5183
92 | 2682047.9784 | 1228058.3323 | 2682053.463 | 1228062.0207
93 | 2682104.3285 | 1228096.1397 | 2682110.8547 | 1228101.6501
94 | 2682005.728 | 1228157.711 | 2681991.4622 | 1228169.2199
95 | 2682017.2331 | 1228117.5183 | 2682007.5588 | 1228109.8786
96 | 2682047.9784 | 1228058.3323 | 2682031.7425 | 1228047.4136
97 | 2682110.8547 | 1228101.6501 | 2682117.2877 | 1228107.0816 | 2682117.2877 | 1228107.0816
98 | 2681991.4622 | 1228169.2199 | 2681990.7057 | 1228169.8302
99 | 2682001.4024 | 1228105.0169 | 2682007.5588 | 1228109.8786
100 | 2682021.1673 | 1228040.3017 | 2682031.7425 | 1228047.4136
101 | 2682117.2877 | 1228107.0816 | 2682121.8612 | 1228112.1306
102 | 2681992.685 | 1228098.1329 | 2682001.4024 | 1228105.0169
103 | 2681992.685 | 1228098.1329 | 2681989.0908 | 1228095.2945 | 2681980.7625 | 1228090.1903
104 | 2682021.1673 | 1228040.3017 | 2682015.3042 | 1228036.3587
105 | 2682015.3042 | 1228036.3587 | 2682013.2635 | 1228034.9864 | 2682007.5767 | 1228031.7312
106 | 2681997.2589 | 1228025.8253 | 2682007.5767 | 1228031.7312
107 | 2681968.8916 | 1228009.5876 | 2681963.3132 | 1228006.3945
108 | 2681968.8916 | 1228009.5876 | 2681980.3759 | 1228016.1613
109 | 2681988.3446 | 1228020.7226 | 2681980.3759 | 1228016.1613
110 | 2681988.3446 | 1228020.7226 | 2681997.2589 | 1228025.8253
111 | 2681974.3311 | 1228183.0404 | 2681990.7057 | 1228169.8302
112 | 2681960.708 | 1228193.8709 | 2681973.925 | 1228183.368 | 2681974.3311 | 1228183.0404
113 | 2681960.708 | 1228193.8709 | 2681956.3136 | 1228197.4421
114 | 2681960.708 | 1228193.8709 | 2681950.4135 | 1228182.1192
115 | 2681956.3136 | 1228197.4421 | 2681955.3971 | 1228198.1869
116 | 2681950.3331 | 1228202.3023 | 2681955.3971 | 1228198.1869
117 | 2681937.4935 | 1228212.7137 | 2681940.9581 | 1228209.921 | 2681950.3331 | 1228202.3023
118 | 2681937.4935 | 1228212.7137 | 2681924.8601 | 1228222.897
119 | 2681798.4527 | 1227871.1507 | 2681799.7658 | 1227869.2021

## bus_geodata
| x | y | coords
0 | 2681927.5355 | 1227947.1675
1 | 2681927.9401 | 1227946.816
2 | 2681903.6598 | 1227973.3011
3 | 2681935.6681 | 1227940.1018
4 | 2681919.5314 | 1227981.5725
5 | 2681893.4605 | 1227983.4441
6 | 2681951.9626 | 1227927.5917
7 | 2681924.1936 | 1227984.0022
8 | 2681882.1172 | 1227992.3621
9 | 2681957.1711 | 1227924.1918
10 | 2681913.8787 | 1227992.6855
11 | 2681936.267 | 1227990.9131
12 | 2681839.191 | 1227986.032
13 | 2681866.7034 | 1228010.0571
14 | 2681995.9272 | 1227940.6639
15 | 2681989.6548 | 1227936.713
16 | 2682029.6858 | 1227961.8019
17 | 2682042.1493 | 1227969.5129
18 | 2681977.9699 | 1227920.2215
19 | 2682075.7044 | 1227990.2732
20 | 2681982.207 | 1227913.0194
21 | 2682085.9873 | 1227996.6352
22 | 2681982.2971 | 1227903.7365
23 | 2682011.5707 | 1227866.5145
24 | 2682043.8699 | 1227886.5444
25 | 2681958.597 | 1227836.5215
26 | 2682128.1847 | 1227996.8343
27 | 2682117.8887 | 1228016.3723
28 | 2682141.5255 | 1228005.5943
29 | 2682106.54 | 1228035.5909
30 | 2682161.3948 | 1228018.6411
31 | 2681989.2666 | 1227892.0608
32 | 2681915.3265 | 1228050.0426
33 | 2681928.0811 | 1228057.8892
34 | 2681911.4933 | 1228047.6845
35 | 2681931.1042 | 1228059.749
36 | 2681899.787 | 1228040.4828
37 | 2681945.7647 | 1228068.7408
38 | 2681892.7472 | 1228036.152
39 | 2681946.9918 | 1228069.4928
40 | 2681903.2593 | 1228009.754
41 | 2681961.77 | 1228078.5501
42 | 2681964.8079 | 1228080.412
43 | 2681979.1418 | 1228089.197
44 | 2681911.2318 | 1227996.9402
45 | 2681947.3951 | 1227997.2829
46 | 2681951.8853 | 1227999.8531
47 | 2681717.4827 | 1227975.863
48 | 2681706.018 | 1227971.8777
49 | 2681723.2171 | 1227977.8564
50 | 2681696.6656 | 1227968.6267
51 | 2681716.3116 | 1228000.5882
52 | 2681685.109 | 1227964.6094
53 | 2681732.4908 | 1228007.9708
54 | 2681756.2468 | 1227991.0106
55 | 2681779.6511 | 1228000.4728
56 | 2681677.5648 | 1227961.987
57 | 2681760.0638 | 1228020.9559
58 | 2681802.3582 | 1228010.2788
59 | 2681784.7327 | 1228033.6746
60 | 2681786.986 | 1228034.8363
61 | 2681806.5644 | 1228044.9473
62 | 2681673.7451 | 1227960.6591
63 | 2681656.8809 | 1227954.7969
64 | 2681649.3721 | 1227952.1867
65 | 2681633.3705 | 1227946.6243
66 | 2681625.9434 | 1227944.0425
67 | 2681862.42 | 1228018.7166
68 | 2681850.9937 | 1228040.7558
69 | 2681851.2989 | 1228065.9328
70 | 2681830.066 | 1228022.2444
71 | 2681799.4894 | 1227956.7961
72 | 2681827.802 | 1228055.9334
73 | 2681804.0019 | 1227942.6763
74 | 2681821.2523 | 1228052.5453
75 | 2681766.4915 | 1228146.8574
76 | 2681739.0054 | 1228131.791
77 | 2681800.4949 | 1228187.0725
78 | 2681899.869 | 1228123.8944
79 | 2681928.7365 | 1228157.1979
80 | 2681877.2543 | 1228261.2903
81 | 2681910.8425 | 1228234.2015
82 | 2682069.6053 | 1228097.7032
83 | 2682080.4953 | 1228080.2
84 | 2682047.7111 | 1228122.6915
85 | 2682036.7583 | 1228132.5993
86 | 2682053.463 | 1228062.0207
87 | 2682092.6633 | 1228058.7967
88 | 2682104.3285 | 1228096.1397
89 | 2682005.728 | 1228157.711
90 | 2682017.2331 | 1228117.5183
91 | 2682047.9784 | 1228058.3323
92 | 2682110.8547 | 1228101.6501
93 | 2681991.4622 | 1228169.2199
94 | 2682007.5588 | 1228109.8786
95 | 2682031.7425 | 1228047.4136
96 | 2682117.2877 | 1228107.0816
97 | 2681992.685 | 1228098.1329
98 | 2682001.4024 | 1228105.0169
99 | 2681980.7625 | 1228090.1903
100 | 2682175.7822 | 1228024.7862
101 | 2682021.1673 | 1228040.3017
102 | 2682015.3042 | 1228036.3587
103 | 2682007.5767 | 1228031.7312
104 | 2681963.3132 | 1228006.3945
105 | 2681968.8916 | 1228009.5876
106 | 2681980.3759 | 1228016.1613
107 | 2681988.3446 | 1228020.7226
108 | 2681997.2589 | 1228025.8253
109 | 2681974.3311 | 1228183.0404
110 | 2681990.7057 | 1228169.8302
111 | 2681960.708 | 1228193.8709
112 | 2681956.3136 | 1228197.4421
113 | 2681950.4135 | 1228182.1192
114 | 2681955.3971 | 1228198.1869
115 | 2681950.3331 | 1228202.3023
116 | 2681937.4935 | 1228212.7137
117 | 2681924.8601 | 1228222.897
118 | 2681798.4527 | 1227871.1507
119 | 2681799.7658 | 1227869.2021
120 | 2682121.8612 | 1228112.1306
121 | 2681924.1936 | 1227984.0022

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99152 | -0.16176 | 0.012559 | 0.0031476
1 | 0.99147 | -0.16262 | 0.0013498 | 0.00033829
2 | 0.99488 | -0.097227 | 0 | 0
3 | 0.99063 | -0.17884 | 0.002893 | 0.00072504
4 | 0.99631 | -0.069906 | 0.0025653 | 0.00064292
5 | 0.99418 | -0.11051 | 0.00646 | 0.001619
6 | 0.989 | -0.21048 | 0.0020911 | 0.00052409
7 | 0.99674 | -0.061816 | 0 | 0
8 | 0.99317 | -0.12977 | 0 | 0
9 | 0.98851 | -0.21983 | 0.0019038 | 0.00047713
10 | 0.99615 | -0.072956 | 0.0030892 | 0.00077423
11 | 0.99843 | -0.029777 | 0.0045935 | 0.0011512
12 | 0.99094 | -0.17279 | 0.0065938 | 0.0016526
13 | 0.99091 | -0.17297 | 0.0019496 | 0.00048863
14 | 0.98632 | -0.26246 | 0.013163 | 0.0032991
15 | 0.98641 | -0.26071 | 0.0088193 | 0.0022103
16 | 0.97941 | -0.39686 | 0.01237 | 0.0031002
17 | 0.97958 | -0.39357 | 0.015038 | 0.0037689
18 | 0.98689 | -0.25145 | 0 | 0
19 | 0.98058 | -0.37395 | 0.01861 | 0.0046641
20 | 0.98642 | -0.26048 | 0 | 0
21 | 0.9811 | -0.36386 | 0.012784 | 0.003204
22 | 0.9862 | -0.26471 | 0.010647 | 0.0026684
23 | 0.98465 | -0.29498 | 0 | 0
24 | 0.98395 | -0.30862 | 0.019947 | 0.0049991
25 | 0.98381 | -0.31145 | 0.015026 | 0.003766
26 | 0.98266 | -0.33328 | 0 | 0
27 | 0.98314 | -0.324 | 0 | 0
28 | 0.98232 | -0.34 | 0.0050089 | 0.0012553
29 | 0.98483 | -0.29101 | 0.010991 | 0.0027547
30 | 0.98192 | -0.34786 | 0.015707 | 0.0039365
31 | 0.98602 | -0.26831 | 0.014773 | 0.0037026
32 | 0.99274 | -0.13802 | 0.0056188 | 0.0014082
33 | 0.99127 | -0.16606 | 0.0045495 | 0.0011402
34 | 0.9932 | -0.12916 | 0.0019384 | 0.00048581
35 | 0.99094 | -0.17244 | 0.0053105 | 0.0013309
36 | 0.99392 | -0.11541 | 0.0051245 | 0.0012843
37 | 0.98941 | -0.20175 | 0.0043048 | 0.0010789
38 | 0.99422 | -0.10966 | 0.0022669 | 0.00056814
39 | 0.98929 | -0.2041 | 0.003714 | 0.00093082
40 | 0.99538 | -0.08754 | 0.0016053 | 0.00040232
41 | 0.98787 | -0.23126 | 0.0046627 | 0.0011686
42 | 0.9876 | -0.23655 | 0.0033618 | 0.00084256
43 | 0.98635 | -0.26057 | 0.0029383 | 0.0007364
44 | 0.99595 | -0.076723 | 0.006099 | 0.0015286
45 | 1 | 0 | -0.59168 | -0.15103
46 | 0.99971 | -0.0054978 | 0.0032665 | 0.00081866
47 | 0.97545 | -0.47294 | 0.005402 | 0.0013539
48 | 0.97496 | -0.48266 | 0.0048682 | 0.0012201
49 | 0.97573 | -0.46748 | 0 | 0
50 | 0.9746 | -0.48972 | 0.0027451 | 0.00068799
51 | 0.97681 | -0.44614 | 0.00069206 | 0.00017345
52 | 0.97419 | -0.49783 | 0.0044957 | 0.0011267
53 | 0.97767 | -0.42943 | 0.0090815 | 0.002276
54 | 0.98647 | -0.2586 | 0.0061319 | 0.0015368
55 | 0.98661 | -0.25583 | 0.0064233 | 0.0016098
56 | 0.97395 | -0.50246 | 0.007212 | 0.0018075
57 | 0.97934 | -0.39669 | 0.00053571 | 0.00013426
58 | 0.9869 | -0.25027 | 0.0017051 | 0.00042734
59 | 0.98087 | -0.36676 | 0.0032896 | 0.00082444
60 | 0.98102 | -0.36388 | 0.00072042 | 0.00018055
61 | 0.98232 | -0.3386 | 0.0030339 | 0.00076038
62 | 0.97386 | -0.50428 | 0.0041168 | 0.0010318
63 | 0.97352 | -0.51093 | 0.004184 | 0.0010486
64 | 0.9734 | -0.51328 | 0.0029589 | 0.00074157
65 | 0.9732 | -0.51738 | 0.0082808 | 0.0020754
66 | 0.97316 | -0.51808 | 0.0048517 | 0.001216
67 | 0.99002 | -0.19011 | 0.0024268 | 0.00060821
68 | 0.98776 | -0.23348 | 0 | 0
69 | 0.98581 | -0.27108 | 0 | 0
70 | 0.98729 | -0.24257 | 0.0026527 | 0.00066483
71 | 0.98852 | -0.21962 | 0.011833 | 0.0029656
72 | 0.98387 | -0.30859 | 0.0036002 | 0.00090229
73 | 0.9881 | -0.22778 | 0.0066354 | 0.001663
74 | 0.98335 | -0.31876 | 0.010143 | 0.002542
75 | 0.97073 | -0.56581 | 0.019879 | 0.0049821
76 | 0.97067 | -0.567 | 0.002044 | 0.00051228
77 | 0.97181 | -0.54447 | 0 | 0
78 | 0.97634 | -0.45536 | 0.0028961 | 0.00072584
79 | 0.97646 | -0.45303 | 0.001944 | 0.00048721
80 | 0.974 | -0.50136 | 0 | 0
81 | 0.97488 | -0.48399 | 0.0038138 | 0.00095583
82 | 0.98921 | -0.20624 | 0.0084013 | 0.0021056
83 | 0.98937 | -0.20315 | 0 | 0
84 | 0.98161 | -0.35242 | 0.0052582 | 0.0013178
85 | 0.98168 | -0.35102 | 0 | 0
86 | 0.99295 | -0.13437 | 0.017385 | 0.004357
87 | 0.98716 | -0.24588 | 0.0041293 | 0.0010349
88 | 0.98902 | -0.20997 | 0.0029799 | 0.00074683
89 | 0.97951 | -0.39332 | 0 | 0
90 | 0.98315 | -0.32258 | 0.0049536 | 0.0012415
91 | 0.99378 | -0.11845 | 0.0042468 | 0.0010644
92 | 0.98894 | -0.21155 | 0.0035212 | 0.00088249
93 | 0.97851 | -0.41284 | 0.0033984 | 0.00085173
94 | 0.98393 | -0.3073 | 0.0023825 | 0.00059711
95 | 0.99505 | -0.094203 | 0.004395 | 0.0011015
96 | 0.98889 | -0.21258 | 0.003512 | 0.0008802
97 | 0.9852 | -0.28274 | 0.0032507 | 0.00081471
98 | 0.98445 | -0.29726 | 0.0015617 | 0.0003914
99 | 0.98622 | -0.26319 | 0.00091895 | 0.00023031
100 | 0.98188 | -0.34859 | 0.0025908 | 0.00064931
101 | 0.99562 | -0.083364 | 0.0037923 | 0.00095045
102 | 0.99594 | -0.077203 | 0.0072749 | 0.0018233
103 | 0.99637 | -0.068967 | 0.0030696 | 0.00076931
104 | 0.99899 | -0.019254 | 0.0046852 | 0.0011742
105 | 0.99864 | -0.025801 | 0.0026493 | 0.00066398
106 | 0.99794 | -0.039088 | 0.0031432 | 0.00078775
107 | 0.99747 | -0.048151 | 0.0066485 | 0.0016663
108 | 0.99695 | -0.057899 | 0.003284 | 0.00082304
109 | 0.97745 | -0.43353 | 0.0050518 | 0.0012661
110 | 0.97846 | -0.41382 | 0.0037549 | 0.00094108
111 | 0.9767 | -0.44826 | 0 | 0
112 | 0.97649 | -0.45239 | 0.0040223 | 0.0010081
113 | 0.97661 | -0.45011 | 0.0016138 | 0.00040446
114 | 0.97645 | -0.45317 | 0.0020917 | 0.00052422
115 | 0.97624 | -0.4572 | 0.0014343 | 0.00035946
116 | 0.97575 | -0.46698 | 0.0037109 | 0.00093004
117 | 0.97531 | -0.47549 | 0.0028967 | 0.00072599
118 | 0.9859 | -0.27071 | 0 | 0
119 | 0.98585 | -0.27173 | 0.024209 | 0.0060674
120 | 0.98887 | -0.21299 | 0.0033442 | 0.00083813
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.091109 | 0.023023 | -0.091105 | -0.023021 | 3.7614e-06 | 2.4004e-06 | 0.1368 | 0.1368 | 0.1368 | 0.99152 | -0.16176 | 0.99147 | -0.16262 | 37.5818
1 | -0.10367 | -0.026171 | 0.10399 | 0.026376 | 0.00032158 | 0.00020535 | 0.15565 | 0.15565 | 0.15565 | 0.99152 | -0.16176 | 0.99488 | -0.097227 | 42.7598
2 | 0.089755 | 0.022682 | -0.089685 | -0.022638 | 6.973e-05 | 4.4495e-05 | 0.13477 | 0.13477 | 0.13477 | 0.99147 | -0.16262 | 0.99063 | -0.17884 | 37.0253
3 | -0.26307 | -0.066957 | 0.26342 | 0.067179 | 0.00034701 | 0.00022139 | 0.39384 | 0.39384 | 0.39384 | 0.99488 | -0.097227 | 0.99631 | -0.069906 | 36.0656
4 | 0.15908 | 0.040581 | -0.15898 | -0.040517 | 0.00010201 | 6.4727e-05 | 0.23819 | 0.23819 | 0.23819 | 0.99488 | -0.097227 | 0.99418 | -0.11051 | 21.8123
5 | 0.086792 | 0.021913 | -0.086661 | -0.021829 | 0.00013135 | 8.38e-05 | 0.13043 | 0.13043 | 0.13043 | 0.99063 | -0.17884 | 0.989 | -0.21048 | 35.8315
6 | -0.26599 | -0.067822 | 0.26609 | 0.067888 | 0.00010392 | 6.6306e-05 | 0.39767 | 0.39767 | 0.39767 | 0.99631 | -0.069906 | 0.99674 | -0.061816 | 36.4164
7 | 0.15252 | 0.038898 | -0.15238 | -0.038807 | 0.0001417 | 9.0311e-05 | 0.22852 | 0.22852 | 0.22852 | 0.99418 | -0.11051 | 0.99317 | -0.12977 | 31.3904
8 | 0.08457 | 0.021305 | -0.084532 | -0.021281 | 3.7787e-05 | 2.4104e-05 | 0.12728 | 0.12728 | 0.12728 | 0.989 | -0.21048 | 0.98851 | -0.21983 | 34.9672
9 | 0.13317 | 0.034029 | -0.1331 | -0.033984 | 7.1697e-05 | 4.532e-05 | 0.19904 | 0.19904 | 0.19904 | 0.99674 | -0.061816 | 0.99615 | -0.072956 | 18.227
10 | -0.39926 | -0.10192 | 0.39988 | 0.10231 | 0.00061916 | 0.00039572 | 0.59671 | 0.59671 | 0.59671 | 0.99674 | -0.061816 | 0.99843 | -0.029777 | 54.6434
11 | 0.049531 | 0.012512 | -0.04943 | -0.012448 | 0.0001019 | 6.4582e-05 | 0.074245 | 0.074245 | 0.074245 | 0.99317 | -0.12977 | 0.99094 | -0.17279 | 20.3971
12 | 0.10285 | 0.026295 | -0.10263 | -0.026158 | 0.00021444 | 0.00013693 | 0.15428 | 0.15428 | 0.15428 | 0.99317 | -0.12977 | 0.99091 | -0.17297 | 42.3839
13 | 0.082628 | 0.020804 | -0.082504 | -0.020724 | 0.0001247 | 7.9533e-05 | 0.12441 | 0.12441 | 0.12441 | 0.98851 | -0.21983 | 0.98689 | -0.25145 | 34.1799
14 | 0.13001 | 0.03321 | -0.12998 | -0.033195 | 2.3677e-05 | 1.4957e-05 | 0.19442 | 0.19442 | 0.19442 | 0.99615 | -0.072956 | 0.99595 | -0.076723 | 17.8045
15 | -0.40447 | -0.10346 | 0.40506 | 0.10384 | 0.00058385 | 0.00037316 | 0.60355 | 0.60355 | 0.60355 | 0.99843 | -0.029777 | 1 | 0 | 55.2703
16 | 0.042836 | 0.010795 | -0.04274 | -0.010735 | 9.5737e-05 | 6.0479e-05 | 0.064344 | 0.064344 | 0.064344 | 0.99094 | -0.17279 | 0.98852 | -0.21962 | 17.677
17 | 0.10068 | 0.02567 | -0.1006 | -0.025616 | 8.3249e-05 | 5.3155e-05 | 0.15135 | 0.15135 | 0.15135 | 0.99091 | -0.17297 | 0.99002 | -0.19011 | 41.5796
18 | -0.013163 | -0.0032991 | 0.013165 | 0.0032997 | 1.0963e-06 | 6.0704e-07 | 0.019859 | 0.019859 | 0.019859 | 0.98632 | -0.26246 | 0.98641 | -0.26071 | 5.4558
19 | -0.021984 | -0.00551 | 0.021994 | 0.0055159 | 9.7009e-06 | 5.9081e-06 | 0.033163 | 0.033163 | 0.033163 | 0.98641 | -0.26071 | 0.98689 | -0.25145 | 9.1108
20 | -0.01237 | -0.0031002 | 0.012372 | 0.0031013 | 1.9412e-06 | 1.0579e-06 | 0.018794 | 0.018794 | 0.018794 | 0.97941 | -0.39686 | 0.97958 | -0.39357 | 5.1631
21 | -0.02741 | -0.0068702 | 0.027436 | 0.0068861 | 2.5652e-05 | 1.592e-05 | 0.041637 | 0.041637 | 0.041637 | 0.97958 | -0.39357 | 0.98058 | -0.37395 | 11.4387
22 | 0.06051 | 0.015208 | -0.060484 | -0.015192 | 2.6077e-05 | 1.6582e-05 | 0.091252 | 0.091252 | 0.091252 | 0.98689 | -0.25145 | 0.98642 | -0.26048 | 25.0692
23 | -0.046046 | -0.01155 | 0.046068 | 0.011564 | 2.2141e-05 | 1.4018e-05 | 0.069877 | 0.069877 | 0.069877 | 0.98058 | -0.37395 | 0.9811 | -0.36386 | 19.1971
24 | 0.025428 | 0.0063756 | -0.025423 | -0.0063725 | 5.1225e-06 | 3.1599e-06 | 0.03836 | 0.03836 | 0.03836 | 0.98642 | -0.26048 | 0.9862 | -0.26471 | 10.5384
25 | 0.035056 | 0.0088159 | -0.034998 | -0.0087797 | 5.766e-05 | 3.6202e-05 | 0.052892 | 0.052892 | 0.052892 | 0.98642 | -0.26048 | 0.98465 | -0.29498 | 14.5309
26 | -0.058852 | -0.014768 | 0.058964 | 0.014839 | 0.0001121 | 7.1267e-05 | 0.089266 | 0.089266 | 0.089266 | 0.9811 | -0.36386 | 0.98314 | -0.324 | 24.5238
27 | 0.014776 | 0.003704 | -0.014773 | -0.0037026 | 2.5346e-06 | 1.4487e-06 | 0.022295 | 0.022295 | 0.022295 | 0.9862 | -0.26471 | 0.98602 | -0.26831 | 6.125
28 | 0.015038 | 0.0037727 | -0.015026 | -0.003766 | 1.18e-05 | 6.7775e-06 | 0.022727 | 0.022728 | 0.022728 | 0.98465 | -0.29498 | 0.98381 | -0.31145 | 6.2438
29 | 0.01996 | 0.0050069 | -0.019947 | -0.0049991 | 1.2969e-05 | 7.8168e-06 | 0.030165 | 0.030165 | 0.030165 | 0.98465 | -0.29498 | 0.98395 | -0.30862 | 8.2871
30 | -0.023321 | -0.0058496 | 0.023331 | 0.005856 | 1.0324e-05 | 6.3275e-06 | 0.035316 | 0.035315 | 0.035316 | 0.98266 | -0.33328 | 0.98314 | -0.324 | 9.7021
31 | 0.023321 | 0.0058496 | -0.023313 | -0.0058451 | 7.4643e-06 | 4.5751e-06 | 0.035316 | 0.035316 | 0.035316 | 0.98266 | -0.33328 | 0.98232 | -0.34 | 9.7021
32 | -0.082295 | -0.020695 | 0.082425 | 0.020778 | 0.0001299 | 8.2855e-05 | 0.12458 | 0.12458 | 0.12458 | 0.98314 | -0.324 | 0.98483 | -0.29101 | 34.2258
33 | 0.018304 | 0.0045897 | -0.018298 | -0.0045856 | 6.8534e-06 | 4.0854e-06 | 0.027728 | 0.027728 | 0.027728 | 0.98232 | -0.34 | 0.98192 | -0.34786 | 7.6177
34 | -0.093416 | -0.023533 | 0.093618 | 0.023662 | 0.00020212 | 0.00012901 | 0.14119 | 0.14119 | 0.14119 | 0.98483 | -0.29101 | 0.98716 | -0.24588 | 38.7881
35 | 0.0025909 | 0.00064917 | -0.0025908 | -0.00064931 | 9.0476e-08 | -1.4006e-07 | 0.0039262 | 0.0039263 | 0.0039263 | 0.98192 | -0.34786 | 0.98188 | -0.34859 | 1.0786
36 | 0.10698 | 0.027294 | -0.10683 | -0.027201 | 0.0001447 | 9.2416e-05 | 0.16052 | 0.16052 | 0.16052 | 0.99274 | -0.13802 | 0.99127 | -0.16606 | 44.0997
37 | -0.1126 | -0.028702 | 0.11265 | 0.028733 | 4.817e-05 | 3.077e-05 | 0.16894 | 0.16894 | 0.16894 | 0.99274 | -0.13802 | 0.9932 | -0.12916 | 46.4135
38 | 0.10228 | 0.026061 | -0.10225 | -0.026041 | 3.144e-05 | 2.0076e-05 | 0.15369 | 0.15369 | 0.15369 | 0.99127 | -0.16606 | 0.99094 | -0.17244 | 42.2236
39 | -0.11458 | -0.029219 | 0.11466 | 0.029267 | 7.6105e-05 | 4.8351e-05 | 0.17185 | 0.17185 | 0.17185 | 0.9932 | -0.12916 | 0.99392 | -0.11541 | 23.6056
40 | 0.096943 | 0.02471 | -0.096806 | -0.024623 | 0.00013695 | 8.7425e-05 | 0.14572 | 0.14572 | 0.14572 | 0.99094 | -0.17244 | 0.98941 | -0.20175 | 40.0328
41 | -0.11978 | -0.030551 | 0.11982 | 0.030572 | 3.3296e-05 | 2.0988e-05 | 0.17952 | 0.17952 | 0.17952 | 0.99392 | -0.11541 | 0.99422 | -0.10966 | 16.4396
42 | 0.092501 | 0.023544 | -0.092491 | -0.023537 | 1.0464e-05 | 6.6787e-06 | 0.13925 | 0.13925 | 0.13925 | 0.98941 | -0.20175 | 0.98929 | -0.2041 | 38.2542
43 | -0.12209 | -0.03114 | 0.12222 | 0.031223 | 0.00013055 | 8.2336e-05 | 0.18291 | 0.18291 | 0.18291 | 0.99422 | -0.10966 | 0.99538 | -0.08754 | 16.7503
44 | 0.088777 | 0.022606 | -0.08866 | -0.022532 | 0.00011612 | 7.4093e-05 | 0.13366 | 0.13366 | 0.13366 | 0.98929 | -0.2041 | 0.98787 | -0.23126 | 36.7195
45 | -0.12382 | -0.031625 | 0.12389 | 0.031666 | 6.4782e-05 | 4.0871e-05 | 0.18531 | 0.18531 | 0.18531 | 0.99538 | -0.08754 | 0.99595 | -0.076723 | 16.97
46 | 0.083998 | 0.021364 | -0.083976 | -0.02135 | 2.1427e-05 | 1.3668e-05 | 0.12664 | 0.12664 | 0.12664 | 0.98787 | -0.23126 | 0.9876 | -0.23655 | 34.7901
47 | 0.080614 | 0.020508 | -0.080521 | -0.020448 | 9.3176e-05 | 5.9418e-05 | 0.12157 | 0.12157 | 0.12157 | 0.9876 | -0.23655 | 0.98635 | -0.26057 | 33.3985
48 | 0.077583 | 0.019712 | -0.077573 | -0.019705 | 9.7806e-06 | 6.2353e-06 | 0.11714 | 0.11714 | 0.11714 | 0.98635 | -0.26057 | 0.98622 | -0.26319 | 32.1808
49 | 0.18498 | 0.047189 | -0.18493 | -0.047158 | 4.9103e-05 | 3.1222e-05 | 0.27555 | 0.27555 | 0.27555 | 1 | 0 | 0.99971 | -0.0054978 | 25.2332
50 | 0.18166 | 0.046339 | -0.18154 | -0.046263 | 0.0001206 | 7.6666e-05 | 0.27068 | 0.27068 | 0.27068 | 0.99971 | -0.0054978 | 0.99899 | -0.019254 | 24.7879
51 | 0.043781 | 0.010998 | -0.04376 | -0.010985 | 2.0307e-05 | 1.2845e-05 | 0.066795 | 0.066795 | 0.066795 | 0.97545 | -0.47294 | 0.97496 | -0.48266 | 18.3503
52 | -0.049183 | -0.012351 | 0.049195 | 0.012359 | 1.2818e-05 | 8.1278e-06 | 0.075035 | 0.075035 | 0.075035 | 0.97545 | -0.47294 | 0.97573 | -0.46748 | 20.6141
53 | 0.038892 | 0.0097646 | -0.038879 | -0.0097563 | 1.3085e-05 | 8.2512e-06 | 0.059365 | 0.059365 | 0.059365 | 0.97496 | -0.48266 | 0.9746 | -0.48972 | 16.3091
54 | -0.049195 | -0.012359 | 0.049246 | 0.012391 | 5.0161e-05 | 3.1806e-05 | 0.075035 | 0.075035 | 0.075035 | 0.97573 | -0.46748 | 0.97681 | -0.44614 | 20.6141
55 | 0.036134 | 0.0090683 | -0.03612 | -0.0090595 | 1.3967e-05 | 8.7864e-06 | 0.055174 | 0.055174 | 0.055174 | 0.9746 | -0.48972 | 0.97419 | -0.49783 | 15.1576
56 | -0.049938 | -0.012565 | 0.049978 | 0.01259 | 3.9892e-05 | 2.5301e-05 | 0.07609 | 0.076089 | 0.07609 | 0.97681 | -0.44614 | 0.97767 | -0.42943 | 20.9037
57 | 0.031624 | 0.0079328 | -0.031617 | -0.0079284 | 6.9893e-06 | 4.3737e-06 | 0.048307 | 0.048307 | 0.048307 | 0.97419 | -0.49783 | 0.97395 | -0.50246 | 13.2711
58 | -0.059059 | -0.014866 | 0.059152 | 0.014925 | 9.2585e-05 | 5.8871e-05 | 0.089912 | 0.089911 | 0.089912 | 0.97767 | -0.42943 | 0.97934 | -0.39669 | 24.701
59 | -0.0061319 | -0.0015368 | 0.0061327 | 0.001537 | 8.0995e-07 | 1.9601e-07 | 0.0092495 | 0.0092494 | 0.0092495 | 0.98647 | -0.2586 | 0.98661 | -0.25583 | 2.5411
60 | -0.012556 | -0.0031468 | 0.012559 | 0.0031486 | 3.3262e-06 | 1.8128e-06 | 0.018937 | 0.018937 | 0.018937 | 0.98661 | -0.25583 | 0.9869 | -0.25027 | 5.2025
61 | 0.024405 | 0.0061209 | -0.024403 | -0.0061196 | 2.1085e-06 | 1.2991e-06 | 0.037288 | 0.037288 | 0.037288 | 0.97395 | -0.50246 | 0.97386 | -0.50428 | 10.244
62 | -0.059687 | -0.015059 | 0.059773 | 0.015114 | 8.5669e-05 | 5.4478e-05 | 0.090725 | 0.090725 | 0.090725 | 0.97934 | -0.39669 | 0.98087 | -0.36676 | 24.9246
63 | -0.014264 | -0.003576 | 0.01427 | 0.0035789 | 5.2355e-06 | 2.9649e-06 | 0.021508 | 0.021508 | 0.021508 | 0.9869 | -0.25027 | 0.98729 | -0.24257 | 5.9088
64 | -0.063063 | -0.015938 | 0.063071 | 0.015944 | 8.7098e-06 | 5.5423e-06 | 0.095716 | 0.095716 | 0.095716 | 0.98087 | -0.36676 | 0.98102 | -0.36388 | 26.2955
65 | -0.063792 | -0.016124 | 0.063869 | 0.016174 | 7.7441e-05 | 4.9284e-05 | 0.096808 | 0.096808 | 0.096808 | 0.98102 | -0.36388 | 0.98232 | -0.3386 | 26.5957
66 | -0.066903 | -0.016934 | 0.066967 | 0.016974 | 6.3766e-05 | 4.0601e-05 | 0.1014 | 0.1014 | 0.1014 | 0.98232 | -0.3386 | 0.98335 | -0.31876 | 27.8583
67 | 0.020286 | 0.0050879 | -0.02028 | -0.005084 | 6.4333e-06 | 3.8953e-06 | 0.030998 | 0.030998 | 0.030998 | 0.97386 | -0.50428 | 0.97352 | -0.51093 | 8.516
68 | 0.016096 | 0.0040354 | -0.016094 | -0.0040343 | 1.8045e-06 | 1.056e-06 | 0.024603 | 0.024603 | 0.024603 | 0.97352 | -0.51093 | 0.9734 | -0.51328 | 6.7591
69 | 0.013135 | 0.0032928 | -0.013133 | -0.0032913 | 2.5615e-06 | 1.4288e-06 | 0.02008 | 0.02008 | 0.02008 | 0.9734 | -0.51328 | 0.9732 | -0.51738 | 5.5165
70 | 0.0048519 | 0.001216 | -0.0048517 | -0.001216 | 1.6228e-07 | 6.1598e-09 | 0.0074185 | 0.0074186 | 0.0074186 | 0.9732 | -0.51738 | 0.97316 | -0.51808 | 2.0381
71 | 0.098174 | 0.025008 | -0.097969 | -0.024877 | 0.00020492 | 0.00013083 | 0.1477 | 0.1477 | 0.1477 | 0.99002 | -0.19011 | 0.98776 | -0.23348 | 40.5775
72 | 0.08104 | 0.020629 | -0.080893 | -0.020536 | 0.00014665 | 9.3522e-05 | 0.1222 | 0.1222 | 0.1222 | 0.98776 | -0.23348 | 0.98581 | -0.27108 | 33.5706
73 | 0.01693 | 0.0042481 | -0.016922 | -0.0042438 | 7.3354e-06 | 4.3099e-06 | 0.025506 | 0.025506 | 0.025506 | 0.98776 | -0.23348 | 0.98729 | -0.24257 | 7.0071
74 | 0.080893 | 0.020536 | -0.080747 | -0.020443 | 0.00014567 | 9.2895e-05 | 0.1222 | 0.1222 | 0.1222 | 0.98581 | -0.27108 | 0.98387 | -0.30859 | 33.5706
75 | 0.030907 | 0.0077691 | -0.030895 | -0.0077616 | 1.2036e-05 | 7.5133e-06 | 0.046533 | 0.046533 | 0.046533 | 0.98852 | -0.21962 | 0.9881 | -0.22778 | 12.7837
76 | 0.077147 | 0.019541 | -0.077109 | -0.019516 | 3.7694e-05 | 2.4031e-05 | 0.11675 | 0.11675 | 0.11675 | 0.98387 | -0.30859 | 0.98335 | -0.31876 | 32.0747
77 | 0.02426 | 0.0060986 | -0.02421 | -0.0060681 | 4.9623e-05 | 3.0492e-05 | 0.03654 | 0.036541 | 0.036541 | 0.9881 | -0.22778 | 0.9859 | -0.27071 | 10.0387
78 | 0.0020442 | 0.00051197 | -0.002044 | -0.00051228 | 1.1626e-07 | -3.1594e-07 | 0.0031333 | 0.0031335 | 0.0031335 | 0.97073 | -0.56581 | 0.97067 | -0.567 | 0.86084
79 | -0.021923 | -0.0054941 | 0.021945 | 0.0055077 | 2.2303e-05 | 1.3622e-05 | 0.033605 | 0.033605 | 0.033605 | 0.97073 | -0.56581 | 0.97181 | -0.54447 | 9.2322
80 | -0.021945 | -0.0055077 | 0.021991 | 0.0055353 | 4.5216e-05 | 2.7612e-05 | 0.033605 | 0.033605 | 0.033605 | 0.97181 | -0.54447 | 0.974 | -0.50136 | 9.2321
81 | -0.0028961 | -0.00072584 | 0.0028964 | 0.00072549 | 3.2199e-07 | -3.4517e-07 | 0.0044139 | 0.0044137 | 0.0044139 | 0.97634 | -0.45536 | 0.97646 | -0.45303 | 1.2126
82 | -0.0048404 | -0.0012127 | 0.0048411 | 0.0012127 | 6.7389e-07 | 1.806e-08 | 0.0073761 | 0.007376 | 0.0073761 | 0.97646 | -0.45303 | 0.97661 | -0.45011 | 2.0264
83 | -0.021991 | -0.0055353 | 0.022009 | 0.0055465 | 1.8273e-05 | 1.1157e-05 | 0.033605 | 0.033604 | 0.033605 | 0.974 | -0.50136 | 0.97488 | -0.48399 | 9.232
84 | -0.025823 | -0.0065023 | 0.025833 | 0.0065088 | 1.0497e-05 | 6.4932e-06 | 0.039426 | 0.039425 | 0.039426 | 0.97488 | -0.48399 | 0.97531 | -0.47549 | 10.8312
85 | -0.0084013 | -0.0021056 | 0.0084025 | 0.0021061 | 1.2349e-06 | 5.2558e-07 | 0.012638 | 0.012638 | 0.012638 | 0.98921 | -0.20624 | 0.98937 | -0.20315 | 3.4719
86 | -0.11971 | -0.030282 | 0.12011 | 0.030535 | 0.00039646 | 0.00025331 | 0.18015 | 0.18015 | 0.18015 | 0.98937 | -0.20315 | 0.99295 | -0.13437 | 49.4913
87 | 0.097948 | 0.024825 | -0.097747 | -0.024697 | 0.00020065 | 0.0001281 | 0.14741 | 0.14741 | 0.14741 | 0.98937 | -0.20315 | 0.98716 | -0.24588 | 40.498
88 | 0.013363 | 0.0033505 | -0.013358 | -0.0033481 | 4.3435e-06 | 2.4117e-06 | 0.020098 | 0.020098 | 0.020098 | 0.98937 | -0.20315 | 0.98902 | -0.20997 | 5.5215
89 | -0.0052582 | -0.0013178 | 0.0052585 | 0.0013179 | 3.5188e-07 | 3.8489e-08 | 0.0079708 | 0.0079708 | 0.0079708 | 0.98161 | -0.35242 | 0.98168 | -0.35102 | 2.1898
90 | 0.058951 | 0.014924 | -0.058831 | -0.014848 | 0.00011947 | 7.5958e-05 | 0.08941 | 0.08941 | 0.08941 | 0.98168 | -0.35102 | 0.97951 | -0.39332 | 24.5633
91 | -0.064209 | -0.016242 | 0.064297 | 0.016297 | 8.7736e-05 | 5.5839e-05 | 0.097381 | 0.097381 | 0.097381 | 0.98168 | -0.35102 | 0.98315 | -0.32258 | 26.753
92 | -0.13749 | -0.034892 | 0.1376 | 0.034959 | 0.00010538 | 6.736e-05 | 0.2062 | 0.2062 | 0.2062 | 0.99295 | -0.13437 | 0.99378 | -0.11845 | 56.6485
93 | 0.010379 | 0.0026013 | -0.010378 | -0.0026009 | 7.8099e-07 | 3.9023e-07 | 0.015615 | 0.015615 | 0.015615 | 0.98902 | -0.20997 | 0.98894 | -0.21155 | 4.2898
94 | 0.058831 | 0.014848 | -0.058776 | -0.014813 | 5.4949e-05 | 3.4937e-05 | 0.08941 | 0.089411 | 0.089411 | 0.97951 | -0.39332 | 0.97851 | -0.41284 | 24.5633
95 | -0.069251 | -0.017539 | 0.069301 | 0.017571 | 5.0847e-05 | 3.2385e-05 | 0.10488 | 0.10488 | 0.10488 | 0.98315 | -0.32258 | 0.98393 | -0.3073 | 28.8127
96 | -0.14185 | -0.036024 | 0.14201 | 0.036129 | 0.00016575 | 0.00010557 | 0.21256 | 0.21256 | 0.21256 | 0.99378 | -0.11845 | 0.99505 | -0.094203 | 29.1977
97 | 0.0068566 | 0.0017184 | -0.0068563 | -0.0017183 | 3.3605e-07 | 1.0705e-07 | 0.010317 | 0.010317 | 0.010317 | 0.98894 | -0.21155 | 0.98889 | -0.21258 | 2.8343
98 | 0.055378 | 0.013961 | -0.055375 | -0.013959 | 2.5866e-06 | 1.6432e-06 | 0.084243 | 0.084243 | 0.084243 | 0.97851 | -0.41284 | 0.97846 | -0.41382 | 23.1436
99 | -0.071684 | -0.018168 | 0.071719 | 0.01819 | 3.4619e-05 | 2.2056e-05 | 0.10848 | 0.10848 | 0.10848 | 0.98393 | -0.3073 | 0.98445 | -0.29726 | 29.8026
100 | -0.14641 | -0.037231 | 0.14648 | 0.037279 | 7.6495e-05 | 4.846e-05 | 0.21913 | 0.21913 | 0.21913 | 0.99505 | -0.094203 | 0.99562 | -0.083364 | 20.067
101 | 0.0033442 | 0.00083808 | -0.0033442 | -0.00083813 | 6.4693e-08 | -4.5994e-08 | 0.0050322 | 0.0050322 | 0.0050322 | 0.98889 | -0.21258 | 0.98887 | -0.21299 | 1.3825
102 | 0.073331 | 0.018614 | -0.07328 | -0.018582 | 5.1176e-05 | 3.2611e-05 | 0.11084 | 0.11084 | 0.11084 | 0.9852 | -0.28274 | 0.98445 | -0.29726 | 30.4511
103 | -0.076582 | -0.019429 | 0.076654 | 0.019475 | 7.2089e-05 | 4.5954e-05 | 0.11575 | 0.11575 | 0.11575 | 0.9852 | -0.28274 | 0.98622 | -0.26319 | 31.7999
104 | -0.15028 | -0.03823 | 0.15032 | 0.038258 | 4.4632e-05 | 2.8289e-05 | 0.2248 | 0.2248 | 0.2248 | 0.99562 | -0.083364 | 0.99594 | -0.077203 | 20.586
105 | -0.1576 | -0.040081 | 0.15766 | 0.040121 | 6.2564e-05 | 3.9689e-05 | 0.23567 | 0.23567 | 0.23567 | 0.99594 | -0.077203 | 0.99637 | -0.068967 | 21.5813
106 | -0.16073 | -0.04089 | 0.16081 | 0.040945 | 8.5777e-05 | 5.4432e-05 | 0.24025 | 0.24025 | 0.24025 | 0.99637 | -0.068967 | 0.99695 | -0.057899 | 22.0011
107 | 0.17686 | 0.045088 | -0.1768 | -0.045053 | 5.5873e-05 | 3.5506e-05 | 0.26371 | 0.26371 | 0.26371 | 0.99899 | -0.019254 | 0.99864 | -0.025801 | 24.1489
108 | 0.17415 | 0.044389 | -0.17404 | -0.044318 | 0.00011161 | 7.091e-05 | 0.25976 | 0.25976 | 0.25976 | 0.99864 | -0.025801 | 0.99794 | -0.039088 | 23.7874
109 | 0.1709 | 0.04353 | -0.17082 | -0.043483 | 7.4672e-05 | 4.7431e-05 | 0.25507 | 0.25507 | 0.25507 | 0.99794 | -0.039088 | 0.99747 | -0.048151 | 23.3582
110 | 0.16418 | 0.041817 | -0.1641 | -0.041768 | 7.7164e-05 | 4.8983e-05 | 0.24515 | 0.24515 | 0.24515 | 0.99747 | -0.048151 | 0.99695 | -0.057899 | 22.45
111 | -0.051572 | -0.012988 | 0.05162 | 0.013018 | 4.8658e-05 | 3.0877e-05 | 0.078532 | 0.078532 | 0.078532 | 0.97745 | -0.43353 | 0.97846 | -0.41382 | 21.5748
112 | 0.04652 | 0.011721 | -0.046487 | -0.011701 | 3.2753e-05 | 2.0744e-05 | 0.070842 | 0.070842 | 0.070842 | 0.97745 | -0.43353 | 0.9767 | -0.44826 | 19.462
113 | 0.040032 | 0.010083 | -0.040024 | -0.010078 | 7.9032e-06 | 4.9872e-06 | 0.061007 | 0.061007 | 0.061007 | 0.9767 | -0.44826 | 0.97649 | -0.45239 | 16.7601
114 | 0.0064555 | 0.0016173 | -0.0064549 | -0.0016172 | 5.6668e-07 | 1.6717e-07 | 0.0098348 | 0.0098349 | 0.0098349 | 0.9767 | -0.44826 | 0.97661 | -0.45011 | 2.7019
115 | 0.036001 | 0.0090702 | -0.036 | -0.0090694 | 1.3337e-06 | 8.3878e-07 | 0.054878 | 0.054878 | 0.054878 | 0.97649 | -0.45239 | 0.97645 | -0.45317 | 15.0762
116 | 0.033908 | 0.0085452 | -0.033902 | -0.0085411 | 6.5381e-06 | 4.1028e-06 | 0.05169 | 0.05169 | 0.05169 | 0.97645 | -0.45317 | 0.97624 | -0.4572 | 14.2006
117 | 0.032468 | 0.0081816 | -0.032452 | -0.0081721 | 1.5191e-05 | 9.5158e-06 | 0.049504 | 0.049504 | 0.049504 | 0.97624 | -0.4572 | 0.97575 | -0.46698 | 13.6
118 | 0.028742 | 0.0072421 | -0.02873 | -0.0072348 | 1.1698e-05 | 7.2839e-06 | 0.043845 | 0.043845 | 0.043845 | 0.97575 | -0.46698 | 0.97531 | -0.47549 | 12.0453
119 | 0.02421 | 0.0060681 | -0.024209 | -0.0060674 | 1.1765e-06 | 7.2303e-07 | 0.036541 | 0.036541 | 0.036541 | 0.9859 | -0.27071 | 0.98585 | -0.27173 | 10.0387

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59629 | 0.15218

## res_load
| p_mw | q_mvar
0 | 0.012559 | 0.0031476
1 | 0.0013498 | 0.00033829
2 | 0.002893 | 0.00072504
3 | 0.0025653 | 0.00064292
4 | 0.00646 | 0.001619
5 | 0.0020911 | 0.00052409
6 | 0.0019038 | 0.00047713
7 | 0.0030892 | 0.00077423
8 | 0.0045935 | 0.0011512
9 | 0.0065938 | 0.0016526
10 | 0.0019496 | 0.00048863
11 | 0.013163 | 0.0032991
12 | 0.0088193 | 0.0022103
13 | 0.01237 | 0.0031002
14 | 0.015038 | 0.0037689
15 | 0.01861 | 0.0046641
16 | 0.012784 | 0.003204
17 | 0.010647 | 0.0026684
18 | 0.019947 | 0.0049991
19 | 0.015026 | 0.003766
20 | 0.0050089 | 0.0012553
21 | 0.010991 | 0.0027547
22 | 0.015707 | 0.0039365
23 | 0.014773 | 0.0037026
24 | 0.0056188 | 0.0014082
25 | 0.0045495 | 0.0011402
26 | 0.0019384 | 0.00048581
27 | 0.0053105 | 0.0013309
28 | 0.0051245 | 0.0012843
29 | 0.0043048 | 0.0010789
30 | 0.0022669 | 0.00056814
31 | 0.003714 | 0.00093082
32 | 0.0016053 | 0.00040232
33 | 0.0046627 | 0.0011686
34 | 0.0033618 | 0.00084256
35 | 0.0029383 | 0.0007364
36 | 0.006099 | 0.0015286
37 | 0.0046071 | 0.0011547
38 | 0.0032665 | 0.00081866
39 | 0.005402 | 0.0013539
40 | 0.0048682 | 0.0012201
41 | 0.0027451 | 0.00068799
42 | 0.00069206 | 0.00017345
43 | 0.0044957 | 0.0011267
44 | 0.0090815 | 0.002276
45 | 0.0061319 | 0.0015368
46 | 0.0064233 | 0.0016098
47 | 0.007212 | 0.0018075
48 | 0.00053571 | 0.00013426
49 | 0.0017051 | 0.00042734
50 | 0.0032896 | 0.00082444
51 | 0.00072042 | 0.00018055
52 | 0.0030339 | 0.00076038
53 | 0.0041168 | 0.0010318
54 | 0.004184 | 0.0010486
55 | 0.0029589 | 0.00074157
56 | 0.0082808 | 0.0020754
57 | 0.0048517 | 0.001216
58 | 0.0024268 | 0.00060821
59 | 0.0026527 | 0.00066483
60 | 0.011833 | 0.0029656
61 | 0.0036002 | 0.00090229
62 | 0.0066354 | 0.001663
63 | 0.010143 | 0.002542
64 | 0.019879 | 0.0049821
65 | 0.002044 | 0.00051228
66 | 0.0028961 | 0.00072584
67 | 0.001944 | 0.00048721
68 | 0.0038138 | 0.00095583
69 | 0.0084013 | 0.0021056
70 | 0.0052582 | 0.0013178
71 | 0.017385 | 0.004357
72 | 0.0041293 | 0.0010349
73 | 0.0029799 | 0.00074683
74 | 0.0049536 | 0.0012415
75 | 0.0042468 | 0.0010644
76 | 0.0035212 | 0.00088249
77 | 0.0033984 | 0.00085173
78 | 0.0023825 | 0.00059711
79 | 0.004395 | 0.0011015
80 | 0.003512 | 0.0008802
81 | 0.0032507 | 0.00081471
82 | 0.0015617 | 0.0003914
83 | 0.00091895 | 0.00023031
84 | 0.0025908 | 0.00064931
85 | 0.0037923 | 0.00095045
86 | 0.0072749 | 0.0018233
87 | 0.0030696 | 0.00076931
88 | 0.0046852 | 0.0011742
89 | 0.0026493 | 0.00066398
90 | 0.0031432 | 0.00078775
91 | 0.0066485 | 0.0016663
92 | 0.003284 | 0.00082304
93 | 0.0050518 | 0.0012661
94 | 0.0037549 | 0.00094108
95 | 0.0040223 | 0.0010081
96 | 0.0016138 | 0.00040446
97 | 0.0020917 | 0.00052422
98 | 0.0014343 | 0.00035946
99 | 0.0037109 | 0.00093004
100 | 0.0028967 | 0.00072599
101 | 0.024209 | 0.0060674
102 | 0.0033442 | 0.00083813

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1