## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-56_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1701-56_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1701-56_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1701-56_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1701-56_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1701-56_0_6_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1701-56_0_6_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1701-56_0_6_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1701-56_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1701-56_0_6_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_1701-56_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1701-56_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1701-56_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1701-56_0_6_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_1701-56_0_6_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_1701-56_0_6_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1701-56_0_6_node_44 | 0.4 | n |  | TRUE
17 | bus_LV_1701-56_0_6_node_87 | 0.4 | n |  | TRUE
18 | bus_LV_1701-56_0_6_node_86 | 0.4 | n |  | TRUE
19 | bus_LV_1701-56_0_6_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_1701-56_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1701-56_0_6_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1701-56_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1701-56_0_6_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1701-56_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1701-56_0_6_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1701-56_0_6_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1701-56_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1701-56_0_6_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1701-56_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1701-56_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1701-56_0_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1701-56_0_6_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_1701-56_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1701-56_0_6_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1701-56_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1701-56_0_6_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1701-56_0_6_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_1701-56_0_6_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_1701-56_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_1701-56_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1701-56_0_6_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_1701-56_0_6_node_92 | 0.4 | n |  | TRUE
43 | bus_LV_1701-56_0_6_node_91 | 0.4 | n |  | TRUE
44 | bus_LV_1701-56_0_6_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1701-56_0_6_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_1701-56_0_6_node_93 | 0.4 | n |  | TRUE
47 | bus_LV_1701-56_0_6_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_1701-56_0_6_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1701-56_0_6_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_1701-56_0_6_node_81 | 0.4 | n |  | TRUE
51 | bus_LV_1701-56_0_6_node_80 | 0.4 | n |  | TRUE
52 | bus_LV_1701-56_0_6_node_78 | 0.4 | n |  | TRUE
53 | bus_LV_1701-56_0_6_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_1701-56_0_6_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_1701-56_0_6_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_1701-56_0_6_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_1701-56_0_6_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_1701-56_0_6_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_1701-56_0_6_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_1701-56_0_6_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_1701-56_0_6_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_1701-56_0_6_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1701-56_0_6_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_1701-56_0_6_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_1701-56_0_6_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_1701-56_0_6_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_1701-56_0_6_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_1701-56_0_6_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_1701-56_0_6_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1701-56_0_6_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_1701-56_0_6_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_1701-56_0_6_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_1701-56_0_6_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_1701-56_0_6_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_1701-56_0_6_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_1701-56_0_6_node_72 | 0.4 | n |  | TRUE
77 | bus_LV_1701-56_0_6_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_1701-56_0_6_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_1701-56_0_6_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_1701-56_0_6_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_1701-56_0_6_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_1701-56_0_6_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_1701-56_0_6_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_1701-56_0_6_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_1701-56_0_6_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_1701-56_0_6_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_1701-56_0_6_node_88 | 0.4 | n |  | TRUE
88 | bus_LV_1701-56_0_6_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_1701-56_0_6_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_1701-56_0_6_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_1701-56_0_6_node_85 | 0.4 | n |  | TRUE
92 | bus_LV_1701-56_0_6_node_97 | 0.4 | n |  | TRUE
93 | bus_LV_1701-56_0_6_node_94 | 0.4 | n |  | TRUE
94 | bus_LV_1701-56_0_6_node_95 | 0.4 | n |  | TRUE
95 | bus_LV_1701-56_0_6_node_96 | 0.4 | n |  | TRUE
96 | bus_MV_497_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-56_0_6_load_0 | 0 | 0.0049082 | 0.0012301 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-56_0_6_load_1 | 1 | 0.0024512 | 0.00061432 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-56_0_6_load_2 | 2 | 0.0018866 | 0.00047283 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-56_0_6_load_3 | 3 | 0.0088953 | 0.0022294 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-56_0_6_load_4 | 4 | 0.0024716 | 0.00061943 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-56_0_6_load_35 | 6 | 0.0029212 | 0.00073212 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-56_0_6_load_5 | 8 | 0.0066892 | 0.0016765 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-56_0_6_load_36 | 9 | 0.0084743 | 0.0021239 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-56_0_6_load_8 | 10 | 0.0021099 | 0.0005288 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-56_0_6_load_9 | 11 | 0.0052293 | 0.0013106 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-56_0_6_load_10 | 12 | 0.0028714 | 0.00071964 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-56_0_6_load_24 | 13 | 0.0045151 | 0.0011316 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-56_0_6_load_39 | 14 | 0.0025929 | 0.00064985 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-56_0_6_load_22 | 15 | 0.0063945 | 0.0016026 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-56_0_6_load_44 | 16 | 0.0054712 | 0.0013712 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-56_0_6_load_87 | 17 | 0.0058348 | 0.0014624 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-56_0_6_load_86 | 18 | 0.0075172 | 0.001884 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1701-56_0_6_load_11 | 20 | 0.0026643 | 0.00066773 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1701-56_0_6_load_12 | 21 | 0.002337 | 0.00058571 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1701-56_0_6_load_13 | 22 | 0.0057769 | 0.0014478 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1701-56_0_6_load_14 | 23 | 0.0067228 | 0.0016849 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1701-56_0_6_load_15 | 24 | 0.004876 | 0.001222 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1701-56_0_6_load_33 | 25 | 0.0022359 | 0.00056037 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1701-56_0_6_load_26 | 27 | 0.0062229 | 0.0015596 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1701-56_0_6_load_16 | 28 | 0.007172 | 0.0017975 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1701-56_0_6_load_17 | 29 | 0.0076034 | 0.0019056 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1701-56_0_6_load_18 | 30 | 0.0078041 | 0.0019559 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1701-56_0_6_load_34 | 32 | 0.0024156 | 0.0006054 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1701-56_0_6_load_25 | 35 | 0.005629 | 0.0014108 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1701-56_0_6_load_21 | 36 | 0.0056343 | 0.0014121 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1701-56_0_6_load_40 | 37 | 0.0135 | 0.0033834 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1701-56_0_6_load_30 | 39 | 0.010176 | 0.0025502 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1701-56_0_6_load_31 | 40 | 0.010495 | 0.0026304 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1701-56_0_6_load_92 | 42 | 0.012136 | 0.0030414 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1701-56_0_6_load_91 | 43 | 0.0098074 | 0.002458 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1701-56_0_6_load_37 | 44 | 0.0057938 | 0.0014521 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1701-56_0_6_load_38 | 45 | 0.0021152 | 0.00053012 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1701-56_0_6_load_93 | 46 | 0.0084621 | 0.0021208 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1701-56_0_6_load_89 | 47 | 0.01197 | 0.003 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1701-56_0_6_load_79 | 49 | 0.005875 | 0.0014724 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1701-56_0_6_load_81 | 50 | 0.0020231 | 0.00050703 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1701-56_0_6_load_80 | 51 | 0.0049707 | 0.0012458 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1701-56_0_6_load_78 | 52 | 0.0034332 | 0.00086045 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1701-56_0_6_load_45 | 53 | 0.077073 | 0.019316 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1701-56_0_6_load_46 | 54 | 0.01007 | 0.0025238 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1701-56_0_6_load_48 | 56 | 0.00084362 | 0.00021143 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1701-56_0_6_load_49 | 57 | 0.0021111 | 0.00052909 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1701-56_0_6_load_53 | 58 | 0.0010229 | 0.00025637 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1701-56_0_6_load_52 | 61 | 0.023567 | 0.0059064 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1701-56_0_6_load_50 | 62 | 0.0096884 | 0.0024281 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1701-56_0_6_load_67 | 63 | 0.024495 | 0.0061391 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1701-56_0_6_load_54 | 64 | 0.00939 | 0.0023534 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1701-56_0_6_load_55 | 65 | 0.0065729 | 0.0016473 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1701-56_0_6_load_56 | 66 | 0.0023351 | 0.00058522 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1701-56_0_6_load_57 | 67 | 0.012515 | 0.0031365 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1701-56_0_6_load_59 | 68 | 0.006719 | 0.0016839 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1701-56_0_6_load_65 | 69 | 0.0043661 | 0.0010943 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1701-56_0_6_load_60 | 71 | 0.0043976 | 0.0011021 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1701-56_0_6_load_61 | 72 | 0.0089111 | 0.0022333 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1701-56_0_6_load_62 | 73 | 0.016881 | 0.0042308 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1701-56_0_6_load_63 | 74 | 0.0020187 | 0.00050592 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1701-56_0_6_load_64 | 75 | 0.0046999 | 0.0011779 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1701-56_0_6_load_76 | 78 | 0.0017399 | 0.00043606 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1701-56_0_6_load_77 | 79 | 0.0025327 | 0.00063475 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1701-56_0_6_load_70 | 80 | 0.012953 | 0.0032463 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1701-56_0_6_load_73 | 82 | 0.013012 | 0.0032611 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1701-56_0_6_load_74 | 83 | 0.011683 | 0.0029279 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1701-56_0_6_load_90 | 86 | 0.012019 | 0.0030123 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1701-56_0_6_load_88 | 87 | 0.0084274 | 0.0021121 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1701-56_0_6_load_82 | 88 | 0.0014023 | 0.00035145 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1701-56_0_6_load_83 | 89 | 0.0031457 | 0.00078839 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1701-56_0_6_load_84 | 90 | 0.0084626 | 0.0021209 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1701-56_0_6_load_85 | 91 | 0.0084635 | 0.0021212 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1701-56_0_6_load_97 | 92 | 0.0043831 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1701-56_0_6_load_94 | 93 | 0.007549 | 0.001892 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1701-56_0_6_load_95 | 94 | 0.0084626 | 0.0021209 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1701-56_0_6_load_96 | 95 | 0.0075479 | 0.0018917 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 89 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-56_0_6_line_0 |  | 0 | 1 | 0.00097092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-56_0_6_line_1 |  | 0 | 2 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-56_0_6_line_2 |  | 1 | 3 | 0.036824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-56_0_6_line_3 |  | 2 | 4 | 0.0017706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1701-56_0_6_line_4 |  | 4 | 5 | 0.022975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1701-56_0_6_line_5 |  | 5 | 6 | 0.0075501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1701-56_0_6_line_6 |  | 5 | 7 | 0.024669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1701-56_0_6_line_7 |  | 6 | 9 | 0.0028255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1701-56_0_6_line_8 |  | 6 | 8 | 0.090243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-56_0_6_line_9 |  | 7 | 38 | 0.003589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1701-56_0_6_line_10 |  | 7 | 27 | 0.022046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1701-56_0_6_line_11 |  | 9 | 44 | 0.041284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-56_0_6_line_12 |  | 10 | 11 | 0.039775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1701-56_0_6_line_13 |  | 11 | 12 | 0.022384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1701-56_0_6_line_14 |  | 12 | 16 | 0.09844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1701-56_0_6_line_15 |  | 13 | 14 | 0.0097597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1701-56_0_6_line_16 |  | 13 | 15 | 0.026369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-56_0_6_line_17 |  | 14 | 37 | 0.019406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-56_0_6_line_18 |  | 15 | 36 | 0.0053218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1701-56_0_6_line_19 |  | 16 | 19 | 0.04275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_1701-56_0_6_line_20 |  | 16 | 17 | 0.040871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1701-56_0_6_line_21 |  | 17 | 18 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1701-56_0_6_line_22 |  | 18 | 35 | 0.018144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1701-56_0_6_line_23 |  | 19 | 48 | 0.015925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_1701-56_0_6_line_24 |  | 20 | 21 | 0.018652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1701-56_0_6_line_25 |  | 20 | 22 | 0.011505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1701-56_0_6_line_26 |  | 21 | 23 | 0.00026566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1701-56_0_6_line_27 |  | 22 | 24 | 0.015722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1701-56_0_6_line_28 |  | 23 | 25 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1701-56_0_6_line_29 |  | 25 | 26 | 0.01971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1701-56_0_6_line_30 |  | 26 | 32 | 0.016928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1701-56_0_6_line_31 |  | 26 | 29 | 0.020714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1701-56_0_6_line_32 |  | 28 | 29 | 0.0026402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1701-56_0_6_line_33 |  | 28 | 30 | 0.028297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1701-56_0_6_line_34 |  | 30 | 31 | 0.024592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1701-56_0_6_line_35 |  | 31 | 33 | 0.008518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1701-56_0_6_line_36 |  | 32 | 34 | 0.021541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1701-56_0_6_line_37 |  | 33 | 35 | 0.027068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1701-56_0_6_line_38 |  | 33 | 36 | 0.058444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1701-56_0_6_line_39 |  | 34 | 38 | 0.006753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1701-56_0_6_line_40 |  | 38 | 39 | 0.028539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1701-56_0_6_line_41 |  | 39 | 40 | 0.042324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1701-56_0_6_line_42 |  | 41 | 42 | 0.03286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1701-56_0_6_line_43 |  | 41 | 43 | 0.011821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1701-56_0_6_line_44 |  | 42 | 46 | 0.023155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1701-56_0_6_line_45 |  | 43 | 47 | 0.007623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1701-56_0_6_line_46 |  | 44 | 45 | 0.035709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1701-56_0_6_line_47 |  | 46 | 93 | 0.027279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1701-56_0_6_line_48 |  | 47 | 87 | 0.022637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1701-56_0_6_line_49 |  | 48 | 49 | 0.051726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_1701-56_0_6_line_50 |  | 48 | 50 | 0.036322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1701-56_0_6_line_51 |  | 48 | 51 | 0.071838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1701-56_0_6_line_52 |  | 49 | 52 | 0.014588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_1701-56_0_6_line_53 |  | 52 | 78 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_1701-56_0_6_line_54 |  | 53 | 54 | 0.0030547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1701-56_0_6_line_55 |  | 53 | 55 | 0.041616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1701-56_0_6_line_56 |  | 54 | 56 | 0.018224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1701-56_0_6_line_57 |  | 55 | 57 | 0.010165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1701-56_0_6_line_58 |  | 56 | 58 | 0.06741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1701-56_0_6_line_59 |  | 57 | 59 | 0.0044526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1701-56_0_6_line_60 |  | 58 | 60 | 0.032727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1701-56_0_6_line_61 |  | 59 | 61 | 0.022393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1701-56_0_6_line_62 |  | 59 | 62 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1701-56_0_6_line_63 |  | 60 | 63 | 0.031869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1701-56_0_6_line_64 |  | 63 | 70 | 0.02721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1701-56_0_6_line_65 |  | 64 | 65 | 0.0099041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1701-56_0_6_line_66 |  | 64 | 66 | 0.0075832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1701-56_0_6_line_67 |  | 65 | 67 | 0.022458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1701-56_0_6_line_68 |  | 67 | 68 | 0.0091002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1701-56_0_6_line_69 |  | 68 | 69 | 0.030828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1701-56_0_6_line_70 |  | 69 | 70 | 0.0098861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1701-56_0_6_line_71 |  | 70 | 81 | 0.007998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_1701-56_0_6_line_72 |  | 71 | 72 | 0.025045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_1701-56_0_6_line_73 |  | 71 | 73 | 0.0096484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_1701-56_0_6_line_74 |  | 72 | 74 | 0.041279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_1701-56_0_6_line_75 |  | 73 | 75 | 0.019634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_1701-56_0_6_line_76 |  | 74 | 76 | 0.0062106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_1701-56_0_6_line_77 |  | 75 | 77 | 0.0174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_1701-56_0_6_line_78 |  | 76 | 78 | 0.026466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_1701-56_0_6_line_79 |  | 76 | 79 | 0.015166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_1701-56_0_6_line_80 |  | 77 | 80 | 0.022137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_1701-56_0_6_line_81 |  | 79 | 88 | 0.037624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_1701-56_0_6_line_82 |  | 80 | 81 | 0.01553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_1701-56_0_6_line_83 |  | 81 | 82 | 0.022597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_1701-56_0_6_line_84 |  | 82 | 83 | 0.037899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_1701-56_0_6_line_85 |  | 83 | 85 | 0.018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1701-56_0_6_line_86 |  | 84 | 85 | 0.050671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1701-56_0_6_line_87 |  | 84 | 86 | 0.023765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1701-56_0_6_line_88 |  | 86 | 87 | 0.012291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1701-56_0_6_line_89 |  | 88 | 89 | 0.0011757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_1701-56_0_6_line_90 |  | 89 | 90 | 0.034386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1701-56_0_6_line_91 |  | 90 | 91 | 0.013789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1701-56_0_6_line_92 |  | 91 | 92 | 0.011341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1701-56_0_6_line_93 |  | 93 | 94 | 0.0002049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1701-56_0_6_line_94 |  | 94 | 95 | 0.026914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-56_0_6_trafo_83 | 0.63 MVA 20/0.4 kV | 96 | 89 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2681538.2242 | 1228515.8897 | 2681538.6579 | 1228515.021
1 | 2681538.2242 | 1228515.8897 | 2681529.0552 | 1228534.2551
2 | 2681538.6579 | 1228515.021 | 2681543.0555 | 1228506.2125 | 2681554.5845 | 1228491.605 | 2681560.6523 | 1228485.8405
3 | 2681528.2643 | 1228535.8392 | 2681529.0552 | 1228534.2551
4 | 2681516.1031 | 1228555.299 | 2681526.1242 | 1228540.1259 | 2681528.2643 | 1228535.8392
5 | 2681516.1031 | 1228555.299 | 2681510.8183 | 1228560.6911
6 | 2681533.9874 | 1228572.3446 | 2681516.1031 | 1228555.299
7 | 2681510.8183 | 1228560.6911 | 2681508.8405 | 1228562.709
8 | 2681510.8183 | 1228560.6911 | 2681445.5542 | 1228498.3663
9 | 2681533.9874 | 1228572.3446 | 2681537.1185 | 1228570.5752
10 | 2681533.9874 | 1228572.3446 | 2681517.2528 | 1228586.6969
11 | 2681508.8405 | 1228562.709 | 2681502.3929 | 1228569.2874 | 2681478.3517 | 1228590.516
12 | 2681551.7033 | 1228772.6713 | 2681553.9432 | 1228772.0215 | 2681561.5462 | 1228775.1167 | 2681570.3183 | 1228779.7179 | 2681577.4239 | 1228785.9307 | 2681586.7386 | 1228789.2537
13 | 2681586.7386 | 1228789.2537 | 2681607.8213 | 1228796.7749
14 | 2681675.2223 | 1228725.0285 | 2681607.8213 | 1228796.7749
15 | 2681502.4284 | 1228682.4102 | 2681493.9224 | 1228687.1954
16 | 2681502.4284 | 1228682.4102 | 2681509.3749 | 1228678.5022 | 2681526.4383 | 1228671.6208
17 | 2681477.9244 | 1228698.1515 | 2681490.8721 | 1228688.9114 | 2681493.9224 | 1228687.1954
18 | 2681526.4383 | 1228671.6208 | 2681530.4659 | 1228669.9965 | 2681531.4204 | 1228669.7789
19 | 2681716.6856 | 1228732.5832 | 2681698.9202 | 1228732.8727 | 2681679.5741 | 1228726.8808 | 2681675.2223 | 1228725.0285
20 | 2681640.7175 | 1228703.4656 | 2681646.3676 | 1228707.7452 | 2681665.321 | 1228720.8143 | 2681675.2223 | 1228725.0285
21 | 2681640.7175 | 1228703.4656 | 2681626.0623 | 1228692.365
22 | 2681611.5993 | 1228681.4101 | 2681626.0623 | 1228692.365
23 | 2681732.6548 | 1228732.3135 | 2681716.6856 | 1228732.5832
24 | 2681524.9242 | 1228616.8299 | 2681513.9954 | 1228621.7044 | 2681507.6672 | 1228623.8606
25 | 2681496.777 | 1228627.571 | 2681507.6672 | 1228623.8606
26 | 2681525.1668 | 1228616.7217 | 2681524.9242 | 1228616.8299
27 | 2681481.3753 | 1228629.3628 | 2681481.3753 | 1228629.3628 | 2681491.1258 | 1228629.4965 | 2681496.777 | 1228627.571
28 | 2681525.1668 | 1228616.7217 | 2681536.8984 | 1228611.4891 | 2681542.1016 | 1228608.5089
29 | 2681559.3699 | 1228599.033 | 2681555.6104 | 1228600.7715 | 2681542.1016 | 1228608.5089
30 | 2681559.3699 | 1228599.033 | 2681561.7874 | 1228597.9098 | 2681560.9922 | 1228591.2499 | 2681557.833 | 1228584.3876
31 | 2681559.3699 | 1228599.033 | 2681561.4739 | 1228601.4302 | 2681566.9028 | 1228602.8389 | 2681570.0528 | 1228608.5304 | 2681572.2614 | 1228613.4698
32 | 2681573.3392 | 1228615.8801 | 2681572.2614 | 1228613.4698
33 | 2681584.8901 | 1228641.7124 | 2681573.3392 | 1228615.8801
34 | 2681596.7221 | 1228662.9 | 2681592.5937 | 1228658.9407 | 2681584.8901 | 1228641.7124
35 | 2681589.0257 | 1228666.597 | 2681596.7221 | 1228662.9
36 | 2681543.8705 | 1228571.1014 | 2681552.5081 | 1228572.821 | 2681557.833 | 1228584.3876
37 | 2681589.0257 | 1228666.597 | 2681600.276 | 1228672.8333 | 2681611.5993 | 1228681.4101
38 | 2681589.0257 | 1228666.597 | 2681572.4635 | 1228663.679 | 2681552.5475 | 1228664.9624 | 2681531.4204 | 1228669.7789
39 | 2681543.8705 | 1228571.1014 | 2681537.1185 | 1228570.5752
40 | 2681537.1185 | 1228570.5752 | 2681544.8393 | 1228566.2114 | 2681561.7938 | 1228556.2382
41 | 2681597.7597 | 1228533.9549 | 2681582.539 | 1228544.0352 | 2681561.7938 | 1228556.2382
42 | 2681622.4534 | 1228522.8349 | 2681623.0614 | 1228527.1239 | 2681626.2756 | 1228531.9936 | 2681639.2888 | 1228550.5849
43 | 2681622.4534 | 1228522.8349 | 2681622.1492 | 1228520.707 | 2681623.1658 | 1228515.106 | 2681625.3633 | 1228511.7895
44 | 2681627.171 | 1228567.0722 | 2681636.8731 | 1228562.0596 | 2681639.282 | 1228557.7008 | 2681639.9898 | 1228554.1636 | 2681639.2888 | 1228550.5849
45 | 2681625.3633 | 1228511.7895 | 2681625.3633 | 1228511.7895 | 2681631.0891 | 1228506.7569
46 | 2681454.1696 | 1228616.7711 | 2681476.4286 | 1228592.2141 | 2681478.3517 | 1228590.516
47 | 2681627.171 | 1228567.0722 | 2681602.9354 | 1228579.5935
48 | 2681648.0918 | 1228491.8129 | 2681631.0891 | 1228506.7569
49 | 2681732.6548 | 1228732.3135 | 2681731.7475 | 1228691.3841 | 2681732.1358 | 1228680.6048
50 | 2681732.6548 | 1228732.3135 | 2681737.1816 | 1228748.0754 | 2681743.4419 | 1228759.547 | 2681748.0133 | 1228764.6536
51 | 2681732.6548 | 1228732.3135 | 2681744.3838 | 1228730.718 | 2681767.4187 | 1228726.8875 | 2681798.6229 | 1228725.2042 | 2681803.9877 | 1228725.8191
52 | 2681732.1358 | 1228680.6048 | 2681732.6608 | 1228666.0265
53 | 2681733.5139 | 1228647.0834 | 2681733.1813 | 1228651.5765 | 2681732.6608 | 1228666.0265
54 | 2681877.8483 | 1228522.1125 | 2681875.5947 | 1228520.0502
55 | 2681908.5495 | 1228550.2078 | 2681877.8483 | 1228522.1125
56 | 2681875.5947 | 1228520.0502 | 2681862.1508 | 1228507.7475
57 | 2681908.5495 | 1228550.2078 | 2681904.1693 | 1228554.6283 | 2681901.4912 | 1228557.5205
58 | 2681862.1508 | 1228507.7475 | 2681848.1664 | 1228494.95 | 2681812.8149 | 1228461.8127
59 | 2681898.6642 | 1228560.9568 | 2681900.6925 | 1228558.383 | 2681901.4912 | 1228557.5205
60 | 2681788.9375 | 1228439.4308 | 2681812.8149 | 1228461.8127
61 | 2681904.6709 | 1228576.528 | 2681899.0378 | 1228571.2357 | 2681904.102 | 1228566.113 | 2681898.6642 | 1228560.9568
62 | 2681898.6642 | 1228560.9568 | 2681887.0499 | 1228573.2126
63 | 2681788.9375 | 1228439.4308 | 2681767.5203 | 1228463.0301
64 | 2681751.6686 | 1228484.1826 | 2681751.8431 | 1228480.3045 | 2681767.5203 | 1228463.0301
65 | 2681811.7713 | 1228540.095 | 2681804.4408 | 1228533.435
66 | 2681817.3839 | 1228545.1944 | 2681811.7713 | 1228540.095
67 | 2681804.4408 | 1228533.435 | 2681787.8184 | 1228518.3328
68 | 2681781.083 | 1228512.2133 | 2681787.8184 | 1228518.3328
69 | 2681781.083 | 1228512.2133 | 2681758.2662 | 1228491.4832
70 | 2681751.6686 | 1228484.1826 | 2681754.6819 | 1228488.2267 | 2681758.2662 | 1228491.4832
71 | 2681751.6686 | 1228484.1826 | 2681744.0199 | 1228486.5902
72 | 2681746.0425 | 1228551.5887 | 2681747.6175 | 1228554.5084 | 2681750.5927 | 1228561.8765 | 2681751.7892 | 1228569.6427 | 2681751.1065 | 1228575.5269
73 | 2681746.0425 | 1228551.5887 | 2681743.6051 | 1228547.0704 | 2681741.0753 | 1228543.3311
74 | 2681751.1065 | 1228575.5269 | 2681751.0499 | 1228576.0147 | 2681739.1498 | 1228615.0279
75 | 2681729.6862 | 1228527.3576 | 2681733.0814 | 1228531.5151 | 2681741.0753 | 1228543.3311
76 | 2681737.3378 | 1228620.9682 | 2681739.1498 | 1228615.0279
77 | 2681718.3616 | 1228514.1677 | 2681721.4187 | 1228517.234 | 2681729.6862 | 1228527.3576
78 | 2681737.3378 | 1228620.9682 | 2681734.5214 | 1228633.4714 | 2681733.5139 | 1228647.0834
79 | 2681737.3378 | 1228620.9682 | 2681731.8239 | 1228619.1357 | 2681722.4727 | 1228618.848
80 | 2681718.3616 | 1228514.1677 | 2681733.441 | 1228497.9604
81 | 2681722.4727 | 1228618.848 | 2681706.9952 | 1228618.3719 | 2681686.7195 | 1228609.481
82 | 2681744.0199 | 1228486.5902 | 2681733.441 | 1228497.9604
83 | 2681744.0199 | 1228486.5902 | 2681730.4664 | 1228468.5087
84 | 2681730.4664 | 1228468.5087 | 2681721.9566 | 1228457.1559 | 2681711.3564 | 1228464.2484 | 2681705.0267 | 1228455.3046
85 | 2681696.2031 | 1228439.8236 | 2681696.0361 | 1228442.601 | 2681705.0267 | 1228455.3046
86 | 2681675.1741 | 1228468.0098 | 2681666.3892 | 1228455.4917 | 2681690.2422 | 1228438.5187 | 2681696.2031 | 1228439.8236
87 | 2681675.1741 | 1228468.0098 | 2681657.3241 | 1228483.6985
88 | 2681648.0918 | 1228491.8129 | 2681657.3241 | 1228483.6985
89 | 2681686.7195 | 1228609.481 | 2681685.6428 | 1228609.0088
90 | 2681685.6428 | 1228609.0088 | 2681661.4482 | 1228598.3995 | 2681654.0162 | 1228595.5289
91 | 2681640.6028 | 1228597.2682 | 2681647.1497 | 1228595.0676 | 2681654.0162 | 1228595.5289
92 | 2681631.4704 | 1228603.9919 | 2681640.6028 | 1228597.2682
93 | 2681602.9354 | 1228579.5935 | 2681602.7534 | 1228579.6876
94 | 2681578.8422 | 1228592.0413 | 2681602.7534 | 1228579.6876

## bus_geodata
| x | y | coords
0 | 2681538.2242 | 1228515.8897
1 | 2681538.6579 | 1228515.021
2 | 2681529.0552 | 1228534.2551
3 | 2681560.6523 | 1228485.8405
4 | 2681528.2643 | 1228535.8392
5 | 2681516.1031 | 1228555.299
6 | 2681510.8183 | 1228560.6911
7 | 2681533.9874 | 1228572.3446
8 | 2681445.5542 | 1228498.3663
9 | 2681508.8405 | 1228562.709
10 | 2681551.7033 | 1228772.6713
11 | 2681586.7386 | 1228789.2537
12 | 2681607.8213 | 1228796.7749
13 | 2681502.4284 | 1228682.4102
14 | 2681493.9224 | 1228687.1954
15 | 2681526.4383 | 1228671.6208
16 | 2681675.2223 | 1228725.0285
17 | 2681640.7175 | 1228703.4656
18 | 2681626.0623 | 1228692.365
19 | 2681716.6856 | 1228732.5832
20 | 2681507.6672 | 1228623.8606
21 | 2681524.9242 | 1228616.8299
22 | 2681496.777 | 1228627.571
23 | 2681525.1668 | 1228616.7217
24 | 2681481.3753 | 1228629.3628
25 | 2681542.1016 | 1228608.5089
26 | 2681559.3699 | 1228599.033
27 | 2681517.2528 | 1228586.6969
28 | 2681573.3392 | 1228615.8801
29 | 2681572.2614 | 1228613.4698
30 | 2681584.8901 | 1228641.7124
31 | 2681596.7221 | 1228662.9
32 | 2681557.833 | 1228584.3876
33 | 2681589.0257 | 1228666.597
34 | 2681543.8705 | 1228571.1014
35 | 2681611.5993 | 1228681.4101
36 | 2681531.4204 | 1228669.7789
37 | 2681477.9244 | 1228698.1515
38 | 2681537.1185 | 1228570.5752
39 | 2681561.7938 | 1228556.2382
40 | 2681597.7597 | 1228533.9549
41 | 2681622.4534 | 1228522.8349
42 | 2681639.2888 | 1228550.5849
43 | 2681625.3633 | 1228511.7895
44 | 2681478.3517 | 1228590.516
45 | 2681454.1696 | 1228616.7711
46 | 2681627.171 | 1228567.0722
47 | 2681631.0891 | 1228506.7569
48 | 2681732.6548 | 1228732.3135
49 | 2681732.1358 | 1228680.6048
50 | 2681748.0133 | 1228764.6536
51 | 2681803.9877 | 1228725.8191
52 | 2681732.6608 | 1228666.0265
53 | 2681877.8483 | 1228522.1125
54 | 2681875.5947 | 1228520.0502
55 | 2681908.5495 | 1228550.2078
56 | 2681862.1508 | 1228507.7475
57 | 2681901.4912 | 1228557.5205
58 | 2681812.8149 | 1228461.8127
59 | 2681898.6642 | 1228560.9568
60 | 2681788.9375 | 1228439.4308
61 | 2681904.6709 | 1228576.528
62 | 2681887.0499 | 1228573.2126
63 | 2681767.5203 | 1228463.0301
64 | 2681811.7713 | 1228540.0951
65 | 2681804.4408 | 1228533.435
66 | 2681817.3839 | 1228545.1944
67 | 2681787.8184 | 1228518.3328
68 | 2681781.083 | 1228512.2133
69 | 2681758.2662 | 1228491.4832
70 | 2681751.6686 | 1228484.1826
71 | 2681746.0425 | 1228551.5887
72 | 2681751.1065 | 1228575.5269
73 | 2681741.0753 | 1228543.3311
74 | 2681739.1498 | 1228615.0279
75 | 2681729.6862 | 1228527.3576
76 | 2681737.3378 | 1228620.9682
77 | 2681718.3616 | 1228514.1677
78 | 2681733.5139 | 1228647.0834
79 | 2681722.4727 | 1228618.848
80 | 2681733.441 | 1228497.9604
81 | 2681744.0199 | 1228486.5902
82 | 2681730.4664 | 1228468.5087
83 | 2681705.0267 | 1228455.3046
84 | 2681675.1741 | 1228468.0098
85 | 2681696.2031 | 1228439.8236
86 | 2681657.3241 | 1228483.6985
87 | 2681648.0918 | 1228491.8129
88 | 2681686.7195 | 1228609.481
89 | 2681685.6428 | 1228609.0088
90 | 2681654.0162 | 1228595.5289
91 | 2681640.6028 | 1228597.2682
92 | 2681631.4704 | 1228603.9919
93 | 2681602.9354 | 1228579.5935
94 | 2681602.7534 | 1228579.6876
95 | 2681578.8422 | 1228592.0413
96 | 2681737.3378 | 1228620.9682

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9706 | -0.56735 | 0.0049082 | 0.0012301
1 | 0.97059 | -0.56755 | 0.0024512 | 0.00061432
2 | 0.97091 | -0.56118 | 0.0018866 | 0.00047283
3 | 0.97028 | -0.57362 | 0.0088953 | 0.0022294
4 | 0.97094 | -0.56058 | 0.0024716 | 0.00061943
5 | 0.97138 | -0.55183 | 0 | 0
6 | 0.9712 | -0.55546 | 0.0029212 | 0.00073212
7 | 0.97246 | -0.53061 | 0 | 0
8 | 0.97064 | -0.56662 | 0.0066892 | 0.0016765
9 | 0.97116 | -0.55631 | 0.0084743 | 0.0021239
10 | 0.98694 | -0.24866 | 0.0021099 | 0.0005288
11 | 0.98702 | -0.24716 | 0.0052293 | 0.0013106
12 | 0.98717 | -0.24422 | 0.0028714 | 0.00071964
13 | 0.98194 | -0.34545 | 0.0045151 | 0.0011316
14 | 0.9818 | -0.34829 | 0.0025929 | 0.00064985
15 | 0.98244 | -0.33563 | 0.0063945 | 0.0016026
16 | 0.9881 | -0.22625 | 0.0054712 | 0.0013712
17 | 0.98677 | -0.25179 | 0.0058348 | 0.0014624
18 | 0.98619 | -0.26291 | 0.0075172 | 0.001884
19 | 0.98961 | -0.19723 | 0 | 0
20 | 0.9747 | -0.48656 | 0.0026643 | 0.00066773
21 | 0.97493 | -0.48201 | 0.002337 | 0.00058571
22 | 0.97458 | -0.48881 | 0.0057769 | 0.0014478
23 | 0.97493 | -0.48193 | 0.0067228 | 0.0016849
24 | 0.97451 | -0.49022 | 0.004876 | 0.001222
25 | 0.97532 | -0.4742 | 0.0022359 | 0.00056037
26 | 0.97577 | -0.46532 | 0 | 0
27 | 0.97233 | -0.53314 | 0.0062229 | 0.0015596
28 | 0.97798 | -0.42206 | 0.007172 | 0.0017975
29 | 0.97772 | -0.42727 | 0.0076034 | 0.0019056
30 | 0.98103 | -0.36278 | 0.0078041 | 0.0019559
31 | 0.98385 | -0.3081 | 0 | 0
32 | 0.97458 | -0.48887 | 0.0024156 | 0.0006054
33 | 0.98434 | -0.29866 | 0 | 0
34 | 0.9731 | -0.51798 | 0 | 0
35 | 0.98565 | -0.27342 | 0.005629 | 0.0014108
36 | 0.98258 | -0.33304 | 0.0056343 | 0.0014121
37 | 0.98156 | -0.35303 | 0.0135 | 0.0033834
38 | 0.97263 | -0.52712 | 0 | 0
39 | 0.97208 | -0.53799 | 0.010176 | 0.0025502
40 | 0.97167 | -0.54619 | 0.010495 | 0.0026304
41 | 0.973 | -0.52002 | 0 | 0
42 | 0.97164 | -0.54677 | 0.012136 | 0.0030414
43 | 0.97349 | -0.51042 | 0.0098074 | 0.002458
44 | 0.97085 | -0.56235 | 0.0057938 | 0.0014521
45 | 0.97078 | -0.56375 | 0.0021152 | 0.00053012
46 | 0.97095 | -0.56047 | 0.0084621 | 0.0021208
47 | 0.97387 | -0.50285 | 0.01197 | 0.003
48 | 0.99017 | -0.18644 | 0 | 0
49 | 0.99207 | -0.15019 | 0.005875 | 0.0014724
50 | 0.9901 | -0.18774 | 0.0020231 | 0.00050703
51 | 0.98984 | -0.19279 | 0.0049707 | 0.0012458
52 | 0.99262 | -0.13969 | 0.0034332 | 0.00086045
53 | 0.97596 | -0.4623 | 0.077073 | 0.019316
54 | 0.97628 | -0.45602 | 0.01007 | 0.0025238
55 | 0.97459 | -0.48928 | 0 | 0
56 | 0.97836 | -0.41528 | 0.00084362 | 0.00021143
57 | 0.97426 | -0.49587 | 0.0021111 | 0.00052909
58 | 0.98222 | -0.33987 | 0.0010229 | 0.00025637
59 | 0.97412 | -0.49859 | 0 | 0
60 | 0.98298 | -0.32517 | 0 | 0
61 | 0.97363 | -0.50829 | 0.023567 | 0.0059064
62 | 0.97397 | -0.5016 | 0.0096884 | 0.0024281
63 | 0.98372 | -0.31088 | 0.024495 | 0.0061391
64 | 0.98227 | -0.33917 | 0.00939 | 0.0023534
65 | 0.98238 | -0.33707 | 0.0065729 | 0.0016473
66 | 0.98226 | -0.33949 | 0.0023351 | 0.00058522
67 | 0.98276 | -0.32965 | 0.012515 | 0.0031365
68 | 0.98302 | -0.3246 | 0.006719 | 0.0016839
69 | 0.98409 | -0.30375 | 0.0043661 | 0.0010943
70 | 0.98447 | -0.2963 | 0 | 0
71 | 0.9897 | -0.19547 | 0.0043976 | 0.0011021
72 | 0.99129 | -0.16513 | 0.0089111 | 0.0022333
73 | 0.9891 | -0.20702 | 0.016881 | 0.0042308
74 | 0.99396 | -0.11406 | 0.0020187 | 0.00050592
75 | 0.98793 | -0.22941 | 0.0046999 | 0.0011779
76 | 0.99437 | -0.10635 | 0 | 0
77 | 0.98692 | -0.24899 | 0 | 0
78 | 0.99335 | -0.12583 | 0.0017399 | 0.00043606
79 | 0.99595 | -0.076441 | 0.0025327 | 0.00063475
80 | 0.98562 | -0.27397 | 0.012953 | 0.0032463
81 | 0.98475 | -0.29081 | 0 | 0
82 | 0.98429 | -0.29984 | 0.013012 | 0.0032611
83 | 0.98359 | -0.31322 | 0.011683 | 0.0029279
84 | 0.97803 | -0.42124 | 0 | 0
85 | 0.98211 | -0.34182 | 0 | 0
86 | 0.97612 | -0.45872 | 0.012019 | 0.0030123
87 | 0.97526 | -0.47546 | 0.0084274 | 0.0021121
88 | 0.99988 | -0.0023128 | 0.0014023 | 0.00035145
89 | 1 | 0 | -0.59829 | -0.15384
90 | 0.99934 | -0.01278 | 0.0084626 | 0.0021209
91 | 0.99917 | -0.015873 | 0.0084635 | 0.0021212
92 | 0.99913 | -0.01674 | 0.0043831 | 0.0010985
93 | 0.97035 | -0.57236 | 0.007549 | 0.001892
94 | 0.97035 | -0.57242 | 0.0084626 | 0.0021209
95 | 0.97016 | -0.57618 | 0.0075479 | 0.0018917
96 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.011349 | 0.0028449 | -0.011349 | -0.0028449 | 1.1023e-07 | 5.8546e-08 | 0.017399 | 0.017399 | 0.017399 | 0.9706 | -0.56735 | 0.97059 | -0.56755 | 4.7801
1 | -0.016257 | -0.004075 | 0.016262 | 0.0040779 | 4.7819e-06 | 2.8066e-06 | 0.024924 | 0.024924 | 0.024924 | 0.9706 | -0.56735 | 0.97091 | -0.56118 | 6.8473
2 | 0.0088979 | 0.0022306 | -0.0088953 | -0.0022294 | 2.5698e-06 | 1.1897e-06 | 0.013642 | 0.013642 | 0.013642 | 0.97059 | -0.56755 | 0.97028 | -0.57362 | 3.7477
3 | -0.018149 | -0.0045507 | 0.018149 | 0.004551 | 5.1371e-07 | 3.0688e-07 | 0.027816 | 0.027816 | 0.027816 | 0.97091 | -0.56118 | 0.97094 | -0.56058 | 7.6416
4 | -0.020621 | -0.0051704 | 0.020629 | 0.0051756 | 8.6049e-06 | 5.2229e-06 | 0.031603 | 0.031603 | 0.031603 | 0.97094 | -0.56058 | 0.97138 | -0.55183 | 8.6822
5 | 0.026005 | 0.0065196 | -0.026 | -0.0065168 | 4.4931e-06 | 2.7821e-06 | 0.039836 | 0.039836 | 0.039836 | 0.97138 | -0.55183 | 0.9712 | -0.55546 | 10.9441
6 | -0.046634 | -0.011695 | 0.046682 | 0.011725 | 4.7213e-05 | 2.9911e-05 | 0.07144 | 0.07144 | 0.07144 | 0.97138 | -0.55183 | 0.97246 | -0.53061 | 19.6263
7 | 0.016386 | 0.004107 | -0.016386 | -0.0041067 | 6.6789e-07 | 3.9249e-07 | 0.025106 | 0.025106 | 0.025106 | 0.9712 | -0.55546 | 0.97116 | -0.55631 | 6.8974
8 | 0.0066928 | 0.0016776 | -0.0066892 | -0.0016765 | 3.5586e-06 | 1.1614e-06 | 0.010254 | 0.010255 | 0.010255 | 0.9712 | -0.55546 | 0.97064 | -0.56662 | 2.8172
9 | -0.052905 | -0.013285 | 0.052914 | 0.013291 | 8.8222e-06 | 5.6016e-06 | 0.080963 | 0.080963 | 0.080963 | 0.97246 | -0.53061 | 0.97263 | -0.52712 | 22.2425
10 | 0.0062236 | 0.0015598 | -0.0062229 | -0.0015596 | 7.4978e-07 | 2.0637e-07 | 0.0095231 | 0.0095232 | 0.0095232 | 0.97246 | -0.53061 | 0.97233 | -0.53314 | 2.6163
11 | 0.0079115 | 0.0019828 | -0.0079092 | -0.0019818 | 2.2749e-06 | 9.453e-07 | 0.012122 | 0.012122 | 0.012122 | 0.97116 | -0.55631 | 0.97085 | -0.56235 | 3.3303
12 | -0.0021099 | -0.0005288 | 0.0021101 | 0.00052839 | 1.5093e-07 | -4.1173e-07 | 0.0031811 | 0.003181 | 0.0031811 | 0.98694 | -0.24866 | 0.98702 | -0.24716 | 0.87394
13 | -0.0073394 | -0.001839 | 0.0073404 | 0.0018393 | 1.0276e-06 | 3.7154e-07 | 0.011065 | 0.011064 | 0.011065 | 0.98702 | -0.24716 | 0.98717 | -0.24422 | 3.0397
14 | -0.010212 | -0.002559 | 0.010221 | 0.0025633 | 8.7462e-06 | 4.3378e-06 | 0.015393 | 0.015392 | 0.015393 | 0.98717 | -0.24422 | 0.9881 | -0.22625 | 4.2288
15 | 0.016098 | 0.0040362 | -0.016096 | -0.004035 | 2.1781e-06 | 1.2706e-06 | 0.024395 | 0.024395 | 0.024395 | 0.98194 | -0.34545 | 0.9818 | -0.34829 | 6.702
16 | -0.020613 | -0.0051678 | 0.020623 | 0.0051737 | 9.6488e-06 | 5.8415e-06 | 0.031237 | 0.031237 | 0.031237 | 0.98194 | -0.34545 | 0.98244 | -0.33563 | 8.5817
17 | 0.013503 | 0.0033851 | -0.0135 | -0.0033834 | 3.0481e-06 | 1.7054e-06 | 0.020466 | 0.020466 | 0.020466 | 0.9818 | -0.34829 | 0.98156 | -0.35303 | 5.6224
18 | -0.027017 | -0.0067763 | 0.027021 | 0.0067784 | 3.342e-06 | 2.0715e-06 | 0.040923 | 0.040922 | 0.040923 | 0.98244 | -0.33563 | 0.98258 | -0.33304 | 11.2424
19 | -0.19234 | -0.04894 | 0.19261 | 0.049109 | 0.00026949 | 0.00016973 | 0.28991 | 0.28991 | 0.28991 | 0.9881 | -0.22625 | 0.98961 | -0.19723 | 15.9294
20 | 0.17665 | 0.045005 | -0.17643 | -0.044869 | 0.00021735 | 0.00013649 | 0.26628 | 0.26628 | 0.26628 | 0.9881 | -0.22625 | 0.98677 | -0.25179 | 14.631
21 | 0.1706 | 0.043406 | -0.1705 | -0.043349 | 9.1417e-05 | 5.7333e-05 | 0.25749 | 0.25749 | 0.25749 | 0.98677 | -0.25179 | 0.98619 | -0.26291 | 14.1476
22 | 0.16299 | 0.041465 | -0.1629 | -0.041413 | 8.2444e-05 | 5.1608e-05 | 0.24614 | 0.24614 | 0.24614 | 0.98619 | -0.26291 | 0.98565 | -0.27342 | 13.5244
23 | -0.19261 | -0.049109 | 0.19271 | 0.049173 | 0.00010039 | 6.3224e-05 | 0.28991 | 0.28991 | 0.28991 | 0.98961 | -0.19723 | 0.99017 | -0.18644 | 15.9293
24 | -0.013319 | -0.0033382 | 0.013321 | 0.0033398 | 2.8917e-06 | 1.6182e-06 | 0.020333 | 0.020333 | 0.020333 | 0.9747 | -0.48656 | 0.97493 | -0.48201 | 5.586
25 | 0.010654 | 0.0026705 | -0.010653 | -0.0026699 | 1.1414e-06 | 5.8714e-07 | 0.016265 | 0.016266 | 0.016266 | 0.9747 | -0.48656 | 0.97458 | -0.48881 | 4.4686
26 | -0.015659 | -0.0039255 | 0.015659 | 0.0039256 | 5.6904e-08 | 3.3106e-08 | 0.0239 | 0.0239 | 0.0239 | 0.97493 | -0.48201 | 0.97493 | -0.48193 | 6.5659
27 | 0.0048763 | 0.0012221 | -0.004876 | -0.001222 | 3.2681e-07 | 1.3268e-08 | 0.0074453 | 0.0074454 | 0.0074454 | 0.97458 | -0.48881 | 0.97451 | -0.49022 | 2.0454
28 | -0.022381 | -0.0056105 | 0.02239 | 0.0056155 | 8.2453e-06 | 5.042e-06 | 0.034161 | 0.034161 | 0.034161 | 0.97493 | -0.48193 | 0.97532 | -0.4742 | 9.3848
29 | -0.024626 | -0.0061759 | 0.024636 | 0.0061823 | 1.0434e-05 | 6.4314e-06 | 0.037572 | 0.037572 | 0.037572 | 0.97532 | -0.4742 | 0.97577 | -0.46532 | 10.3219
30 | 0.076236 | 0.019226 | -0.07615 | -0.019171 | 8.5857e-05 | 5.4737e-05 | 0.1163 | 0.1163 | 0.1163 | 0.97577 | -0.46532 | 0.97458 | -0.48887 | 31.9503
31 | -0.10087 | -0.025408 | 0.10106 | 0.025525 | 0.00018391 | 0.00011744 | 0.15387 | 0.15387 | 0.15387 | 0.97577 | -0.46532 | 0.97772 | -0.42727 | 42.2722
32 | 0.10869 | 0.027448 | -0.10866 | -0.027431 | 2.71e-05 | 1.7311e-05 | 0.16544 | 0.16544 | 0.16544 | 0.97798 | -0.42206 | 0.97772 | -0.42727 | 45.4512
33 | -0.11586 | -0.029246 | 0.11619 | 0.029457 | 0.00033003 | 0.00021086 | 0.17635 | 0.17635 | 0.17635 | 0.97798 | -0.42206 | 0.98103 | -0.36278 | 48.4491
34 | -0.12399 | -0.031413 | 0.12432 | 0.031621 | 0.00032661 | 0.00020872 | 0.18819 | 0.18819 | 0.18819 | 0.98103 | -0.36278 | 0.98385 | -0.3081 | 51.7011
35 | -0.12432 | -0.031621 | 0.12438 | 0.031657 | 5.6564e-05 | 3.5984e-05 | 0.18819 | 0.18819 | 0.18819 | 0.98385 | -0.3081 | 0.98434 | -0.29866 | 25.8505
36 | 0.073734 | 0.018565 | -0.073632 | -0.0185 | 0.00010244 | 6.529e-05 | 0.11261 | 0.11261 | 0.11261 | 0.97458 | -0.48887 | 0.9731 | -0.51798 | 30.9371
37 | -0.15708 | -0.039881 | 0.15728 | 0.040002 | 0.00019109 | 0.00012126 | 0.23765 | 0.23765 | 0.23765 | 0.98434 | -0.29866 | 0.98565 | -0.27342 | 21.7625
38 | 0.032709 | 0.008224 | -0.032655 | -0.0081904 | 5.3603e-05 | 3.3564e-05 | 0.049455 | 0.049455 | 0.049455 | 0.98434 | -0.29866 | 0.98258 | -0.33304 | 13.5866
39 | 0.073632 | 0.0185 | -0.0736 | -0.01848 | 3.2114e-05 | 2.0469e-05 | 0.11261 | 0.11261 | 0.11261 | 0.9731 | -0.51798 | 0.97263 | -0.52712 | 30.9371
40 | 0.020686 | 0.0051892 | -0.020675 | -0.0051827 | 1.0719e-05 | 6.5065e-06 | 0.031648 | 0.031648 | 0.031648 | 0.97263 | -0.52712 | 0.97208 | -0.53799 | 8.6946
41 | 0.010499 | 0.0026325 | -0.010495 | -0.0026304 | 4.1e-06 | 2.0995e-06 | 0.016072 | 0.016072 | 0.016072 | 0.97208 | -0.53799 | 0.97167 | -0.54619 | 4.4155
42 | 0.044249 | 0.011124 | -0.044193 | -0.011089 | 5.6449e-05 | 3.572e-05 | 0.067683 | 0.067683 | 0.067683 | 0.973 | -0.52002 | 0.97164 | -0.54677 | 18.5943
43 | -0.044249 | -0.011124 | 0.04427 | 0.011137 | 2.0306e-05 | 1.2849e-05 | 0.067683 | 0.067683 | 0.067683 | 0.973 | -0.52002 | 0.97349 | -0.51042 | 18.5943
44 | 0.032057 | 0.0080473 | -0.032036 | -0.0080341 | 2.0932e-05 | 1.311e-05 | 0.049099 | 0.049099 | 0.049099 | 0.97164 | -0.54677 | 0.97095 | -0.56047 | 13.4886
45 | -0.054077 | -0.013595 | 0.054096 | 0.013608 | 1.9539e-05 | 1.241e-05 | 0.082674 | 0.082674 | 0.082674 | 0.97349 | -0.51042 | 0.97387 | -0.50285 | 22.7127
46 | 0.0021154 | 0.00052977 | -0.0021152 | -0.00053012 | 1.4076e-07 | -3.5145e-07 | 0.0032421 | 0.0032422 | 0.0032422 | 0.97085 | -0.56235 | 0.97078 | -0.56375 | 0.89072
47 | 0.023574 | 0.0059133 | -0.023561 | -0.0059051 | 1.3354e-05 | 8.2092e-06 | 0.03613 | 0.03613 | 0.03613 | 0.97095 | -0.56047 | 0.97035 | -0.57236 | 9.9259
48 | -0.066066 | -0.016608 | 0.066153 | 0.016663 | 8.6531e-05 | 5.5098e-05 | 0.10096 | 0.10096 | 0.10096 | 0.97387 | -0.50285 | 0.97526 | -0.47546 | 27.7372
49 | -0.1997 | -0.050925 | 0.20005 | 0.051146 | 0.00035014 | 0.00022076 | 0.30043 | 0.30042 | 0.30043 | 0.99017 | -0.18644 | 0.99207 | -0.15019 | 16.5069
50 | 0.0020232 | 0.00050664 | -0.0020231 | -0.00050703 | 1.2591e-07 | -3.8658e-07 | 0.0030403 | 0.0030404 | 0.0030404 | 0.99017 | -0.18644 | 0.9901 | -0.18774 | 0.83529
51 | 0.0049722 | 0.0012458 | -0.0049707 | -0.0012458 | 1.5041e-06 | 3.8907e-08 | 0.007472 | 0.0074723 | 0.0074723 | 0.99017 | -0.18644 | 0.98984 | -0.19279 | 2.0528
52 | -0.20593 | -0.052618 | 0.20603 | 0.052684 | 0.00010462 | 6.6017e-05 | 0.30924 | 0.30924 | 0.30924 | 0.99207 | -0.15019 | 0.99262 | -0.13969 | 16.991
53 | -0.20947 | -0.053545 | 0.20961 | 0.053633 | 0.00014058 | 8.8745e-05 | 0.31438 | 0.31438 | 0.31438 | 0.99262 | -0.13969 | 0.99335 | -0.12583 | 17.2738
54 | -0.11251 | -0.028226 | 0.11255 | 0.028247 | 3.3714e-05 | 2.1539e-05 | 0.17155 | 0.17155 | 0.17155 | 0.97596 | -0.4623 | 0.97628 | -0.45602 | 47.1304
55 | 0.03544 | 0.0089094 | -0.035394 | -0.0088807 | 4.5581e-05 | 2.8652e-05 | 0.054044 | 0.054044 | 0.054044 | 0.97596 | -0.4623 | 0.97459 | -0.48928 | 14.8472
56 | -0.12262 | -0.030771 | 0.12286 | 0.030924 | 0.00023872 | 0.00015256 | 0.1869 | 0.1869 | 0.1869 | 0.97628 | -0.45602 | 0.97836 | -0.41528 | 51.3471
57 | 0.035394 | 0.0088807 | -0.035383 | -0.0088737 | 1.1133e-05 | 6.9986e-06 | 0.054044 | 0.054044 | 0.054044 | 0.97459 | -0.48928 | 0.97426 | -0.49587 | 14.8472
58 | -0.1237 | -0.031135 | 0.12415 | 0.03142 | 0.00044761 | 0.00028477 | 0.18819 | 0.18819 | 0.18819 | 0.97836 | -0.41528 | 0.98222 | -0.33987 | 25.8498
59 | 0.033272 | 0.0083446 | -0.033268 | -0.0083419 | 4.3122e-06 | 2.7044e-06 | 0.050819 | 0.050819 | 0.050819 | 0.97426 | -0.49587 | 0.97412 | -0.49859 | 13.9614
60 | -0.12517 | -0.031676 | 0.12526 | 0.031731 | 8.8362e-05 | 5.4479e-05 | 0.18974 | 0.18973 | 0.18974 | 0.98222 | -0.33987 | 0.98298 | -0.32517 | 10.425
61 | 0.023578 | 0.0059131 | -0.023567 | -0.0059064 | 1.0894e-05 | 6.6934e-06 | 0.036018 | 0.036018 | 0.036018 | 0.97412 | -0.49859 | 0.97363 | -0.50829 | 9.895
62 | 0.0096898 | 0.0024288 | -0.0096884 | -0.0024281 | 1.3873e-06 | 6.7768e-07 | 0.014802 | 0.014802 | 0.014802 | 0.97412 | -0.49859 | 0.97397 | -0.5016 | 4.0664
63 | -0.12526 | -0.031731 | 0.12534 | 0.031784 | 8.6044e-05 | 5.3047e-05 | 0.18973 | 0.18973 | 0.18973 | 0.98298 | -0.32517 | 0.98372 | -0.31088 | 10.425
64 | -0.14984 | -0.037923 | 0.14994 | 0.037988 | 0.00010496 | 6.5445e-05 | 0.22679 | 0.22679 | 0.22679 | 0.98372 | -0.31088 | 0.98447 | -0.2963 | 12.4608
65 | -0.011725 | -0.0029385 | 0.011726 | 0.0029391 | 1.1717e-06 | 6.2452e-07 | 0.017762 | 0.017762 | 0.017762 | 0.98227 | -0.33917 | 0.98238 | -0.33707 | 4.8797
66 | 0.0023351 | 0.00058515 | -0.0023351 | -0.00058522 | 3.5583e-08 | -7.3216e-08 | 0.0035373 | 0.0035374 | 0.0035374 | 0.98227 | -0.33917 | 0.98226 | -0.33949 | 0.97181
67 | -0.018299 | -0.0045865 | 0.018306 | 0.0045903 | 6.4704e-06 | 3.8566e-06 | 0.027718 | 0.027718 | 0.027718 | 0.98238 | -0.33707 | 0.98276 | -0.32965 | 7.6148
68 | -0.03082 | -0.0077268 | 0.030828 | 0.0077314 | 7.4318e-06 | 4.641e-06 | 0.046667 | 0.046667 | 0.046667 | 0.98276 | -0.32965 | 0.98302 | -0.3246 | 12.8205
69 | -0.037547 | -0.0094154 | 0.037584 | 0.0094389 | 3.7345e-05 | 2.351e-05 | 0.056837 | 0.056837 | 0.056837 | 0.98302 | -0.3246 | 0.98409 | -0.30375 | 15.6146
70 | -0.04195 | -0.010533 | 0.041965 | 0.010543 | 1.492e-05 | 9.4232e-06 | 0.063439 | 0.063439 | 0.063439 | 0.98409 | -0.30375 | 0.98447 | -0.2963 | 17.4283
71 | -0.19191 | -0.048531 | 0.19196 | 0.048563 | 5.0526e-05 | 3.1828e-05 | 0.29022 | 0.29022 | 0.29022 | 0.98447 | -0.2963 | 0.98475 | -0.29081 | 15.9464
72 | -0.34443 | -0.087722 | 0.34494 | 0.088043 | 0.0005047 | 0.00032139 | 0.51835 | 0.51835 | 0.51835 | 0.9897 | -0.19547 | 0.99129 | -0.16513 | 28.4808
73 | 0.34003 | 0.08662 | -0.33984 | -0.086499 | 0.0001895 | 0.00012066 | 0.51174 | 0.51174 | 0.51174 | 0.9897 | -0.19547 | 0.9891 | -0.20702 | 28.1176
74 | -0.35385 | -0.090277 | 0.35472 | 0.090834 | 0.00087532 | 0.00055753 | 0.53173 | 0.53173 | 0.53173 | 0.99129 | -0.16513 | 0.99396 | -0.11406 | 29.2158
75 | 0.32296 | 0.082268 | -0.32261 | -0.082047 | 0.0003483 | 0.00022165 | 0.48634 | 0.48634 | 0.48634 | 0.9891 | -0.20702 | 0.98793 | -0.22941 | 26.7222
76 | -0.35674 | -0.09134 | 0.35687 | 0.091425 | 0.0001332 | 8.4842e-05 | 0.53475 | 0.53475 | 0.53475 | 0.99396 | -0.11406 | 0.99437 | -0.10635 | 29.3818
77 | 0.31791 | 0.080869 | -0.31761 | -0.080678 | 0.00029976 | 0.00019073 | 0.47926 | 0.47927 | 0.47927 | 0.98793 | -0.22941 | 0.98692 | -0.24899 | 26.3333
78 | 0.21155 | 0.054195 | -0.21135 | -0.054069 | 0.00019945 | 0.00012593 | 0.31699 | 0.31699 | 0.31699 | 0.99437 | -0.10635 | 0.99335 | -0.12583 | 17.4169
79 | -0.56842 | -0.14562 | 0.56925 | 0.14615 | 0.00082517 | 0.00052713 | 0.85174 | 0.85173 | 0.85174 | 0.99437 | -0.10635 | 0.99595 | -0.076441 | 46.7986
80 | 0.31761 | 0.080678 | -0.31723 | -0.080435 | 0.00038136 | 0.00024266 | 0.47927 | 0.47927 | 0.47927 | 0.98692 | -0.24899 | 0.98562 | -0.27397 | 26.3333
81 | -0.57178 | -0.14678 | 0.57384 | 0.1481 | 0.0020653 | 0.0013193 | 0.85552 | 0.85552 | 0.85552 | 0.99595 | -0.076441 | 0.99988 | -0.0023128 | 47.0065
82 | 0.30428 | 0.077189 | -0.30403 | -0.077033 | 0.00024616 | 0.00015655 | 0.45971 | 0.45971 | 0.45971 | 0.98562 | -0.27397 | 0.98475 | -0.29081 | 25.2588
83 | 0.11207 | 0.02847 | -0.11202 | -0.02844 | 4.8684e-05 | 2.9721e-05 | 0.16949 | 0.16949 | 0.16949 | 0.98475 | -0.29081 | 0.98429 | -0.29984 | 9.3125
84 | 0.099013 | 0.025179 | -0.098949 | -0.025141 | 6.3799e-05 | 3.8424e-05 | 0.14982 | 0.14982 | 0.14982 | 0.98429 | -0.29984 | 0.98359 | -0.31322 | 8.2317
85 | 0.087267 | 0.022213 | -0.087147 | -0.022136 | 0.00012013 | 7.6651e-05 | 0.13214 | 0.13214 | 0.13214 | 0.98359 | -0.31322 | 0.98211 | -0.34182 | 36.3031
86 | -0.086815 | -0.021924 | 0.087147 | 0.022136 | 0.0003318 | 0.00021171 | 0.13214 | 0.13214 | 0.13214 | 0.97803 | -0.42124 | 0.98211 | -0.34182 | 36.3031
87 | 0.086815 | 0.021924 | -0.086659 | -0.021825 | 0.00015562 | 9.9297e-05 | 0.13214 | 0.13214 | 0.13214 | 0.97803 | -0.42124 | 0.97612 | -0.45872 | 36.3032
88 | 0.07464 | 0.018813 | -0.07458 | -0.018775 | 5.9715e-05 | 3.8064e-05 | 0.11382 | 0.11382 | 0.11382 | 0.97612 | -0.45872 | 0.97526 | -0.47546 | 31.2697
89 | -0.57525 | -0.14845 | 0.57531 | 0.14849 | 6.4854e-05 | 4.1429e-05 | 0.8576 | 0.8576 | 0.8576 | 0.99988 | -0.0023128 | 1 | 0 | 47.1211
90 | 0.021324 | 0.0053495 | -0.021311 | -0.0053416 | 1.2984e-05 | 7.8592e-06 | 0.031733 | 0.031733 | 0.031733 | 1 | 0 | 0.99934 | -0.01278 | 8.7178
91 | 0.012849 | 0.0032207 | -0.012847 | -0.0032196 | 1.8927e-06 | 1.0307e-06 | 0.019132 | 0.019132 | 0.019132 | 0.99934 | -0.01278 | 0.99917 | -0.015873 | 5.256
92 | 0.0043833 | 0.0010985 | -0.0043831 | -0.0010985 | 1.8121e-07 | -3.2551e-08 | 0.0065277 | 0.0065278 | 0.0065278 | 0.99917 | -0.015873 | 0.99913 | -0.01674 | 1.7933
93 | 0.016012 | 0.0040132 | -0.016012 | -0.0040131 | 4.6326e-08 | 2.7117e-08 | 0.024554 | 0.024554 | 0.024554 | 0.97035 | -0.57236 | 0.97035 | -0.57242 | 6.7456
94 | 0.0075493 | 0.0018922 | -0.0075479 | -0.0018917 | 1.3527e-06 | 5.333e-07 | 0.011577 | 0.011577 | 0.011577 | 0.97035 | -0.57242 | 0.97016 | -0.57618 | 3.1805

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60143 | 0.15463

## res_load
| p_mw | q_mvar
0 | 0.0049082 | 0.0012301
1 | 0.0024512 | 0.00061432
2 | 0.0018866 | 0.00047283
3 | 0.0088953 | 0.0022294
4 | 0.0024716 | 0.00061943
5 | 0.0029212 | 0.00073212
6 | 0.0066892 | 0.0016765
7 | 0.0084743 | 0.0021239
8 | 0.0021099 | 0.0005288
9 | 0.0052293 | 0.0013106
10 | 0.0028714 | 0.00071964
11 | 0.0045151 | 0.0011316
12 | 0.0025929 | 0.00064985
13 | 0.0063945 | 0.0016026
14 | 0.0054712 | 0.0013712
15 | 0.0058348 | 0.0014624
16 | 0.0075172 | 0.001884
17 | 0.0026643 | 0.00066773
18 | 0.002337 | 0.00058571
19 | 0.0057769 | 0.0014478
20 | 0.0067228 | 0.0016849
21 | 0.004876 | 0.001222
22 | 0.0022359 | 0.00056037
23 | 0.0062229 | 0.0015596
24 | 0.007172 | 0.0017975
25 | 0.0076034 | 0.0019056
26 | 0.0078041 | 0.0019559
27 | 0.0024156 | 0.0006054
28 | 0.005629 | 0.0014108
29 | 0.0056343 | 0.0014121
30 | 0.0135 | 0.0033834
31 | 0.010176 | 0.0025502
32 | 0.010495 | 0.0026304
33 | 0.012136 | 0.0030414
34 | 0.0098074 | 0.002458
35 | 0.0057938 | 0.0014521
36 | 0.0021152 | 0.00053012
37 | 0.0084621 | 0.0021208
38 | 0.01197 | 0.003
39 | 0.005875 | 0.0014724
40 | 0.0020231 | 0.00050703
41 | 0.0049707 | 0.0012458
42 | 0.0034332 | 0.00086045
43 | 0.077073 | 0.019316
44 | 0.01007 | 0.0025238
45 | 0.00084362 | 0.00021143
46 | 0.0021111 | 0.00052909
47 | 0.0010229 | 0.00025637
48 | 0.023567 | 0.0059064
49 | 0.0096884 | 0.0024281
50 | 0.024495 | 0.0061391
51 | 0.00939 | 0.0023534
52 | 0.0065729 | 0.0016473
53 | 0.0023351 | 0.00058522
54 | 0.012515 | 0.0031365
55 | 0.006719 | 0.0016839
56 | 0.0043661 | 0.0010943
57 | 0.0043976 | 0.0011021
58 | 0.0089111 | 0.0022333
59 | 0.016881 | 0.0042308
60 | 0.0020187 | 0.00050592
61 | 0.0046999 | 0.0011779
62 | 0.0017399 | 0.00043606
63 | 0.0025327 | 0.00063475
64 | 0.012953 | 0.0032463
65 | 0.013012 | 0.0032611
66 | 0.011683 | 0.0029279
67 | 0.012019 | 0.0030123
68 | 0.0084274 | 0.0021121
69 | 0.0014023 | 0.00035145
70 | 0.0031457 | 0.00078839
71 | 0.0084626 | 0.0021209
72 | 0.0084635 | 0.0021212
73 | 0.0043831 | 0.0010985
74 | 0.007549 | 0.001892
75 | 0.0084626 | 0.0021209
76 | 0.0075479 | 0.0018917

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1