## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1701-67_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1701-67_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1701-67_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1701-67_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1701-67_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1701-67_0_4_node_75 | 0.4 | n |  | TRUE
6 | bus_LV_1701-67_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1701-67_0_4_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_1701-67_0_4_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_1701-67_0_4_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_1701-67_0_4_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_1701-67_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1701-67_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1701-67_0_4_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_1701-67_0_4_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_1701-67_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1701-67_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1701-67_0_4_node_77 | 0.4 | n |  | TRUE
18 | bus_LV_1701-67_0_4_node_54 | 0.4 | n |  | TRUE
19 | bus_LV_1701-67_0_4_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1701-67_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_1701-67_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1701-67_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1701-67_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1701-67_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1701-67_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1701-67_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1701-67_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1701-67_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1701-67_0_4_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_1701-67_0_4_node_82 | 0.4 | n |  | TRUE
31 | bus_LV_1701-67_0_4_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_1701-67_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1701-67_0_4_node_67 | 0.4 | n |  | TRUE
34 | bus_LV_1701-67_0_4_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_1701-67_0_4_node_73 | 0.4 | n |  | TRUE
36 | bus_LV_1701-67_0_4_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_1701-67_0_4_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_1701-67_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1701-67_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1701-67_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_1701-67_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1701-67_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1701-67_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_1701-67_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_1701-67_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_1701-67_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1701-67_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_1701-67_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1701-67_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_1701-67_0_4_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_1701-67_0_4_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_1701-67_0_4_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1701-67_0_4_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_1701-67_0_4_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_1701-67_0_4_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_1701-67_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_1701-67_0_4_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_1701-67_0_4_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_1701-67_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_1701-67_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_1701-67_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1701-67_0_4_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_1701-67_0_4_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_1701-67_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1701-67_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_1701-67_0_4_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_1701-67_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1701-67_0_4_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_1701-67_0_4_node_81 | 0.4 | n |  | TRUE
70 | bus_LV_1701-67_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_1701-67_0_4_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_1701-67_0_4_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_1701-67_0_4_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_1701-67_0_4_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_1701-67_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_1701-67_0_4_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_1701-67_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1701-67_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_1701-67_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_MV_228_2_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1701-67_0_4_load_0 | 0 | 0.0012261 | 0.00030728 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1701-67_0_4_load_1 | 1 | 0.0019086 | 0.00047835 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1701-67_0_4_load_2 | 2 | 0.0037957 | 0.00095129 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1701-67_0_4_load_4 | 4 | 0.0029479 | 0.00073881 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1701-67_0_4_load_75 | 5 | 0.0030472 | 0.0007637 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1701-67_0_4_load_44 | 8 | 0.0013082 | 0.00032788 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1701-67_0_4_load_45 | 9 | 0.0010132 | 0.00025392 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1701-67_0_4_load_42 | 10 | 0.0032894 | 0.0008244 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1701-67_0_4_load_7 | 11 | 0.0031486 | 0.00078912 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1701-67_0_4_load_8 | 12 | 0.004328 | 0.0010847 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1701-67_0_4_load_46 | 13 | 0.020772 | 0.0052061 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1701-67_0_4_load_10 | 16 | 0.003091 | 0.00077468 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1701-67_0_4_load_77 | 17 | 0.003476 | 0.00087116 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1701-67_0_4_load_54 | 18 | 0.0032856 | 0.00082346 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1701-67_0_4_load_39 | 19 | 0.002241 | 0.00056164 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1701-67_0_4_load_51 | 20 | 0.0035038 | 0.00087813 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1701-67_0_4_load_11 | 21 | 0.0021662 | 0.0005429 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1701-67_0_4_load_12 | 22 | 0.016592 | 0.0041583 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1701-67_0_4_load_14 | 24 | 0.015926 | 0.0039913 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1701-67_0_4_load_15 | 25 | 0.0063315 | 0.0015868 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1701-67_0_4_load_17 | 27 | 0.014464 | 0.0036251 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1701-67_0_4_load_82 | 30 | 0.00099563 | 0.00024953 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1701-67_0_4_load_78 | 31 | 0.013442 | 0.0033689 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1701-67_0_4_load_19 | 32 | 0.0091648 | 0.0022969 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1701-67_0_4_load_73 | 35 | 0.0057219 | 0.001434 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1701-67_0_4_load_69 | 37 | 0.0095104 | 0.0023835 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1701-67_0_4_load_20 | 39 | 0.01029 | 0.002579 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1701-67_0_4_load_21 | 40 | 0.0096336 | 0.0024144 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1701-67_0_4_load_23 | 42 | 0.0041246 | 0.0010337 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1701-67_0_4_load_24 | 43 | 0.010294 | 0.00258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1701-67_0_4_load_35 | 47 | 0.0070835 | 0.0017753 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1701-67_0_4_load_27 | 48 | 0.01267 | 0.0031755 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1701-67_0_4_load_47 | 49 | 0.0036724 | 0.00092038 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1701-67_0_4_load_28 | 50 | 0.0093435 | 0.0023417 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1701-67_0_4_load_63 | 51 | 0.011768 | 0.0029494 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1701-67_0_4_load_62 | 52 | 0.0068862 | 0.0017258 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1701-67_0_4_load_29 | 53 | 0.010294 | 0.00258 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1701-67_0_4_load_31 | 55 | 0.039856 | 0.0099889 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1701-67_0_4_load_32 | 56 | 0.01175 | 0.0029449 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1701-67_0_4_load_64 | 57 | 0.01091 | 0.0027343 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1701-67_0_4_load_65 | 58 | 0.048002 | 0.01203 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1701-67_0_4_load_37 | 59 | 0.0037374 | 0.00093669 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1701-67_0_4_load_38 | 60 | 0.00329 | 0.00082455 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1701-67_0_4_load_40 | 61 | 0.0017088 | 0.00042827 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1701-67_0_4_load_79 | 62 | 0.0021586 | 0.00054099 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1701-67_0_4_load_74 | 63 | 0.0017328 | 0.00043427 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1701-67_0_4_load_41 | 64 | 0.001558 | 0.00039048 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1701-67_0_4_load_52 | 66 | 0.011621 | 0.0029126 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1701-67_0_4_load_53 | 67 | 0.0080232 | 0.0020108 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1701-67_0_4_load_80 | 68 | 0.047752 | 0.011968 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1701-67_0_4_load_81 | 69 | 0.0087951 | 0.0022043 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1701-67_0_4_load_55 | 70 | 0.021497 | 0.0053877 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1701-67_0_4_load_56 | 71 | 0.0019428 | 0.0004869 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1701-67_0_4_load_58 | 73 | 0.0021389 | 0.00053606 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1701-67_0_4_load_59 | 74 | 0.006545 | 0.0016403 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1701-67_0_4_load_72 | 77 | 0.0017548 | 0.0004398 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1701-67_0_4_load_71 | 78 | 0.00086603 | 0.00021705 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1701-67_0_4_load_70 | 79 | 0.0041128 | 0.0010308 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1701-67_0_4_line_0 |  | 0 | 1 | 0.017938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1701-67_0_4_line_1 |  | 0 | 2 | 0.0032343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1701-67_0_4_line_2 |  | 1 | 3 | 0.014265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1701-67_0_4_line_3 |  | 2 | 4 | 0.01131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1701-67_0_4_line_4 |  | 3 | 5 | 0.061555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1701-67_0_4_line_5 |  | 4 | 6 | 0.018446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1701-67_0_4_line_6 |  | 5 | 9 | 0.020035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1701-67_0_4_line_7 |  | 6 | 11 | 0.025395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1701-67_0_4_line_8 |  | 6 | 12 | 0.011984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1701-67_0_4_line_9 |  | 7 | 8 | 0.0066888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1701-67_0_4_line_10 |  | 7 | 9 | 0.023555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1701-67_0_4_line_11 |  | 8 | 10 | 0.098989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1701-67_0_4_line_12 |  | 10 | 64 | 0.010624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1701-67_0_4_line_13 |  | 11 | 15 | 0.034193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1701-67_0_4_line_14 |  | 12 | 16 | 0.037244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1701-67_0_4_line_15 |  | 13 | 14 | 0.0024736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1701-67_0_4_line_16 |  | 14 | 65 | 0.038852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1701-67_0_4_line_17 |  | 15 | 17 | 0.013417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1701-67_0_4_line_18 |  | 16 | 18 | 0.01363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1701-67_0_4_line_19 |  | 17 | 19 | 0.022996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1701-67_0_4_line_20 |  | 18 | 20 | 0.015259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1701-67_0_4_line_21 |  | 19 | 59 | 0.025769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1701-67_0_4_line_22 |  | 20 | 29 | 0.032627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1701-67_0_4_line_23 |  | 21 | 22 | 0.021157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1701-67_0_4_line_24 |  | 21 | 23 | 0.01827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1701-67_0_4_line_25 |  | 22 | 24 | 0.040444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1701-67_0_4_line_26 |  | 23 | 25 | 0.023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1701-67_0_4_line_27 |  | 23 | 26 | 0.033352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1701-67_0_4_line_28 |  | 24 | 27 | 8.674e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1701-67_0_4_line_29 |  | 26 | 28 | 0.008664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1701-67_0_4_line_30 |  | 27 | 29 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1701-67_0_4_line_31 |  | 28 | 30 | 0.02164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1701-67_0_4_line_32 |  | 28 | 31 | 0.027031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1701-67_0_4_line_33 |  | 29 | 34 | 0.016169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1701-67_0_4_line_34 |  | 30 | 35 | 0.00025036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1701-67_0_4_line_35 |  | 31 | 36 | 0.0026115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1701-67_0_4_line_36 |  | 32 | 33 | 0.036214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1701-67_0_4_line_37 |  | 33 | 37 | 0.02059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1701-67_0_4_line_38 |  | 33 | 38 | 0.034193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1701-67_0_4_line_39 |  | 34 | 66 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1701-67_0_4_line_40 |  | 34 | 67 | 0.032961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1701-67_0_4_line_41 |  | 35 | 78 | 0.00033408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1701-67_0_4_line_42 |  | 36 | 47 | 0.033952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1701-67_0_4_line_43 |  | 37 | 68 | 0.0089254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1701-67_0_4_line_44 |  | 38 | 57 | 0.015772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1701-67_0_4_line_45 |  | 38 | 55 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1701-67_0_4_line_46 |  | 39 | 40 | 0.027459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1701-67_0_4_line_47 |  | 39 | 41 | 0.0019562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1701-67_0_4_line_48 |  | 40 | 42 | 0.027027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1701-67_0_4_line_49 |  | 41 | 43 | 0.044288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1701-67_0_4_line_50 |  | 42 | 44 | 0.019019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1701-67_0_4_line_51 |  | 43 | 45 | 0.0034887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1701-67_0_4_line_52 |  | 44 | 46 | 0.044574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1701-67_0_4_line_53 |  | 44 | 47 | 0.0058202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1701-67_0_4_line_54 |  | 45 | 48 | 0.020089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1701-67_0_4_line_55 |  | 46 | 49 | 0.051075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1701-67_0_4_line_56 |  | 48 | 50 | 0.046387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1701-67_0_4_line_57 |  | 50 | 51 | 0.020575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1701-67_0_4_line_58 |  | 51 | 52 | 0.021967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1701-67_0_4_line_59 |  | 53 | 54 | 0.018435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1701-67_0_4_line_60 |  | 54 | 55 | 0.018811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1701-67_0_4_line_61 |  | 54 | 56 | 0.014152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1701-67_0_4_line_62 |  | 57 | 58 | 0.014847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1701-67_0_4_line_63 |  | 58 | 65 | 0.038605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1701-67_0_4_line_64 |  | 60 | 61 | 0.012737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1701-67_0_4_line_65 |  | 61 | 62 | 0.029499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1701-67_0_4_line_66 |  | 62 | 63 | 0.023601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1701-67_0_4_line_67 |  | 63 | 77 | 0.021179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1701-67_0_4_line_68 |  | 66 | 68 | 0.016279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1701-67_0_4_line_69 |  | 67 | 69 | 0.01398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1701-67_0_4_line_70 |  | 70 | 71 | 0.012777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1701-67_0_4_line_71 |  | 70 | 72 | 0.011496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1701-67_0_4_line_72 |  | 71 | 73 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1701-67_0_4_line_73 |  | 72 | 74 | 0.016482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1701-67_0_4_line_74 |  | 73 | 75 | 0.012086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1701-67_0_4_line_75 |  | 74 | 76 | 0.0096239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1701-67_0_4_line_76 |  | 75 | 77 | 0.0045499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1701-67_0_4_line_77 |  | 76 | 78 | 0.033862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1701-67_0_4_line_78 |  | 76 | 79 | 0.016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1701-67_0_4_trafo_19 | 0.63 MVA 20/0.4 kV | 80 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2684594.1477 | 1224461.7351 | 2684578.276 | 1224453.3777
1 | 2684594.1477 | 1224461.7351 | 2684597.0095 | 1224463.2419
2 | 2684565.0905 | 1224448.0137 | 2684574.4006 | 1224451.3371 | 2684578.276 | 1224453.3777
3 | 2684607.0172 | 1224468.5116 | 2684597.0095 | 1224463.2419
4 | 2684565.0905 | 1224448.0137 | 2684509.0386 | 1224422.5728
5 | 2684623.3384 | 1224477.1056 | 2684607.0172 | 1224468.5116
6 | 2684489.682 | 1224417.4035 | 2684509.0386 | 1224422.5728
7 | 2684623.3384 | 1224477.1056 | 2684640.9363 | 1224486.3065 | 2684645.7069 | 1224489.1172
8 | 2684623.3384 | 1224477.1056 | 2684633.3128 | 1224470.4631
9 | 2684466.991 | 1224411.0847 | 2684460.4548 | 1224412.5052
10 | 2684466.991 | 1224411.0847 | 2684483.5993 | 1224415.7791 | 2684489.682 | 1224417.4035
11 | 2684460.4548 | 1224412.5052 | 2684371.3543 | 1224369.3779
12 | 2684371.3543 | 1224369.3779 | 2684371.3543 | 1224369.3779 | 2684360.9794 | 1224367.092
13 | 2684675.1667 | 1224506.4737 | 2684645.7069 | 1224489.1172
14 | 2684633.3128 | 1224470.4631 | 2684644.0004 | 1224463.3455 | 2684654.4397 | 1224456.5894 | 2684663.4302 | 1224448.6888
15 | 2684586.0865 | 1224360.6301 | 2684584.7949 | 1224362.7397
16 | 2684586.0865 | 1224360.6301 | 2684568.3305 | 1224341.7094 | 2684561.7134 | 1224334.5661 | 2684560.3901 | 1224331.6342
17 | 2684675.1667 | 1224506.4737 | 2684685.6248 | 1224498.0693
18 | 2684670.8469 | 1224437.3447 | 2684670.5162 | 1224438.4278 | 2684664.0768 | 1224448.1206 | 2684663.4302 | 1224448.6888
19 | 2684685.6248 | 1224498.0693 | 2684685.6754 | 1224498.0285 | 2684697.2248 | 1224488.9311 | 2684704.1286 | 1224484.4535
20 | 2684670.8469 | 1224437.3447 | 2684672.7035 | 1224431.2651 | 2684671.3431 | 1224422.4671
21 | 2684725.8446 | 1224470.5812 | 2684706.6693 | 1224482.8057 | 2684704.1286 | 1224484.4535
22 | 2684659.2801 | 1224393.0037 | 2684669.0093 | 1224407.3741 | 2684671.3431 | 1224422.4671
23 | 2684714.8279 | 1224346.2058 | 2684694.2144 | 1224350.9719
24 | 2684732.6278 | 1224342.0902 | 2684714.8279 | 1224346.2058
25 | 2684676.353 | 1224381.8344 | 2684687.4809 | 1224379.1842 | 2684694.2144 | 1224350.9719 | 2684694.2144 | 1224350.9719
26 | 2684732.6278 | 1224342.0902 | 2684737.032 | 1224365.0929
27 | 2684732.6278 | 1224342.0902 | 2684725.889 | 1224309.4276
28 | 2684676.2686 | 1224381.8545 | 2684676.353 | 1224381.8344
29 | 2684734.3994 | 1224307.6808 | 2684725.889 | 1224309.4276
30 | 2684659.2801 | 1224393.0037 | 2684663.1631 | 1224384.9757 | 2684676.2686 | 1224381.8545
31 | 2684734.3994 | 1224307.6808 | 2684755.6195 | 1224303.4375
32 | 2684734.3994 | 1224307.6808 | 2684733.2558 | 1224280.6742
33 | 2684659.2801 | 1224393.0037 | 2684643.296 | 1224390.2745
34 | 2684755.865 | 1224303.3884 | 2684755.6195 | 1224303.4375
35 | 2684733.1453 | 1224278.065 | 2684733.2558 | 1224280.6742
36 | 2684628.3619 | 1224331.8557 | 2684663.5515 | 1224323.3055
37 | 2684628.3619 | 1224331.8557 | 2684635.0766 | 1224351.32
38 | 2684617.8355 | 1224299.4062 | 2684623.3163 | 1224315.5284 | 2684626.0791 | 1224327.0756 | 2684628.3619 | 1224331.8557
39 | 2684643.296 | 1224390.2745 | 2684640.9909 | 1224375.8144
40 | 2684643.296 | 1224390.2745 | 2684639.0981 | 1224397.5198 | 2684630.24 | 1224403.4646 | 2684622.9321 | 1224415.3118
41 | 2684756.1926 | 1224303.3229 | 2684755.865 | 1224303.3884
42 | 2684733.1453 | 1224278.065 | 2684733.1455 | 1224272.1943 | 2684733.6278 | 1224262.8281 | 2684737.892 | 1224252.0037 | 2684741.7814 | 1224246.1016
43 | 2684635.0766 | 1224351.32 | 2684637.2215 | 1224359.9839
44 | 2684617.8355 | 1224299.4062 | 2684603.6741 | 1224303.3965 | 2684602.6704 | 1224303.7338
45 | 2684617.8355 | 1224299.4062 | 2684619.9369 | 1224298.8134 | 2684639.2053 | 1224294.1215
46 | 2684677.8016 | 1224226.9903 | 2684696.0959 | 1224221.9996 | 2684704.5917 | 1224221.9351
47 | 2684675.9144 | 1224227.5051 | 2684677.8016 | 1224226.9903
48 | 2684729.7711 | 1224229.8266 | 2684725.4235 | 1224226.5644 | 2684711.3778 | 1224221.8836 | 2684704.5917 | 1224221.9351
49 | 2684675.9144 | 1224227.5051 | 2684634.2411 | 1224242.4961
50 | 2684744.984 | 1224241.2417 | 2684729.7711 | 1224229.8266
51 | 2684630.9584 | 1224243.6769 | 2684634.2411 | 1224242.4961
52 | 2684744.984 | 1224241.2417 | 2684755.352 | 1224230.4709 | 2684759.798 | 1224223.396 | 2684762.7459 | 1224213.9537 | 2684763.969 | 1224202.619
53 | 2684744.984 | 1224241.2417 | 2684741.7814 | 1224246.1016
54 | 2684630.9584 | 1224243.6769 | 2684612.0564 | 1224250.4809
55 | 2684763.969 | 1224202.619 | 2684770.935 | 1224203.3631 | 2684777.4918 | 1224206.214 | 2684791.8582 | 1224240.2235
56 | 2684612.0564 | 1224250.4809 | 2684604.6312 | 1224253.1537 | 2684574.5766 | 1224263.9896 | 2684568.1166 | 1224265.0522
57 | 2684568.1166 | 1224265.0522 | 2684551.4317 | 1224267.7968 | 2684547.766 | 1224267.7447
58 | 2684525.9102 | 1224266.2939 | 2684532.834 | 1224267.5325 | 2684547.766 | 1224267.7447
59 | 2684656.6209 | 1224287.316 | 2684662.8889 | 1224281.1454 | 2684671.6793 | 1224277.1899
60 | 2684656.6209 | 1224287.316 | 2684646.5549 | 1224292.3319 | 2684639.2053 | 1224294.1215
61 | 2684656.6209 | 1224287.316 | 2684661.1608 | 1224294.9413 | 2684663.678 | 1224299.5801
62 | 2684602.6704 | 1224303.7338 | 2684588.5968 | 1224308.4632
63 | 2684560.3901 | 1224331.6342 | 2684563.0628 | 1224324.4561 | 2684574.2475 | 1224313.2852 | 2684588.5968 | 1224308.4632
64 | 2684791.6627 | 1224410.8754 | 2684796.2012 | 1224405.6276 | 2684798.9748 | 1224400.5351
65 | 2684812.6314 | 1224374.4009 | 2684812.011 | 1224375.8992 | 2684808.2552 | 1224383.4953 | 2684798.9748 | 1224400.5351
66 | 2684812.6314 | 1224374.4009 | 2684814.579 | 1224369.6982 | 2684815.9172 | 1224365.192 | 2684818.6972 | 1224351.6641
67 | 2684818.6972 | 1224351.6641 | 2684822.5582 | 1224332.8756 | 2684822.8916 | 1224330.9062
68 | 2684640.9909 | 1224375.8144 | 2684640.7201 | 1224374.1158 | 2684637.2215 | 1224359.9839
69 | 2684611.5747 | 1224414.3734 | 2684620.9799 | 1224418.4765 | 2684622.9321 | 1224415.3118
70 | 2684819.6853 | 1224289.4827 | 2684819.8975 | 1224289.7194 | 2684821.1064 | 1224291.6268 | 2684821.9757 | 1224293.4182 | 2684822.4854 | 1224295.4268 | 2684823.7681 | 1224301.4282
71 | 2684810.7669 | 1224282.3065 | 2684817.8075 | 1224287.388 | 2684819.6853 | 1224289.4827
72 | 2684823.7681 | 1224301.4282 | 2684824.5115 | 1224304.9066 | 2684825.0877 | 1224314.5087
73 | 2684810.7669 | 1224282.3065 | 2684809.5438 | 1224284.0569 | 2684807.9112 | 1224285.8126 | 2684805.8279 | 1224287.7954 | 2684803.1734 | 1224289.948 | 2684799.2141 | 1224292.1375 | 2684798.1991 | 1224292.6362
74 | 2684823.6512 | 1224326.4201 | 2684825.3141 | 1224318.2827 | 2684825.0877 | 1224314.5087
75 | 2684789.3193 | 1224296.3105 | 2684794.6398 | 1224294.385 | 2684798.1991 | 1224292.6362
76 | 2684823.6512 | 1224326.4201 | 2684822.8916 | 1224330.9062
77 | 2684789.3193 | 1224296.3105 | 2684770.9405 | 1224300.3738 | 2684756.1926 | 1224303.3229
78 | 2684789.3193 | 1224296.3105 | 2684794.4647 | 1224305.6013 | 2684798.3878 | 1224310.183

## bus_geodata
| x | y | coords
0 | 2684594.1477 | 1224461.7351
1 | 2684578.276 | 1224453.3777
2 | 2684597.0095 | 1224463.2419
3 | 2684565.0905 | 1224448.0137
4 | 2684607.0172 | 1224468.5116
5 | 2684509.0386 | 1224422.5728
6 | 2684623.3384 | 1224477.1056
7 | 2684466.991 | 1224411.0847
8 | 2684460.4548 | 1224412.5052
9 | 2684489.682 | 1224417.4035
10 | 2684371.3543 | 1224369.3779
11 | 2684645.7069 | 1224489.1172
12 | 2684633.3128 | 1224470.4631
13 | 2684584.7949 | 1224362.7397
14 | 2684586.0865 | 1224360.6301
15 | 2684675.1667 | 1224506.4737
16 | 2684663.4302 | 1224448.6888
17 | 2684685.6248 | 1224498.0693
18 | 2684670.8469 | 1224437.3447
19 | 2684704.1286 | 1224484.4535
20 | 2684671.3431 | 1224422.4671
21 | 2684714.8279 | 1224346.2058
22 | 2684694.2144 | 1224350.9719
23 | 2684732.6278 | 1224342.0902
24 | 2684676.353 | 1224381.8344
25 | 2684737.032 | 1224365.0929
26 | 2684725.889 | 1224309.4276
27 | 2684676.2686 | 1224381.8545
28 | 2684734.3994 | 1224307.6808
29 | 2684659.2801 | 1224393.0037
30 | 2684755.6195 | 1224303.4375
31 | 2684733.2558 | 1224280.6742
32 | 2684663.5515 | 1224323.3055
33 | 2684628.3619 | 1224331.8557
34 | 2684643.296 | 1224390.2745
35 | 2684755.865 | 1224303.3884
36 | 2684733.1453 | 1224278.065
37 | 2684635.0766 | 1224351.32
38 | 2684617.8355 | 1224299.4062
39 | 2684677.8016 | 1224226.9903
40 | 2684704.5917 | 1224221.9351
41 | 2684675.9144 | 1224227.5051
42 | 2684729.7711 | 1224229.8266
43 | 2684634.2411 | 1224242.4961
44 | 2684744.984 | 1224241.2417
45 | 2684630.9584 | 1224243.6769
46 | 2684763.969 | 1224202.619
47 | 2684741.7814 | 1224246.1016
48 | 2684612.0564 | 1224250.4809
49 | 2684791.8582 | 1224240.2235
50 | 2684568.1166 | 1224265.0522
51 | 2684547.766 | 1224267.7447
52 | 2684525.9102 | 1224266.2939
53 | 2684671.6793 | 1224277.1899
54 | 2684656.6209 | 1224287.316
55 | 2684639.2053 | 1224294.1215
56 | 2684663.678 | 1224299.5801
57 | 2684602.6704 | 1224303.7338
58 | 2684588.5968 | 1224308.4632
59 | 2684725.8446 | 1224470.5812
60 | 2684791.6627 | 1224410.8754
61 | 2684798.9748 | 1224400.5351
62 | 2684812.6314 | 1224374.4009
63 | 2684818.6972 | 1224351.6641
64 | 2684360.9794 | 1224367.092
65 | 2684560.3901 | 1224331.6342
66 | 2684640.9909 | 1224375.8144
67 | 2684622.9321 | 1224415.3118
68 | 2684637.2215 | 1224359.9839
69 | 2684611.5747 | 1224414.3734
70 | 2684819.6853 | 1224289.4827
71 | 2684823.7681 | 1224301.4282
72 | 2684810.7669 | 1224282.3065
73 | 2684825.0877 | 1224314.5087
74 | 2684798.1991 | 1224292.6362
75 | 2684823.6512 | 1224326.4201
76 | 2684789.3193 | 1224296.3105
77 | 2684822.8916 | 1224330.9062
78 | 2684756.1926 | 1224303.3229
79 | 2684798.3878 | 1224310.183
80 | 2684628.3619 | 1224331.8557

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98601 | -0.26851 | 0.0012261 | 0.00030728
1 | 0.98581 | -0.27242 | 0.0019086 | 0.00047835
2 | 0.98605 | -0.26774 | 0.0037957 | 0.00095129
3 | 0.98568 | -0.27503 | 0 | 0
4 | 0.98623 | -0.26426 | 0.0029479 | 0.00073881
5 | 0.9851 | -0.28633 | 0.0030472 | 0.0007637
6 | 0.98657 | -0.25762 | 0 | 0
7 | 0.98483 | -0.29152 | 0 | 0
8 | 0.9848 | -0.29226 | 0.0013082 | 0.00032788
9 | 0.98497 | -0.28891 | 0.0010132 | 0.00025392
10 | 0.98435 | -0.30089 | 0.0032894 | 0.0008244
11 | 0.98628 | -0.26335 | 0.0031486 | 0.00078912
12 | 0.98693 | -0.2506 | 0.004328 | 0.0010847
13 | 0.99016 | -0.18898 | 0.020772 | 0.0052061
14 | 0.9902 | -0.18807 | 0 | 0
15 | 0.98598 | -0.26915 | 0 | 0
16 | 0.9882 | -0.22595 | 0.003091 | 0.00077468
17 | 0.98586 | -0.27142 | 0.003476 | 0.00087116
18 | 0.9887 | -0.21619 | 0.0032856 | 0.00082346
19 | 0.98574 | -0.27389 | 0.002241 | 0.00056164
20 | 0.98931 | -0.20438 | 0.0035038 | 0.00087813
21 | 0.98716 | -0.24561 | 0.0021662 | 0.0005429
22 | 0.98796 | -0.23028 | 0.016592 | 0.0041583
23 | 0.98648 | -0.25869 | 0 | 0
24 | 0.98963 | -0.19805 | 0.015926 | 0.0039913
25 | 0.98635 | -0.26135 | 0.0063315 | 0.0015868
26 | 0.9853 | -0.28168 | 0 | 0
27 | 0.98964 | -0.19798 | 0.014464 | 0.0036251
28 | 0.98488 | -0.28965 | 0 | 0
29 | 0.99072 | -0.17716 | 0 | 0
30 | 0.98379 | -0.31085 | 0.00099563 | 0.00024953
31 | 0.98405 | -0.30573 | 0.013442 | 0.0033689
32 | 1 | 0 | -0.49097 | -0.12493
33 | 0.99597 | -0.076591 | 0 | 0
34 | 0.99168 | -0.15879 | 0 | 0
35 | 0.98378 | -0.31109 | 0.0057219 | 0.001434
36 | 0.98384 | -0.30976 | 0 | 0
37 | 0.99435 | -0.10756 | 0.0095104 | 0.0023835
38 | 0.99376 | -0.11922 | 0 | 0
39 | 0.97603 | -0.46214 | 0.01029 | 0.002579
40 | 0.97759 | -0.43141 | 0.0096336 | 0.0024144
41 | 0.97593 | -0.46396 | 0 | 0
42 | 0.97938 | -0.39653 | 0.0041246 | 0.0010337
43 | 0.97383 | -0.50536 | 0.010294 | 0.00258
44 | 0.98071 | -0.37064 | 0 | 0
45 | 0.9737 | -0.50796 | 0 | 0
46 | 0.98056 | -0.37361 | 0 | 0
47 | 0.98113 | -0.36234 | 0.0070835 | 0.0017753
48 | 0.97293 | -0.523 | 0.01267 | 0.0031755
49 | 0.98038 | -0.37701 | 0.0036724 | 0.00092038
50 | 0.97172 | -0.54694 | 0.0093435 | 0.0023417
51 | 0.97136 | -0.55403 | 0.011768 | 0.0029494
52 | 0.97122 | -0.55682 | 0.0068862 | 0.0017258
53 | 0.99196 | -0.154 | 0.010294 | 0.00258
54 | 0.99214 | -0.15064 | 0 | 0
55 | 0.99252 | -0.1433 | 0.039856 | 0.0099889
56 | 0.99199 | -0.15359 | 0.01175 | 0.0029449
57 | 0.99261 | -0.14143 | 0.01091 | 0.0027343
58 | 0.99168 | -0.15951 | 0.048002 | 0.01203
59 | 0.98565 | -0.27562 | 0.0037374 | 0.00093669
60 | 0.97998 | -0.38539 | 0.00329 | 0.00082455
61 | 0.98002 | -0.38463 | 0.0017088 | 0.00042827
62 | 0.98016 | -0.38195 | 0.0021586 | 0.00054099
63 | 0.98032 | -0.37889 | 0.0017328 | 0.00043427
64 | 0.98434 | -0.30118 | 0.001558 | 0.00039048
65 | 0.99094 | -0.17373 | 0 | 0
66 | 0.9926 | -0.1411 | 0.011621 | 0.0029126
67 | 0.99117 | -0.16863 | 0.0080232 | 0.0020108
68 | 0.99367 | -0.12064 | 0.047752 | 0.011968
69 | 0.99106 | -0.17081 | 0.0087951 | 0.0022043
70 | 0.98098 | -0.3658 | 0.021497 | 0.0053877
71 | 0.98081 | -0.36921 | 0.0019428 | 0.0004869
72 | 0.98137 | -0.35826 | 0 | 0
73 | 0.98065 | -0.37226 | 0.0021389 | 0.00053606
74 | 0.98192 | -0.34746 | 0.006545 | 0.0016403
75 | 0.98053 | -0.37459 | 0 | 0
76 | 0.9823 | -0.34002 | 0 | 0
77 | 0.98049 | -0.37547 | 0.0017548 | 0.0004398
78 | 0.98377 | -0.31138 | 0.00086603 | 0.00021705
79 | 0.98224 | -0.34126 | 0.0041128 | 0.0010308
80 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.012138 | 0.0030438 | -0.012135 | -0.0030425 | 2.2571e-06 | 1.2158e-06 | 0.018318 | 0.018318 | 0.018318 | 0.98601 | -0.26851 | 0.98581 | -0.27242 | 5.0324
1 | -0.013364 | -0.003351 | 0.013364 | 0.0033513 | 4.9332e-07 | 2.7447e-07 | 0.020168 | 0.020168 | 0.020168 | 0.98601 | -0.26851 | 0.98605 | -0.26774 | 5.5407
2 | 0.010227 | 0.0025642 | -0.010225 | -0.0025636 | 1.2748e-06 | 6.34e-07 | 0.015437 | 0.015437 | 0.015437 | 0.98581 | -0.27242 | 0.98568 | -0.27503 | 4.2409
3 | -0.01716 | -0.0043026 | 0.017163 | 0.0043043 | 2.8443e-06 | 1.676e-06 | 0.025896 | 0.025896 | 0.025896 | 0.98605 | -0.26774 | 0.98623 | -0.26426 | 7.1143
4 | 0.010225 | 0.0025636 | -0.01022 | -0.0025608 | 5.5008e-06 | 2.7364e-06 | 0.015437 | 0.015437 | 0.015437 | 0.98568 | -0.27503 | 0.9851 | -0.28633 | 4.241
5 | -0.020111 | -0.0050431 | 0.020117 | 0.0050469 | 6.3688e-06 | 3.8406e-06 | 0.030344 | 0.030344 | 0.030344 | 0.98623 | -0.26426 | 0.98657 | -0.25762 | 8.3362
6 | 0.0071727 | 0.0017971 | -0.0071718 | -0.0017968 | 8.8193e-07 | 3.094e-07 | 0.010834 | 0.010834 | 0.010834 | 0.9851 | -0.28633 | 0.98497 | -0.28891 | 2.9765
7 | 0.012611 | 0.0031622 | -0.012608 | -0.0031604 | 3.4457e-06 | 1.881e-06 | 0.019021 | 0.019022 | 0.019022 | 0.98657 | -0.25762 | 0.98628 | -0.26335 | 5.2257
8 | -0.032728 | -0.0082092 | 0.032739 | 0.008216 | 1.0951e-05 | 6.8557e-06 | 0.049365 | 0.049365 | 0.049365 | 0.98657 | -0.25762 | 0.98693 | -0.2506 | 13.5618
9 | 0.0061579 | 0.0015427 | -0.0061577 | -0.0015427 | 2.1713e-07 | 5.3855e-08 | 0.009304 | 0.009304 | 0.009304 | 0.98483 | -0.29152 | 0.9848 | -0.29226 | 2.556
10 | -0.0061579 | -0.0015427 | 0.0061587 | 0.0015429 | 7.6462e-07 | 1.8959e-07 | 0.009304 | 0.0093039 | 0.009304 | 0.98483 | -0.29152 | 0.98497 | -0.28891 | 2.556
11 | 0.0048495 | 0.0012148 | -0.0048475 | -0.0012148 | 1.9931e-06 | 1.6669e-08 | 0.0073273 | 0.0073277 | 0.0073277 | 0.9848 | -0.29226 | 0.98435 | -0.30089 | 2.0131
12 | 0.0015581 | 0.00039036 | -0.001558 | -0.00039048 | 2.21e-08 | -1.209e-07 | 0.0023552 | 0.0023553 | 0.0023553 | 0.98435 | -0.30089 | 0.98434 | -0.30118 | 0.64705
13 | 0.009459 | 0.0023712 | -0.0094564 | -0.00237 | 2.6115e-06 | 1.2351e-06 | 0.014271 | 0.014271 | 0.014271 | 0.98628 | -0.26335 | 0.98598 | -0.26915 | 3.9207
14 | -0.037067 | -0.0093007 | 0.037111 | 0.0093282 | 4.3628e-05 | 2.7445e-05 | 0.05589 | 0.05589 | 0.05589 | 0.98693 | -0.2506 | 0.9882 | -0.22595 | 15.3545
15 | -0.020772 | -0.0052061 | 0.020773 | 0.0052066 | 9.0393e-07 | 5.467e-07 | 0.031217 | 0.031217 | 0.031217 | 0.99016 | -0.18898 | 0.9902 | -0.18807 | 8.5761
16 | -0.020773 | -0.0052066 | 0.020787 | 0.0052152 | 1.4198e-05 | 8.5865e-06 | 0.031217 | 0.031217 | 0.031217 | 0.9902 | -0.18807 | 0.99094 | -0.17373 | 8.5761
17 | 0.0094564 | 0.00237 | -0.0094554 | -0.0023695 | 1.0247e-06 | 4.8473e-07 | 0.014271 | 0.014271 | 0.014271 | 0.98598 | -0.26915 | 0.98586 | -0.27142 | 3.9207
18 | -0.040202 | -0.010103 | 0.04022 | 0.010115 | 1.8736e-05 | 1.1816e-05 | 0.060545 | 0.060545 | 0.060545 | 0.9882 | -0.22595 | 0.9887 | -0.21619 | 16.6332
19 | 0.0059794 | 0.0014984 | -0.0059787 | -0.0014982 | 7.0239e-07 | 1.5635e-07 | 0.009025 | 0.0090251 | 0.0090251 | 0.98586 | -0.27142 | 0.98574 | -0.27389 | 2.4794
20 | -0.043506 | -0.010938 | 0.043531 | 0.010954 | 2.4542e-05 | 1.5511e-05 | 0.06549 | 0.065489 | 0.06549 | 0.9887 | -0.21619 | 0.98931 | -0.20438 | 17.9916
21 | 0.0037378 | 0.00093656 | -0.0037374 | -0.00093669 | 3.0763e-07 | -1.3158e-07 | 0.0056422 | 0.0056423 | 0.0056423 | 0.98574 | -0.27389 | 0.98565 | -0.27562 | 1.5501
22 | -0.047034 | -0.011832 | 0.047096 | 0.011871 | 6.1259e-05 | 3.8786e-05 | 0.070759 | 0.070759 | 0.070759 | 0.98931 | -0.20438 | 0.99072 | -0.17716 | 19.4394
23 | -0.16351 | -0.041487 | 0.16363 | 0.041564 | 0.00012067 | 7.6144e-05 | 0.24665 | 0.24665 | 0.24665 | 0.98716 | -0.24561 | 0.98796 | -0.23028 | 16.9401
24 | 0.16134 | 0.040944 | -0.16124 | -0.04088 | 0.00010146 | 6.3998e-05 | 0.24338 | 0.24338 | 0.24338 | 0.98716 | -0.24561 | 0.98648 | -0.25869 | 16.7159
25 | -0.18022 | -0.045722 | 0.1805 | 0.045899 | 0.00027977 | 0.00017698 | 0.27164 | 0.27164 | 0.27164 | 0.98796 | -0.23028 | 0.98963 | -0.19805 | 18.6564
26 | 0.0063323 | 0.001587 | -0.0063315 | -0.0015868 | 8.0128e-07 | 2.1385e-07 | 0.0095516 | 0.0095517 | 0.0095517 | 0.98648 | -0.25869 | 0.98635 | -0.26135 | 2.6241
27 | 0.15491 | 0.039293 | -0.15474 | -0.039186 | 0.00017096 | 0.00010771 | 0.23383 | 0.23383 | 0.23383 | 0.98648 | -0.25869 | 0.9853 | -0.28168 | 16.0599
28 | -0.19643 | -0.04989 | 0.19643 | 0.049891 | 7.1048e-07 | 4.5024e-07 | 0.29558 | 0.29558 | 0.29558 | 0.98963 | -0.19805 | 0.98964 | -0.19798 | 20.301
29 | 0.15474 | 0.039186 | -0.15468 | -0.039148 | 5.9216e-05 | 3.7567e-05 | 0.23383 | 0.23383 | 0.23383 | 0.9853 | -0.28168 | 0.98488 | -0.28965 | 21.4132
30 | -0.21089 | -0.053516 | 0.2111 | 0.05365 | 0.00021137 | 0.00013413 | 0.31733 | 0.31733 | 0.31733 | 0.98964 | -0.19798 | 0.99072 | -0.17716 | 21.7947
31 | 0.054642 | 0.013761 | -0.054587 | -0.013725 | 5.5341e-05 | 3.5143e-05 | 0.08258 | 0.08258 | 0.08258 | 0.98488 | -0.28965 | 0.98379 | -0.31085 | 22.6869
32 | 0.10004 | 0.025388 | -0.099958 | -0.025339 | 7.7299e-05 | 4.8441e-05 | 0.15125 | 0.15125 | 0.15125 | 0.98488 | -0.28965 | 0.98405 | -0.30573 | 13.851
33 | -0.2582 | -0.06552 | 0.25843 | 0.065666 | 0.00022831 | 0.00014528 | 0.38809 | 0.38809 | 0.38809 | 0.99072 | -0.17716 | 0.99168 | -0.15879 | 26.6545
34 | 0.053591 | 0.013476 | -0.053591 | -0.013476 | 6.1711e-07 | 3.9177e-07 | 0.081074 | 0.081074 | 0.081074 | 0.98379 | -0.31085 | 0.98378 | -0.31109 | 22.2732
35 | 0.086516 | 0.02197 | -0.0865 | -0.02196 | 1.6787e-05 | 1.0711e-05 | 0.13093 | 0.13093 | 0.13093 | 0.98405 | -0.30573 | 0.98384 | -0.30976 | 35.969
36 | 0.48932 | 0.12493 | -0.48751 | -0.12377 | 0.0018039 | 0.0011526 | 0.72892 | 0.72892 | 0.72892 | 1 | 0 | 0.99597 | -0.076591 | 50.0633
37 | 0.34538 | 0.087943 | -0.34487 | -0.087614 | 0.00051495 | 0.0003285 | 0.5165 | 0.5165 | 0.5165 | 0.99597 | -0.076591 | 0.99435 | -0.10756 | 35.474
38 | 0.14213 | 0.03583 | -0.14184 | -0.035646 | 0.00028929 | 0.00018426 | 0.21242 | 0.21242 | 0.21242 | 0.99597 | -0.076591 | 0.99376 | -0.11922 | 29.1787
39 | -0.27525 | -0.069886 | 0.27549 | 0.070035 | 0.00023453 | 0.00014935 | 0.41334 | 0.41334 | 0.41334 | 0.99168 | -0.15879 | 0.9926 | -0.1411 | 28.3887
40 | 0.016827 | 0.0042201 | -0.016819 | -0.0042154 | 7.8807e-06 | 4.6186e-06 | 0.02525 | 0.02525 | 0.02525 | 0.99168 | -0.15879 | 0.99117 | -0.16863 | 6.9369
41 | 0.047869 | 0.012041 | -0.047868 | -0.012041 | 6.5704e-07 | 4.1626e-07 | 0.07242 | 0.07242 | 0.07242 | 0.98378 | -0.31109 | 0.98377 | -0.31138 | 19.8955
42 | 0.0865 | 0.02196 | -0.086281 | -0.02182 | 0.00021825 | 0.00013925 | 0.13093 | 0.13093 | 0.13093 | 0.98384 | -0.30976 | 0.98113 | -0.36234 | 35.969
43 | 0.33536 | 0.085231 | -0.33514 | -0.085096 | 0.00021109 | 0.00013464 | 0.50227 | 0.50227 | 0.50227 | 0.99435 | -0.10756 | 0.99367 | -0.12064 | 34.4965
44 | 0.079858 | 0.02008 | -0.079773 | -0.020026 | 8.4599e-05 | 5.3939e-05 | 0.1196 | 0.1196 | 0.1196 | 0.99376 | -0.11922 | 0.99261 | -0.14143 | 32.8569
45 | 0.061983 | 0.015565 | -0.061912 | -0.01552 | 7.113e-05 | 4.5238e-05 | 0.092822 | 0.092822 | 0.092822 | 0.99376 | -0.11922 | 0.99252 | -0.1433 | 25.5006
46 | -0.061432 | -0.015464 | 0.061522 | 0.015521 | 9.0368e-05 | 5.7492e-05 | 0.093681 | 0.093681 | 0.093681 | 0.97603 | -0.46214 | 0.97759 | -0.43141 | 25.7365
47 | 0.051141 | 0.012885 | -0.051137 | -0.012882 | 4.4624e-06 | 2.8315e-06 | 0.077993 | 0.077993 | 0.077993 | 0.97603 | -0.46214 | 0.97593 | -0.46396 | 21.4267
48 | -0.071156 | -0.017936 | 0.071275 | 0.018012 | 0.00011897 | 7.5801e-05 | 0.10834 | 0.10834 | 0.10834 | 0.97759 | -0.43141 | 0.97938 | -0.39653 | 29.7649
49 | 0.051137 | 0.012882 | -0.051036 | -0.012818 | 0.00010102 | 6.4103e-05 | 0.077993 | 0.077993 | 0.077993 | 0.97593 | -0.46396 | 0.97383 | -0.50536 | 21.4267
50 | -0.075399 | -0.019045 | 0.075493 | 0.019105 | 9.3687e-05 | 5.972e-05 | 0.11461 | 0.11461 | 0.11461 | 0.97938 | -0.39653 | 0.98071 | -0.37064 | 31.4865
51 | 0.040742 | 0.010238 | -0.040737 | -0.010235 | 5.0718e-06 | 3.2025e-06 | 0.062263 | 0.062263 | 0.062263 | 0.97383 | -0.50536 | 0.9737 | -0.50796 | 17.1053
52 | 0.0036735 | 0.00091989 | -0.003673 | -0.00092012 | 5.1925e-07 | -2.3002e-07 | 0.0055735 | 0.0055737 | 0.0055737 | 0.98071 | -0.37064 | 0.98056 | -0.37361 | 1.5312
53 | -0.079166 | -0.020025 | 0.079198 | 0.020045 | 3.1526e-05 | 2.0103e-05 | 0.12018 | 0.12018 | 0.12018 | 0.98071 | -0.37064 | 0.98113 | -0.36234 | 33.0176
54 | 0.040737 | 0.010235 | -0.040707 | -0.010216 | 2.9205e-05 | 1.8442e-05 | 0.062263 | 0.062264 | 0.062264 | 0.9737 | -0.50796 | 0.97293 | -0.523 | 17.1054
55 | 0.003673 | 0.00092012 | -0.0036724 | -0.00092038 | 5.9503e-07 | -2.6333e-07 | 0.0055737 | 0.0055739 | 0.0055739 | 0.98056 | -0.37361 | 0.98038 | -0.37701 | 1.5313
56 | 0.028037 | 0.0070409 | -0.028005 | -0.007021 | 3.1992e-05 | 1.99e-05 | 0.042885 | 0.042885 | 0.042885 | 0.97293 | -0.523 | 0.97172 | -0.54694 | 11.7817
57 | 0.018662 | 0.0046793 | -0.018655 | -0.0046755 | 6.3013e-06 | 3.7781e-06 | 0.028578 | 0.028578 | 0.028578 | 0.97172 | -0.54694 | 0.97136 | -0.55403 | 7.851
58 | 0.0068871 | 0.0017262 | -0.0068862 | -0.0017258 | 9.1693e-07 | 3.1495e-07 | 0.01055 | 0.01055 | 0.01055 | 0.97136 | -0.55403 | 0.97122 | -0.55682 | 2.8984
59 | -0.010294 | -0.00258 | 0.010296 | 0.0025809 | 1.6486e-06 | 8.1706e-07 | 0.015442 | 0.015442 | 0.015442 | 0.99196 | -0.154 | 0.99214 | -0.15064 | 4.2424
60 | -0.022048 | -0.0055267 | 0.022056 | 0.0055313 | 7.7137e-06 | 4.6937e-06 | 0.033068 | 0.033068 | 0.033068 | 0.99214 | -0.15064 | 0.99252 | -0.1433 | 9.0847
61 | 0.011752 | 0.0029458 | -0.01175 | -0.0029449 | 1.6488e-06 | 8.7249e-07 | 0.017626 | 0.017626 | 0.017626 | 0.99214 | -0.15064 | 0.99199 | -0.15359 | 4.8423
62 | 0.068863 | 0.017292 | -0.068804 | -0.017254 | 5.9347e-05 | 3.779e-05 | 0.10324 | 0.10324 | 0.10324 | 0.99261 | -0.14143 | 0.99168 | -0.15951 | 28.3638
63 | 0.020802 | 0.0052237 | -0.020787 | -0.0052152 | 1.4107e-05 | 8.5311e-06 | 0.031217 | 0.031217 | 0.031217 | 0.99168 | -0.15951 | 0.99094 | -0.17373 | 8.576
64 | -0.00329 | -0.00082455 | 0.0032901 | 0.00082446 | 1.192e-07 | -8.4199e-08 | 0.0049955 | 0.0049955 | 0.0049955 | 0.97998 | -0.38539 | 0.98002 | -0.38463 | 1.3724
65 | -0.0049989 | -0.0012527 | 0.0049996 | 0.0012528 | 6.3726e-07 | 3.6103e-08 | 0.0075901 | 0.0075899 | 0.0075901 | 0.98002 | -0.38463 | 0.98016 | -0.38195 | 2.0852
66 | -0.0071581 | -0.0017938 | 0.0071592 | 0.0017941 | 1.0452e-06 | 3.7138e-07 | 0.010867 | 0.010867 | 0.010867 | 0.98016 | -0.38195 | 0.98032 | -0.37889 | 2.9854
67 | -0.0088919 | -0.0022284 | 0.0088934 | 0.0022291 | 1.4468e-06 | 6.5887e-07 | 0.013497 | 0.013497 | 0.013497 | 0.98032 | -0.37889 | 0.98049 | -0.37547 | 3.708
68 | -0.28711 | -0.072948 | 0.28739 | 0.073128 | 0.00028318 | 0.00018039 | 0.43076 | 0.43076 | 0.43076 | 0.9926 | -0.1411 | 0.99367 | -0.12064 | 29.5852
69 | 0.008796 | 0.0022047 | -0.0087951 | -0.0022043 | 9.1416e-07 | 4.049e-07 | 0.013205 | 0.013205 | 0.013205 | 0.99117 | -0.16863 | 0.99106 | -0.17081 | 3.6278
70 | 0.014736 | 0.0036951 | -0.014733 | -0.0036937 | 2.3939e-06 | 1.3708e-06 | 0.022353 | 0.022353 | 0.022353 | 0.98098 | -0.3658 | 0.98081 | -0.36921 | 6.1409
71 | -0.036233 | -0.0090828 | 0.036246 | 0.009091 | 1.3022e-05 | 8.1891e-06 | 0.054961 | 0.054961 | 0.054961 | 0.98098 | -0.3658 | 0.98137 | -0.35826 | 15.0992
72 | 0.012791 | 0.0032068 | -0.012789 | -0.0032058 | 1.8607e-06 | 1.0246e-06 | 0.019405 | 0.019406 | 0.019406 | 0.98081 | -0.36921 | 0.98065 | -0.37226 | 5.3312
73 | -0.036246 | -0.009091 | 0.036265 | 0.0091027 | 1.867e-05 | 1.1741e-05 | 0.054961 | 0.054961 | 0.054961 | 0.98137 | -0.35826 | 0.98192 | -0.34746 | 15.0992
74 | 0.01065 | 0.0026697 | -0.010649 | -0.0026691 | 1.1836e-06 | 6.0504e-07 | 0.01616 | 0.01616 | 0.01616 | 0.98065 | -0.37226 | 0.98053 | -0.37459 | 4.4396
75 | -0.04281 | -0.010743 | 0.042825 | 0.010753 | 1.5191e-05 | 9.6007e-06 | 0.06488 | 0.06488 | 0.06488 | 0.98192 | -0.34746 | 0.9823 | -0.34002 | 17.8241
76 | 0.010649 | 0.0026691 | -0.010648 | -0.0026689 | 4.4558e-07 | 2.2778e-07 | 0.01616 | 0.01616 | 0.01616 | 0.98053 | -0.37459 | 0.98049 | -0.37547 | 4.4396
77 | -0.046938 | -0.011783 | 0.047002 | 0.011824 | 6.4211e-05 | 4.0666e-05 | 0.07111 | 0.07111 | 0.07111 | 0.9823 | -0.34002 | 0.98377 | -0.31138 | 19.5357
78 | 0.004113 | 0.0010307 | -0.0041128 | -0.0010308 | 2.4241e-07 | -5.5645e-08 | 0.0062305 | 0.0062305 | 0.0062305 | 0.9823 | -0.34002 | 0.98224 | -0.34126 | 1.7117

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50013 | 0.12722

## res_load
| p_mw | q_mvar
0 | 0.0012261 | 0.00030728
1 | 0.0019086 | 0.00047835
2 | 0.0037957 | 0.00095129
3 | 0.0029479 | 0.00073881
4 | 0.0030472 | 0.0007637
5 | 0.0013082 | 0.00032788
6 | 0.0010132 | 0.00025392
7 | 0.0032894 | 0.0008244
8 | 0.0031486 | 0.00078912
9 | 0.004328 | 0.0010847
10 | 0.020772 | 0.0052061
11 | 0.003091 | 0.00077468
12 | 0.003476 | 0.00087116
13 | 0.0032856 | 0.00082346
14 | 0.002241 | 0.00056164
15 | 0.0035038 | 0.00087813
16 | 0.0021662 | 0.0005429
17 | 0.016592 | 0.0041583
18 | 0.015926 | 0.0039913
19 | 0.0063315 | 0.0015868
20 | 0.014464 | 0.0036251
21 | 0.00099563 | 0.00024953
22 | 0.013442 | 0.0033689
23 | 0.0091648 | 0.0022969
24 | 0.0057219 | 0.001434
25 | 0.0095104 | 0.0023835
26 | 0.01029 | 0.002579
27 | 0.0096336 | 0.0024144
28 | 0.0041246 | 0.0010337
29 | 0.010294 | 0.00258
30 | 0.0070835 | 0.0017753
31 | 0.01267 | 0.0031755
32 | 0.0036724 | 0.00092038
33 | 0.0093435 | 0.0023417
34 | 0.011768 | 0.0029494
35 | 0.0068862 | 0.0017258
36 | 0.010294 | 0.00258
37 | 0.039856 | 0.0099889
38 | 0.01175 | 0.0029449
39 | 0.01091 | 0.0027343
40 | 0.048002 | 0.01203
41 | 0.0037374 | 0.00093669
42 | 0.00329 | 0.00082455
43 | 0.0017088 | 0.00042827
44 | 0.0021586 | 0.00054099
45 | 0.0017328 | 0.00043427
46 | 0.001558 | 0.00039048
47 | 0.011621 | 0.0029126
48 | 0.0080232 | 0.0020108
49 | 0.047752 | 0.011968
50 | 0.0087951 | 0.0022043
51 | 0.021497 | 0.0053877
52 | 0.0019428 | 0.0004869
53 | 0.0021389 | 0.00053606
54 | 0.006545 | 0.0016403
55 | 0.0017548 | 0.0004398
56 | 0.00086603 | 0.00021705
57 | 0.0041128 | 0.0010308

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1