## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1702-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1702-11_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1702-11_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1702-11_0_4_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_1702-11_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1702-11_0_4_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1702-11_0_4_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1702-11_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1702-11_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1702-11_0_4_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_1702-11_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1702-11_0_4_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_1702-11_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_1702-11_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1702-11_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_1702-11_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1702-11_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1702-11_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1702-11_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1702-11_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1702-11_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1702-11_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1702-11_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1702-11_0_4_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1702-11_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1702-11_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1702-11_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_MV_498_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1702-11_0_4_load_0 | 0 | 0.0038429 | 0.00096312 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1702-11_0_4_load_33 | 3 | 0.0046304 | 0.0011605 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1702-11_0_4_load_20 | 6 | 0.081444 | 0.020412 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1702-11_0_4_load_25 | 9 | 0.039918 | 0.010005 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1702-11_0_4_load_26 | 11 | 0.012318 | 0.0030873 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1702-11_0_4_load_29 | 14 | 0.062861 | 0.015754 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1702-11_0_4_load_28 | 15 | 0.014268 | 0.0035758 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1702-11_0_4_load_19 | 18 | 0.022139 | 0.0055486 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1702-11_0_4_load_22 | 19 | 0.065618 | 0.016446 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1702-11_0_4_load_30 | 22 | 0.035772 | 0.0089653 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1702-11_0_4_load_31 | 23 | 0.013911 | 0.0034865 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1702-11_0_4_load_21 | 24 | 0.097449 | 0.024423 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1702-11_0_4_load_27 | 25 | 0.0036048 | 0.00090345 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1702-11_0_4_line_0 |  | 0 | 1 | 0.039767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1702-11_0_4_line_1 |  | 1 | 2 | 0.073966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1702-11_0_4_line_2 |  | 2 | 3 | 0.015738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1702-11_0_4_line_3 |  | 3 | 10 | 0.019943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1702-11_0_4_line_4 |  | 4 | 5 | 0.062544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1702-11_0_4_line_5 |  | 4 | 6 | 0.056545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1702-11_0_4_line_6 |  | 5 | 20 | 0.005857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1702-11_0_4_line_7 |  | 5 | 21 | 0.095943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1702-11_0_4_line_8 |  | 5 | 9 | 0.04879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1702-11_0_4_line_9 |  | 6 | 24 | 0.042021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1702-11_0_4_line_10 |  | 7 | 8 | 0.054664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1702-11_0_4_line_11 |  | 7 | 9 | 0.05427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1702-11_0_4_line_12 |  | 8 | 10 | 0.080074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1702-11_0_4_line_13 |  | 8 | 11 | 0.029735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1702-11_0_4_line_14 |  | 10 | 12 | 0.075302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1702-11_0_4_line_15 |  | 11 | 25 | 0.038356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1702-11_0_4_line_16 |  | 12 | 23 | 0.019214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1702-11_0_4_line_17 |  | 13 | 14 | 0.036571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1702-11_0_4_line_18 |  | 13 | 15 | 0.025287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1702-11_0_4_line_19 |  | 15 | 20 | 0.013133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1702-11_0_4_line_20 |  | 16 | 17 | 0.030688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1702-11_0_4_line_21 |  | 16 | 18 | 0.017313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1702-11_0_4_line_22 |  | 17 | 19 | 0.02371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1702-11_0_4_line_23 |  | 19 | 26 | 0.014489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1702-11_0_4_line_24 |  | 20 | 26 | 0.024284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1702-11_0_4_line_25 |  | 21 | 22 | 0.017266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1702-11_0_4_trafo_23 | 0.63 MVA 20/0.4 kV | 27 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2677565.3117 | 1225853.2962 | 2677569.3513 | 1225841.174 | 2677569.7244 | 1225833.4848 | 2677567.4088 | 1225827.9398 | 2677559.7213 | 1225817.1079
1 | 2677539.4338 | 1225898.9896 | 2677549.7529 | 1225902.3596 | 2677556.8719 | 1225890.0997 | 2677565.6004 | 1225874.7587 | 2677563.6103 | 1225871.5751 | 2677554.1957 | 1225862.2017 | 2677565.3117 | 1225853.2962
2 | 2677539.4338 | 1225898.9896 | 2677530.3519 | 1225911.8426
3 | 2677518.8434 | 1225928.1298 | 2677530.3519 | 1225911.8426
4 | 2677487.1966 | 1226055.9144 | 2677475.99 | 1226051.4433 | 2677463.2685 | 1226043.3834 | 2677489.5941 | 1226019.688
5 | 2677489.5941 | 1226019.688 | 2677468.6453 | 1226025.7638 | 2677455.8037 | 1226039.7283 | 2677453.5325 | 1226038.3311 | 2677446.865 | 1226046.2163 | 2677444.7423 | 1226047.9934
6 | 2677489.6898 | 1226061.2171 | 2677487.1966 | 1226055.9144
7 | 2677415.6892 | 1226066.3353 | 2677416.6556 | 1226064.8914 | 2677424.3062 | 1226055.4401 | 2677433.6208 | 1226044.5318 | 2677440.7013 | 1226036.3628 | 2677446.0266 | 1226030.2614 | 2677463.2685 | 1226043.3834 | 2677475.99 | 1226051.4433 | 2677487.1966 | 1226055.9144
8 | 2677487.1966 | 1226055.9144 | 2677534.3136 | 1226043.2484
9 | 2677420.1498 | 1226081.8817 | 2677422.508 | 1226077.109 | 2677442.9026 | 1226049.5336 | 2677444.7423 | 1226047.9934
10 | 2677572.7012 | 1225981.9119 | 2677574.4735 | 1225984.3589 | 2677577.4199 | 1225985.1311 | 2677582.0437 | 1225991.5624 | 2677582.0903 | 1225995.5434 | 2677590.7434 | 1226008.0646 | 2677589.8155 | 1226012.9447 | 2677586.7233 | 1226029.1597
11 | 2677586.7233 | 1226029.1597 | 2677534.3136 | 1226043.2484
12 | 2677518.8434 | 1225928.1298 | 2677526.0449 | 1225933.9719 | 2677545.1506 | 1225948.3527 | 2677550.4339 | 1225951.8794 | 2677552.0647 | 1225952.9681 | 2677549.893 | 1225955.5748 | 2677557.7701 | 1225961.3369 | 2677572.7012 | 1225981.9119
13 | 2677572.7012 | 1225981.9119 | 2677570.1277 | 1225984.5134 | 2677549.3295 | 1226000.241
14 | 2677450.7121 | 1225896.8886 | 2677462.7478 | 1225899.4247 | 2677477.3194 | 1225905.1515 | 2677494.9575 | 1225913.4867 | 2677518.8434 | 1225928.1298
15 | 2677520.2409 | 1226009.3691 | 2677526.9391 | 1226017.1726 | 2677549.3295 | 1226000.241
16 | 2677450.7121 | 1225896.8886 | 2677452.9543 | 1225877.8061
17 | 2677526.6749 | 1226050.8139 | 2677529.2957 | 1226087.2907
18 | 2677526.6749 | 1226050.8139 | 2677502.3326 | 1226057.6609
19 | 2677489.6898 | 1226061.2171 | 2677502.3326 | 1226057.6609
20 | 2677460.0116 | 1226114.1885 | 2677460.6624 | 1226120.6791 | 2677484.4805 | 1226124.7585
21 | 2677484.4805 | 1226124.7585 | 2677484.3439 | 1226142.0712
22 | 2677460.0116 | 1226114.1885 | 2677462.0268 | 1226105.5533 | 2677465.2058 | 1226094.2872 | 2677466.4937 | 1226091.4267
23 | 2677472.4423 | 1226078.215 | 2677466.4937 | 1226091.4267
24 | 2677489.6898 | 1226061.2171 | 2677475.0539 | 1226074.4243 | 2677472.4423 | 1226078.215
25 | 2677415.6892 | 1226066.3353 | 2677414.831 | 1226067.625 | 2677411.0698 | 1226073.5356 | 2677406.8153 | 1226081.1365

## bus_geodata
| x | y | coords
0 | 2677559.7213 | 1225817.1079
1 | 2677565.3117 | 1225853.2962
2 | 2677539.4338 | 1225898.9896
3 | 2677530.3519 | 1225911.8426
4 | 2677489.5941 | 1226019.688
5 | 2677487.1966 | 1226055.9144
6 | 2677444.7423 | 1226047.9934
7 | 2677586.7233 | 1226029.1597
8 | 2677572.7012 | 1225981.9119
9 | 2677534.3136 | 1226043.2484
10 | 2677518.8434 | 1225928.1298
11 | 2677549.3295 | 1226000.241
12 | 2677450.7121 | 1225896.8886
13 | 2677526.6749 | 1226050.8139
14 | 2677529.2957 | 1226087.2907
15 | 2677502.3326 | 1226057.6609
16 | 2677484.4805 | 1226124.7585
17 | 2677460.0116 | 1226114.1885
18 | 2677484.3439 | 1226142.0712
19 | 2677466.4937 | 1226091.4267
20 | 2677489.6898 | 1226061.2171
21 | 2677415.6892 | 1226066.3353
22 | 2677406.8153 | 1226081.1365
23 | 2677452.9543 | 1225877.8061
24 | 2677420.1498 | 1226081.8817
25 | 2677520.2409 | 1226009.3691
26 | 2677472.4423 | 1226078.215
27 | 2677489.6898 | 1226061.2171

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98714 | -0.24753 | 0.0038429 | 0.00096312
1 | 0.98728 | -0.2448 | 0 | 0
2 | 0.98754 | -0.23972 | 0 | 0
3 | 0.9876 | -0.23863 | 0.0046304 | 0.0011605
4 | 0.9933 | -0.12804 | 0 | 0
5 | 0.99673 | -0.062381 | 0 | 0
6 | 0.98865 | -0.21781 | 0.081444 | 0.020412
7 | 0.99132 | -0.16641 | 0 | 0
8 | 0.9894 | -0.20363 | 0 | 0
9 | 0.99323 | -0.12959 | 0.039918 | 0.010005
10 | 0.98776 | -0.23561 | 0 | 0
11 | 0.98897 | -0.21207 | 0.012318 | 0.0030873
12 | 0.98679 | -0.25435 | 0 | 0
13 | 0.99488 | -0.098074 | 0 | 0
14 | 0.99278 | -0.13864 | 0.062861 | 0.015754
15 | 0.99633 | -0.070123 | 0.014268 | 0.0035758
16 | 0.99775 | -0.043252 | 0 | 0
17 | 0.99837 | -0.031364 | 0 | 0
18 | 0.9974 | -0.049965 | 0.022139 | 0.0055486
19 | 0.99885 | -0.022188 | 0.065618 | 0.016446
20 | 0.99725 | -0.052354 | 0 | 0
21 | 0.99359 | -0.12279 | 0 | 0
22 | 0.99303 | -0.1337 | 0.035772 | 0.0089653
23 | 0.98655 | -0.25913 | 0.013911 | 0.0034865
24 | 0.98488 | -0.29111 | 0.097449 | 0.024423
25 | 0.98884 | -0.21453 | 0.0036048 | 0.00090345
26 | 1 | 0 | -0.46316 | -0.1171
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0038429 | -0.00096312 | 0.0038434 | 0.00096293 | 5.004e-07 | -1.8821e-07 | 0.0057928 | 0.0057926 | 0.0057928 | 0.98714 | -0.24753 | 0.98728 | -0.2448 | 1.5914
1 | -0.0038434 | -0.00096293 | 0.0038443 | 0.00096258 | 9.3064e-07 | -3.5049e-07 | 0.0057926 | 0.0057923 | 0.0057926 | 0.98728 | -0.2448 | 0.98754 | -0.23972 | 1.5914
2 | -0.0038443 | -0.00096258 | 0.0038445 | 0.00096251 | 1.98e-07 | -7.4649e-08 | 0.0057923 | 0.0057922 | 0.0057923 | 0.98754 | -0.23972 | 0.9876 | -0.23863 | 1.5913
3 | -0.0084749 | -0.002123 | 0.0084761 | 0.0021235 | 1.2193e-06 | 5.2513e-07 | 0.012769 | 0.012769 | 0.012769 | 0.9876 | -0.23863 | 0.98776 | -0.23561 | 3.5079
4 | -0.18001 | -0.045546 | 0.18058 | 0.045907 | 0.00056915 | 0.00036182 | 0.26981 | 0.26981 | 0.26981 | 0.9933 | -0.12804 | 0.99673 | -0.062381 | 24.7082
5 | 0.18001 | 0.045546 | -0.17924 | -0.045053 | 0.00077183 | 0.00049251 | 0.26981 | 0.26981 | 0.26981 | 0.9933 | -0.12804 | 0.98865 | -0.21781 | 37.0624
6 | -0.29514 | -0.074834 | 0.29529 | 0.074925 | 0.00014234 | 9.0867e-05 | 0.44093 | 0.44093 | 0.44093 | 0.99673 | -0.062381 | 0.99725 | -0.052354 | 40.378
7 | 0.035894 | 0.0090419 | -0.035791 | -0.008977 | 0.00010338 | 6.4914e-05 | 0.053603 | 0.053603 | 0.053603 | 0.99673 | -0.062381 | 0.99359 | -0.12279 | 14.7261
8 | 0.078675 | 0.019885 | -0.078422 | -0.019724 | 0.00025266 | 0.00016107 | 0.11751 | 0.11751 | 0.11751 | 0.99673 | -0.062381 | 0.99323 | -0.12959 | 32.2837
9 | 0.097791 | 0.024641 | -0.097449 | -0.024423 | 0.00034159 | 0.00021808 | 0.14723 | 0.14723 | 0.14723 | 0.98865 | -0.21781 | 0.98488 | -0.29111 | 40.4485
10 | 0.038436 | 0.0096769 | -0.038367 | -0.0096339 | 6.8269e-05 | 4.2989e-05 | 0.057709 | 0.057709 | 0.057709 | 0.99132 | -0.16641 | 0.9894 | -0.20363 | 15.8542
11 | -0.038436 | -0.0096769 | 0.038503 | 0.0097196 | 6.7777e-05 | 4.2676e-05 | 0.057709 | 0.057709 | 0.057709 | 0.99132 | -0.16641 | 0.99323 | -0.12959 | 15.8541
12 | 0.022437 | 0.0056397 | -0.022403 | -0.0056188 | 3.4205e-05 | 2.0865e-05 | 0.033751 | 0.033751 | 0.033751 | 0.9894 | -0.20363 | 0.98776 | -0.23561 | 9.2723
13 | 0.01593 | 0.0039942 | -0.015924 | -0.0039905 | 6.4006e-06 | 3.7147e-06 | 0.023959 | 0.023959 | 0.023959 | 0.9894 | -0.20363 | 0.98897 | -0.21207 | 6.5821
14 | 0.013927 | 0.0034953 | -0.013915 | -0.0034883 | 1.2432e-05 | 6.9938e-06 | 0.020982 | 0.020983 | 0.020983 | 0.98776 | -0.23561 | 0.98679 | -0.25435 | 5.7645
15 | 0.0036052 | 0.00090323 | -0.0036048 | -0.00090345 | 4.2323e-07 | -2.2123e-07 | 0.0054244 | 0.0054245 | 0.0054245 | 0.98897 | -0.21207 | 0.98884 | -0.21453 | 1.4903
16 | 0.013915 | 0.0034883 | -0.013911 | -0.0034865 | 3.1723e-06 | 1.7849e-06 | 0.020983 | 0.020983 | 0.020983 | 0.98679 | -0.25435 | 0.98655 | -0.25913 | 5.7645
17 | 0.062983 | 0.015832 | -0.062861 | -0.015754 | 0.00012174 | 7.7441e-05 | 0.094219 | 0.094219 | 0.094219 | 0.99488 | -0.098074 | 0.99278 | -0.13864 | 25.8843
18 | -0.062983 | -0.015832 | 0.063067 | 0.015885 | 8.4178e-05 | 5.3545e-05 | 0.094219 | 0.094219 | 0.094219 | 0.99488 | -0.098074 | 0.99633 | -0.070123 | 25.8842
19 | -0.077335 | -0.019461 | 0.0774 | 0.019503 | 6.5732e-05 | 4.1897e-05 | 0.11553 | 0.11553 | 0.11553 | 0.99633 | -0.070123 | 0.99725 | -0.052354 | 31.7382
20 | -0.022146 | -0.0055529 | 0.022159 | 0.0055605 | 1.2554e-05 | 7.6336e-06 | 0.033029 | 0.033029 | 0.033029 | 0.99775 | -0.043252 | 0.99837 | -0.031364 | 9.0739
21 | 0.022146 | 0.0055529 | -0.022139 | -0.0055486 | 7.0827e-06 | 4.3069e-06 | 0.033029 | 0.033029 | 0.033029 | 0.99775 | -0.043252 | 0.9974 | -0.049965 | 9.0739
22 | -0.022159 | -0.0055605 | 0.022168 | 0.0055664 | 9.6996e-06 | 5.8975e-06 | 0.033029 | 0.033029 | 0.033029 | 0.99837 | -0.031364 | 0.99885 | -0.022188 | 9.0739
23 | -0.087787 | -0.022012 | 0.08788 | 0.022071 | 9.2934e-05 | 5.9288e-05 | 0.13078 | 0.13078 | 0.13078 | 0.99885 | -0.022188 | 1 | 0 | 35.9294
24 | -0.37269 | -0.094428 | 0.37363 | 0.095029 | 0.00093992 | 0.00060059 | 0.55645 | 0.55645 | 0.55645 | 0.99725 | -0.052354 | 1 | 0 | 50.9574
25 | 0.035791 | 0.008977 | -0.035772 | -0.0089653 | 1.8603e-05 | 1.1683e-05 | 0.053603 | 0.053603 | 0.053603 | 0.99359 | -0.12279 | 0.99303 | -0.1337 | 14.7261

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46316 | 0.1171

## res_load
| p_mw | q_mvar
0 | 0.0038429 | 0.00096312
1 | 0.0046304 | 0.0011605
2 | 0.081444 | 0.020412
3 | 0.039918 | 0.010005
4 | 0.012318 | 0.0030873
5 | 0.062861 | 0.015754
6 | 0.014268 | 0.0035758
7 | 0.022139 | 0.0055486
8 | 0.065618 | 0.016446
9 | 0.035772 | 0.0089653
10 | 0.013911 | 0.0034865
11 | 0.097449 | 0.024423
12 | 0.0036048 | 0.00090345

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1