## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1702-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1702-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1702-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1702-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1702-20_0_3_node_52 | 0.4 | n |  | TRUE
5 | bus_LV_1702-20_0_3_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_1702-20_0_3_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_1702-20_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1702-20_0_3_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_1702-20_0_3_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_1702-20_0_3_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_1702-20_0_3_node_86 | 0.4 | n |  | TRUE
12 | bus_LV_1702-20_0_3_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_1702-20_0_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1702-20_0_3_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_1702-20_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1702-20_0_3_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1702-20_0_3_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_1702-20_0_3_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_1702-20_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1702-20_0_3_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_1702-20_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1702-20_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1702-20_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1702-20_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1702-20_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1702-20_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1702-20_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1702-20_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1702-20_0_3_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1702-20_0_3_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_1702-20_0_3_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1702-20_0_3_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1702-20_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1702-20_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1702-20_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1702-20_0_3_node_61 | 0.4 | n |  | TRUE
37 | bus_LV_1702-20_0_3_node_59 | 0.4 | n |  | TRUE
38 | bus_LV_1702-20_0_3_node_16 | 0.4 | n |  | TRUE
39 | bus_LV_1702-20_0_3_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_1702-20_0_3_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_1702-20_0_3_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1702-20_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1702-20_0_3_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_1702-20_0_3_node_69 | 0.4 | n |  | TRUE
45 | bus_LV_1702-20_0_3_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_1702-20_0_3_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1702-20_0_3_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_1702-20_0_3_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_1702-20_0_3_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_1702-20_0_3_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_1702-20_0_3_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_1702-20_0_3_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_1702-20_0_3_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_1702-20_0_3_node_75 | 0.4 | n |  | TRUE
55 | bus_LV_1702-20_0_3_node_85 | 0.4 | n |  | TRUE
56 | bus_LV_1702-20_0_3_node_73 | 0.4 | n |  | TRUE
57 | bus_LV_1702-20_0_3_node_87 | 0.4 | n |  | TRUE
58 | bus_LV_1702-20_0_3_node_74 | 0.4 | n |  | TRUE
59 | bus_LV_1702-20_0_3_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_1702-20_0_3_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_1702-20_0_3_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1702-20_0_3_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_1702-20_0_3_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_1702-20_0_3_node_40 | 0.4 | n |  | TRUE
65 | bus_LV_1702-20_0_3_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_1702-20_0_3_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_1702-20_0_3_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1702-20_0_3_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_1702-20_0_3_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_1702-20_0_3_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1702-20_0_3_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1702-20_0_3_node_72 | 0.4 | n |  | TRUE
73 | bus_LV_1702-20_0_3_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_1702-20_0_3_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_1702-20_0_3_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_1702-20_0_3_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_1702-20_0_3_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_1702-20_0_3_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_1702-20_0_3_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_1702-20_0_3_node_78 | 0.4 | n |  | TRUE
81 | bus_LV_1702-20_0_3_node_80 | 0.4 | n |  | TRUE
82 | bus_LV_1702-20_0_3_node_83 | 0.4 | n |  | TRUE
83 | bus_MV_498_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1702-20_0_3_load_0 | 0 | 0.006768 | 0.0016962 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1702-20_0_3_load_1 | 1 | 0.0007148 | 0.00017915 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1702-20_0_3_load_51 | 5 | 0.0024089 | 0.00060372 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1702-20_0_3_load_48 | 8 | 0.0048868 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1702-20_0_3_load_47 | 9 | 0.00085247 | 0.00021365 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1702-20_0_3_load_50 | 10 | 0.00081144 | 0.00020337 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1702-20_0_3_load_86 | 11 | 0.0031027 | 0.00077761 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1702-20_0_3_load_46 | 12 | 0.0011224 | 0.00028129 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1702-20_0_3_load_49 | 13 | 0.0010784 | 0.00027028 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1702-20_0_3_load_5 | 14 | 0.0050298 | 0.0012606 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1702-20_0_3_load_6 | 15 | 0.0022224 | 0.00055698 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1702-20_0_3_load_7 | 16 | 0.0016935 | 0.00042443 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1702-20_0_3_load_42 | 17 | 0.0046661 | 0.0011694 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1702-20_0_3_load_43 | 18 | 0.005534 | 0.001387 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1702-20_0_3_load_44 | 20 | 0.00079496 | 0.00019924 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1702-20_0_3_load_9 | 21 | 0.00083306 | 0.00020878 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1702-20_0_3_load_10 | 22 | 0.0097951 | 0.0024549 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1702-20_0_3_load_11 | 23 | 0.011288 | 0.0028291 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1702-20_0_3_load_14 | 26 | 0.010366 | 0.0025981 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1702-20_0_3_load_15 | 27 | 0.0099099 | 0.0024837 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1702-20_0_3_load_22 | 32 | 0.02005 | 0.005025 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1702-20_0_3_load_32 | 34 | 0.010184 | 0.0025523 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1702-20_0_3_load_34 | 35 | 0.0091197 | 0.0022856 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1702-20_0_3_load_61 | 36 | 0.011277 | 0.0028262 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1702-20_0_3_load_59 | 37 | 0.0045421 | 0.0011384 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1702-20_0_3_load_16 | 38 | 0.0029573 | 0.00074117 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1702-20_0_3_load_17 | 39 | 0.003343 | 0.00083784 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1702-20_0_3_load_45 | 43 | 0.0056452 | 0.0014148 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1702-20_0_3_load_69 | 44 | 0.0035403 | 0.00088729 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1702-20_0_3_load_36 | 47 | 0.016572 | 0.0041534 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1702-20_0_3_load_77 | 52 | 0.0035299 | 0.00088469 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1702-20_0_3_load_88 | 53 | 0.012248 | 0.0030697 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1702-20_0_3_load_85 | 55 | 0.020925 | 0.0052442 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1702-20_0_3_load_87 | 57 | 0.019577 | 0.0049063 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1702-20_0_3_load_76 | 60 | 0.0043147 | 0.0010814 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1702-20_0_3_load_56 | 61 | 0.0049285 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1702-20_0_3_load_39 | 63 | 0.00087916 | 0.00022034 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1702-20_0_3_load_37 | 65 | 0.011708 | 0.0029344 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1702-20_0_3_load_41 | 66 | 0.0026071 | 0.0006534 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1702-20_0_3_load_53 | 67 | 0.003445 | 0.0008634 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1702-20_0_3_load_54 | 68 | 0.0034455 | 0.00086353 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1702-20_0_3_load_58 | 70 | 0.0048013 | 0.0012033 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1702-20_0_3_load_57 | 71 | 0.0030425 | 0.00076252 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1702-20_0_3_load_66 | 73 | 0.0028233 | 0.00070757 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1702-20_0_3_load_63 | 75 | 0.003535 | 0.00088597 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1702-20_0_3_load_64 | 76 | 0.0035322 | 0.00088524 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1702-20_0_3_load_67 | 78 | 0.0035424 | 0.0008878 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1702-20_0_3_load_68 | 79 | 0.0035315 | 0.00088508 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1702-20_0_3_load_78 | 80 | 0.002472 | 0.00061953 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1702-20_0_3_load_83 | 82 | 0.028151 | 0.0070553 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1702-20_0_3_line_0 |  | 0 | 1 | 0.0063495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1702-20_0_3_line_1 |  | 0 | 2 | 0.056481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1702-20_0_3_line_2 |  | 1 | 3 | 0.030346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1702-20_0_3_line_3 |  | 2 | 4 | 0.063268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1702-20_0_3_line_4 |  | 3 | 6 | 0.021606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1702-20_0_3_line_5 |  | 4 | 5 | 0.11883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1702-20_0_3_line_6 |  | 5 | 46 | 0.0061591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1702-20_0_3_line_7 |  | 6 | 11 | 0.023764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1702-20_0_3_line_8 |  | 7 | 8 | 0.041667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1702-20_0_3_line_9 |  | 7 | 9 | 0.0012917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1702-20_0_3_line_10 |  | 7 | 10 | 0.06045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1702-20_0_3_line_11 |  | 10 | 12 | 0.020637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1702-20_0_3_line_12 |  | 10 | 13 | 0.012735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1702-20_0_3_line_13 |  | 12 | 41 | 0.015675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1702-20_0_3_line_14 |  | 13 | 66 | 0.0044211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1702-20_0_3_line_15 |  | 14 | 15 | 0.023223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1702-20_0_3_line_16 |  | 15 | 16 | 0.0041006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1702-20_0_3_line_17 |  | 16 | 19 | 0.044463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1702-20_0_3_line_18 |  | 17 | 18 | 0.048809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1702-20_0_3_line_19 |  | 18 | 20 | 0.01553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1702-20_0_3_line_20 |  | 18 | 19 | 0.058019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1702-20_0_3_line_21 |  | 19 | 21 | 0.012392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1702-20_0_3_line_22 |  | 20 | 43 | 0.0083586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1702-20_0_3_line_23 |  | 22 | 23 | 0.0142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1702-20_0_3_line_24 |  | 22 | 24 | 0.018671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1702-20_0_3_line_25 |  | 23 | 25 | 0.028681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1702-20_0_3_line_26 |  | 24 | 26 | 0.01521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1702-20_0_3_line_27 |  | 24 | 27 | 0.020401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1702-20_0_3_line_28 |  | 25 | 28 | 0.01848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1702-20_0_3_line_29 |  | 26 | 29 | 0.020126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1702-20_0_3_line_30 |  | 27 | 30 | 0.024109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1702-20_0_3_line_31 |  | 28 | 34 | 0.011669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1702-20_0_3_line_32 |  | 29 | 35 | 0.01201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1702-20_0_3_line_33 |  | 30 | 36 | 0.017866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1702-20_0_3_line_34 |  | 30 | 37 | 0.024675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1702-20_0_3_line_35 |  | 31 | 32 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1702-20_0_3_line_36 |  | 31 | 33 | 0.016248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1702-20_0_3_line_37 |  | 32 | 48 | 0.027061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1702-20_0_3_line_38 |  | 33 | 41 | 0.005464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1702-20_0_3_line_39 |  | 35 | 58 | 0.018334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1702-20_0_3_line_40 |  | 37 | 71 | 0.018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1702-20_0_3_line_41 |  | 38 | 39 | 0.02665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1702-20_0_3_line_42 |  | 39 | 40 | 0.0202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1702-20_0_3_line_43 |  | 40 | 42 | 0.051309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1702-20_0_3_line_44 |  | 41 | 43 | 0.019275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1702-20_0_3_line_45 |  | 42 | 44 | 0.019638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1702-20_0_3_line_46 |  | 44 | 62 | 0.024854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1702-20_0_3_line_47 |  | 45 | 46 | 0.040223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1702-20_0_3_line_48 |  | 45 | 47 | 0.020507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1702-20_0_3_line_49 |  | 46 | 64 | 0.006502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1702-20_0_3_line_50 |  | 47 | 65 | 0.0052462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1702-20_0_3_line_51 |  | 48 | 49 | 0.026978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1702-20_0_3_line_52 |  | 48 | 50 | 0.019098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1702-20_0_3_line_53 |  | 49 | 51 | 0.005833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1702-20_0_3_line_54 |  | 49 | 52 | 0.013782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1702-20_0_3_line_55 |  | 50 | 53 | 0.022994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1702-20_0_3_line_56 |  | 50 | 54 | 0.013299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1702-20_0_3_line_57 |  | 51 | 55 | 0.039594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1702-20_0_3_line_58 |  | 52 | 56 | 0.01754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1702-20_0_3_line_59 |  | 54 | 57 | 0.036368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1702-20_0_3_line_60 |  | 54 | 58 | 0.011531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1702-20_0_3_line_61 |  | 56 | 80 | 0.027955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1702-20_0_3_line_62 |  | 56 | 72 | 0.010939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1702-20_0_3_line_63 |  | 59 | 60 | 0.038393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1702-20_0_3_line_64 |  | 59 | 61 | 0.01893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1702-20_0_3_line_65 |  | 60 | 74 | 0.038569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1702-20_0_3_line_66 |  | 61 | 68 | 0.00068634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1702-20_0_3_line_67 |  | 62 | 78 | 0.011492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1702-20_0_3_line_68 |  | 63 | 64 | 0.013788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1702-20_0_3_line_69 |  | 64 | 66 | 0.013803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1702-20_0_3_line_70 |  | 67 | 68 | 0.0017857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1702-20_0_3_line_71 |  | 67 | 69 | 0.013042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1702-20_0_3_line_72 |  | 69 | 70 | 0.012435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1702-20_0_3_line_73 |  | 70 | 72 | 0.013569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1702-20_0_3_line_74 |  | 72 | 73 | 0.011782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1702-20_0_3_line_75 |  | 73 | 76 | 0.002294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1702-20_0_3_line_76 |  | 74 | 81 | 0.008052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1702-20_0_3_line_77 |  | 75 | 76 | 0.010533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1702-20_0_3_line_78 |  | 75 | 77 | 0.0036736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1702-20_0_3_line_79 |  | 77 | 78 | 0.017498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1702-20_0_3_line_80 |  | 77 | 79 | 0.011962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1702-20_0_3_line_81 |  | 81 | 82 | 0.018845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1702-20_0_3_trafo_23 | 0.63 MVA 20/0.4 kV | 83 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2678044.3741 | 1226003.3507 | 2678045.1466 | 1226002.3238 | 2678047.5024 | 1225997.8406
1 | 2677997.8642 | 1226034.8036 | 2678034.2982 | 1226012.7552 | 2678038.4599 | 1226009.8745 | 2678042.1068 | 1226006.3644 | 2678044.3741 | 1226003.3507
2 | 2678045.1857 | 1225968.724 | 2678047.5301 | 1225973.2022 | 2678049.1272 | 1225978.0041 | 2678049.9334 | 1225983.007 | 2678049.9278 | 1225988.0547 | 2678049.1118 | 1225993.0474 | 2678047.5024 | 1225997.8406
3 | 2677968.6102 | 1226090.9024 | 2677997.8642 | 1226034.8036
4 | 2678045.1857 | 1225968.724 | 2678057.698 | 1225951.0874
5 | 2677968.6102 | 1226090.9024 | 2677979.5485 | 1226093.8365 | 2678030.5034 | 1226119.9997 | 2678038.6795 | 1226124.8768 | 2678044.0913 | 1226133.598 | 2678054.3891 | 1226156.4484 | 2678057.7551 | 1226160.6447
6 | 2678061.6089 | 1226165.4491 | 2678057.7551 | 1226160.6447
7 | 2678057.698 | 1225951.0874 | 2678061.585 | 1225959.3216 | 2678063.9864 | 1225964.0786 | 2678066.4119 | 1225966.9901 | 2678068.7792 | 1225968.5666 | 2678071.4321 | 1225969.1685
8 | 2678120.8694 | 1226134.5948 | 2678136.9299 | 1226096.1354
9 | 2678120.8694 | 1226134.5948 | 2678122.0392 | 1226135.1425
10 | 2678091.5758 | 1226187.4734 | 2678120.8694 | 1226134.5948
11 | 2678109.8702 | 1226197.017 | 2678099.883 | 1226192.0024 | 2678091.5758 | 1226187.4734
12 | 2678080.3949 | 1226181.3778 | 2678091.5758 | 1226187.4734
13 | 2678117.7472 | 1226207.2471 | 2678118.5972 | 1226201.3987 | 2678109.8702 | 1226197.017
14 | 2678076.7271 | 1226178.9322 | 2678078.7558 | 1226180.4841 | 2678080.3949 | 1226181.3778
15 | 2678233.6293 | 1226135.1661 | 2678212.6885 | 1226125.1277
16 | 2678212.6885 | 1226125.1277 | 2678212.6885 | 1226125.1277 | 2678208.9813 | 1226126.8801 | 2678208.9813 | 1226126.8801
17 | 2678189.3177 | 1226166.6374 | 2678203.5458 | 1226134.9697 | 2678208.9813 | 1226126.8801
18 | 2678206.1903 | 1226231.914 | 2678179.1209 | 1226222.074 | 2678159.87 | 1226216.6278
19 | 2678144.7878 | 1226212.9392 | 2678156.4109 | 1226215.6492 | 2678159.87 | 1226216.6278
20 | 2678159.87 | 1226216.6278 | 2678189.3177 | 1226166.6374
21 | 2678189.3177 | 1226166.6374 | 2678178.0943 | 1226161.3834
22 | 2678144.7878 | 1226212.9392 | 2678144.7878 | 1226212.9392 | 2678136.6077 | 1226211.221
23 | 2678187.8574 | 1226326.1587 | 2678183.393 | 1226324.977 | 2678174.2076 | 1226322.2507
24 | 2678156.308 | 1226316.9381 | 2678174.2076 | 1226322.2507
25 | 2678206.9954 | 1226305.007 | 2678195.3099 | 1226315.7051 | 2678187.8574 | 1226326.1587 | 2678187.8574 | 1226326.1587
26 | 2678156.308 | 1226316.9381 | 2678160.6905 | 1226303.0085 | 2678160.9519 | 1226302.4599
27 | 2678156.308 | 1226316.9381 | 2678145.5463 | 1226333.4857 | 2678145.2682 | 1226334.0864
28 | 2678206.9954 | 1226305.007 | 2678214.1088 | 1226300.1639 | 2678217.86 | 1226291.0293
29 | 2678169.6085 | 1226284.2908 | 2678160.9519 | 1226302.4599
30 | 2678135.1389 | 1226355.9641 | 2678145.2682 | 1226334.0864
31 | 2678217.86 | 1226291.0293 | 2678207.9539 | 1226288.6086 | 2678206.4839 | 1226288.6657
32 | 2678169.6085 | 1226284.2908 | 2678173.0118 | 1226272.7722
33 | 2678135.1389 | 1226355.9641 | 2678151.2775 | 1226363.6288
34 | 2678135.1389 | 1226355.9641 | 2678112.5718 | 1226345.9854
35 | 2678129.8752 | 1226217.6911 | 2678127.4287 | 1226228.4995 | 2678125.778 | 1226237.5951 | 2678123.8426 | 1226245.1833
36 | 2678129.8752 | 1226217.6911 | 2678130.4339 | 1226215.5525 | 2678116.6686 | 1226212.6032
37 | 2678117.1547 | 1226271.4046 | 2678123.8426 | 1226245.1833
38 | 2678117.7472 | 1226207.2471 | 2678116.6686 | 1226212.6032
39 | 2678154.7654 | 1226270.4977 | 2678173.0118 | 1226272.7722
40 | 2678112.5718 | 1226345.9854 | 2678108.3691 | 1226344.127 | 2678095.0524 | 1226339.1442
41 | 2678035.0203 | 1226198.5104 | 2678043.2307 | 1226199.1863 | 2678060.9751 | 1226201.6095 | 2678061.4661 | 1226201.7157
42 | 2678019.3002 | 1226207.1891 | 2678020.2775 | 1226204.3444 | 2678022.1906 | 1226201.8234 | 2678024.57 | 1226199.5753 | 2678027.9925 | 1226198.1414 | 2678030.5395 | 1226198.1415 | 2678035.0203 | 1226198.5104
43 | 2678019.3002 | 1226207.1891 | 2678017.5064 | 1226216.2272 | 2678015.1195 | 1226234.0746 | 2678014.3195 | 1226240.7352 | 2678013.7845 | 1226244.5419 | 2678018.5543 | 1226245.5606 | 2678026.9564 | 1226247.6499
44 | 2678117.7472 | 1226207.2471 | 2678130.9537 | 1226210.0334 | 2678136.6077 | 1226211.221
45 | 2678026.9564 | 1226247.6499 | 2678046.1739 | 1226251.6928
46 | 2678065.8702 | 1226260.669 | 2678065.7369 | 1226255.8084 | 2678046.1739 | 1226251.6928
47 | 2678022.0916 | 1226157.3589 | 2678038.559 | 1226160.6325 | 2678061.6089 | 1226165.4491
48 | 2678022.0916 | 1226157.3589 | 2678001.9991 | 1226153.2587
49 | 2678061.6089 | 1226165.4491 | 2678066.1414 | 1226170.1228
50 | 2678001.9991 | 1226153.2587 | 2677996.8588 | 1226152.2097
51 | 2678117.1547 | 1226271.4046 | 2678098.9533 | 1226268.0079 | 2678090.5759 | 1226266.3524
52 | 2678136.0034 | 1226274.5764 | 2678124.8549 | 1226272.095 | 2678117.1547 | 1226271.4046
53 | 2678085.1073 | 1226264.2793 | 2678090.5759 | 1226266.3524
54 | 2678090.5759 | 1226266.3524 | 2678086.9392 | 1226279.646
55 | 2678136.0034 | 1226274.5764 | 2678130.1737 | 1226293.646 | 2678127.2125 | 1226292.8621
56 | 2678136.0034 | 1226274.5764 | 2678149.067 | 1226277.2608
57 | 2678085.1073 | 1226264.2793 | 2678093.3811 | 1226231.0989 | 2678089.3194 | 1226227.5321
58 | 2678082.3108 | 1226296.5643 | 2678086.9392 | 1226279.646
59 | 2678149.067 | 1226277.2608 | 2678155.9578 | 1226246.097 | 2678151.6762 | 1226244.8399
60 | 2678149.067 | 1226277.2608 | 2678152.4662 | 1226278.1727 | 2678154.7654 | 1226270.4977
61 | 2678082.3108 | 1226296.5643 | 2678086.5972 | 1226297.4544 | 2678092.2481 | 1226301.8093 | 2678095.012 | 1226306.6488 | 2678095.6386 | 1226313.7729 | 2678095.9296 | 1226317.4796
62 | 2678078.3876 | 1226306.6974 | 2678080.6067 | 1226299.3438 | 2678082.3108 | 1226296.5643
63 | 2678049.071 | 1226358.948 | 2678054.7821 | 1226363.3258 | 2678076.6189 | 1226376.7657 | 2678080.2445 | 1226380.975
64 | 2678049.071 | 1226358.948 | 2678060.0426 | 1226343.5222
65 | 2678109.7306 | 1226402.6509 | 2678091.6512 | 1226396.3427 | 2678086.5186 | 1226391.7834 | 2678081.9947 | 1226383.0071 | 2678080.2445 | 1226380.975
66 | 2678060.0426 | 1226343.5222 | 2678060.4404 | 1226342.9629
67 | 2678065.8702 | 1226260.669 | 2678063.0496 | 1226271.8092
68 | 2678066.1414 | 1226170.1228 | 2678063.2813 | 1226183.6111
69 | 2678066.1414 | 1226170.1228 | 2678068.7739 | 1226172.8481 | 2678076.7271 | 1226178.9322
70 | 2678061.4754 | 1226341.5077 | 2678060.4404 | 1226342.9629
71 | 2678069.0345 | 1226330.8798 | 2678061.4754 | 1226341.5077
72 | 2678069.0345 | 1226330.8798 | 2678071.9376 | 1226325.6922 | 2678074.0246 | 1226319.5462
73 | 2678078.3876 | 1226306.6974 | 2678074.0246 | 1226319.5462
74 | 2678078.3876 | 1226306.6974 | 2678076.5808 | 1226305.7508 | 2678068.7181 | 1226299.9987
75 | 2678066.8667 | 1226298.6443 | 2678068.7181 | 1226299.9987
76 | 2678116.964 | 1226400.7779 | 2678112.3828 | 1226400.4064 | 2678109.7306 | 1226402.6509
77 | 2678058.3657 | 1226292.4252 | 2678066.8667 | 1226298.6443
78 | 2678058.7548 | 1226288.7723 | 2678058.3657 | 1226292.4252 | 2678058.3657 | 1226292.4252
79 | 2678058.7548 | 1226288.7723 | 2678063.0496 | 1226271.8092
80 | 2678048.419 | 1226282.6993 | 2678058.7548 | 1226288.7723
81 | 2678116.964 | 1226400.7779 | 2678125.3909 | 1226400.3771 | 2678135.7883 | 1226399.8999

## bus_geodata
| x | y | coords
0 | 2678044.3741 | 1226003.3507
1 | 2678047.5024 | 1225997.8406
2 | 2677997.8642 | 1226034.8036
3 | 2678045.1857 | 1225968.724
4 | 2677968.6102 | 1226090.9024
5 | 2678057.7551 | 1226160.6447
6 | 2678057.698 | 1225951.0874
7 | 2678120.8694 | 1226134.5948
8 | 2678136.9299 | 1226096.1354
9 | 2678122.0392 | 1226135.1425
10 | 2678091.5758 | 1226187.4734
11 | 2678071.4321 | 1225969.1685
12 | 2678109.8702 | 1226197.017
13 | 2678080.3949 | 1226181.3778
14 | 2678233.6293 | 1226135.1661
15 | 2678212.6885 | 1226125.1277
16 | 2678208.9813 | 1226126.8801
17 | 2678206.1903 | 1226231.914
18 | 2678159.87 | 1226216.6278
19 | 2678189.3177 | 1226166.6374
20 | 2678144.7877 | 1226212.9392
21 | 2678178.0943 | 1226161.3834
22 | 2678174.2076 | 1226322.2507
23 | 2678187.8574 | 1226326.1587
24 | 2678156.308 | 1226316.9381
25 | 2678206.9954 | 1226305.007
26 | 2678160.9519 | 1226302.4599
27 | 2678145.2682 | 1226334.0864
28 | 2678217.86 | 1226291.0293
29 | 2678169.6085 | 1226284.2908
30 | 2678135.1389 | 1226355.9641
31 | 2678129.8752 | 1226217.6911
32 | 2678123.8426 | 1226245.1833
33 | 2678116.6686 | 1226212.6032
34 | 2678206.4839 | 1226288.6657
35 | 2678173.0118 | 1226272.7722
36 | 2678151.2775 | 1226363.6288
37 | 2678112.5718 | 1226345.9854
38 | 2678061.4661 | 1226201.7157
39 | 2678035.0203 | 1226198.5104
40 | 2678019.3002 | 1226207.1891
41 | 2678117.7472 | 1226207.2471
42 | 2678026.9564 | 1226247.6499
43 | 2678136.6077 | 1226211.221
44 | 2678046.1739 | 1226251.6928
45 | 2678022.0916 | 1226157.3589
46 | 2678061.6089 | 1226165.4491
47 | 2678001.9991 | 1226153.2587
48 | 2678117.1547 | 1226271.4046
49 | 2678090.5759 | 1226266.3524
50 | 2678136.0034 | 1226274.5764
51 | 2678085.1073 | 1226264.2793
52 | 2678086.9392 | 1226279.646
53 | 2678127.2125 | 1226292.8621
54 | 2678149.067 | 1226277.2608
55 | 2678089.3194 | 1226227.5321
56 | 2678082.3108 | 1226296.5643
57 | 2678151.6762 | 1226244.8399
58 | 2678154.7654 | 1226270.4977
59 | 2678049.071 | 1226358.948
60 | 2678080.2445 | 1226380.975
61 | 2678060.0426 | 1226343.5222
62 | 2678065.8702 | 1226260.669
63 | 2678063.2813 | 1226183.6111
64 | 2678066.1414 | 1226170.1228
65 | 2677996.8588 | 1226152.2097
66 | 2678076.7271 | 1226178.9322
67 | 2678061.4754 | 1226341.5077
68 | 2678060.4404 | 1226342.9629
69 | 2678069.0345 | 1226330.8798
70 | 2678074.0246 | 1226319.5462
71 | 2678095.0524 | 1226339.1442
72 | 2678078.3876 | 1226306.6974
73 | 2678068.7181 | 1226299.9987
74 | 2678109.7306 | 1226402.6509
75 | 2678058.3657 | 1226292.4252
76 | 2678066.8667 | 1226298.6443
77 | 2678058.7548 | 1226288.7723
78 | 2678063.0496 | 1226271.8092
79 | 2678048.419 | 1226282.6993
80 | 2678095.9296 | 1226317.4796
81 | 2678116.964 | 1226400.7779
82 | 2678135.7883 | 1226399.8999
83 | 2678136.0034 | 1226274.5764

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98823 | -0.22671 | 0.006768 | 0.0016962
1 | 0.98821 | -0.22714 | 0.0007148 | 0.00017915
2 | 0.98878 | -0.21604 | 0 | 0
3 | 0.98812 | -0.22882 | 0 | 0
4 | 0.98939 | -0.2041 | 0 | 0
5 | 0.99055 | -0.18171 | 0.0024089 | 0.00060372
6 | 0.98806 | -0.23002 | 0 | 0
7 | 0.9918 | -0.15749 | 0 | 0
8 | 0.99161 | -0.1611 | 0.0048868 | 0.0012248
9 | 0.9918 | -0.15751 | 0.00085247 | 0.00021365
10 | 0.99212 | -0.15134 | 0.00081144 | 0.00020337
11 | 0.98799 | -0.23133 | 0.0031027 | 0.00077761
12 | 0.99311 | -0.13221 | 0.0011224 | 0.00028129
13 | 0.99158 | -0.16168 | 0.0010784 | 0.00027028
14 | 0.99195 | -0.15461 | 0.0050298 | 0.0012606
15 | 0.99206 | -0.15254 | 0.0022224 | 0.00055698
16 | 0.99209 | -0.15201 | 0.0016935 | 0.00042443
17 | 0.99276 | -0.13896 | 0.0046661 | 0.0011694
18 | 0.99297 | -0.13493 | 0.005534 | 0.001387
19 | 0.99245 | -0.14497 | 0 | 0
20 | 0.99325 | -0.12945 | 0.00079496 | 0.00019924
21 | 0.99244 | -0.14515 | 0.00083306 | 0.00020878
22 | 0.99124 | -0.16845 | 0.0097951 | 0.0024549
23 | 0.99096 | -0.17386 | 0.011288 | 0.0028291
24 | 0.99177 | -0.1581 | 0 | 0
25 | 0.99069 | -0.17905 | 0 | 0
26 | 0.99261 | -0.14193 | 0.010366 | 0.0025981
27 | 0.99124 | -0.16851 | 0.0099099 | 0.0024837
28 | 0.99052 | -0.18239 | 0 | 0
29 | 0.99391 | -0.11689 | 0 | 0
30 | 0.99082 | -0.17658 | 0 | 0
31 | 0.99546 | -0.086805 | 0 | 0
32 | 0.99753 | -0.047287 | 0.02005 | 0.005025
33 | 0.99428 | -0.10968 | 0 | 0
34 | 0.99041 | -0.1845 | 0.010184 | 0.0025523
35 | 0.99468 | -0.10198 | 0.0091197 | 0.0022856
36 | 0.99064 | -0.18015 | 0.011277 | 0.0028262
37 | 0.99065 | -0.1799 | 0.0045421 | 0.0011384
38 | 0.99269 | -0.1405 | 0.0029573 | 0.00074117
39 | 0.99276 | -0.1391 | 0.003343 | 0.00083784
40 | 0.99288 | -0.13685 | 0 | 0
41 | 0.99388 | -0.11739 | 0 | 0
42 | 0.99317 | -0.13114 | 0 | 0
43 | 0.99341 | -0.12638 | 0.0056452 | 0.0014148
44 | 0.99329 | -0.12895 | 0.0035403 | 0.00088729
45 | 0.98958 | -0.20051 | 0 | 0
46 | 0.99062 | -0.18029 | 0 | 0
47 | 0.98905 | -0.21084 | 0.016572 | 0.0041534
48 | 1 | 0 | -0.31793 | -0.080071
49 | 0.99747 | -0.048477 | 0 | 0
50 | 0.99806 | -0.037141 | 0 | 0
51 | 0.99735 | -0.050615 | 0 | 0
52 | 0.99643 | -0.068272 | 0.0035299 | 0.00088469
53 | 0.9978 | -0.04207 | 0.012248 | 0.0030697
54 | 0.99685 | -0.060231 | 0 | 0
55 | 0.9966 | -0.065143 | 0.020925 | 0.0052442
56 | 0.99518 | -0.092435 | 0 | 0
57 | 0.9962 | -0.072727 | 0.019577 | 0.0049063
58 | 0.99601 | -0.076331 | 0 | 0
59 | 0.99212 | -0.15136 | 0 | 0
60 | 0.99098 | -0.17346 | 0.0043147 | 0.0010814
61 | 0.99268 | -0.14048 | 0.0049285 | 0.0012352
62 | 0.99351 | -0.12463 | 0 | 0
63 | 0.99085 | -0.17574 | 0.00087916 | 0.00022034
64 | 0.99087 | -0.17552 | 0 | 0
65 | 0.98899 | -0.21194 | 0.011708 | 0.0029344
66 | 0.9914 | -0.16519 | 0.0026071 | 0.0006534
67 | 0.99278 | -0.13874 | 0.003445 | 0.0008634
68 | 0.99271 | -0.14003 | 0.0034455 | 0.00086353
69 | 0.9933 | -0.12853 | 0 | 0
70 | 0.99381 | -0.11881 | 0.0048013 | 0.0012033
71 | 0.9906 | -0.18092 | 0.0030425 | 0.00076252
72 | 0.99442 | -0.10706 | 0 | 0
73 | 0.99413 | -0.11263 | 0.0028233 | 0.00070757
74 | 0.98998 | -0.19275 | 0 | 0
75 | 0.99388 | -0.1174 | 0.003535 | 0.00088597
76 | 0.99408 | -0.1136 | 0.0035322 | 0.00088524
77 | 0.99383 | -0.1185 | 0 | 0
78 | 0.99361 | -0.12263 | 0.0035424 | 0.0008878
79 | 0.99379 | -0.11924 | 0.0035315 | 0.00088508
80 | 0.99511 | -0.093652 | 0.002472 | 0.00061953
81 | 0.98978 | -0.19678 | 0 | 0
82 | 0.98929 | -0.20623 | 0.028151 | 0.0070553
83 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038182 | 0.00095615 | -0.0038181 | -0.00095618 | 7.8695e-08 | -3.0985e-08 | 0.0057489 | 0.005749 | 0.005749 | 0.98823 | -0.22671 | 0.98821 | -0.22714 | 1.5794
1 | -0.010586 | -0.0026524 | 0.010592 | 0.0026551 | 5.3813e-06 | 2.72e-06 | 0.01594 | 0.015939 | 0.01594 | 0.98823 | -0.22671 | 0.98878 | -0.21604 | 4.379
2 | 0.0031033 | 0.00077704 | -0.0031031 | -0.00077727 | 2.4846e-07 | -2.2973e-07 | 0.0046726 | 0.0046728 | 0.0046728 | 0.98821 | -0.22714 | 0.98812 | -0.22882 | 1.2837
3 | -0.010592 | -0.0026551 | 0.010598 | 0.0026581 | 6.0278e-06 | 3.0458e-06 | 0.015939 | 0.015939 | 0.015939 | 0.98878 | -0.21604 | 0.98939 | -0.2041 | 4.379
4 | 0.0031031 | 0.00077727 | -0.0031029 | -0.00077743 | 1.7691e-07 | -1.6352e-07 | 0.0046728 | 0.0046729 | 0.0046729 | 0.98812 | -0.22882 | 0.98806 | -0.23002 | 1.2838
5 | -0.010598 | -0.0026581 | 0.010609 | 0.0026638 | 1.1321e-05 | 5.7175e-06 | 0.015939 | 0.015939 | 0.015939 | 0.98939 | -0.2041 | 0.99055 | -0.18171 | 4.3789
6 | -0.013018 | -0.0032676 | 0.013019 | 0.0032681 | 8.8342e-07 | 4.861e-07 | 0.019557 | 0.019557 | 0.019557 | 0.99055 | -0.18171 | 0.99062 | -0.18029 | 5.3729
7 | 0.0031029 | 0.00077743 | -0.0031027 | -0.00077761 | 1.9459e-07 | -1.7981e-07 | 0.0046729 | 0.004673 | 0.004673 | 0.98806 | -0.23002 | 0.98799 | -0.23133 | 1.2838
8 | 0.0048877 | 0.0012248 | -0.0048868 | -0.0012248 | 8.4023e-07 | 1.3439e-10 | 0.007333 | 0.0073332 | 0.0073332 | 0.9918 | -0.15749 | 0.99161 | -0.1611 | 2.0146
9 | 0.00085247 | 0.00021363 | -0.00085247 | -0.00021365 | 7.9229e-10 | -1.6162e-08 | 0.001279 | 0.001279 | 0.001279 | 0.9918 | -0.15749 | 0.9918 | -0.15751 | 0.35137
10 | -0.0057401 | -0.0014384 | 0.0057418 | 0.0014387 | 1.6812e-06 | 2.9561e-07 | 0.008612 | 0.0086117 | 0.008612 | 0.9918 | -0.15749 | 0.99212 | -0.15134 | 2.3659
11 | -0.052519 | -0.013206 | 0.052567 | 0.013236 | 4.8037e-05 | 3.0477e-05 | 0.078786 | 0.078786 | 0.078786 | 0.99212 | -0.15134 | 0.99311 | -0.13221 | 21.6445
12 | 0.045966 | 0.011564 | -0.045943 | -0.011549 | 2.2708e-05 | 1.4369e-05 | 0.068957 | 0.068957 | 0.068957 | 0.99212 | -0.15134 | 0.99158 | -0.16168 | 18.9444
13 | -0.05369 | -0.013518 | 0.053728 | 0.013542 | 3.8061e-05 | 2.4156e-05 | 0.080468 | 0.080468 | 0.080468 | 0.99311 | -0.13221 | 0.99388 | -0.11739 | 22.1065
14 | 0.044865 | 0.011279 | -0.044858 | -0.011274 | 7.5179e-06 | 4.7545e-06 | 0.067339 | 0.067339 | 0.067339 | 0.99158 | -0.16168 | 0.9914 | -0.16519 | 18.4998
15 | -0.0050298 | -0.0012606 | 0.0050303 | 0.0012606 | 4.9576e-07 | 1.7472e-08 | 0.0075451 | 0.007545 | 0.0075451 | 0.99195 | -0.15461 | 0.99206 | -0.15254 | 2.0728
16 | -0.0072527 | -0.0018176 | 0.0072528 | 0.0018176 | 1.8197e-07 | 6.3515e-08 | 0.010878 | 0.010878 | 0.010878 | 0.99206 | -0.15254 | 0.99209 | -0.15201 | 2.9886
17 | -0.0089463 | -0.0022421 | 0.0089493 | 0.0022434 | 3.0021e-06 | 1.347e-06 | 0.013418 | 0.013418 | 0.013418 | 0.99209 | -0.15201 | 0.99245 | -0.14497 | 3.6864
18 | -0.0046661 | -0.0011694 | 0.004667 | 0.0011694 | 8.9526e-07 | -5.8268e-08 | 0.0069938 | 0.0069936 | 0.0069938 | 0.99276 | -0.13896 | 0.99297 | -0.13493 | 1.9214
19 | -0.019988 | -0.0050106 | 0.019993 | 0.0050138 | 5.2251e-06 | 3.1431e-06 | 0.029954 | 0.029954 | 0.029954 | 0.99297 | -0.13493 | 0.99325 | -0.12945 | 8.229
20 | 0.0097871 | 0.0024543 | -0.0097824 | -0.002452 | 4.6805e-06 | 2.2454e-06 | 0.014667 | 0.014667 | 0.014667 | 0.99297 | -0.13493 | 0.99245 | -0.14497 | 4.0295
21 | 0.00083306 | 0.00020863 | -0.00083306 | -0.00020878 | 7.2497e-09 | -1.5549e-07 | 0.001249 | 0.001249 | 0.001249 | 0.99245 | -0.14497 | 0.99244 | -0.14515 | 0.34314
22 | -0.020788 | -0.005213 | 0.020791 | 0.0052148 | 3.0404e-06 | 1.8376e-06 | 0.031145 | 0.031144 | 0.031145 | 0.99325 | -0.12945 | 0.99341 | -0.12638 | 8.5562
23 | 0.021483 | 0.0053873 | -0.021477 | -0.0053839 | 5.5383e-06 | 3.3615e-06 | 0.03225 | 0.03225 | 0.03225 | 0.99124 | -0.16845 | 0.99096 | -0.17386 | 8.86
24 | -0.031278 | -0.0078422 | 0.031293 | 0.0078518 | 1.5437e-05 | 9.6388e-06 | 0.046954 | 0.046954 | 0.046954 | 0.99124 | -0.16845 | 0.99177 | -0.1581 | 12.8995
25 | 0.010189 | 0.0025549 | -0.010186 | -0.0025536 | 2.5178e-06 | 1.242e-06 | 0.0153 | 0.0153 | 0.0153 | 0.99096 | -0.17386 | 0.99069 | -0.17905 | 4.2034
26 | -0.060089 | -0.015077 | 0.060136 | 0.015107 | 4.6368e-05 | 2.9479e-05 | 0.090162 | 0.090162 | 0.090162 | 0.99177 | -0.1581 | 0.99261 | -0.14193 | 24.7697
27 | 0.028796 | 0.0072253 | -0.028782 | -0.0072164 | 1.4283e-05 | 8.8777e-06 | 0.043207 | 0.043208 | 0.043208 | 0.99177 | -0.1581 | 0.99124 | -0.16851 | 11.8702
28 | 0.010186 | 0.0025536 | -0.010185 | -0.0025528 | 1.6223e-06 | 8.0038e-07 | 0.0153 | 0.0153 | 0.0153 | 0.99069 | -0.17905 | 0.99052 | -0.18239 | 4.2034
29 | -0.070502 | -0.017705 | 0.070587 | 0.017758 | 8.4324e-05 | 5.3707e-05 | 0.1057 | 0.1057 | 0.1057 | 0.99261 | -0.14193 | 0.99391 | -0.11689 | 29.039
30 | 0.018872 | 0.0047328 | -0.018865 | -0.0047284 | 7.2566e-06 | 4.3336e-06 | 0.028331 | 0.028331 | 0.028331 | 0.99124 | -0.16851 | 0.99082 | -0.17658 | 7.7833
31 | 0.010185 | 0.0025528 | -0.010184 | -0.0025523 | 1.0244e-06 | 5.0541e-07 | 0.0153 | 0.0153 | 0.0153 | 0.99052 | -0.18239 | 0.99041 | -0.1845 | 4.2034
32 | -0.070587 | -0.017758 | 0.070637 | 0.01779 | 5.032e-05 | 3.2049e-05 | 0.1057 | 0.1057 | 0.1057 | 0.99391 | -0.11689 | 0.99468 | -0.10198 | 29.039
33 | 0.011279 | 0.0028272 | -0.011277 | -0.0028262 | 1.9223e-06 | 1.0002e-06 | 0.016939 | 0.016939 | 0.016939 | 0.99082 | -0.17658 | 0.99064 | -0.18015 | 4.6535
34 | 0.0075859 | 0.0019012 | -0.0075847 | -0.0019007 | 1.201e-06 | 4.5087e-07 | 0.011393 | 0.011393 | 0.011393 | 0.99082 | -0.17658 | 0.99065 | -0.1799 | 3.1299
35 | -0.080293 | -0.020253 | 0.080445 | 0.02035 | 0.00015222 | 9.7054e-05 | 0.12007 | 0.12007 | 0.12007 | 0.99546 | -0.086805 | 0.99753 | -0.047287 | 32.9857
36 | 0.080293 | 0.020253 | -0.080205 | -0.020197 | 8.7838e-05 | 5.6006e-05 | 0.12007 | 0.12007 | 0.12007 | 0.99546 | -0.086805 | 0.99428 | -0.10968 | 32.9857
37 | -0.1005 | -0.025375 | 0.10072 | 0.025521 | 0.00022825 | 0.00014573 | 0.14998 | 0.14998 | 0.14998 | 0.99753 | -0.047287 | 1 | 0 | 41.2023
38 | 0.080205 | 0.020197 | -0.080176 | -0.020178 | 2.9539e-05 | 1.8834e-05 | 0.12007 | 0.12007 | 0.12007 | 0.99428 | -0.10968 | 0.99388 | -0.11739 | 32.9857
39 | -0.079757 | -0.020076 | 0.079854 | 0.020138 | 9.7925e-05 | 6.2434e-05 | 0.11934 | 0.11934 | 0.11934 | 0.99468 | -0.10198 | 0.99601 | -0.076331 | 32.787
40 | 0.0030427 | 0.00076238 | -0.0030425 | -0.00076252 | 1.4736e-07 | -1.479e-07 | 0.0045702 | 0.0045703 | 0.0045703 | 0.99065 | -0.1799 | 0.9906 | -0.18092 | 1.2556
41 | -0.0029573 | -0.00074117 | 0.0029575 | 0.00074095 | 1.9638e-07 | -2.1888e-07 | 0.0044329 | 0.0044328 | 0.0044329 | 0.99269 | -0.1405 | 0.99276 | -0.1391 | 1.2178
42 | -0.0063005 | -0.0015788 | 0.0063012 | 0.001579 | 6.7553e-07 | 1.7113e-07 | 0.0094436 | 0.0094435 | 0.0094436 | 0.99276 | -0.1391 | 0.99288 | -0.13685 | 2.5944
43 | -0.0063012 | -0.001579 | 0.0063029 | 0.0015794 | 1.7158e-06 | 4.3436e-07 | 0.0094435 | 0.0094432 | 0.0094435 | 0.99288 | -0.13685 | 0.99317 | -0.13114 | 2.5944
44 | 0.026448 | 0.0066367 | -0.026437 | -0.0066297 | 1.1335e-05 | 7.0046e-06 | 0.0396 | 0.0396 | 0.0396 | 0.99388 | -0.11739 | 0.99341 | -0.12638 | 10.8792
45 | -0.0063029 | -0.0015794 | 0.0063036 | 0.0015796 | 6.567e-07 | 1.6613e-07 | 0.0094432 | 0.0094431 | 0.0094432 | 0.99317 | -0.13114 | 0.99329 | -0.12895 | 2.5943
46 | -0.0098439 | -0.0024669 | 0.009846 | 0.0024678 | 2.0268e-06 | 9.754e-07 | 0.014747 | 0.014747 | 0.014747 | 0.99329 | -0.12895 | 0.99351 | -0.12463 | 4.0513
47 | -0.028295 | -0.0070967 | 0.028322 | 0.0071137 | 2.7307e-05 | 1.6959e-05 | 0.042549 | 0.042549 | 0.042549 | 0.98958 | -0.20051 | 0.99062 | -0.18029 | 11.6892
48 | 0.028295 | 0.0070967 | -0.028281 | -0.0070881 | 1.3922e-05 | 8.6468e-06 | 0.042549 | 0.042549 | 0.042549 | 0.98958 | -0.20051 | 0.98905 | -0.21084 | 11.6893
49 | -0.041341 | -0.010382 | 0.04135 | 0.010388 | 9.4047e-06 | 5.9353e-06 | 0.062106 | 0.062106 | 0.062106 | 0.99062 | -0.18029 | 0.99087 | -0.17552 | 17.0621
50 | 0.011709 | 0.0029347 | -0.011708 | -0.0029344 | 6.1053e-07 | 3.2341e-07 | 0.017616 | 0.017616 | 0.017616 | 0.98905 | -0.21084 | 0.98899 | -0.21194 | 4.8397
51 | 0.10349 | 0.02619 | -0.10325 | -0.026037 | 0.00024018 | 0.00015336 | 0.15408 | 0.15408 | 0.15408 | 1 | 0 | 0.99747 | -0.048477 | 42.3296
52 | 0.11206 | 0.02836 | -0.11187 | -0.028233 | 0.00019938 | 0.00012735 | 0.16685 | 0.16685 | 0.16685 | 1 | 0 | 0.99806 | -0.037141 | 45.8381
53 | 0.020941 | 0.0052543 | -0.020939 | -0.005253 | 2.135e-06 | 1.2903e-06 | 0.031242 | 0.031242 | 0.031242 | 0.99747 | -0.048477 | 0.99735 | -0.050615 | 8.583
54 | 0.082305 | 0.020783 | -0.082227 | -0.020733 | 7.7984e-05 | 4.973e-05 | 0.12284 | 0.12284 | 0.12284 | 0.99747 | -0.048477 | 0.99643 | -0.068272 | 33.7466
55 | 0.012251 | 0.0030712 | -0.012248 | -0.0030697 | 2.8768e-06 | 1.5407e-06 | 0.018265 | 0.018265 | 0.018265 | 0.99806 | -0.037141 | 0.9978 | -0.04207 | 5.018
56 | 0.099614 | 0.025161 | -0.099504 | -0.025091 | 0.0001101 | 7.0293e-05 | 0.14859 | 0.14859 | 0.14859 | 0.99806 | -0.037141 | 0.99685 | -0.060231 | 40.8202
57 | 0.020939 | 0.005253 | -0.020925 | -0.0052442 | 1.4493e-05 | 8.759e-06 | 0.031242 | 0.031242 | 0.031242 | 0.99735 | -0.050615 | 0.9966 | -0.065143 | 8.5831
58 | 0.078698 | 0.019848 | -0.078607 | -0.01979 | 9.0913e-05 | 5.7956e-05 | 0.11757 | 0.11757 | 0.11757 | 0.99643 | -0.068272 | 0.99518 | -0.092435 | 32.2985
59 | 0.019588 | 0.0049133 | -0.019577 | -0.0049063 | 1.1661e-05 | 6.9892e-06 | 0.029241 | 0.029241 | 0.029241 | 0.99685 | -0.060231 | 0.9962 | -0.072727 | 8.0333
60 | 0.079916 | 0.020178 | -0.079854 | -0.020138 | 6.1591e-05 | 3.9268e-05 | 0.11934 | 0.11934 | 0.11934 | 0.99685 | -0.060231 | 0.99601 | -0.076331 | 32.787
61 | 0.0024721 | 0.00061926 | -0.002472 | -0.00061953 | 1.4323e-07 | -2.7153e-07 | 0.0036962 | 0.0036964 | 0.0036964 | 0.99518 | -0.092435 | 0.99511 | -0.093652 | 1.0155
62 | 0.076134 | 0.019171 | -0.076081 | -0.019137 | 5.319e-05 | 3.3899e-05 | 0.11387 | 0.11387 | 0.11387 | 0.99518 | -0.092435 | 0.99442 | -0.10706 | 31.283
63 | 0.032544 | 0.0081855 | -0.03251 | -0.008164 | 3.4316e-05 | 2.1467e-05 | 0.048821 | 0.048821 | 0.048821 | 0.99212 | -0.15136 | 0.99098 | -0.17346 | 13.4124
64 | -0.032544 | -0.0081855 | 0.032561 | 0.008196 | 1.6919e-05 | 1.0584e-05 | 0.048821 | 0.048821 | 0.048821 | 0.99212 | -0.15136 | 0.99268 | -0.14048 | 13.4123
65 | 0.028195 | 0.0070826 | -0.028169 | -0.0070665 | 2.5931e-05 | 1.6099e-05 | 0.042342 | 0.042342 | 0.042342 | 0.99098 | -0.17346 | 0.98998 | -0.19275 | 11.6325
66 | -0.037489 | -0.0094312 | 0.03749 | 0.0094317 | 8.1316e-07 | 5.1155e-07 | 0.056208 | 0.056208 | 0.056208 | 0.99268 | -0.14048 | 0.99271 | -0.14003 | 15.4419
67 | -0.009846 | -0.0024678 | 0.0098469 | 0.0024683 | 9.3714e-07 | 4.5094e-07 | 0.014747 | 0.014747 | 0.014747 | 0.99351 | -0.12463 | 0.99361 | -0.12263 | 4.0513
68 | -0.00087916 | -0.00022034 | 0.00087917 | 0.00022017 | 9.0126e-09 | -1.7183e-07 | 0.0013203 | 0.0013202 | 0.0013203 | 0.99085 | -0.17574 | 0.99087 | -0.17552 | 0.36271
69 | -0.04223 | -0.010608 | 0.04225 | 0.010621 | 2.0822e-05 | 1.3148e-05 | 0.063426 | 0.063426 | 0.063426 | 0.99087 | -0.17552 | 0.9914 | -0.16519 | 17.4248
70 | 0.040938 | 0.010297 | -0.040936 | -0.010295 | 2.5223e-06 | 1.5912e-06 | 0.061373 | 0.061373 | 0.061373 | 0.99278 | -0.13874 | 0.99271 | -0.14003 | 16.8607
71 | -0.044383 | -0.01116 | 0.044405 | 0.011174 | 2.1652e-05 | 1.3688e-05 | 0.066537 | 0.066537 | 0.066537 | 0.99278 | -0.13874 | 0.9933 | -0.12853 | 18.2793
72 | -0.044405 | -0.011174 | 0.044426 | 0.011187 | 2.0645e-05 | 1.3052e-05 | 0.066537 | 0.066537 | 0.066537 | 0.9933 | -0.12853 | 0.99381 | -0.11881 | 18.2793
73 | -0.049227 | -0.01239 | 0.049255 | 0.012408 | 2.7658e-05 | 1.7525e-05 | 0.073725 | 0.073725 | 0.073725 | 0.99381 | -0.11881 | 0.99442 | -0.10706 | 20.2542
74 | 0.026827 | 0.0067292 | -0.02682 | -0.0067248 | 7.1204e-06 | 4.4043e-06 | 0.040145 | 0.040145 | 0.040145 | 0.99442 | -0.10706 | 0.99413 | -0.11263 | 11.0288
75 | 0.023996 | 0.0060172 | -0.023995 | -0.0060165 | 1.1099e-06 | 6.8057e-07 | 0.035919 | 0.035919 | 0.035919 | 0.99413 | -0.11263 | 0.99408 | -0.1136 | 9.8679
76 | 0.028169 | 0.0070665 | -0.028164 | -0.0070632 | 5.4136e-06 | 3.3612e-06 | 0.042342 | 0.042342 | 0.042342 | 0.98998 | -0.19275 | 0.98978 | -0.19678 | 11.6325
77 | -0.020459 | -0.005129 | 0.020463 | 0.0051313 | 3.7062e-06 | 2.2354e-06 | 0.030632 | 0.030632 | 0.030632 | 0.99388 | -0.1174 | 0.99408 | -0.1136 | 8.4153
78 | 0.016924 | 0.0042431 | -0.016924 | -0.0042425 | 8.8452e-07 | 5.1849e-07 | 0.025339 | 0.025339 | 0.025339 | 0.99388 | -0.1174 | 0.99383 | -0.1185 | 6.9613
79 | 0.013392 | 0.0033575 | -0.013389 | -0.0033561 | 2.6383e-06 | 1.4618e-06 | 0.020052 | 0.020052 | 0.020052 | 0.99383 | -0.1185 | 0.99361 | -0.12263 | 5.5087
80 | 0.0035316 | 0.000885 | -0.0035315 | -0.00088508 | 1.2542e-07 | -7.4725e-08 | 0.0052877 | 0.0052878 | 0.0052878 | 0.99383 | -0.1185 | 0.99379 | -0.11924 | 1.4527
81 | 0.028164 | 0.0070632 | -0.028151 | -0.0070553 | 1.267e-05 | 7.8667e-06 | 0.042342 | 0.042343 | 0.042343 | 0.98978 | -0.19678 | 0.98929 | -0.20623 | 11.6326

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31793 | 0.080071

## res_load
| p_mw | q_mvar
0 | 0.006768 | 0.0016962
1 | 0.0007148 | 0.00017915
2 | 0.0024089 | 0.00060372
3 | 0.0048868 | 0.0012248
4 | 0.00085247 | 0.00021365
5 | 0.00081144 | 0.00020337
6 | 0.0031027 | 0.00077761
7 | 0.0011224 | 0.00028129
8 | 0.0010784 | 0.00027028
9 | 0.0050298 | 0.0012606
10 | 0.0022224 | 0.00055698
11 | 0.0016935 | 0.00042443
12 | 0.0046661 | 0.0011694
13 | 0.005534 | 0.001387
14 | 0.00079496 | 0.00019924
15 | 0.00083306 | 0.00020878
16 | 0.0097951 | 0.0024549
17 | 0.011288 | 0.0028291
18 | 0.010366 | 0.0025981
19 | 0.0099099 | 0.0024837
20 | 0.02005 | 0.005025
21 | 0.010184 | 0.0025523
22 | 0.0091197 | 0.0022856
23 | 0.011277 | 0.0028262
24 | 0.0045421 | 0.0011384
25 | 0.0029573 | 0.00074117
26 | 0.003343 | 0.00083784
27 | 0.0056452 | 0.0014148
28 | 0.0035403 | 0.00088729
29 | 0.016572 | 0.0041534
30 | 0.0035299 | 0.00088469
31 | 0.012248 | 0.0030697
32 | 0.020925 | 0.0052442
33 | 0.019577 | 0.0049063
34 | 0.0043147 | 0.0010814
35 | 0.0049285 | 0.0012352
36 | 0.00087916 | 0.00022034
37 | 0.011708 | 0.0029344
38 | 0.0026071 | 0.0006534
39 | 0.003445 | 0.0008634
40 | 0.0034455 | 0.00086353
41 | 0.0048013 | 0.0012033
42 | 0.0030425 | 0.00076252
43 | 0.0028233 | 0.00070757
44 | 0.003535 | 0.00088597
45 | 0.0035322 | 0.00088524
46 | 0.0035424 | 0.0008878
47 | 0.0035315 | 0.00088508
48 | 0.002472 | 0.00061953
49 | 0.028151 | 0.0070553

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1