## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1702-26_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1702-26_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1702-26_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1702-26_0_5_node_93 | 0.4 | n |  | TRUE
4 | bus_LV_1702-26_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1702-26_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1702-26_0_5_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_1702-26_0_5_node_89 | 0.4 | n |  | TRUE
8 | bus_LV_1702-26_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1702-26_0_5_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_1702-26_0_5_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1702-26_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1702-26_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1702-26_0_5_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1702-26_0_5_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1702-26_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1702-26_0_5_node_88 | 0.4 | n |  | TRUE
17 | bus_LV_1702-26_0_5_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_1702-26_0_5_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_1702-26_0_5_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_1702-26_0_5_node_86 | 0.4 | n |  | TRUE
21 | bus_LV_1702-26_0_5_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_1702-26_0_5_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1702-26_0_5_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1702-26_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1702-26_0_5_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_1702-26_0_5_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_1702-26_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1702-26_0_5_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1702-26_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1702-26_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1702-26_0_5_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1702-26_0_5_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1702-26_0_5_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_1702-26_0_5_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_1702-26_0_5_node_13 | 0.4 | n |  | TRUE
36 | bus_LV_1702-26_0_5_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1702-26_0_5_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_1702-26_0_5_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1702-26_0_5_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_1702-26_0_5_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_1702-26_0_5_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_1702-26_0_5_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1702-26_0_5_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_1702-26_0_5_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1702-26_0_5_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1702-26_0_5_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_1702-26_0_5_node_75 | 0.4 | n |  | TRUE
48 | bus_LV_1702-26_0_5_node_76 | 0.4 | n |  | TRUE
49 | bus_LV_1702-26_0_5_node_73 | 0.4 | n |  | TRUE
50 | bus_LV_1702-26_0_5_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_1702-26_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1702-26_0_5_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_1702-26_0_5_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_1702-26_0_5_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_1702-26_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_1702-26_0_5_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_1702-26_0_5_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_1702-26_0_5_node_77 | 0.4 | n |  | TRUE
59 | bus_LV_1702-26_0_5_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_1702-26_0_5_node_78 | 0.4 | n |  | TRUE
61 | bus_LV_1702-26_0_5_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_1702-26_0_5_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1702-26_0_5_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_1702-26_0_5_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_1702-26_0_5_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_1702-26_0_5_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_1702-26_0_5_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_1702-26_0_5_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_1702-26_0_5_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_1702-26_0_5_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_1702-26_0_5_node_90 | 0.4 | n |  | TRUE
72 | bus_LV_1702-26_0_5_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_1702-26_0_5_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_1702-26_0_5_node_92 | 0.4 | n |  | TRUE
75 | bus_LV_1702-26_0_5_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_1702-26_0_5_node_87 | 0.4 | n |  | TRUE
77 | bus_LV_1702-26_0_5_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_1702-26_0_5_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_1702-26_0_5_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_1702-26_0_5_node_83 | 0.4 | n |  | TRUE
81 | bus_LV_1702-26_0_5_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_1702-26_0_5_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_1702-26_0_5_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1702-26_0_5_node_80 | 0.4 | n |  | TRUE
85 | bus_MV_498_0_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1702-26_0_5_load_0 | 0 | 0.040917 | 0.010255 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1702-26_0_5_load_93 | 3 | 0.0070361 | 0.0017634 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1702-26_0_5_load_32 | 6 | 0.080182 | 0.020096 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1702-26_0_5_load_89 | 7 | 0.012099 | 0.0030323 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1702-26_0_5_load_18 | 13 | 0.0081258 | 0.0020365 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1702-26_0_5_load_26 | 14 | 0.020247 | 0.0050745 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1702-26_0_5_load_88 | 16 | 0.0031152 | 0.00078075 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1702-26_0_5_load_85 | 19 | 0.025688 | 0.0064379 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1702-26_0_5_load_91 | 21 | 0.012684 | 0.0031789 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1702-26_0_5_load_23 | 23 | 0.008199 | 0.0020549 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1702-26_0_5_load_47 | 25 | 0.0013424 | 0.00033644 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1702-26_0_5_load_30 | 28 | 0.0015216 | 0.00038134 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1702-26_0_5_load_22 | 30 | 0.0033273 | 0.00083389 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1702-26_0_5_load_14 | 31 | 0.0029976 | 0.00075128 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1702-26_0_5_load_44 | 33 | 0.019867 | 0.0049791 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1702-26_0_5_load_41 | 34 | 0.010787 | 0.0027034 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1702-26_0_5_load_13 | 35 | 0.0013422 | 0.00033639 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1702-26_0_5_load_40 | 38 | 0.012275 | 0.0030765 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1702-26_0_5_load_84 | 39 | 0.003589 | 0.00089949 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1702-26_0_5_load_25 | 43 | 0.0032106 | 0.00080466 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1702-26_0_5_load_28 | 45 | 0.0028002 | 0.00070181 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1702-26_0_5_load_76 | 48 | 0.030874 | 0.0077377 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1702-26_0_5_load_73 | 49 | 0.0021529 | 0.00053956 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1702-26_0_5_load_66 | 50 | 0.0088334 | 0.0022139 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1702-26_0_5_load_56 | 52 | 0.0026489 | 0.00066387 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1702-26_0_5_load_35 | 53 | 0.010233 | 0.0025647 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1702-26_0_5_load_36 | 54 | 0.016103 | 0.0040358 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1702-26_0_5_load_49 | 56 | 0.020694 | 0.0051864 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1702-26_0_5_load_39 | 57 | 0.011405 | 0.0028583 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1702-26_0_5_load_65 | 59 | 0.0032085 | 0.00080412 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1702-26_0_5_load_78 | 60 | 0.006253 | 0.0015672 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1702-26_0_5_load_53 | 61 | 0.0045383 | 0.0011374 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1702-26_0_5_load_50 | 62 | 0.0088534 | 0.0022189 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1702-26_0_5_load_57 | 64 | 0.0022049 | 0.00055259 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1702-26_0_5_load_58 | 65 | 0.0042707 | 0.0010703 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1702-26_0_5_load_60 | 67 | 0.0028849 | 0.00072302 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1702-26_0_5_load_69 | 70 | 0.0035676 | 0.00089413 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1702-26_0_5_load_90 | 71 | 0.0042654 | 0.001069 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1702-26_0_5_load_62 | 72 | 0.011209 | 0.0028092 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1702-26_0_5_load_92 | 74 | 0.0073067 | 0.0018312 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1702-26_0_5_load_70 | 75 | 0.0028805 | 0.00072192 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1702-26_0_5_load_79 | 77 | 0.012582 | 0.0031533 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1702-26_0_5_load_67 | 78 | 0.0032839 | 0.00082301 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1702-26_0_5_load_68 | 79 | 0.046123 | 0.01156 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1702-26_0_5_load_83 | 80 | 0.0032629 | 0.00081777 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1702-26_0_5_load_72 | 81 | 0.0032721 | 0.00082008 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1702-26_0_5_load_71 | 82 | 0.0017429 | 0.00043681 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1702-26_0_5_load_82 | 83 | 0.03082 | 0.0077241 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1702-26_0_5_load_80 | 84 | 0.016713 | 0.0041886 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1702-26_0_5_line_0 |  | 0 | 1 | 0.038096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1702-26_0_5_line_1 |  | 1 | 2 | 0.027714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1702-26_0_5_line_2 |  | 2 | 3 | 0.001521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1702-26_0_5_line_3 |  | 2 | 4 | 0.058765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1702-26_0_5_line_4 |  | 4 | 5 | 0.045486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1702-26_0_5_line_5 |  | 4 | 6 | 0.01194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1702-26_0_5_line_6 |  | 5 | 7 | 0.043558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1702-26_0_5_line_7 |  | 7 | 9 | 0.044553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1702-26_0_5_line_8 |  | 8 | 9 | 0.048484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1702-26_0_5_line_9 |  | 8 | 10 | 0.025021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1702-26_0_5_line_10 |  | 9 | 15 | 0.038445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1702-26_0_5_line_11 |  | 10 | 23 | 0.037473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1702-26_0_5_line_12 |  | 10 | 24 | 0.021644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1702-26_0_5_line_13 |  | 11 | 12 | 0.097176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1702-26_0_5_line_14 |  | 11 | 13 | 0.037256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1702-26_0_5_line_15 |  | 12 | 14 | 0.026001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1702-26_0_5_line_16 |  | 13 | 24 | 0.027973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1702-26_0_5_line_17 |  | 15 | 16 | 0.025586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1702-26_0_5_line_18 |  | 17 | 18 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1702-26_0_5_line_19 |  | 18 | 50 | 0.012012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1702-26_0_5_line_20 |  | 18 | 51 | 0.027086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1702-26_0_5_line_21 |  | 19 | 20 | 0.025866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1702-26_0_5_line_22 |  | 20 | 76 | 0.014648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1702-26_0_5_line_23 |  | 21 | 22 | 0.040772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1702-26_0_5_line_24 |  | 22 | 68 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1702-26_0_5_line_25 |  | 23 | 36 | 0.034161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1702-26_0_5_line_26 |  | 24 | 35 | 0.014975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1702-26_0_5_line_27 |  | 24 | 27 | 0.099802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1702-26_0_5_line_28 |  | 25 | 26 | 0.015165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1702-26_0_5_line_29 |  | 26 | 44 | 0.015426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1702-26_0_5_line_30 |  | 26 | 43 | 0.020095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1702-26_0_5_line_31 |  | 27 | 28 | 0.0088884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1702-26_0_5_line_32 |  | 28 | 42 | 0.022565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1702-26_0_5_line_33 |  | 29 | 30 | 0.028409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1702-26_0_5_line_34 |  | 29 | 31 | 0.017666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1702-26_0_5_line_35 |  | 30 | 36 | 0.014897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1702-26_0_5_line_36 |  | 32 | 33 | 0.02654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_1702-26_0_5_line_37 |  | 32 | 34 | 0.0065529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1702-26_0_5_line_38 |  | 33 | 37 | 0.0022153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_1702-26_0_5_line_39 |  | 34 | 41 | 0.025648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1702-26_0_5_line_40 |  | 36 | 43 | 0.0049821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_1702-26_0_5_line_41 |  | 37 | 38 | 0.027129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_1702-26_0_5_line_42 |  | 38 | 55 | 0.014975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_1702-26_0_5_line_43 |  | 39 | 40 | 0.0070379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1702-26_0_5_line_44 |  | 40 | 63 | 0.009834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1702-26_0_5_line_45 |  | 41 | 44 | 0.029332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_1702-26_0_5_line_46 |  | 41 | 57 | 0.014513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1702-26_0_5_line_47 |  | 42 | 46 | 0.005952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1702-26_0_5_line_48 |  | 42 | 45 | 0.035439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1702-26_0_5_line_49 |  | 44 | 52 | 0.0116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1702-26_0_5_line_50 |  | 46 | 47 | 0.15322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1702-26_0_5_line_51 |  | 46 | 48 | 0.010027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1702-26_0_5_line_52 |  | 47 | 49 | 0.03624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1702-26_0_5_line_53 |  | 50 | 59 | 0.017454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1702-26_0_5_line_54 |  | 51 | 56 | 0.016703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1702-26_0_5_line_55 |  | 51 | 54 | 0.019909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1702-26_0_5_line_56 |  | 53 | 54 | 0.034827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1702-26_0_5_line_57 |  | 53 | 55 | 0.00038222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_1702-26_0_5_line_58 |  | 56 | 58 | 0.031824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1702-26_0_5_line_59 |  | 58 | 60 | 0.040606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1702-26_0_5_line_60 |  | 58 | 61 | 0.019482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1702-26_0_5_line_61 |  | 59 | 78 | 0.0071759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1702-26_0_5_line_62 |  | 60 | 83 | 0.019256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1702-26_0_5_line_63 |  | 61 | 63 | 0.023249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1702-26_0_5_line_64 |  | 62 | 63 | 0.083433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1702-26_0_5_line_65 |  | 64 | 65 | 0.0050592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1702-26_0_5_line_66 |  | 64 | 66 | 0.011713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1702-26_0_5_line_67 |  | 65 | 67 | 0.011547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1702-26_0_5_line_68 |  | 66 | 68 | 0.041031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1702-26_0_5_line_69 |  | 66 | 69 | 0.09251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1702-26_0_5_line_70 |  | 67 | 70 | 0.0014729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1702-26_0_5_line_71 |  | 68 | 71 | 0.046069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1702-26_0_5_line_72 |  | 69 | 74 | 0.026256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1702-26_0_5_line_73 |  | 70 | 75 | 0.01648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1702-26_0_5_line_74 |  | 71 | 76 | 0.033627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1702-26_0_5_line_75 |  | 72 | 73 | 0.047021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1702-26_0_5_line_76 |  | 73 | 77 | 0.022515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1702-26_0_5_line_77 |  | 75 | 82 | 0.018405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1702-26_0_5_line_78 |  | 77 | 84 | 0.026922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1702-26_0_5_line_79 |  | 78 | 79 | 0.0066803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1702-26_0_5_line_80 |  | 79 | 80 | 0.00089859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1702-26_0_5_line_81 |  | 80 | 81 | 0.0075674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1702-26_0_5_line_82 |  | 81 | 82 | 0.007172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1702-26_0_5_line_83 |  | 83 | 84 | 0.02607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1702-26_0_5_trafo_34 | 0.63 MVA 20/0.4 kV | 85 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2676965.5547 | 1226327.9505 | 2676959.4227 | 1226349.0075 | 2676951.4382 | 1226359.7448 | 2676949.3136 | 1226361.5432
1 | 2676965.5547 | 1226327.9505 | 2676974.2115 | 1226332.0429 | 2676981.2426 | 1226315.3227
2 | 2676981.2426 | 1226315.3227 | 2676982.7316 | 1226315.6533
3 | 2676981.2426 | 1226315.3227 | 2676984.3884 | 1226304.7785 | 2676990.3624 | 1226288.9119 | 2677019.5558 | 1226298.7517
4 | 2677019.5558 | 1226298.7517 | 2677018.8518 | 1226301.6001 | 2677023.8945 | 1226302.6327 | 2677029.8998 | 1226312.4503 | 2677040.8222 | 1226335.9296
5 | 2677019.5558 | 1226298.7517 | 2677022.2413 | 1226292.738 | 2677026.9833 | 1226290.2517
6 | 2677040.8222 | 1226335.9296 | 2677050.1914 | 1226355.2416 | 2677050.5954 | 1226360.9173 | 2677049.5273 | 1226364.3724 | 2677046.1412 | 1226367.1193 | 2677041.6928 | 1226370.5418 | 2677040.372 | 1226373.0264
7 | 2677025.9947 | 1226414.9795 | 2677032.9154 | 1226393.9105 | 2677034.2649 | 1226390.3812 | 2677037.2606 | 1226385.5834 | 2677038.4033 | 1226381.64 | 2677040.372 | 1226373.0264
8 | 2677025.9947 | 1226414.9795 | 2677057.7654 | 1226426.5207 | 2677063.6253 | 1226428.2422 | 2677066.9491 | 1226436.146
9 | 2677066.9491 | 1226436.146 | 2677084.8075 | 1226453.7224
10 | 2676991.8473 | 1226401.4175 | 2676997.6182 | 1226400.6472 | 2677002.6765 | 1226401.6355 | 2677012.8481 | 1226405.8143 | 2677019.5035 | 1226408.1576 | 2677025.9947 | 1226414.9795
11 | 2677084.8075 | 1226453.7224 | 2677102.3448 | 1226433.5027 | 2677105.4695 | 1226423.2615
12 | 2677099.8736 | 1226469.1724 | 2677098.3304 | 1226466.5951 | 2677084.8075 | 1226453.7224
13 | 2676989.17 | 1226460.0888 | 2676986.2741 | 1226471.8258 | 2677003.4028 | 1226477.8626 | 2677021.668 | 1226488.028 | 2677034.5883 | 1226497.6794 | 2677051.237 | 1226512.6716 | 2677056.5582 | 1226517.9441
14 | 2677056.5582 | 1226517.9441 | 2677081.298 | 1226490.0879
15 | 2676989.17 | 1226460.0888 | 2676988.7787 | 1226451.667 | 2676983.7488 | 1226442.0399 | 2676980.7717 | 1226436.028
16 | 2677099.8736 | 1226469.1724 | 2677081.298 | 1226490.0879
17 | 2676991.8473 | 1226401.4175 | 2676990.122 | 1226395.9137 | 2676992.5705 | 1226384.7824 | 2676996.3063 | 1226377.2356
18 | 2677128.9841 | 1226259.0978 | 2677124.4844 | 1226274.0606
19 | 2677128.9841 | 1226259.0978 | 2677132.3492 | 1226247.5665
20 | 2677128.9841 | 1226259.0978 | 2677136.3879 | 1226260.439 | 2677154.0762 | 1226268.9518
21 | 2677088.633 | 1226201.8367 | 2677078.9463 | 1226209.9389 | 2677077.214 | 1226223.0625
22 | 2677088.633 | 1226201.8367 | 2677102.7086 | 1226206.0329
23 | 2677108.9033 | 1226126.3932 | 2677081.0223 | 1226115.258 | 2677078.4064 | 1226118.2261 | 2677076.5645 | 1226124.765
24 | 2677108.9033 | 1226126.3932 | 2677124.0501 | 1226129.2469
25 | 2677115.4387 | 1226390.5881 | 2677105.4695 | 1226423.2615
26 | 2677099.8736 | 1226469.1724 | 2677110.3402 | 1226458.4624
27 | 2677099.8736 | 1226469.1724 | 2677102.7953 | 1226475.3477 | 2677109.2128 | 1226480.2452 | 2677112.5223 | 1226483.4013 | 2677120.4903 | 1226472.7752 | 2677131.4688 | 1226461.4766 | 2677136.8568 | 1226458.6667 | 2677144.0382 | 1226458.4375 | 2677161.6577 | 1226462.8577 | 2677165.3026 | 1226459.436 | 2677171.2904 | 1226457.7236 | 2677179.5331 | 1226455.151
28 | 2677092.2613 | 1226381.0147 | 2677087.3988 | 1226395.3796
29 | 2677092.2613 | 1226381.0147 | 2677097.211 | 1226366.4024
30 | 2677092.2613 | 1226381.0147 | 2677110.834 | 1226388.6861
31 | 2677179.5331 | 1226455.151 | 2677182.9998 | 1226452.0272 | 2677184.951 | 1226448.2833
32 | 2677196.6286 | 1226429.2776 | 2677186.9491 | 1226442.094 | 2677184.951 | 1226448.2833
33 | 2677152.0621 | 1226412.5329 | 2677137.4413 | 1226399.5681 | 2677129.2312 | 1226396.2172
34 | 2677152.0621 | 1226412.5329 | 2677140.2336 | 1226425.6539
35 | 2677115.4387 | 1226390.5881 | 2677129.2312 | 1226396.2172
36 | 2677156.2018 | 1226366.3001 | 2677173.5404 | 1226346.2063
37 | 2677156.2018 | 1226366.3001 | 2677151.7648 | 1226362.4066 | 2677151.132 | 1226362.5545
38 | 2677174.9877 | 1226344.5291 | 2677173.5404 | 1226346.2063
39 | 2677126.157 | 1226368.3898 | 2677151.132 | 1226362.5545
40 | 2677115.4387 | 1226390.5881 | 2677110.834 | 1226388.6861
41 | 2677174.9877 | 1226344.5291 | 2677155.7774 | 1226327.7243 | 2677154.2613 | 1226327.1965
42 | 2677140.119 | 1226322.2732 | 2677154.2613 | 1226327.1965
43 | 2677229.9477 | 1226320.9484 | 2677226.8802 | 1226327.2827
44 | 2677234.4276 | 1226312.1895 | 2677229.9477 | 1226320.9484
45 | 2677097.211 | 1226366.4024 | 2677118.0782 | 1226370.0085 | 2677126.157 | 1226368.3898
46 | 2677126.157 | 1226368.3898 | 2677130.3622 | 1226354.4999
47 | 2677201.9909 | 1226426.701 | 2677200.7577 | 1226427.0963 | 2677196.6286 | 1226429.2776
48 | 2677196.6286 | 1226429.2776 | 2677194.9283 | 1226419.5268 | 2677200.6747 | 1226404.8804 | 2677197.1497 | 1226406.647 | 2677194.3532 | 1226408.9344 | 2677193.5551 | 1226406.8284
49 | 2677097.211 | 1226366.4024 | 2677100.4969 | 1226355.2772
50 | 2677201.9909 | 1226426.701 | 2677204.4863 | 1226427.167 | 2677215.4759 | 1226432.5465 | 2677225.7726 | 1226437.5835 | 2677232.5365 | 1226440.8957 | 2677236.7587 | 1226443.2298 | 2677250.8631 | 1226401.3848 | 2677255.7357 | 1226388.0725 | 2677263.1959 | 1226371.6361 | 2677270.3799 | 1226358.376 | 2677281.1826 | 1226337.8914
51 | 2677201.9909 | 1226426.701 | 2677206.2989 | 1226417.6462
52 | 2677281.1826 | 1226337.8914 | 2677286.6992 | 1226329.8688 | 2677291.1448 | 1226326.68 | 2677295.2902 | 1226325.5886 | 2677300.2386 | 1226325.7085 | 2677311.8776 | 1226327.6286
53 | 2677137.2387 | 1226230.8117 | 2677132.3492 | 1226247.5665
54 | 2677154.0762 | 1226268.9518 | 2677168.9063 | 1226276.6376
55 | 2677154.0762 | 1226268.9518 | 2677149.0348 | 1226288.2118
56 | 2677149.0348 | 1226288.2118 | 2677140.2158 | 1226321.9035
57 | 2677140.2158 | 1226321.9035 | 2677140.119 | 1226322.2732
58 | 2677197.1613 | 1226291.281 | 2677168.9063 | 1226276.6376
59 | 2677197.1613 | 1226291.281 | 2677213.3293 | 1226266.8188 | 2677216.7756 | 1226256.0741
60 | 2677197.1613 | 1226291.281 | 2677214.1425 | 1226300.8304
61 | 2677137.2387 | 1226230.8117 | 2677139.249 | 1226223.9232
62 | 2677222.6566 | 1226237.7385 | 2677216.7756 | 1226256.0741
63 | 2677234.4276 | 1226312.1895 | 2677218.5334 | 1226303.2996 | 2677214.1425 | 1226300.8304
64 | 2677234.4276 | 1226312.1895 | 2677264.0017 | 1226250.0873 | 2677270.2673 | 1226236.8469
65 | 2677160.3385 | 1226151.6556 | 2677158.9212 | 1226156.5122
66 | 2677163.6198 | 1226140.4117 | 2677160.3385 | 1226151.6556
67 | 2677155.6865 | 1226167.5965 | 2677158.9212 | 1226156.5122
68 | 2677163.6198 | 1226140.4117 | 2677139.9136 | 1226132.955 | 2677124.0501 | 1226129.2469
69 | 2677163.6198 | 1226140.4117 | 2677167.7013 | 1226126.7221 | 2677176.0708 | 1226098.6341 | 2677178.229 | 1226091.8019 | 2677186.95 | 1226096.218 | 2677185.3474 | 1226099.9664 | 2677186.8557 | 1226100.5641 | 2677188.2791 | 1226097.7807 | 2677190.6145 | 1226098.9006 | 2677193.0149 | 1226101.4446 | 2677203.858 | 1226106.4775 | 2677208.4922 | 1226108.6279
70 | 2677155.6865 | 1226167.5965 | 2677155.2739 | 1226169.0105
71 | 2677124.0501 | 1226129.2469 | 2677111.7134 | 1226173.6339
72 | 2677197.3207 | 1226132.3989 | 2677208.4922 | 1226108.6279
73 | 2677150.6573 | 1226184.8301 | 2677155.2739 | 1226169.0105
74 | 2677102.7086 | 1226206.0329 | 2677111.7134 | 1226173.6339
75 | 2677254.9869 | 1226169.672 | 2677210.2063 | 1226155.331
76 | 2677254.9869 | 1226169.672 | 2677245.9525 | 1226190.295
77 | 2677150.6573 | 1226184.8301 | 2677145.5012 | 1226202.4985
78 | 2677245.9525 | 1226190.295 | 2677237.6676 | 1226209.2071 | 2677234.5403 | 1226214.6467
79 | 2677141.1204 | 1226217.5104 | 2677139.249 | 1226223.9232
80 | 2677141.1204 | 1226217.5104 | 2677141.3721 | 1226216.6478
81 | 2677141.3721 | 1226216.6478 | 2677143.4921 | 1226209.3834
82 | 2677143.4921 | 1226209.3834 | 2677145.5012 | 1226202.4985
83 | 2677222.6566 | 1226237.7385 | 2677224.4133 | 1226232.2616 | 2677234.5403 | 1226214.6467

## bus_geodata
| x | y | coords
0 | 2676949.3136 | 1226361.5432
1 | 2676965.5547 | 1226327.9505
2 | 2676981.2426 | 1226315.3227
3 | 2676982.7316 | 1226315.6533
4 | 2677019.5558 | 1226298.7517
5 | 2677040.8222 | 1226335.9296
6 | 2677026.9833 | 1226290.2517
7 | 2677040.372 | 1226373.0264
8 | 2677066.9491 | 1226436.146
9 | 2677025.9947 | 1226414.9795
10 | 2677084.8075 | 1226453.7224
11 | 2677056.5582 | 1226517.9441
12 | 2676989.17 | 1226460.0888
13 | 2677081.298 | 1226490.0879
14 | 2676980.7717 | 1226436.028
15 | 2676991.8473 | 1226401.4175
16 | 2676996.3063 | 1226377.2356
17 | 2677124.4844 | 1226274.0606
18 | 2677128.9841 | 1226259.0978
19 | 2677077.214 | 1226223.0625
20 | 2677088.633 | 1226201.8367
21 | 2677076.5645 | 1226124.765
22 | 2677108.9033 | 1226126.3932
23 | 2677105.4695 | 1226423.2615
24 | 2677099.8736 | 1226469.1724
25 | 2677087.3988 | 1226395.3796
26 | 2677092.2613 | 1226381.0147
27 | 2677179.5331 | 1226455.151
28 | 2677184.951 | 1226448.2833
29 | 2677152.0621 | 1226412.5329
30 | 2677129.2312 | 1226396.2172
31 | 2677140.2336 | 1226425.6539
32 | 2677156.2018 | 1226366.3001
33 | 2677173.5404 | 1226346.2063
34 | 2677151.132 | 1226362.5545
35 | 2677110.3402 | 1226458.4624
36 | 2677115.4387 | 1226390.5881
37 | 2677174.9877 | 1226344.5291
38 | 2677154.2613 | 1226327.1965
39 | 2677226.8802 | 1226327.2827
40 | 2677229.9477 | 1226320.9484
41 | 2677126.157 | 1226368.3898
42 | 2677196.6286 | 1226429.2776
43 | 2677110.834 | 1226388.6861
44 | 2677097.211 | 1226366.4024
45 | 2677193.5551 | 1226406.8284
46 | 2677201.9909 | 1226426.701
47 | 2677281.1826 | 1226337.8914
48 | 2677206.2989 | 1226417.6462
49 | 2677311.8776 | 1226327.6286
50 | 2677132.3492 | 1226247.5665
51 | 2677154.0762 | 1226268.9518
52 | 2677100.4969 | 1226355.2772
53 | 2677140.2158 | 1226321.9035
54 | 2677149.0348 | 1226288.2118
55 | 2677140.119 | 1226322.2732
56 | 2677168.9063 | 1226276.6376
57 | 2677130.3622 | 1226354.4999
58 | 2677197.1613 | 1226291.281
59 | 2677137.2387 | 1226230.8117
60 | 2677216.7756 | 1226256.0741
61 | 2677214.1425 | 1226300.8304
62 | 2677270.2673 | 1226236.8469
63 | 2677234.4276 | 1226312.1895
64 | 2677160.3385 | 1226151.6556
65 | 2677158.9212 | 1226156.5122
66 | 2677163.6198 | 1226140.4117
67 | 2677155.6865 | 1226167.5965
68 | 2677124.0501 | 1226129.2469
69 | 2677208.4922 | 1226108.6279
70 | 2677155.2739 | 1226169.0105
71 | 2677111.7134 | 1226173.6339
72 | 2677210.2063 | 1226155.331
73 | 2677254.9869 | 1226169.672
74 | 2677197.3207 | 1226132.3989
75 | 2677150.6573 | 1226184.8301
76 | 2677102.7086 | 1226206.0329
77 | 2677245.9525 | 1226190.295
78 | 2677139.249 | 1226223.9232
79 | 2677141.1204 | 1226217.5104
80 | 2677141.3721 | 1226216.6478
81 | 2677143.4921 | 1226209.3834
82 | 2677145.5012 | 1226202.4985
83 | 2677222.6566 | 1226237.7385
84 | 2677234.5403 | 1226214.6467
85 | 2677128.9841 | 1226259.0978

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97024 | -0.57482 | 0.040917 | 0.010255
1 | 0.9717 | -0.546 | 0 | 0
2 | 0.97276 | -0.52509 | 0 | 0
3 | 0.97275 | -0.52528 | 0.0070361 | 0.0017634
4 | 0.97539 | -0.47332 | 0 | 0
5 | 0.97811 | -0.42008 | 0 | 0
6 | 0.9745 | -0.49088 | 0.080182 | 0.020096
7 | 0.97915 | -0.39976 | 0.012099 | 0.0030323
8 | 0.98161 | -0.35189 | 0 | 0
9 | 0.98031 | -0.37707 | 0 | 0
10 | 0.98228 | -0.33892 | 0 | 0
11 | 0.97949 | -0.39327 | 0 | 0
12 | 0.97767 | -0.42909 | 0 | 0
13 | 0.98019 | -0.37957 | 0.0081258 | 0.0020365
14 | 0.97718 | -0.43869 | 0.020247 | 0.0050745
15 | 0.9802 | -0.37924 | 0 | 0
16 | 0.98013 | -0.38069 | 0.0031152 | 0.00078075
17 | 1 | 0 | -0.57352 | -0.14651
18 | 0.99838 | -0.03075 | 0 | 0
19 | 0.98415 | -0.30538 | 0.025688 | 0.0064379
20 | 0.98476 | -0.29343 | 0 | 0
21 | 0.98652 | -0.2592 | 0.012684 | 0.0031789
22 | 0.987 | -0.24994 | 0 | 0
23 | 0.98375 | -0.31047 | 0.008199 | 0.0020549
24 | 0.98093 | -0.36518 | 0 | 0
25 | 0.98618 | -0.26349 | 0.0013424 | 0.00033644
26 | 0.9862 | -0.26312 | 0 | 0
27 | 0.97747 | -0.43296 | 0 | 0
28 | 0.97716 | -0.43902 | 0.0015216 | 0.00038134
29 | 0.98497 | -0.28682 | 0 | 0
30 | 0.98505 | -0.28529 | 0.0033273 | 0.00083389
31 | 0.98492 | -0.28777 | 0.0029976 | 0.00075128
32 | 0.98959 | -0.19787 | 0 | 0
33 | 0.99085 | -0.17386 | 0.019867 | 0.0049791
34 | 0.98928 | -0.20381 | 0.010787 | 0.0027034
35 | 0.98091 | -0.36555 | 0.0013422 | 0.00033639
36 | 0.98514 | -0.2836 | 0 | 0
37 | 0.99096 | -0.17171 | 0 | 0
38 | 0.99234 | -0.14533 | 0.012275 | 0.0030765
39 | 0.99108 | -0.17053 | 0.003589 | 0.00089949
40 | 0.9911 | -0.17008 | 0 | 0
41 | 0.98812 | -0.22609 | 0 | 0
42 | 0.97641 | -0.45379 | 0 | 0
43 | 0.98534 | -0.27957 | 0.0032106 | 0.00080466
44 | 0.98686 | -0.25044 | 0 | 0
45 | 0.97632 | -0.4556 | 0.0028002 | 0.00070181
46 | 0.97622 | -0.45738 | 0 | 0
47 | 0.97592 | -0.46343 | 0 | 0
48 | 0.97594 | -0.46305 | 0.030874 | 0.0077377
49 | 0.97585 | -0.46486 | 0.0021529 | 0.00053956
50 | 0.99688 | -0.059253 | 0.0088334 | 0.0022139
51 | 0.99623 | -0.071397 | 0 | 0
52 | 0.98683 | -0.25099 | 0.0026489 | 0.00066387
53 | 0.99316 | -0.12976 | 0.010233 | 0.0025647
54 | 0.99508 | -0.093304 | 0.016103 | 0.0040358
55 | 0.99314 | -0.13015 | 0 | 0
56 | 0.99447 | -0.10527 | 0.020694 | 0.0051864
57 | 0.98797 | -0.22904 | 0.011405 | 0.0028583
58 | 0.9917 | -0.15846 | 0 | 0
59 | 0.99486 | -0.098104 | 0.0032085 | 0.00080412
60 | 0.98881 | -0.21445 | 0.006253 | 0.0015672
61 | 0.9914 | -0.16432 | 0.0045383 | 0.0011374
62 | 0.99046 | -0.18257 | 0.0088534 | 0.0022189
63 | 0.99113 | -0.16946 | 0 | 0
64 | 0.98932 | -0.20479 | 0.0022049 | 0.00055259
65 | 0.98957 | -0.20009 | 0.0042707 | 0.0010703
66 | 0.98879 | -0.21521 | 0 | 0
67 | 0.99017 | -0.1885 | 0.0028849 | 0.00072302
68 | 0.98718 | -0.24646 | 0 | 0
69 | 0.98817 | -0.22728 | 0 | 0
70 | 0.99025 | -0.18695 | 0.0035676 | 0.00089413
71 | 0.9859 | -0.27117 | 0.0042654 | 0.001069
72 | 0.98527 | -0.28332 | 0.011209 | 0.0028092
73 | 0.98575 | -0.27386 | 0 | 0
74 | 0.98799 | -0.2307 | 0.0073067 | 0.0018312
75 | 0.9912 | -0.16855 | 0.0028805 | 0.00072192
76 | 0.98511 | -0.28667 | 0 | 0
77 | 0.98598 | -0.26933 | 0.012582 | 0.0031533
78 | 0.99405 | -0.11372 | 0.0032839 | 0.00082301
79 | 0.99331 | -0.12789 | 0.046123 | 0.01156
80 | 0.99325 | -0.12906 | 0.0032629 | 0.00081777
81 | 0.99276 | -0.13853 | 0.0032721 | 0.00082008
82 | 0.99231 | -0.1471 | 0.0017429 | 0.00043681
83 | 0.98754 | -0.23897 | 0.03082 | 0.0077241
84 | 0.98657 | -0.25786 | 0.016713 | 0.0041886
85 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040917 | -0.010255 | 0.040973 | 0.01029 | 5.6256e-05 | 3.5532e-05 | 0.062752 | 0.062752 | 0.062752 | 0.97024 | -0.57482 | 0.9717 | -0.546 | 17.2396
1 | -0.040973 | -0.01029 | 0.041014 | 0.010316 | 4.0924e-05 | 2.5848e-05 | 0.062752 | 0.062752 | 0.062752 | 0.9717 | -0.546 | 0.97276 | -0.52509 | 17.2395
2 | 0.0070361 | 0.0017634 | -0.0070361 | -0.0017634 | 6.6074e-08 | 2.3406e-08 | 0.010763 | 0.010763 | 0.010763 | 0.97276 | -0.52509 | 0.97275 | -0.52528 | 2.9569
3 | -0.04805 | -0.01208 | 0.048169 | 0.012155 | 0.0001191 | 7.549e-05 | 0.073515 | 0.073515 | 0.073515 | 0.97276 | -0.52509 | 0.97539 | -0.47332 | 20.1964
4 | -0.12842 | -0.032293 | 0.12875 | 0.032502 | 0.00032746 | 0.00020844 | 0.19595 | 0.19595 | 0.19595 | 0.97539 | -0.47332 | 0.97811 | -0.42008 | 26.9161
5 | 0.08025 | 0.020138 | -0.080182 | -0.020096 | 6.7121e-05 | 4.2809e-05 | 0.12243 | 0.12243 | 0.12243 | 0.97539 | -0.47332 | 0.9745 | -0.49088 | 33.6359
6 | -0.12875 | -0.032502 | 0.12887 | 0.032579 | 0.00012543 | 7.7541e-05 | 0.19595 | 0.19595 | 0.19595 | 0.97811 | -0.42008 | 0.97915 | -0.39976 | 10.7664
7 | -0.14097 | -0.035612 | 0.14112 | 0.035707 | 0.0001535 | 9.5437e-05 | 0.21433 | 0.21433 | 0.21433 | 0.97915 | -0.39976 | 0.98031 | -0.37707 | 11.7766
8 | 0.14441 | 0.036596 | -0.14424 | -0.036487 | 0.0001745 | 0.00010862 | 0.21906 | 0.21906 | 0.21906 | 0.98161 | -0.35189 | 0.98031 | -0.37707 | 12.0364
9 | -0.14441 | -0.036596 | 0.1445 | 0.036652 | 9.0053e-05 | 5.6051e-05 | 0.21906 | 0.21906 | 0.21906 | 0.98161 | -0.35189 | 0.98228 | -0.33892 | 12.0364
10 | 0.0031158 | 0.00078028 | -0.0031154 | -0.00078056 | 3.2245e-07 | -2.7829e-07 | 0.0047292 | 0.0047294 | 0.0047294 | 0.98031 | -0.37707 | 0.9802 | -0.37924 | 1.2993
11 | -0.2119 | -0.053666 | 0.21219 | 0.053849 | 0.00028996 | 0.0001832 | 0.3212 | 0.3212 | 0.3212 | 0.98228 | -0.33892 | 0.98375 | -0.31047 | 17.6485
12 | 0.067398 | 0.017014 | -0.067313 | -0.01696 | 8.468e-05 | 5.3922e-05 | 0.10214 | 0.10214 | 0.10214 | 0.98228 | -0.33892 | 0.98093 | -0.36518 | 28.0612
13 | 0.020291 | 0.0051011 | -0.020257 | -0.0050801 | 3.4641e-05 | 2.0949e-05 | 0.030832 | 0.030832 | 0.030832 | 0.97949 | -0.39327 | 0.97767 | -0.42909 | 8.4703
14 | -0.020291 | -0.0051011 | 0.020305 | 0.0051091 | 1.3281e-05 | 8.0304e-06 | 0.030832 | 0.030831 | 0.030832 | 0.97949 | -0.39327 | 0.98019 | -0.37957 | 8.4702
15 | 0.020257 | 0.0050801 | -0.020247 | -0.0050745 | 9.269e-06 | 5.6063e-06 | 0.030832 | 0.030832 | 0.030832 | 0.97767 | -0.42909 | 0.97718 | -0.43869 | 8.4704
16 | -0.02843 | -0.0071456 | 0.02845 | 0.0071578 | 1.9547e-05 | 1.2157e-05 | 0.043167 | 0.043167 | 0.043167 | 0.98019 | -0.37957 | 0.98093 | -0.36518 | 11.8591
17 | 0.0031154 | 0.00078056 | -0.0031152 | -0.00078075 | 2.1461e-07 | -1.8514e-07 | 0.0047294 | 0.0047295 | 0.0047295 | 0.9802 | -0.37924 | 0.98013 | -0.38069 | 1.2993
18 | 0.57187 | 0.14651 | -0.57102 | -0.14597 | 0.00085078 | 0.00054347 | 0.85208 | 0.85208 | 0.85208 | 1 | 0 | 0.99838 | -0.03075 | 46.8177
19 | 0.13649 | 0.034597 | -0.13631 | -0.034477 | 0.00018667 | 0.00011932 | 0.20357 | 0.20357 | 0.20357 | 0.99838 | -0.03075 | 0.99688 | -0.059253 | 55.9259
20 | 0.43453 | 0.11137 | -0.43367 | -0.11083 | 0.00085436 | 0.00054502 | 0.64851 | 0.64851 | 0.64851 | 0.99838 | -0.03075 | 0.99623 | -0.071397 | 35.6325
21 | -0.025688 | -0.0064379 | 0.025702 | 0.0064469 | 1.4632e-05 | 9.0355e-06 | 0.038839 | 0.038839 | 0.038839 | 0.98415 | -0.30538 | 0.98476 | -0.29343 | 10.6701
22 | -0.025702 | -0.0064469 | 0.02571 | 0.0064521 | 8.286e-06 | 5.1166e-06 | 0.038839 | 0.038839 | 0.038839 | 0.98476 | -0.29343 | 0.98511 | -0.28667 | 10.6701
23 | -0.012684 | -0.0031789 | 0.012689 | 0.0031819 | 5.5962e-06 | 3.0607e-06 | 0.019132 | 0.019131 | 0.019132 | 0.98652 | -0.2592 | 0.987 | -0.24994 | 5.2559
24 | -0.012689 | -0.0031819 | 0.012692 | 0.0031831 | 2.1096e-06 | 1.1537e-06 | 0.019131 | 0.019131 | 0.019131 | 0.987 | -0.24994 | 0.98718 | -0.24646 | 5.2559
25 | -0.22039 | -0.055904 | 0.22068 | 0.056084 | 0.00028513 | 0.00018031 | 0.3336 | 0.3336 | 0.3336 | 0.98375 | -0.31047 | 0.98514 | -0.2836 | 18.3299
26 | 0.0013422 | 0.00033622 | -0.0013422 | -0.00033639 | 2.328e-08 | -1.7414e-07 | 0.002036 | 0.0020361 | 0.0020361 | 0.98093 | -0.36518 | 0.98091 | -0.36555 | 0.55937
27 | 0.037521 | 0.0094661 | -0.0374 | -0.0093897 | 0.00012134 | 7.6402e-05 | 0.05694 | 0.05694 | 0.05694 | 0.98093 | -0.36518 | 0.97747 | -0.43296 | 15.6429
28 | -0.0013424 | -0.00033644 | 0.0013424 | 0.00033626 | 2.3332e-08 | -1.7857e-07 | 0.0020255 | 0.0020255 | 0.0020255 | 0.98618 | -0.26349 | 0.9862 | -0.26312 | 0.55647
29 | -0.23178 | -0.058954 | 0.23192 | 0.059043 | 0.00014175 | 8.9736e-05 | 0.35003 | 0.35003 | 0.35003 | 0.9862 | -0.26312 | 0.98686 | -0.25044 | 19.2325
30 | 0.23044 | 0.058617 | -0.23026 | -0.058502 | 0.00018252 | 0.00011553 | 0.34801 | 0.34801 | 0.34801 | 0.9862 | -0.26312 | 0.98534 | -0.27957 | 19.1212
31 | 0.0374 | 0.0093897 | -0.037389 | -0.0093829 | 1.0807e-05 | 6.8049e-06 | 0.05694 | 0.05694 | 0.05694 | 0.97747 | -0.43296 | 0.97716 | -0.43902 | 15.6429
32 | 0.035867 | 0.0090016 | -0.035842 | -0.0089857 | 2.5247e-05 | 1.5876e-05 | 0.054623 | 0.054623 | 0.054623 | 0.97716 | -0.43902 | 0.97641 | -0.45379 | 15.0064
33 | -0.0029978 | -0.00075114 | 0.002998 | 0.00075092 | 2.1849e-07 | -2.2178e-07 | 0.0045288 | 0.0045286 | 0.0045288 | 0.98497 | -0.28682 | 0.98505 | -0.28529 | 1.2442
34 | 0.0029978 | 0.00075114 | -0.0029976 | -0.00075128 | 1.3587e-07 | -1.3788e-07 | 0.0045288 | 0.0045288 | 0.0045288 | 0.98497 | -0.28682 | 0.98492 | -0.28777 | 1.2442
35 | -0.0063253 | -0.0015848 | 0.0063258 | 0.001585 | 5.1e-07 | 1.3675e-07 | 0.0095548 | 0.0095547 | 0.0095548 | 0.98505 | -0.28529 | 0.98514 | -0.2836 | 2.6249
36 | -0.25738 | -0.065659 | 0.25768 | 0.065849 | 0.00029877 | 0.00018951 | 0.38743 | 0.38742 | 0.38743 | 0.98959 | -0.19787 | 0.99085 | -0.17386 | 21.2871
37 | 0.25738 | 0.065659 | -0.25731 | -0.065612 | 7.3769e-05 | 4.6791e-05 | 0.38743 | 0.38743 | 0.38743 | 0.98959 | -0.19787 | 0.98928 | -0.20381 | 21.2871
38 | -0.27755 | -0.070828 | 0.27757 | 0.070846 | 2.8928e-05 | 1.8371e-05 | 0.41726 | 0.41726 | 0.41726 | 0.99085 | -0.17386 | 0.99096 | -0.17171 | 22.9264
39 | 0.24652 | 0.062909 | -0.24625 | -0.062741 | 0.00026505 | 0.00016799 | 0.3712 | 0.3712 | 0.3712 | 0.98928 | -0.20381 | 0.98812 | -0.22609 | 20.3957
40 | -0.227 | -0.057669 | 0.22705 | 0.057697 | 4.4001e-05 | 2.7843e-05 | 0.34316 | 0.34316 | 0.34316 | 0.98514 | -0.2836 | 0.98534 | -0.27957 | 18.8549
41 | -0.27757 | -0.070846 | 0.27793 | 0.071071 | 0.00035424 | 0.00022497 | 0.41726 | 0.41726 | 0.41726 | 0.99096 | -0.17171 | 0.99234 | -0.14533 | 22.9263
42 | -0.2902 | -0.074148 | 0.29042 | 0.074283 | 0.00021317 | 0.00013546 | 0.43567 | 0.43567 | 0.43567 | 0.99234 | -0.14533 | 0.99314 | -0.13015 | 23.9377
43 | -0.003589 | -0.00089949 | 0.0035891 | 0.00089945 | 7.6635e-08 | -4.1648e-08 | 0.0053886 | 0.0053886 | 0.0053886 | 0.99108 | -0.17053 | 0.9911 | -0.17008 | 1.4804
44 | -0.0035891 | -0.00089945 | 0.0035892 | 0.0008994 | 1.0708e-07 | -5.8203e-08 | 0.0053886 | 0.0053885 | 0.0053886 | 0.9911 | -0.17008 | 0.99113 | -0.16946 | 1.4804
45 | 0.23485 | 0.059882 | -0.23457 | -0.059707 | 0.00027572 | 0.00017459 | 0.35402 | 0.35403 | 0.35403 | 0.98812 | -0.22609 | 0.98686 | -0.25044 | 19.4519
46 | 0.011406 | 0.0028591 | -0.011405 | -0.0028583 | 1.6057e-06 | 8.4177e-07 | 0.017177 | 0.017177 | 0.017177 | 0.98812 | -0.22609 | 0.98797 | -0.22904 | 4.7189
47 | 0.033042 | 0.0082842 | -0.033036 | -0.0082806 | 5.6596e-06 | 3.5477e-06 | 0.050355 | 0.050356 | 0.050356 | 0.97641 | -0.45379 | 0.97622 | -0.45738 | 13.8339
48 | 0.0028005 | 0.00070152 | -0.0028002 | -0.00070181 | 2.4206e-07 | -2.883e-07 | 0.0042677 | 0.0042679 | 0.0042679 | 0.97641 | -0.45379 | 0.97632 | -0.4556 | 1.1725
49 | 0.002649 | 0.00066377 | -0.0026489 | -0.00066387 | 6.9399e-08 | -1.0379e-07 | 0.0039941 | 0.0039942 | 0.0039942 | 0.98686 | -0.25044 | 0.98683 | -0.25099 | 1.0973
50 | 0.0021536 | 0.00053769 | -0.002153 | -0.0005392 | 6.1901e-07 | -1.5189e-06 | 0.003282 | 0.0032827 | 0.0032827 | 0.97622 | -0.45738 | 0.97592 | -0.46343 | 0.90183
51 | 0.030882 | 0.0077429 | -0.030874 | -0.0077377 | 8.3325e-06 | 5.2074e-06 | 0.047074 | 0.047074 | 0.047074 | 0.97622 | -0.45738 | 0.97594 | -0.46305 | 12.9323
52 | 0.002153 | 0.0005392 | -0.0021529 | -0.00053956 | 1.4645e-07 | -3.5906e-07 | 0.0032827 | 0.0032828 | 0.0032828 | 0.97592 | -0.46343 | 0.97585 | -0.46486 | 0.90187
53 | 0.12747 | 0.032264 | -0.12723 | -0.032112 | 0.00023724 | 0.0001516 | 0.19039 | 0.19039 | 0.19039 | 0.99688 | -0.059253 | 0.99486 | -0.098104 | 52.3036
54 | 0.11604 | 0.029387 | -0.11586 | -0.029267 | 0.00018842 | 0.00012037 | 0.17344 | 0.17344 | 0.17344 | 0.99623 | -0.071397 | 0.99447 | -0.10527 | 47.6475
55 | 0.31763 | 0.081439 | -0.31729 | -0.081225 | 0.000337 | 0.00021439 | 0.47508 | 0.47508 | 0.47508 | 0.99623 | -0.071397 | 0.99508 | -0.093304 | 26.1031
56 | -0.30066 | -0.076851 | 0.30119 | 0.077189 | 0.00053128 | 0.00033776 | 0.451 | 0.451 | 0.451 | 0.99316 | -0.12976 | 0.99508 | -0.093304 | 24.7801
57 | 0.29042 | 0.074286 | -0.29042 | -0.074283 | 5.441e-06 | 3.4575e-06 | 0.43567 | 0.43567 | 0.43567 | 0.99316 | -0.12976 | 0.99314 | -0.13015 | 23.9376
58 | 0.095162 | 0.024081 | -0.09492 | -0.023926 | 0.00024224 | 0.00015462 | 0.14247 | 0.14247 | 0.14247 | 0.99447 | -0.10527 | 0.9917 | -0.15846 | 39.1408
59 | 0.077925 | 0.019663 | -0.077717 | -0.019531 | 0.00020835 | 0.00013282 | 0.11697 | 0.11697 | 0.11697 | 0.9917 | -0.15846 | 0.98881 | -0.21445 | 32.1352
60 | 0.016994 | 0.0042626 | -0.016989 | -0.0042598 | 4.7508e-06 | 2.7892e-06 | 0.025501 | 0.025501 | 0.025501 | 0.9917 | -0.15846 | 0.9914 | -0.16432 | 7.0057
61 | 0.12403 | 0.031308 | -0.12393 | -0.031249 | 9.2682e-05 | 5.9224e-05 | 0.18559 | 0.18559 | 0.18559 | 0.99486 | -0.098104 | 0.99405 | -0.11372 | 50.9853
62 | 0.071464 | 0.017963 | -0.07138 | -0.01791 | 8.3543e-05 | 5.3221e-05 | 0.10756 | 0.10756 | 0.10756 | 0.98881 | -0.21445 | 0.98754 | -0.23897 | 29.5501
63 | 0.012451 | 0.0031224 | -0.012448 | -0.0031207 | 3.0452e-06 | 1.6492e-06 | 0.018689 | 0.018689 | 0.018689 | 0.9914 | -0.16432 | 0.99113 | -0.16946 | 5.1344
64 | -0.0088534 | -0.0022189 | 0.008859 | 0.0022213 | 5.535e-06 | 2.4679e-06 | 0.013301 | 0.013301 | 0.013301 | 0.99046 | -0.18257 | 0.99113 | -0.16946 | 3.6541
65 | -0.052328 | -0.01318 | 0.052339 | 0.013187 | 1.1759e-05 | 7.4607e-06 | 0.078728 | 0.078728 | 0.078728 | 0.98932 | -0.20479 | 0.98957 | -0.20009 | 21.6285
66 | 0.050123 | 0.012627 | -0.050098 | -0.012611 | 2.4979e-05 | 1.5836e-05 | 0.075412 | 0.075412 | 0.075412 | 0.98932 | -0.20479 | 0.98879 | -0.21521 | 20.7175
67 | -0.05661 | -0.014258 | 0.056641 | 0.014278 | 3.1394e-05 | 1.9944e-05 | 0.08515 | 0.08515 | 0.08515 | 0.98957 | -0.20009 | 0.99017 | -0.1885 | 23.3927
68 | 0.042786 | 0.010778 | -0.042722 | -0.010738 | 6.3829e-05 | 4.0325e-05 | 0.064407 | 0.064408 | 0.064408 | 0.98879 | -0.21521 | 0.98718 | -0.24646 | 17.6944
69 | 0.0073121 | 0.0018332 | -0.0073079 | -0.0018317 | 4.201e-06 | 1.5028e-06 | 0.011004 | 0.011005 | 0.011005 | 0.98879 | -0.21521 | 0.98817 | -0.22728 | 3.0232
70 | -0.059526 | -0.015001 | 0.059531 | 0.015003 | 4.423e-06 | 2.8118e-06 | 0.089485 | 0.089485 | 0.089485 | 0.99017 | -0.1885 | 0.99025 | -0.18695 | 24.5838
71 | 0.03003 | 0.0075549 | -0.029995 | -0.0075328 | 3.5415e-05 | 2.2077e-05 | 0.045276 | 0.045277 | 0.045277 | 0.98718 | -0.24646 | 0.9859 | -0.27117 | 12.4386
72 | 0.0073079 | 0.0018317 | -0.0073067 | -0.0018312 | 1.1924e-06 | 4.2682e-07 | 0.011005 | 0.011005 | 0.011005 | 0.98817 | -0.22728 | 0.98799 | -0.2307 | 3.0233
73 | -0.063098 | -0.015898 | 0.063154 | 0.015933 | 5.5592e-05 | 3.5367e-05 | 0.094846 | 0.094846 | 0.094846 | 0.99025 | -0.18695 | 0.9912 | -0.16855 | 26.0565
74 | 0.02573 | 0.0064638 | -0.02571 | -0.0064521 | 1.9022e-05 | 1.1746e-05 | 0.038839 | 0.038839 | 0.038839 | 0.9859 | -0.27117 | 0.98511 | -0.28667 | 10.67
75 | -0.011209 | -0.0028092 | 0.011214 | 0.0028118 | 5.053e-06 | 2.6348e-06 | 0.016928 | 0.016928 | 0.016928 | 0.98527 | -0.28332 | 0.98575 | -0.27386 | 4.6507
76 | -0.011214 | -0.0028118 | 0.011216 | 0.0028131 | 2.4195e-06 | 1.2614e-06 | 0.016928 | 0.016928 | 0.016928 | 0.98575 | -0.27386 | 0.98598 | -0.26933 | 4.6506
77 | -0.066034 | -0.016655 | 0.066102 | 0.016698 | 6.7879e-05 | 4.3205e-05 | 0.09917 | 0.09917 | 0.09917 | 0.9912 | -0.16855 | 0.99231 | -0.1471 | 27.2445
78 | -0.023798 | -0.0059664 | 0.023811 | 0.0059744 | 1.3023e-05 | 7.9913e-06 | 0.035916 | 0.035916 | 0.035916 | 0.98598 | -0.26933 | 0.98657 | -0.25786 | 9.8671
79 | 0.12065 | 0.030426 | -0.12057 | -0.030373 | 8.1771e-05 | 5.2247e-05 | 0.18067 | 0.18067 | 0.18067 | 0.99405 | -0.11372 | 0.99331 | -0.12789 | 49.6348
80 | 0.074445 | 0.018814 | -0.07444 | -0.018811 | 4.195e-06 | 2.6732e-06 | 0.11158 | 0.11158 | 0.11158 | 0.99331 | -0.12789 | 0.99325 | -0.12906 | 30.6528
81 | 0.071178 | 0.017993 | -0.071145 | -0.017973 | 3.23e-05 | 2.0574e-05 | 0.10669 | 0.10669 | 0.10669 | 0.99325 | -0.12906 | 0.99276 | -0.13853 | 29.3099
82 | 0.067873 | 0.017153 | -0.067845 | -0.017135 | 2.7863e-05 | 1.774e-05 | 0.10178 | 0.10178 | 0.10178 | 0.99276 | -0.13853 | 0.99231 | -0.1471 | 27.9625
83 | 0.040561 | 0.010186 | -0.040524 | -0.010163 | 3.6525e-05 | 2.3043e-05 | 0.061124 | 0.061124 | 0.061124 | 0.98754 | -0.23897 | 0.98657 | -0.25786 | 16.7923

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57352 | 0.14651

## res_load
| p_mw | q_mvar
0 | 0.040917 | 0.010255
1 | 0.0070361 | 0.0017634
2 | 0.080182 | 0.020096
3 | 0.012099 | 0.0030323
4 | 0.0081258 | 0.0020365
5 | 0.020247 | 0.0050745
6 | 0.0031152 | 0.00078075
7 | 0.025688 | 0.0064379
8 | 0.012684 | 0.0031789
9 | 0.008199 | 0.0020549
10 | 0.0013424 | 0.00033644
11 | 0.0015216 | 0.00038134
12 | 0.0033273 | 0.00083389
13 | 0.0029976 | 0.00075128
14 | 0.019867 | 0.0049791
15 | 0.010787 | 0.0027034
16 | 0.0013422 | 0.00033639
17 | 0.012275 | 0.0030765
18 | 0.003589 | 0.00089949
19 | 0.0032106 | 0.00080466
20 | 0.0028002 | 0.00070181
21 | 0.030874 | 0.0077377
22 | 0.0021529 | 0.00053956
23 | 0.0088334 | 0.0022139
24 | 0.0026489 | 0.00066387
25 | 0.010233 | 0.0025647
26 | 0.016103 | 0.0040358
27 | 0.020694 | 0.0051864
28 | 0.011405 | 0.0028583
29 | 0.0032085 | 0.00080412
30 | 0.006253 | 0.0015672
31 | 0.0045383 | 0.0011374
32 | 0.0088534 | 0.0022189
33 | 0.0022049 | 0.00055259
34 | 0.0042707 | 0.0010703
35 | 0.0028849 | 0.00072302
36 | 0.0035676 | 0.00089413
37 | 0.0042654 | 0.001069
38 | 0.011209 | 0.0028092
39 | 0.0073067 | 0.0018312
40 | 0.0028805 | 0.00072192
41 | 0.012582 | 0.0031533
42 | 0.0032839 | 0.00082301
43 | 0.046123 | 0.01156
44 | 0.0032629 | 0.00081777
45 | 0.0032721 | 0.00082008
46 | 0.0017429 | 0.00043681
47 | 0.03082 | 0.0077241
48 | 0.016713 | 0.0041886

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1