## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1702-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1702-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1702-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1702-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1702-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1702-7_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1702-7_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1702-7_0_6_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_1702-7_0_6_node_66 | 0.4 | n |  | TRUE
9 | bus_LV_1702-7_0_6_node_79 | 0.4 | n |  | TRUE
10 | bus_LV_1702-7_0_6_node_80 | 0.4 | n |  | TRUE
11 | bus_LV_1702-7_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1702-7_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1702-7_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1702-7_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1702-7_0_6_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_1702-7_0_6_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_1702-7_0_6_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_1702-7_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1702-7_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1702-7_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1702-7_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1702-7_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1702-7_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1702-7_0_6_node_110 | 0.4 | n |  | TRUE
25 | bus_LV_1702-7_0_6_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1702-7_0_6_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1702-7_0_6_node_111 | 0.4 | n |  | TRUE
28 | bus_LV_1702-7_0_6_node_95 | 0.4 | n |  | TRUE
29 | bus_LV_1702-7_0_6_node_104 | 0.4 | n |  | TRUE
30 | bus_LV_1702-7_0_6_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1702-7_0_6_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1702-7_0_6_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1702-7_0_6_node_58 | 0.4 | n |  | TRUE
34 | bus_LV_1702-7_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1702-7_0_6_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1702-7_0_6_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1702-7_0_6_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1702-7_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1702-7_0_6_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1702-7_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1702-7_0_6_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_1702-7_0_6_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1702-7_0_6_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_1702-7_0_6_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_1702-7_0_6_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1702-7_0_6_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1702-7_0_6_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1702-7_0_6_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1702-7_0_6_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_1702-7_0_6_node_59 | 0.4 | n |  | TRUE
51 | bus_LV_1702-7_0_6_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1702-7_0_6_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1702-7_0_6_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1702-7_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_1702-7_0_6_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_1702-7_0_6_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_1702-7_0_6_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_1702-7_0_6_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_1702-7_0_6_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1702-7_0_6_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_1702-7_0_6_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1702-7_0_6_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_1702-7_0_6_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_1702-7_0_6_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1702-7_0_6_node_128 | 0.4 | n |  | TRUE
66 | bus_LV_1702-7_0_6_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_1702-7_0_6_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_1702-7_0_6_node_120 | 0.4 | n |  | TRUE
69 | bus_LV_1702-7_0_6_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_1702-7_0_6_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_1702-7_0_6_node_129 | 0.4 | n |  | TRUE
72 | bus_LV_1702-7_0_6_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1702-7_0_6_node_118 | 0.4 | n |  | TRUE
74 | bus_LV_1702-7_0_6_node_117 | 0.4 | n |  | TRUE
75 | bus_LV_1702-7_0_6_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_1702-7_0_6_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_1702-7_0_6_node_125 | 0.4 | n |  | TRUE
78 | bus_LV_1702-7_0_6_node_99 | 0.4 | n |  | TRUE
79 | bus_LV_1702-7_0_6_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_1702-7_0_6_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_1702-7_0_6_node_56 | 0.4 | n |  | TRUE
82 | bus_LV_1702-7_0_6_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_1702-7_0_6_node_122 | 0.4 | n |  | TRUE
84 | bus_LV_1702-7_0_6_node_89 | 0.4 | n |  | TRUE
85 | bus_LV_1702-7_0_6_node_113 | 0.4 | n |  | TRUE
86 | bus_LV_1702-7_0_6_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_1702-7_0_6_node_98 | 0.4 | n |  | TRUE
88 | bus_LV_1702-7_0_6_node_121 | 0.4 | n |  | TRUE
89 | bus_LV_1702-7_0_6_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_1702-7_0_6_node_112 | 0.4 | n |  | TRUE
91 | bus_LV_1702-7_0_6_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_1702-7_0_6_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_1702-7_0_6_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_1702-7_0_6_node_68 | 0.4 | n |  | TRUE
95 | bus_LV_1702-7_0_6_node_69 | 0.4 | n |  | TRUE
96 | bus_LV_1702-7_0_6_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1702-7_0_6_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_1702-7_0_6_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_1702-7_0_6_node_109 | 0.4 | n |  | TRUE
100 | bus_LV_1702-7_0_6_node_124 | 0.4 | n |  | TRUE
101 | bus_LV_1702-7_0_6_node_123 | 0.4 | n |  | TRUE
102 | bus_LV_1702-7_0_6_node_108 | 0.4 | n |  | TRUE
103 | bus_LV_1702-7_0_6_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_1702-7_0_6_node_106 | 0.4 | n |  | TRUE
105 | bus_LV_1702-7_0_6_node_119 | 0.4 | n |  | TRUE
106 | bus_LV_1702-7_0_6_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_1702-7_0_6_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_1702-7_0_6_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_1702-7_0_6_node_74 | 0.4 | n |  | TRUE
110 | bus_LV_1702-7_0_6_node_75 | 0.4 | n |  | TRUE
111 | bus_LV_1702-7_0_6_node_76 | 0.4 | n |  | TRUE
112 | bus_LV_1702-7_0_6_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_1702-7_0_6_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_1702-7_0_6_node_86 | 0.4 | n |  | TRUE
115 | bus_LV_1702-7_0_6_node_82 | 0.4 | n |  | TRUE
116 | bus_LV_1702-7_0_6_node_81 | 0.4 | n |  | TRUE
117 | bus_LV_1702-7_0_6_node_85 | 0.4 | n |  | TRUE
118 | bus_LV_1702-7_0_6_node_96 | 0.4 | n |  | TRUE
119 | bus_LV_1702-7_0_6_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_1702-7_0_6_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_1702-7_0_6_node_92 | 0.4 | n |  | TRUE
122 | bus_LV_1702-7_0_6_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_1702-7_0_6_node_88 | 0.4 | n |  | TRUE
124 | bus_LV_1702-7_0_6_node_90 | 0.4 | n |  | TRUE
125 | bus_LV_1702-7_0_6_node_91 | 0.4 | n |  | TRUE
126 | bus_LV_1702-7_0_6_node_93 | 0.4 | n |  | TRUE
127 | bus_LV_1702-7_0_6_node_102 | 0.4 | n |  | TRUE
128 | bus_MV_232_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1702-7_0_6_load_0 | 0 | 0.0032063 | 0.00080357 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1702-7_0_6_load_1 | 1 | 0.0055588 | 0.0013932 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1702-7_0_6_load_2 | 2 | 0.0026459 | 0.00066313 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1702-7_0_6_load_3 | 3 | 0.0036506 | 0.00091494 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1702-7_0_6_load_4 | 4 | 0.0026202 | 0.00065668 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1702-7_0_6_load_5 | 5 | 0.0042252 | 0.0010589 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1702-7_0_6_load_6 | 6 | 0.00070204 | 0.00017595 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1702-7_0_6_load_67 | 7 | 0.0037428 | 0.00093802 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1702-7_0_6_load_66 | 8 | 0.0038802 | 0.00097247 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1702-7_0_6_load_79 | 9 | 0.003607 | 0.00090399 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1702-7_0_6_load_80 | 10 | 0.0048275 | 0.0012099 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1702-7_0_6_load_7 | 11 | 0.013861 | 0.0034739 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1702-7_0_6_load_8 | 12 | 0.013966 | 0.0035001 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1702-7_0_6_load_9 | 13 | 0.0017246 | 0.00043222 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1702-7_0_6_load_10 | 14 | 0.014228 | 0.0035658 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1702-7_0_6_load_11 | 18 | 0.0061926 | 0.001552 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1702-7_0_6_load_12 | 19 | 0.0080279 | 0.002012 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1702-7_0_6_load_13 | 20 | 0.0038537 | 0.00096582 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1702-7_0_6_load_14 | 21 | 0.0066292 | 0.0016614 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1702-7_0_6_load_110 | 24 | 0.0093899 | 0.0023533 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1702-7_0_6_load_18 | 25 | 0.0084382 | 0.0021148 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1702-7_0_6_load_40 | 26 | 0.006514 | 0.0016326 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1702-7_0_6_load_111 | 27 | 0.0076316 | 0.0019127 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1702-7_0_6_load_104 | 29 | 0.0028552 | 0.00071559 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1702-7_0_6_load_17 | 30 | 0.0073215 | 0.001835 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1702-7_0_6_load_19 | 31 | 0.0074871 | 0.0018764 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1702-7_0_6_load_20 | 32 | 0.0063904 | 0.0016016 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1702-7_0_6_load_58 | 33 | 0.0074484 | 0.0018668 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1702-7_0_6_load_24 | 34 | 0.0036695 | 0.00091966 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1702-7_0_6_load_21 | 35 | 0.0033116 | 0.00082996 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1702-7_0_6_load_22 | 36 | 0.0027287 | 0.00068388 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1702-7_0_6_load_25 | 38 | 0.004677 | 0.0011722 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1702-7_0_6_load_26 | 39 | 0.0052368 | 0.0013125 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1702-7_0_6_load_32 | 40 | 0.0030107 | 0.00075456 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1702-7_0_6_load_73 | 41 | 0.0049515 | 0.001241 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1702-7_0_6_load_33 | 42 | 0.002915 | 0.00073057 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1702-7_0_6_load_72 | 43 | 0.0026366 | 0.0006608 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1702-7_0_6_load_27 | 44 | 0.0033113 | 0.0008299 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1702-7_0_6_load_28 | 45 | 0.0016603 | 0.00041611 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1702-7_0_6_load_29 | 46 | 0.0070508 | 0.0017671 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1702-7_0_6_load_30 | 47 | 0.0023801 | 0.0005965 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1702-7_0_6_load_31 | 48 | 0.003521 | 0.00088245 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1702-7_0_6_load_38 | 49 | 0.0030249 | 0.00075812 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1702-7_0_6_load_59 | 50 | 0.0027831 | 0.0006975 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1702-7_0_6_load_36 | 51 | 0.0027051 | 0.00067797 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1702-7_0_6_load_62 | 52 | 0.0030098 | 0.00075432 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1702-7_0_6_load_34 | 53 | 0.0047402 | 0.001188 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1702-7_0_6_load_71 | 55 | 0.0061915 | 0.0015517 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1702-7_0_6_load_37 | 56 | 0.003618 | 0.00090675 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1702-7_0_6_load_35 | 57 | 0.0036985 | 0.00092694 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1702-7_0_6_load_42 | 59 | 0.0064278 | 0.001611 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1702-7_0_6_load_61 | 60 | 0.0033193 | 0.00083189 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1702-7_0_6_load_126 | 62 | 0.011321 | 0.0028373 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1702-7_0_6_load_128 | 65 | 0.011468 | 0.002874 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1702-7_0_6_load_120 | 68 | 0.0041951 | 0.0010514 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1702-7_0_6_load_65 | 70 | 0.012013 | 0.0030108 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1702-7_0_6_load_129 | 71 | 0.011591 | 0.002905 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1702-7_0_6_load_118 | 73 | 0.015211 | 0.0038124 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1702-7_0_6_load_117 | 74 | 0.0077463 | 0.0019414 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1702-7_0_6_load_97 | 76 | 0.0046622 | 0.0011685 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1702-7_0_6_load_125 | 77 | 0.010217 | 0.0025605 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1702-7_0_6_load_127 | 80 | 0.008945 | 0.0022418 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1702-7_0_6_load_64 | 82 | 0.08097 | 0.020293 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1702-7_0_6_load_122 | 83 | 0.0029291 | 0.0007341 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1702-7_0_6_load_89 | 84 | 0.0034045 | 0.00085326 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1702-7_0_6_load_113 | 85 | 0.0039838 | 0.00099844 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1702-7_0_6_load_60 | 86 | 0.0036245 | 0.00090839 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1702-7_0_6_load_98 | 87 | 0.0016074 | 0.00040285 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1702-7_0_6_load_121 | 88 | 0.0047185 | 0.0011826 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1702-7_0_6_load_114 | 89 | 0.013643 | 0.0034191 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1702-7_0_6_load_112 | 90 | 0.032439 | 0.0081299 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1702-7_0_6_load_63 | 92 | 0.01132 | 0.002837 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1702-7_0_6_load_87 | 93 | 0.0030975 | 0.00077631 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1702-7_0_6_load_69 | 95 | 0.0035258 | 0.00088366 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1702-7_0_6_load_77 | 97 | 0.0034454 | 0.00086349 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1702-7_0_6_load_124 | 100 | 0.015055 | 0.0037731 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1702-7_0_6_load_123 | 101 | 0.0064533 | 0.0016174 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1702-7_0_6_load_119 | 105 | 0.00031855 | 7.9835e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1702-7_0_6_load_105 | 107 | 0.0019966 | 0.00050039 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1702-7_0_6_load_101 | 108 | 0.0035262 | 0.00088374 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1702-7_0_6_load_74 | 109 | 0.0029268 | 0.00073353 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1702-7_0_6_load_75 | 110 | 0.0028318 | 0.00070973 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1702-7_0_6_load_78 | 112 | 0.0024033 | 0.00060231 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1702-7_0_6_load_100 | 113 | 0.0034722 | 0.00087021 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1702-7_0_6_load_82 | 115 | 0.0041711 | 0.0010454 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1702-7_0_6_load_81 | 116 | 0.0034782 | 0.00087173 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1702-7_0_6_load_96 | 118 | 0.0030274 | 0.00075874 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1702-7_0_6_load_94 | 119 | 0.0064298 | 0.0016115 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1702-7_0_6_load_115 | 120 | 0.0066132 | 0.0016574 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1702-7_0_6_load_116 | 122 | 0.0042511 | 0.0010654 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1702-7_0_6_load_88 | 123 | 0.0034724 | 0.00087028 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1702-7_0_6_load_90 | 124 | 0.0029979 | 0.00075135 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1702-7_0_6_load_91 | 125 | 0.003678 | 0.00092179 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1702-7_0_6_load_93 | 126 | 0.001598 | 0.00040051 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1702-7_0_6_load_102 | 127 | 0.0038936 | 0.00097582 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1702-7_0_6_line_0 |  | 0 | 1 | 0.01693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1702-7_0_6_line_1 |  | 0 | 2 | 0.011654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1702-7_0_6_line_2 |  | 1 | 3 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1702-7_0_6_line_3 |  | 2 | 4 | 0.0078267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1702-7_0_6_line_4 |  | 3 | 5 | 0.0001926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1702-7_0_6_line_5 |  | 4 | 6 | 0.0098946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1702-7_0_6_line_6 |  | 5 | 7 | 0.02206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1702-7_0_6_line_7 |  | 7 | 8 | 0.0017154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1702-7_0_6_line_8 |  | 8 | 94 | 0.013745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1702-7_0_6_line_9 |  | 9 | 10 | 0.0028363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1702-7_0_6_line_10 |  | 10 | 115 | 0.022674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1702-7_0_6_line_11 |  | 11 | 12 | 0.029869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1702-7_0_6_line_12 |  | 11 | 13 | 0.024683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1702-7_0_6_line_13 |  | 12 | 14 | 0.030205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1702-7_0_6_line_14 |  | 14 | 15 | 0.089686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1702-7_0_6_line_15 |  | 15 | 16 | 0.022913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1702-7_0_6_line_16 |  | 15 | 17 | 0.32093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_1702-7_0_6_line_17 |  | 16 | 64 | 0.05281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1702-7_0_6_line_18 |  | 16 | 65 | 0.006316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1702-7_0_6_line_19 |  | 17 | 82 | 0.032886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1702-7_0_6_line_20 |  | 17 | 69 | 0.18776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1702-7_0_6_line_21 |  | 18 | 19 | 0.020787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1702-7_0_6_line_22 |  | 18 | 20 | 0.0041032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1702-7_0_6_line_23 |  | 19 | 21 | 0.0073395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1702-7_0_6_line_24 |  | 20 | 22 | 0.021132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1702-7_0_6_line_25 |  | 21 | 23 | 0.0087703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1702-7_0_6_line_26 |  | 22 | 24 | 0.017137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1702-7_0_6_line_27 |  | 23 | 25 | 0.019601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1702-7_0_6_line_28 |  | 23 | 26 | 0.019206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1702-7_0_6_line_29 |  | 24 | 29 | 0.024693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1702-7_0_6_line_30 |  | 25 | 30 | 0.017618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1702-7_0_6_line_31 |  | 27 | 28 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1702-7_0_6_line_32 |  | 28 | 122 | 0.023601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1702-7_0_6_line_33 |  | 28 | 121 | 0.005982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1702-7_0_6_line_34 |  | 29 | 127 | 0.027683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1702-7_0_6_line_35 |  | 30 | 31 | 0.013242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1702-7_0_6_line_36 |  | 31 | 32 | 0.01193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_1702-7_0_6_line_37 |  | 32 | 33 | 0.016765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1702-7_0_6_line_38 |  | 33 | 34 | 0.0043309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_1702-7_0_6_line_39 |  | 34 | 36 | 0.026005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1702-7_0_6_line_40 |  | 35 | 36 | 0.00083817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_1702-7_0_6_line_41 |  | 35 | 37 | 0.016395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_1702-7_0_6_line_42 |  | 37 | 38 | 0.021748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_1702-7_0_6_line_43 |  | 37 | 39 | 0.0037745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_1702-7_0_6_line_44 |  | 38 | 40 | 0.0076152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_1702-7_0_6_line_45 |  | 39 | 41 | 0.017287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1702-7_0_6_line_46 |  | 40 | 42 | 0.024412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_1702-7_0_6_line_47 |  | 41 | 43 | 0.012418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1702-7_0_6_line_48 |  | 42 | 53 | 0.0092517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_1702-7_0_6_line_49 |  | 43 | 109 | 0.0063619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1702-7_0_6_line_50 |  | 44 | 45 | 0.01538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1702-7_0_6_line_51 |  | 44 | 46 | 0.0032438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1702-7_0_6_line_52 |  | 45 | 47 | 0.001019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1702-7_0_6_line_53 |  | 46 | 48 | 0.015619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1702-7_0_6_line_54 |  | 47 | 49 | 0.015798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1702-7_0_6_line_55 |  | 48 | 50 | 0.0019981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1702-7_0_6_line_56 |  | 49 | 51 | 0.001617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1702-7_0_6_line_57 |  | 50 | 52 | 0.014404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1702-7_0_6_line_58 |  | 51 | 57 | 0.019224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1702-7_0_6_line_59 |  | 52 | 86 | 0.0072235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1702-7_0_6_line_60 |  | 53 | 54 | 0.0051961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1702-7_0_6_line_61 |  | 54 | 55 | 0.0233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1702-7_0_6_line_62 |  | 54 | 56 | 0.011207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1702-7_0_6_line_63 |  | 55 | 58 | 0.032132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1702-7_0_6_line_64 |  | 56 | 57 | 0.018816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1702-7_0_6_line_65 |  | 58 | 81 | 0.034167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1702-7_0_6_line_66 |  | 58 | 75 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1702-7_0_6_line_67 |  | 59 | 60 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1702-7_0_6_line_68 |  | 60 | 86 | 0.0092614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1702-7_0_6_line_69 |  | 61 | 62 | 0.011431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1702-7_0_6_line_70 |  | 61 | 63 | 0.055521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1702-7_0_6_line_71 |  | 63 | 77 | 0.005605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1702-7_0_6_line_72 |  | 63 | 78 | 0.057529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_1702-7_0_6_line_73 |  | 63 | 64 | 0.032522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_1702-7_0_6_line_74 |  | 64 | 71 | 0.006324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1702-7_0_6_line_75 |  | 66 | 67 | 0.027776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1702-7_0_6_line_76 |  | 66 | 68 | 0.035395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1702-7_0_6_line_77 |  | 67 | 85 | 0.029485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1702-7_0_6_line_78 |  | 68 | 88 | 0.0057945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1702-7_0_6_line_79 |  | 69 | 70 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1702-7_0_6_line_80 |  | 72 | 73 | 0.020713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1702-7_0_6_line_81 |  | 72 | 74 | 0.018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1702-7_0_6_line_82 |  | 73 | 89 | 0.035879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1702-7_0_6_line_83 |  | 74 | 91 | 0.013725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1702-7_0_6_line_84 |  | 75 | 76 | 0.0022147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_1702-7_0_6_line_85 |  | 76 | 87 | 0.014986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_1702-7_0_6_line_86 |  | 78 | 87 | 0.035496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1702-7_0_6_line_87 |  | 78 | 79 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1702-7_0_6_line_88 |  | 79 | 80 | 0.006654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1702-7_0_6_line_89 |  | 81 | 83 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1702-7_0_6_line_90 |  | 81 | 84 | 0.0085179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1702-7_0_6_line_91 |  | 82 | 92 | 0.025179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1702-7_0_6_line_92 |  | 84 | 93 | 0.015424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1702-7_0_6_line_93 |  | 85 | 90 | 0.0067967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1702-7_0_6_line_94 |  | 88 | 124 | 0.016791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1702-7_0_6_line_95 |  | 91 | 94 | 0.024512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1702-7_0_6_line_96 |  | 93 | 123 | 0.020361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1702-7_0_6_line_97 |  | 94 | 95 | 0.0042061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1702-7_0_6_line_98 |  | 95 | 96 | 0.017167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1702-7_0_6_line_99 |  | 96 | 97 | 0.010752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1702-7_0_6_line_100 |  | 96 | 98 | 0.014389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1702-7_0_6_line_101 |  | 97 | 111 | 0.023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1702-7_0_6_line_102 |  | 98 | 116 | 0.010027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1702-7_0_6_line_103 |  | 99 | 100 | 0.004122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1702-7_0_6_line_104 |  | 99 | 101 | 0.021522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1702-7_0_6_line_105 |  | 101 | 102 | 0.033036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1702-7_0_6_line_106 |  | 102 | 103 | 0.1038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1702-7_0_6_line_107 |  | 103 | 107 | 0.015517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1702-7_0_6_line_108 |  | 104 | 105 | 0.032911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1702-7_0_6_line_109 |  | 104 | 106 | 0.098109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1702-7_0_6_line_110 |  | 106 | 107 | 0.025145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1702-7_0_6_line_111 |  | 106 | 108 | 0.085219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1702-7_0_6_line_112 |  | 108 | 127 | 0.014495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1702-7_0_6_line_113 |  | 109 | 110 | 0.01792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1702-7_0_6_line_114 |  | 110 | 111 | 0.0049538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1702-7_0_6_line_115 |  | 111 | 112 | 0.013712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1702-7_0_6_line_116 |  | 112 | 113 | 0.0049962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1702-7_0_6_line_117 |  | 113 | 114 | 0.0093983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1702-7_0_6_line_118 |  | 114 | 120 | 0.011101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1702-7_0_6_line_119 |  | 115 | 116 | 0.0058748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1702-7_0_6_line_120 |  | 117 | 118 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1702-7_0_6_line_121 |  | 117 | 119 | 0.0073712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1702-7_0_6_line_122 |  | 119 | 121 | 0.009927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1702-7_0_6_line_123 |  | 120 | 122 | 0.016985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1702-7_0_6_line_124 |  | 121 | 125 | 0.01857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1702-7_0_6_line_125 |  | 123 | 124 | 0.0081982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1702-7_0_6_line_126 |  | 125 | 126 | 0.024588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1702-7_0_6_trafo_19 | 0.63 MVA 20/0.4 kV | 128 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2678035.4686 | 1226574.3134 | 2678032.8302 | 1226570.6995 | 2678033.4953 | 1226564.4929 | 2678038.65 | 1226561.0244
1 | 2678035.4686 | 1226574.3134 | 2678042.3405 | 1226583.7262
2 | 2678038.65 | 1226561.0244 | 2678057.636 | 1226548.2489
3 | 2678042.3405 | 1226583.7262 | 2678046.9554 | 1226590.0475
4 | 2678057.7958 | 1226548.1414 | 2678057.636 | 1226548.2489
5 | 2678054.5516 | 1226595.1786 | 2678054.5516 | 1226595.1786 | 2678050.1723 | 1226594.454 | 2678046.9554 | 1226590.0475
6 | 2678076.0984 | 1226535.8258 | 2678057.7958 | 1226548.1414
7 | 2678077.5216 | 1226534.8681 | 2678076.0984 | 1226535.8258
8 | 2678088.925 | 1226527.1949 | 2678077.5216 | 1226534.8681
9 | 2678080.3255 | 1226576.8481 | 2678078.0141 | 1226578.4919
10 | 2678080.3255 | 1226576.8481 | 2678098.8027 | 1226563.7071
11 | 2678245.8488 | 1226677.268 | 2678269.1138 | 1226658.5363
12 | 2678226.6226 | 1226692.7478 | 2678245.8488 | 1226677.268
13 | 2678292.6409 | 1226639.5937 | 2678269.1138 | 1226658.5363
14 | 2678354.0454 | 1226578.4249 | 2678354.5515 | 1226580.2884 | 2678353.882 | 1226586.228 | 2678352.0978 | 1226590.474 | 2678346.0824 | 1226596.5656 | 2678292.6409 | 1226639.5937
15 | 2678343.5023 | 1226558.8063 | 2678350.1069 | 1226565.5311 | 2678352.5999 | 1226573.0801 | 2678354.0454 | 1226578.4249
16 | 2678354.0454 | 1226578.4249 | 2678362.0969 | 1226577.1634 | 2678372.7055 | 1226573.9676 | 2678381.7041 | 1226567.5596 | 2678389.0839 | 1226566.645 | 2678453.3592 | 1226523.8076 | 2678454.3481 | 1226521.8193 | 2678450.005 | 1226506.852 | 2678443.9874 | 1226490.684 | 2678437.5569 | 1226475.9338 | 2678441.4787 | 1226473.9953 | 2678444.6337 | 1226480.7636 | 2678448.5879 | 1226488.432 | 2678458.6665 | 1226520.2641 | 2678464.6705 | 1226539.1782 | 2678469.6219 | 1226557.4446 | 2678471.8611 | 1226564.679 | 2678478.6003 | 1226583.5917 | 2678480.5589 | 1226589.6883 | 2678469.9645 | 1226594.6742 | 2678462.2636 | 1226598.6642 | 2678455.1874 | 1226601.8509
17 | 2678332.7865 | 1226512.0115 | 2678337.277 | 1226517.5299 | 2678338.8016 | 1226525.5109 | 2678336.9075 | 1226533.5024 | 2678334.6159 | 1226544.046 | 2678334.8364 | 1226550.898 | 2678340.3544 | 1226556.0963 | 2678343.5023 | 1226558.8063
18 | 2678346.3886 | 1226553.1849 | 2678343.5023 | 1226558.8063
19 | 2678455.1874 | 1226601.8509 | 2678430.7461 | 1226615.9049 | 2678426.9065 | 1226618.6022
20 | 2678435.2207 | 1226720.323 | 2678440.0283 | 1226719.597 | 2678450.0672 | 1226717.0609 | 2678466.4799 | 1226713.4304 | 2678476.4746 | 1226711.3719 | 2678493.7429 | 1226707.8195 | 2678494.4586 | 1226686.9037 | 2678494.2296 | 1226658.8819 | 2678494.1386 | 1226654.8668 | 2678488.0135 | 1226639.3979 | 2678483.3146 | 1226619.2446 | 2678478.6416 | 1226608.6091 | 2678476.0296 | 1226604.9277 | 2678469.133 | 1226601.9681 | 2678461.5662 | 1226601.5459 | 2678455.1874 | 1226601.8509
21 | 2678194.5783 | 1226616.3503 | 2678214.144 | 1226609.3304
22 | 2678194.5783 | 1226616.3503 | 2678190.7162 | 1226617.7359
23 | 2678221.0523 | 1226606.8518 | 2678214.144 | 1226609.3304
24 | 2678170.516 | 1226623.5752 | 2678176.5444 | 1226622.8205 | 2678190.7162 | 1226617.7359
25 | 2678229.3073 | 1226603.89 | 2678221.0523 | 1226606.8518
26 | 2678170.516 | 1226623.5752 | 2678166.989 | 1226628.9436 | 2678158.3947 | 1226635.3399
27 | 2678229.3073 | 1226603.89 | 2678223.6122 | 1226585.1345
28 | 2678229.3073 | 1226603.89 | 2678247.4753 | 1226597.6625
29 | 2678137.3493 | 1226646.4106 | 2678137.3493 | 1226646.4106 | 2678143.6036 | 1226646.3482 | 2678158.3947 | 1226635.3399
30 | 2678223.6122 | 1226585.1345 | 2678218.4933 | 1226568.2765
31 | 2678142.7418 | 1226594.2463 | 2678151.5056 | 1226605.6947
32 | 2678142.7418 | 1226594.2463 | 2678157.5091 | 1226583.7554 | 2678158.8982 | 1226581.8724 | 2678159.2123 | 1226578.741
33 | 2678142.7418 | 1226594.2463 | 2678139.0976 | 1226589.4953
34 | 2678137.3493 | 1226646.4106 | 2678128.8373 | 1226653.8928 | 2678124.8918 | 1226654.7749 | 2678120.3295 | 1226654.715 | 2678117.054 | 1226652.4816 | 2678113.9759 | 1226650.288
35 | 2678214.6458 | 1226555.6054 | 2678218.4933 | 1226568.2765
36 | 2678214.6458 | 1226555.6054 | 2678211.1796 | 1226544.1902
37 | 2678206.3084 | 1226528.1481 | 2678211.1796 | 1226544.1902
38 | 2678206.3084 | 1226528.1481 | 2678205.0501 | 1226524.004
39 | 2678194.5503 | 1226500.6564 | 2678198.7521 | 1226505.3333 | 2678201.6408 | 1226512.7763 | 2678205.0501 | 1226524.004
40 | 2678193.9902 | 1226500.0329 | 2678194.5503 | 1226500.6564
41 | 2678183.0335 | 1226487.8373 | 2678193.9902 | 1226500.0329
42 | 2678183.0335 | 1226487.8373 | 2678197.3459 | 1226471.4628
43 | 2678183.0335 | 1226487.8373 | 2678180.1458 | 1226490.2678
44 | 2678202.3575 | 1226465.7292 | 2678197.3459 | 1226471.4628
45 | 2678166.9197 | 1226501.4 | 2678180.1458 | 1226490.2678
46 | 2678202.3575 | 1226465.7292 | 2678218.4234 | 1226447.3486
47 | 2678157.419 | 1226509.3967 | 2678166.9197 | 1226501.4
48 | 2678224.512 | 1226440.3828 | 2678218.4234 | 1226447.3486
49 | 2678157.419 | 1226509.3967 | 2678152.5517 | 1226513.4934
50 | 2678257.4458 | 1226495.851 | 2678262.3195 | 1226510.4388
51 | 2678263.3474 | 1226513.5154 | 2678262.3195 | 1226510.4388
52 | 2678257.1229 | 1226494.8845 | 2678257.4458 | 1226495.851
53 | 2678263.3474 | 1226513.5154 | 2678268.2967 | 1226528.3294
54 | 2678257.1229 | 1226494.8845 | 2678252.1169 | 1226479.9009
55 | 2678268.9299 | 1226530.2246 | 2678268.2967 | 1226528.3294
56 | 2678251.6045 | 1226478.3673 | 2678252.1169 | 1226479.9009
57 | 2678268.9299 | 1226530.2246 | 2678273.4943 | 1226543.8865
58 | 2678245.5127 | 1226460.1337 | 2678251.6045 | 1226478.3673
59 | 2678275.7833 | 1226550.7378 | 2678273.4943 | 1226543.8865
60 | 2678227.9316 | 1226436.4705 | 2678224.512 | 1226440.3828
61 | 2678227.9316 | 1226436.4705 | 2678242.6284 | 1226418.3905
62 | 2678227.9316 | 1226436.4705 | 2678235.731 | 1226444.5181
63 | 2678262.8965 | 1226393.4568 | 2678242.6284 | 1226418.3905
64 | 2678245.5127 | 1226460.1337 | 2678244.8095 | 1226458.0291 | 2678242.0663 | 1226451.055 | 2678235.731 | 1226444.5181
65 | 2678252.6636 | 1226371.5297 | 2678270.8134 | 1226385.1553 | 2678262.8965 | 1226393.4568
66 | 2678262.8965 | 1226393.4568 | 2678271.9543 | 1226413.0891
67 | 2678282.2365 | 1226570.7974 | 2678278.6418 | 1226559.5468
68 | 2678275.7833 | 1226550.7378 | 2678276.7888 | 1226553.7473 | 2678278.6418 | 1226559.5468
69 | 2678309.4522 | 1226536.9768 | 2678307.7421 | 1226537.8993 | 2678304.5846 | 1226546.8527
70 | 2678304.5846 | 1226546.8527 | 2678299.8992 | 1226531.3807 | 2678293.3543 | 1226506.867 | 2678298.8521 | 1226505.5495 | 2678307.1158 | 1226506.5923
71 | 2678307.0911 | 1226500.9882 | 2678307.1158 | 1226506.5923
72 | 2678284.045 | 1226464.327 | 2678293.3543 | 1226506.867 | 2678298.8521 | 1226505.5495 | 2678307.1158 | 1226506.5923
73 | 2678307.1158 | 1226506.5923 | 2678318.6309 | 1226506.5215 | 2678324.9263 | 1226501.6233 | 2678328.8199 | 1226507.0004 | 2678332.7865 | 1226512.0115
74 | 2678336.5676 | 1226506.9356 | 2678332.7865 | 1226512.0115
75 | 2678158.7105 | 1226367.1589 | 2678165.8964 | 1226380.44 | 2678166.9906 | 1226388.8934 | 2678168.4097 | 1226392.8035
76 | 2678158.7105 | 1226367.1589 | 2678174.5708 | 1226367.5564 | 2678182.2899 | 1226370.2596 | 2678191.4059 | 1226377.0231
77 | 2678168.4097 | 1226392.8035 | 2678175.4579 | 1226396.9545 | 2678181.0978 | 1226404.4336 | 2678183.9235 | 1226411.4865 | 2678183.9155 | 1226415.8266
78 | 2678191.4059 | 1226377.0231 | 2678192.6946 | 1226377.9792 | 2678196.0958 | 1226380.4261
79 | 2678435.2207 | 1226720.323 | 2678428.6815 | 1226721.3042 | 2678425.7955 | 1226718.8645 | 2678423.9363 | 1226708.2297
80 | 2678099.9163 | 1226494.8507 | 2678103.5461 | 1226492.6302 | 2678108.5274 | 1226490.2273 | 2678119.0132 | 1226487.1517
81 | 2678099.9163 | 1226494.8507 | 2678095.9957 | 1226500.7588 | 2678091.2256 | 1226503.8093 | 2678085.2744 | 1226505.5292
82 | 2678119.0132 | 1226487.1517 | 2678130.6945 | 1226487.1272 | 2678140.0786 | 1226486.5612 | 2678146.1629 | 1226482.7163 | 2678151.5417 | 1226477.3485
83 | 2678072.0891 | 1226509.3398 | 2678085.2744 | 1226505.5292
84 | 2678271.9543 | 1226413.0891 | 2678272.6023 | 1226415.2069
85 | 2678272.6023 | 1226415.2069 | 2678276.7945 | 1226428.9078 | 2678276.9309 | 1226429.5518
86 | 2678284.045 | 1226464.327 | 2678280.0917 | 1226444.4728 | 2678276.9309 | 1226429.5518
87 | 2678300.6563 | 1226460.0538 | 2678294.7064 | 1226461.1651 | 2678284.045 | 1226464.327
88 | 2678298.5716 | 1226453.7332 | 2678300.6563 | 1226460.0538
89 | 2678236.6492 | 1226354.6078 | 2678250.9489 | 1226367.0375 | 2678252.6636 | 1226371.5297
90 | 2678252.6636 | 1226371.5297 | 2678247.0603 | 1226377.9452
91 | 2678406.3033 | 1226633.0764 | 2678426.9065 | 1226618.6022
92 | 2678236.9142 | 1226389.5619 | 2678247.0603 | 1226377.9452
93 | 2678183.903 | 1226422.6232 | 2678183.9155 | 1226415.8266
94 | 2678196.0958 | 1226380.4261 | 2678206.0761 | 1226387.606 | 2678210.483 | 1226388.4984
95 | 2678072.0891 | 1226509.3398 | 2678075.9357 | 1226513.6932 | 2678088.925 | 1226527.1949
96 | 2678236.9142 | 1226389.5619 | 2678233.731 | 1226393.2065 | 2678218.5182 | 1226390.1257
97 | 2678088.925 | 1226527.1949 | 2678091.8826 | 1226530.1855
98 | 2678103.9538 | 1226542.3912 | 2678091.8826 | 1226530.1855
99 | 2678103.9538 | 1226542.3912 | 2678113.7383 | 1226537.9334
100 | 2678103.9538 | 1226542.3912 | 2678111.7615 | 1226554.4907
101 | 2678135.0514 | 1226528.2232 | 2678113.7383 | 1226537.9334
102 | 2678111.7615 | 1226554.4907 | 2678103.5902 | 1226560.3022
103 | 2678010.8253 | 1226571.8674 | 2678014.742 | 1226573.1862
104 | 2678014.742 | 1226573.1862 | 2678007.8195 | 1226593.5648
105 | 2677978.9447 | 1226579.3101 | 2677980.7941 | 1226582.7922 | 2678007.8195 | 1226593.5648
106 | 2677978.9447 | 1226579.3101 | 2677967.7256 | 1226577.0505 | 2677966.0316 | 1226591.2045 | 2677961.3972 | 1226607.0544 | 2677958.4517 | 1226615.4882 | 2677956.6569 | 1226621.1462 | 2677977.4877 | 1226632.6269 | 2677997.5733 | 1226643.6975
107 | 2677997.5733 | 1226643.6975 | 2678006.2476 | 1226648.6812 | 2678009.5829 | 1226653.0705
108 | 2677954.2566 | 1226736.6146 | 2677964.0655 | 1226753.9103 | 2677968.0946 | 1226766.2986
109 | 2678022.1478 | 1226669.0922 | 2677952.8626 | 1226733.094 | 2677954.2566 | 1226736.6146
110 | 2678022.1478 | 1226669.0922 | 2678024.6625 | 1226662.8766 | 2678012.8867 | 1226657.4185 | 2678009.5829 | 1226653.0705
111 | 2678022.1478 | 1226669.0922 | 2678025.758 | 1226668.3502 | 2678031.4493 | 1226669.5923 | 2678038.9167 | 1226668.9231 | 2678046.0564 | 1226667.2378 | 2678051.6387 | 1226665.81 | 2678058.1938 | 1226662.4604 | 2678067.8537 | 1226655.8716 | 2678078.6499 | 1226649.3422 | 2678088.019 | 1226645.2735 | 2678092.0398 | 1226644.4368 | 2678101.1598 | 1226644.3342
112 | 2678101.1598 | 1226644.3342 | 2678101.1598 | 1226644.3342 | 2678104.7711 | 1226644.6595 | 2678107.374 | 1226645.5832 | 2678113.9759 | 1226650.288
113 | 2678138.8414 | 1226525.0332 | 2678152.5517 | 1226513.4934
114 | 2678135.0514 | 1226528.2232 | 2678138.8414 | 1226525.0332
115 | 2678135.0514 | 1226528.2232 | 2678140.6113 | 1226540.7573
116 | 2678140.6113 | 1226540.7573 | 2678141.957 | 1226543.791 | 2678142.7238 | 1226545.2829
117 | 2678147.0199 | 1226553.6418 | 2678142.7238 | 1226545.2829
118 | 2678147.0199 | 1226553.6418 | 2678152.2872 | 1226563.414
119 | 2678103.5902 | 1226560.3022 | 2678098.8027 | 1226563.7071
120 | 2678128.2764 | 1226575.9997 | 2678115.6676 | 1226582.3221
121 | 2678128.2764 | 1226575.9997 | 2678132.8876 | 1226581.7505
122 | 2678139.0976 | 1226589.4953 | 2678132.8876 | 1226581.7505
123 | 2678152.2872 | 1226563.414 | 2678158.7113 | 1226575.3322 | 2678159.2123 | 1226578.741
124 | 2678139.0976 | 1226589.4953 | 2678124.9991 | 1226601.5814
125 | 2678210.483 | 1226388.4984 | 2678218.5182 | 1226390.1257
126 | 2678106.3319 | 1226617.584 | 2678124.9991 | 1226601.5814

## bus_geodata
| x | y | coords
0 | 2678035.4686 | 1226574.3134
1 | 2678038.65 | 1226561.0244
2 | 2678042.3405 | 1226583.7262
3 | 2678057.636 | 1226548.2489
4 | 2678046.9554 | 1226590.0475
5 | 2678057.7958 | 1226548.1414
6 | 2678054.5516 | 1226595.1786
7 | 2678076.0984 | 1226535.8258
8 | 2678077.5216 | 1226534.8681
9 | 2678078.0141 | 1226578.4919
10 | 2678080.3255 | 1226576.8481
11 | 2678245.8488 | 1226677.268
12 | 2678269.1138 | 1226658.5363
13 | 2678226.6226 | 1226692.7478
14 | 2678292.6409 | 1226639.5937
15 | 2678354.0454 | 1226578.4249
16 | 2678343.5023 | 1226558.8063
17 | 2678455.1874 | 1226601.8509
18 | 2678194.5783 | 1226616.3503
19 | 2678214.144 | 1226609.3304
20 | 2678190.7162 | 1226617.7359
21 | 2678221.0523 | 1226606.8518
22 | 2678170.516 | 1226623.5752
23 | 2678229.3073 | 1226603.89
24 | 2678158.3947 | 1226635.3399
25 | 2678223.6122 | 1226585.1345
26 | 2678247.4753 | 1226597.6625
27 | 2678151.5056 | 1226605.6947
28 | 2678142.7418 | 1226594.2463
29 | 2678137.3493 | 1226646.4106
30 | 2678218.4933 | 1226568.2765
31 | 2678214.6458 | 1226555.6054
32 | 2678211.1796 | 1226544.1902
33 | 2678206.3084 | 1226528.1481
34 | 2678205.0501 | 1226524.004
35 | 2678193.9902 | 1226500.0329
36 | 2678194.5503 | 1226500.6564
37 | 2678183.0335 | 1226487.8373
38 | 2678197.3459 | 1226471.4628
39 | 2678180.1458 | 1226490.2678
40 | 2678202.3575 | 1226465.7292
41 | 2678166.9197 | 1226501.4
42 | 2678218.4234 | 1226447.3486
43 | 2678157.419 | 1226509.3967
44 | 2678262.3195 | 1226510.4388
45 | 2678257.4458 | 1226495.851
46 | 2678263.3474 | 1226513.5154
47 | 2678257.1229 | 1226494.8845
48 | 2678268.2967 | 1226528.3294
49 | 2678252.1169 | 1226479.9009
50 | 2678268.9299 | 1226530.2246
51 | 2678251.6045 | 1226478.3673
52 | 2678273.4943 | 1226543.8865
53 | 2678224.512 | 1226440.3828
54 | 2678227.9316 | 1226436.4705
55 | 2678242.6284 | 1226418.3905
56 | 2678235.731 | 1226444.5181
57 | 2678245.5127 | 1226460.1337
58 | 2678262.8965 | 1226393.4568
59 | 2678282.2365 | 1226570.7974
60 | 2678278.6418 | 1226559.5468
61 | 2678304.5846 | 1226546.8527
62 | 2678309.4522 | 1226536.9768
63 | 2678307.1158 | 1226506.5923
64 | 2678332.7865 | 1226512.0115
65 | 2678346.3886 | 1226553.1849
66 | 2678158.7105 | 1226367.1589
67 | 2678168.4097 | 1226392.8035
68 | 2678191.4059 | 1226377.0231
69 | 2678435.2207 | 1226720.323
70 | 2678423.9363 | 1226708.2297
71 | 2678336.5676 | 1226506.9356
72 | 2678099.9163 | 1226494.8507
73 | 2678119.0132 | 1226487.1517
74 | 2678085.2744 | 1226505.5292
75 | 2678271.9543 | 1226413.0891
76 | 2678272.6023 | 1226415.2069
77 | 2678307.0911 | 1226500.9882
78 | 2678284.045 | 1226464.327
79 | 2678300.6563 | 1226460.0538
80 | 2678298.5716 | 1226453.7332
81 | 2678252.6636 | 1226371.5297
82 | 2678426.9065 | 1226618.6022
83 | 2678236.6492 | 1226354.6078
84 | 2678247.0603 | 1226377.9452
85 | 2678183.9155 | 1226415.8266
86 | 2678275.7833 | 1226550.7378
87 | 2678276.9309 | 1226429.5518
88 | 2678196.0958 | 1226380.4261
89 | 2678151.5416 | 1226477.3485
90 | 2678183.903 | 1226422.6232
91 | 2678072.0891 | 1226509.3398
92 | 2678406.3033 | 1226633.0764
93 | 2678236.9142 | 1226389.5619
94 | 2678088.925 | 1226527.1949
95 | 2678091.8826 | 1226530.1855
96 | 2678103.9538 | 1226542.3912
97 | 2678113.7383 | 1226537.9334
98 | 2678111.7615 | 1226554.4907
99 | 2678014.742 | 1226573.1862
100 | 2678010.8253 | 1226571.8674
101 | 2678007.8195 | 1226593.5648
102 | 2677978.9447 | 1226579.3101
103 | 2677997.5733 | 1226643.6975
104 | 2677954.2566 | 1226736.6146
105 | 2677968.0946 | 1226766.2986
106 | 2678022.1478 | 1226669.0922
107 | 2678009.5829 | 1226653.0705
108 | 2678101.1598 | 1226644.3342
109 | 2678152.5517 | 1226513.4934
110 | 2678138.8414 | 1226525.0332
111 | 2678135.0514 | 1226528.2232
112 | 2678140.6113 | 1226540.7573
113 | 2678142.7238 | 1226545.2829
114 | 2678147.0199 | 1226553.6418
115 | 2678098.8027 | 1226563.7071
116 | 2678103.5902 | 1226560.3022
117 | 2678128.2764 | 1226575.9997
118 | 2678115.6676 | 1226582.3221
119 | 2678132.8876 | 1226581.7505
120 | 2678152.2872 | 1226563.414
121 | 2678139.0976 | 1226589.4953
122 | 2678159.2123 | 1226578.741
123 | 2678218.5182 | 1226390.1257
124 | 2678210.483 | 1226388.4984
125 | 2678124.9991 | 1226601.5814
126 | 2678106.3319 | 1226617.584
127 | 2678113.9759 | 1226650.288
128 | 2678229.3073 | 1226603.89

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98105 | -0.36409 | 0.0032063 | 0.00080357
1 | 0.98119 | -0.36127 | 0.0055588 | 0.0013932
2 | 0.98099 | -0.36534 | 0.0026459 | 0.00066313
3 | 0.98151 | -0.35517 | 0.0036506 | 0.00091494
4 | 0.98096 | -0.36582 | 0.0026202 | 0.00065668
5 | 0.98151 | -0.35511 | 0.0042252 | 0.0010589
6 | 0.98096 | -0.36594 | 0.00070204 | 0.00017595
7 | 0.98197 | -0.34608 | 0.0037428 | 0.00093802
8 | 0.98201 | -0.34527 | 0.0038802 | 0.00097247
9 | 0.98316 | -0.32295 | 0.003607 | 0.00090399
10 | 0.98316 | -0.32276 | 0.0048275 | 0.0012099
11 | 0.97285 | -0.52324 | 0.013861 | 0.0034739
12 | 0.97328 | -0.51467 | 0.013966 | 0.0035001
13 | 0.97281 | -0.52403 | 0.0017246 | 0.00043222
14 | 0.97411 | -0.49826 | 0.014228 | 0.0035658
15 | 0.97777 | -0.42641 | 0 | 0
16 | 0.9784 | -0.41404 | 0 | 0
17 | 0.97151 | -0.5493 | 0 | 0
18 | 0.99424 | -0.11029 | 0.0061926 | 0.001552
19 | 0.99526 | -0.090685 | 0.0080279 | 0.002012
20 | 0.99406 | -0.11372 | 0.0038537 | 0.00096582
21 | 0.99568 | -0.082735 | 0.0066292 | 0.0016614
22 | 0.99322 | -0.12995 | 0 | 0
23 | 0.99622 | -0.072224 | 0 | 0
24 | 0.99254 | -0.14313 | 0.0093899 | 0.0023533
25 | 0.99756 | -0.046536 | 0.0084382 | 0.0021148
26 | 0.99611 | -0.074421 | 0.006514 | 0.0016326
27 | 0.98428 | -0.30111 | 0.0076316 | 0.0019127
28 | 0.98438 | -0.29913 | 0 | 0
29 | 0.99176 | -0.15804 | 0.0028552 | 0.00071559
30 | 0.9989 | -0.020908 | 0.0073215 | 0.001835
31 | 1 | 0 | -0.61413 | -0.15735
32 | 0.99887 | -0.021321 | 0.0063904 | 0.0016016
33 | 0.9973 | -0.05099 | 0.0074484 | 0.0018668
34 | 0.9969 | -0.058556 | 0.0036695 | 0.00091966
35 | 0.99444 | -0.10523 | 0.0033116 | 0.00082996
36 | 0.99451 | -0.10378 | 0.0027287 | 0.00068388
37 | 0.99295 | -0.13351 | 0 | 0
38 | 0.99158 | -0.15976 | 0.004677 | 0.0011722
39 | 0.99285 | -0.13548 | 0.0052368 | 0.0013125
40 | 0.9911 | -0.16884 | 0.0030107 | 0.00075456
41 | 0.99171 | -0.15726 | 0.0049515 | 0.001241
42 | 0.98959 | -0.19776 | 0.002915 | 0.00073057
43 | 0.99014 | -0.18755 | 0.0026366 | 0.0006608
44 | 0.98553 | -0.27648 | 0.0033113 | 0.0008299
45 | 0.986 | -0.26736 | 0.0016603 | 0.00041611
46 | 0.98544 | -0.27821 | 0.0070508 | 0.0017671
47 | 0.98603 | -0.26672 | 0.0023801 | 0.0005965
48 | 0.98511 | -0.28457 | 0.003521 | 0.00088245
49 | 0.98657 | -0.25623 | 0.0030249 | 0.00075812
50 | 0.98508 | -0.28526 | 0.0027831 | 0.0006975
51 | 0.98663 | -0.25506 | 0.0027051 | 0.00067797
52 | 0.98486 | -0.2895 | 0.0030098 | 0.00075432
53 | 0.98902 | -0.20864 | 0.0047402 | 0.001188
54 | 0.98871 | -0.21468 | 0 | 0
55 | 0.98751 | -0.23759 | 0.0061915 | 0.0015517
56 | 0.98819 | -0.2247 | 0.003618 | 0.00090675
57 | 0.98739 | -0.24034 | 0.0036985 | 0.00092694
58 | 0.9859 | -0.26857 | 0 | 0
59 | 0.98462 | -0.29422 | 0.0064278 | 0.001611
60 | 0.98469 | -0.29285 | 0.0033193 | 0.00083189
61 | 0.98043 | -0.37459 | 0 | 0
62 | 0.98031 | -0.37693 | 0.011321 | 0.0028373
63 | 0.98101 | -0.3632 | 0 | 0
64 | 0.97998 | -0.38339 | 0 | 0
65 | 0.97834 | -0.41536 | 0.011468 | 0.002874
66 | 0.97925 | -0.39807 | 0 | 0
67 | 0.97832 | -0.41647 | 0 | 0
68 | 0.98045 | -0.37466 | 0.0041951 | 0.0010514
69 | 0.97081 | -0.56321 | 0 | 0
70 | 0.97057 | -0.56792 | 0.012013 | 0.0030108
71 | 0.97991 | -0.38472 | 0.011591 | 0.002905
72 | 0.98059 | -0.37297 | 0 | 0
73 | 0.98004 | -0.38381 | 0.015211 | 0.0038124
74 | 0.9811 | -0.36307 | 0.0077463 | 0.0019414
75 | 0.98507 | -0.2847 | 0 | 0
76 | 0.98498 | -0.28636 | 0.0046622 | 0.0011685
77 | 0.98096 | -0.36423 | 0.010217 | 0.0025605
78 | 0.98308 | -0.32311 | 0 | 0
79 | 0.98294 | -0.32587 | 0 | 0
80 | 0.98288 | -0.32695 | 0.008945 | 0.0022418
81 | 0.98397 | -0.30616 | 0 | 0
82 | 0.97081 | -0.56333 | 0.08097 | 0.020293
83 | 0.9839 | -0.30741 | 0.0029291 | 0.0007341
84 | 0.98351 | -0.31511 | 0.0034045 | 0.00085326
85 | 0.97732 | -0.43605 | 0.0039838 | 0.00099844
86 | 0.98477 | -0.29123 | 0.0036245 | 0.00090839
87 | 0.98441 | -0.29731 | 0.0016074 | 0.00040285
88 | 0.98067 | -0.3704 | 0.0047185 | 0.0011826
89 | 0.97959 | -0.3927 | 0.013643 | 0.0034191
90 | 0.97711 | -0.44007 | 0.032439 | 0.0081299
91 | 0.98156 | -0.35398 | 0 | 0
92 | 0.97054 | -0.5686 | 0.01132 | 0.002837
93 | 0.98272 | -0.33038 | 0.0030975 | 0.00077631
94 | 0.98239 | -0.33776 | 0 | 0
95 | 0.98265 | -0.33268 | 0.0035258 | 0.00088366
96 | 0.98377 | -0.31091 | 0 | 0
97 | 0.98463 | -0.29418 | 0.0034454 | 0.00086349
98 | 0.98356 | -0.31507 | 0 | 0
99 | 0.98488 | -0.29162 | 0 | 0
100 | 0.98482 | -0.29274 | 0.015055 | 0.0037731
101 | 0.98517 | -0.2858 | 0.0064533 | 0.0016174
102 | 0.98583 | -0.27305 | 0 | 0
103 | 0.98788 | -0.23309 | 0 | 0
104 | 0.98871 | -0.21714 | 0 | 0
105 | 0.9887 | -0.21733 | 0.00031855 | 7.9835e-05
106 | 0.98873 | -0.21658 | 0 | 0
107 | 0.98819 | -0.22713 | 0.0019966 | 0.00050039
108 | 0.9906 | -0.18043 | 0.0035262 | 0.00088374
109 | 0.98935 | -0.2028 | 0.0029268 | 0.00073353
110 | 0.98717 | -0.24497 | 0.0028318 | 0.00070973
111 | 0.98658 | -0.2564 | 0 | 0
112 | 0.98608 | -0.26601 | 0.0024033 | 0.00060231
113 | 0.98591 | -0.2693 | 0.0034722 | 0.00087021
114 | 0.98563 | -0.2749 | 0 | 0
115 | 0.98334 | -0.31932 | 0.0041711 | 0.0010454
116 | 0.98341 | -0.31798 | 0.0034782 | 0.00087173
117 | 0.9842 | -0.30281 | 0 | 0
118 | 0.98416 | -0.30358 | 0.0030274 | 0.00075874
119 | 0.98422 | -0.30241 | 0.0064298 | 0.0016115
120 | 0.98529 | -0.28152 | 0.0066132 | 0.0016574
121 | 0.9843 | -0.30072 | 0 | 0
122 | 0.98487 | -0.28964 | 0.0042511 | 0.0010654
123 | 0.98174 | -0.34944 | 0.0034724 | 0.00087028
124 | 0.98138 | -0.35661 | 0.0029979 | 0.00075135
125 | 0.98421 | -0.30248 | 0.003678 | 0.00092179
126 | 0.98418 | -0.30319 | 0.001598 | 0.00040051
127 | 0.99097 | -0.17339 | 0.0038936 | 0.00097582
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0091749 | -0.0022992 | 0.0091761 | 0.0022998 | 1.2294e-06 | 5.7304e-07 | 0.013916 | 0.013916 | 0.013916 | 0.98105 | -0.36409 | 0.98119 | -0.36127 | 3.8231
1 | 0.0059686 | 0.0014957 | -0.0059682 | -0.0014956 | 3.5817e-07 | 8.2084e-08 | 0.0090529 | 0.0090529 | 0.0090529 | 0.98105 | -0.36409 | 0.98099 | -0.36534 | 2.4871
2 | -0.014735 | -0.003693 | 0.014739 | 0.0036954 | 4.2851e-06 | 2.4534e-06 | 0.022346 | 0.022346 | 0.022346 | 0.98119 | -0.36127 | 0.98151 | -0.35517 | 6.139
3 | 0.0033223 | 0.00083246 | -0.0033222 | -0.00083251 | 7.4537e-08 | -5.1107e-08 | 0.0050394 | 0.0050394 | 0.0050394 | 0.98099 | -0.36534 | 0.98096 | -0.36582 | 1.3845
4 | -0.01839 | -0.0046104 | 0.01839 | 0.0046104 | 5.6142e-08 | 3.3497e-08 | 0.027881 | 0.027881 | 0.027881 | 0.98151 | -0.35517 | 0.98151 | -0.35511 | 7.6595
5 | 0.00070204 | 0.00017583 | -0.00070204 | -0.00017595 | 4.2077e-09 | -1.2222e-07 | 0.0010649 | 0.0010649 | 0.0010649 | 0.98096 | -0.36582 | 0.98096 | -0.36594 | 0.29256
6 | -0.022615 | -0.0056694 | 0.022625 | 0.0056753 | 9.7248e-06 | 5.9449e-06 | 0.034286 | 0.034286 | 0.034286 | 0.98151 | -0.35511 | 0.98197 | -0.34608 | 9.4193
7 | -0.026368 | -0.0066133 | 0.026369 | 0.006614 | 1.0271e-06 | 6.3561e-07 | 0.039958 | 0.039958 | 0.039958 | 0.98197 | -0.34608 | 0.98201 | -0.34527 | 10.9774
8 | -0.030249 | -0.0075864 | 0.03026 | 0.0075932 | 1.0829e-05 | 6.7568e-06 | 0.045837 | 0.045837 | 0.045837 | 0.98201 | -0.34527 | 0.98239 | -0.33776 | 12.5926
9 | -0.003607 | -0.00090399 | 0.003607 | 0.00090397 | 3.1698e-08 | -1.5681e-08 | 0.0054592 | 0.0054591 | 0.0054592 | 0.98316 | -0.32295 | 0.98316 | -0.32276 | 1.4998
10 | -0.0084344 | -0.0021138 | 0.0084358 | 0.0021144 | 1.3856e-06 | 5.9917e-07 | 0.012765 | 0.012765 | 0.012765 | 0.98316 | -0.32276 | 0.98334 | -0.31932 | 3.507
11 | -0.015586 | -0.0039059 | 0.015592 | 0.0039096 | 6.3653e-06 | 3.7028e-06 | 0.023839 | 0.023839 | 0.023839 | 0.97285 | -0.52324 | 0.97328 | -0.51467 | 6.5492
12 | 0.0017247 | 0.00043196 | -0.0017246 | -0.00043222 | 6.4411e-08 | -2.6525e-07 | 0.0026379 | 0.002638 | 0.002638 | 0.97285 | -0.52324 | 0.97281 | -0.52403 | 0.72472
13 | -0.029558 | -0.0074096 | 0.029581 | 0.0074241 | 2.3131e-05 | 1.4428e-05 | 0.04519 | 0.04519 | 0.04519 | 0.97328 | -0.51467 | 0.97411 | -0.49826 | 12.4149
14 | -0.043808 | -0.01099 | 0.043959 | 0.011085 | 0.00015063 | 9.5283e-05 | 0.066924 | 0.066923 | 0.066924 | 0.97411 | -0.49826 | 0.97777 | -0.42641 | 18.3857
15 | -0.14895 | -0.037639 | 0.14904 | 0.037694 | 8.8388e-05 | 5.5131e-05 | 0.22679 | 0.22679 | 0.22679 | 0.97777 | -0.42641 | 0.9784 | -0.41404 | 12.4612
16 | 0.10499 | 0.026553 | -0.10438 | -0.02618 | 0.00061521 | 0.00037374 | 0.15987 | 0.15988 | 0.15988 | 0.97777 | -0.42641 | 0.97151 | -0.5493 | 8.7845
17 | -0.16051 | -0.040568 | 0.16075 | 0.040716 | 0.00023626 | 0.00014789 | 0.24423 | 0.24423 | 0.24423 | 0.9784 | -0.41404 | 0.97998 | -0.38339 | 13.4195
18 | 0.011468 | 0.0028744 | -0.011468 | -0.002874 | 7.2053e-07 | 3.8183e-07 | 0.017442 | 0.017442 | 0.017442 | 0.9784 | -0.41404 | 0.97834 | -0.41536 | 4.7917
19 | 0.092354 | 0.023169 | -0.092292 | -0.023131 | 6.1697e-05 | 3.7859e-05 | 0.14146 | 0.14146 | 0.14146 | 0.97151 | -0.5493 | 0.97081 | -0.56333 | 9.7158
20 | 0.012024 | 0.0030104 | -0.012016 | -0.0030123 | 7.9603e-06 | -1.8752e-06 | 0.018415 | 0.018418 | 0.018418 | 0.97151 | -0.5493 | 0.97081 | -0.56321 | 1.6866
21 | -0.053779 | -0.013567 | 0.05383 | 0.013599 | 5.0538e-05 | 3.2075e-05 | 0.080519 | 0.080519 | 0.080519 | 0.99424 | -0.11029 | 0.99526 | -0.090685 | 22.1207
22 | 0.047587 | 0.012015 | -0.047579 | -0.01201 | 7.8115e-06 | 4.9462e-06 | 0.071251 | 0.071251 | 0.071251 | 0.99424 | -0.11029 | 0.99406 | -0.11372 | 19.5745
23 | -0.061858 | -0.015611 | 0.061881 | 0.015626 | 2.356e-05 | 1.4983e-05 | 0.092522 | 0.092522 | 0.092522 | 0.99526 | -0.090685 | 0.99568 | -0.082735 | 25.418
24 | 0.043725 | 0.011044 | -0.043691 | -0.011023 | 3.398e-05 | 2.1473e-05 | 0.065483 | 0.065483 | 0.065483 | 0.99406 | -0.11372 | 0.99322 | -0.12995 | 17.9898
25 | -0.068511 | -0.017287 | 0.068545 | 0.017309 | 3.4506e-05 | 2.1969e-05 | 0.10243 | 0.10243 | 0.10243 | 0.99568 | -0.082735 | 0.99622 | -0.072224 | 28.1398
26 | 0.043691 | 0.011023 | -0.043664 | -0.011005 | 2.7556e-05 | 1.7414e-05 | 0.065483 | 0.065483 | 0.065483 | 0.99322 | -0.12995 | 0.99254 | -0.14313 | 17.9898
27 | -0.07506 | -0.018942 | 0.075152 | 0.019001 | 9.2466e-05 | 5.8923e-05 | 0.11216 | 0.11216 | 0.11216 | 0.99622 | -0.072224 | 0.99756 | -0.046536 | 30.813
28 | 0.0065147 | 0.0016327 | -0.006514 | -0.0016326 | 6.8195e-07 | 1.8641e-07 | 0.0097307 | 0.0097308 | 0.0097308 | 0.99622 | -0.072224 | 0.99611 | -0.074421 | 2.6733
29 | 0.034274 | 0.0086519 | -0.034249 | -0.0086365 | 2.4469e-05 | 1.5341e-05 | 0.051405 | 0.051405 | 0.051405 | 0.99254 | -0.14313 | 0.99176 | -0.15804 | 14.1224
30 | -0.08359 | -0.021116 | 0.083693 | 0.021181 | 0.00010281 | 6.5569e-05 | 0.12475 | 0.12475 | 0.12475 | 0.99756 | -0.046536 | 0.9989 | -0.020908 | 34.2709
31 | -0.0076316 | -0.0019127 | 0.0076323 | 0.0019129 | 7.1966e-07 | 2.7731e-07 | 0.011537 | 0.011537 | 0.011537 | 0.98428 | -0.30111 | 0.98438 | -0.29913 | 3.1696
32 | -0.022368 | -0.005606 | 0.022378 | 0.0056122 | 1.0118e-05 | 6.1756e-06 | 0.033812 | 0.033812 | 0.033812 | 0.98438 | -0.29913 | 0.98487 | -0.28964 | 9.289
33 | 0.014736 | 0.0036931 | -0.014735 | -0.0036925 | 1.113e-06 | 6.363e-07 | 0.022275 | 0.022275 | 0.022275 | 0.98438 | -0.29913 | 0.9843 | -0.30072 | 6.1195
34 | 0.031394 | 0.0079209 | -0.031371 | -0.0079065 | 2.3051e-05 | 1.4395e-05 | 0.047122 | 0.047122 | 0.047122 | 0.99176 | -0.15804 | 0.99097 | -0.17339 | 12.9455
35 | -0.091015 | -0.023016 | 0.091106 | 0.023075 | 9.1381e-05 | 5.831e-05 | 0.13565 | 0.13565 | 0.13565 | 0.9989 | -0.020908 | 1 | 0 | 37.2672
36 | 0.52138 | 0.13428 | -0.52083 | -0.13393 | 0.00054031 | 0.00034502 | 0.7771 | 0.7771 | 0.7771 | 1 | 0 | 0.99887 | -0.021321 | 42.6977
37 | 0.51444 | 0.13233 | -0.5137 | -0.13186 | 0.00074083 | 0.00047304 | 0.76758 | 0.76758 | 0.76758 | 0.99887 | -0.021321 | 0.9973 | -0.05099 | 42.1746
38 | 0.50626 | 0.12999 | -0.50607 | -0.12987 | 0.00018587 | 0.00011868 | 0.75646 | 0.75646 | 0.75646 | 0.9973 | -0.05099 | 0.9969 | -0.058556 | 41.564
39 | 0.5024 | 0.12895 | -0.5013 | -0.12825 | 0.0011 | 0.00070229 | 0.75099 | 0.75099 | 0.75099 | 0.9969 | -0.058556 | 0.99451 | -0.10378 | 41.2631
40 | -0.49854 | -0.12754 | 0.49857 | 0.12757 | 3.5069e-05 | 2.239e-05 | 0.74691 | 0.74691 | 0.74691 | 0.99444 | -0.10523 | 0.99451 | -0.10378 | 41.0388
41 | 0.49522 | 0.12671 | -0.49455 | -0.12628 | 0.00067688 | 0.00043214 | 0.74195 | 0.74195 | 0.74195 | 0.99444 | -0.10523 | 0.99295 | -0.13351 | 40.7665
42 | 0.34567 | 0.088466 | -0.34523 | -0.088187 | 0.00043878 | 0.00027941 | 0.51866 | 0.51866 | 0.51866 | 0.99295 | -0.13351 | 0.99158 | -0.15976 | 28.4979
43 | 0.14888 | 0.037815 | -0.14887 | -0.037806 | 1.4114e-05 | 8.7891e-06 | 0.22329 | 0.22329 | 0.22329 | 0.99295 | -0.13351 | 0.99285 | -0.13548 | 12.2687
44 | 0.34055 | 0.087015 | -0.3404 | -0.086919 | 0.00014951 | 9.5196e-05 | 0.51164 | 0.51164 | 0.51164 | 0.99158 | -0.15976 | 0.9911 | -0.16884 | 28.1123
45 | 0.14363 | 0.036493 | -0.14348 | -0.036397 | 0.00015045 | 9.5841e-05 | 0.21544 | 0.21544 | 0.21544 | 0.99285 | -0.13548 | 0.99171 | -0.15726 | 29.5936
46 | 0.33739 | 0.086165 | -0.33692 | -0.085865 | 0.00047086 | 0.00029978 | 0.50712 | 0.50712 | 0.50712 | 0.9911 | -0.16884 | 0.98959 | -0.19776 | 27.8639
47 | 0.13853 | 0.035157 | -0.13833 | -0.035028 | 0.0002015 | 0.0001288 | 0.20801 | 0.20801 | 0.20801 | 0.99171 | -0.15726 | 0.99014 | -0.18755 | 57.1462
48 | 0.334 | 0.085134 | -0.33383 | -0.085023 | 0.00017538 | 0.00011165 | 0.50274 | 0.50274 | 0.50274 | 0.98959 | -0.19776 | 0.98902 | -0.20864 | 27.6231
49 | 0.13569 | 0.034367 | -0.13559 | -0.034303 | 9.9332e-05 | 6.3491e-05 | 0.20405 | 0.20405 | 0.20405 | 0.99014 | -0.18755 | 0.98935 | -0.2028 | 56.0576
50 | -0.033063 | -0.0082916 | 0.033078 | 0.0083007 | 1.4375e-05 | 9.0037e-06 | 0.049923 | 0.049923 | 0.049923 | 0.98553 | -0.27648 | 0.986 | -0.26736 | 13.715
51 | 0.029752 | 0.0074618 | -0.029749 | -0.0074602 | 2.4548e-06 | 1.5298e-06 | 0.044923 | 0.044923 | 0.044923 | 0.98553 | -0.27648 | 0.98544 | -0.27821 | 12.3415
52 | -0.034738 | -0.0087168 | 0.034739 | 0.0087174 | 1.0504e-06 | 6.5923e-07 | 0.052428 | 0.052428 | 0.052428 | 0.986 | -0.26736 | 0.98603 | -0.26672 | 14.4034
53 | 0.022699 | 0.0056931 | -0.022692 | -0.0056889 | 6.8814e-06 | 4.2051e-06 | 0.034276 | 0.034276 | 0.034276 | 0.98544 | -0.27821 | 0.98511 | -0.28457 | 9.4166
54 | -0.037119 | -0.0093139 | 0.037137 | 0.0093256 | 1.8591e-05 | 1.1697e-05 | 0.05602 | 0.05602 | 0.05602 | 0.98603 | -0.26672 | 0.98657 | -0.25623 | 15.3901
55 | 0.019171 | 0.0048065 | -0.01917 | -0.0048061 | 6.2833e-07 | 3.767e-07 | 0.028958 | 0.028958 | 0.028958 | 0.98511 | -0.28457 | 0.98508 | -0.28526 | 7.9555
56 | -0.040162 | -0.010084 | 0.040165 | 0.010085 | 2.2255e-06 | 1.4037e-06 | 0.060582 | 0.060582 | 0.060582 | 0.98657 | -0.25623 | 0.98663 | -0.25506 | 16.6435
57 | 0.016387 | 0.0041086 | -0.016384 | -0.0041066 | 3.3099e-06 | 1.935e-06 | 0.024754 | 0.024754 | 0.024754 | 0.98508 | -0.28526 | 0.98486 | -0.2895 | 6.8005
58 | -0.04287 | -0.010763 | 0.0429 | 0.010782 | 3.0143e-05 | 1.9046e-05 | 0.064662 | 0.064662 | 0.064662 | 0.98663 | -0.25506 | 0.98739 | -0.24034 | 17.7644
59 | 0.013374 | 0.0033523 | -0.013373 | -0.0033517 | 1.106e-06 | 6.1595e-07 | 0.020207 | 0.020207 | 0.020207 | 0.98486 | -0.2895 | 0.98477 | -0.29123 | 5.5513
60 | 0.32909 | 0.083835 | -0.32899 | -0.083774 | 9.5724e-05 | 6.093e-05 | 0.49561 | 0.49561 | 0.49561 | 0.98902 | -0.20864 | 0.98871 | -0.21468 | 27.2313
61 | 0.27872 | 0.071121 | -0.27841 | -0.070925 | 0.00030815 | 0.00019572 | 0.41993 | 0.41993 | 0.41993 | 0.98871 | -0.21468 | 0.98751 | -0.23759 | 23.0729
62 | 0.050275 | 0.012653 | -0.050251 | -0.012638 | 2.4073e-05 | 1.5263e-05 | 0.075684 | 0.075684 | 0.075684 | 0.98871 | -0.21468 | 0.98819 | -0.2247 | 20.7923
63 | 0.27222 | 0.069373 | -0.27181 | -0.069115 | 0.00040629 | 0.00025797 | 0.4106 | 0.4106 | 0.4106 | 0.98751 | -0.23759 | 0.9859 | -0.26857 | 22.5603
64 | 0.046633 | 0.011731 | -0.046598 | -0.011709 | 3.4808e-05 | 2.2037e-05 | 0.070236 | 0.070236 | 0.070236 | 0.98819 | -0.2247 | 0.98739 | -0.24034 | 19.2956
65 | 0.06163 | 0.015596 | -0.061519 | -0.015525 | 0.00011098 | 7.0594e-05 | 0.09307 | 0.093071 | 0.093071 | 0.9859 | -0.26857 | 0.98397 | -0.30616 | 25.5688
66 | 0.21018 | 0.05352 | -0.21002 | -0.053417 | 0.00016343 | 0.00010322 | 0.31753 | 0.31753 | 0.31753 | 0.9859 | -0.26857 | 0.98507 | -0.2847 | 17.4466
67 | -0.0064278 | -0.001611 | 0.0064282 | 0.0016111 | 4.1794e-07 | 1.1725e-07 | 0.0097141 | 0.009714 | 0.0097141 | 0.98462 | -0.29422 | 0.98469 | -0.29285 | 2.6687
68 | -0.0097475 | -0.002443 | 0.0097482 | 0.0024433 | 7.5354e-07 | 3.6444e-07 | 0.01473 | 0.01473 | 0.01473 | 0.98469 | -0.29285 | 0.98477 | -0.29123 | 4.0467
69 | 0.011322 | 0.0028379 | -0.011321 | -0.0028373 | 1.2658e-06 | 6.6595e-07 | 0.017184 | 0.017184 | 0.017184 | 0.98043 | -0.37459 | 0.98031 | -0.37693 | 4.7208
70 | -0.011322 | -0.0028379 | 0.011328 | 0.0028412 | 6.1478e-06 | 3.234e-06 | 0.017184 | 0.017184 | 0.017184 | 0.98043 | -0.37459 | 0.98101 | -0.3632 | 4.7208
71 | 0.010217 | 0.0025608 | -0.010217 | -0.0025605 | 5.0482e-07 | 2.5232e-07 | 0.015498 | 0.015498 | 0.015498 | 0.98101 | -0.3632 | 0.98096 | -0.36423 | 4.2576
72 | -0.19405 | -0.049128 | 0.19442 | 0.049364 | 0.00037425 | 0.00023588 | 0.29452 | 0.29451 | 0.29452 | 0.98101 | -0.3632 | 0.98308 | -0.32311 | 16.1822
73 | 0.1725 | 0.043726 | -0.17234 | -0.043621 | 0.00016722 | 0.00010497 | 0.26183 | 0.26184 | 0.26184 | 0.98101 | -0.3632 | 0.97998 | -0.38339 | 14.3865
74 | 0.011592 | 0.0029054 | -0.011591 | -0.002905 | 7.3472e-07 | 3.9055e-07 | 0.017601 | 0.017601 | 0.017601 | 0.97998 | -0.38339 | 0.97991 | -0.38472 | 4.8356
75 | 0.036495 | 0.0091738 | -0.036463 | -0.0091536 | 3.2043e-05 | 2.0159e-05 | 0.055465 | 0.055465 | 0.055465 | 0.97925 | -0.39807 | 0.97832 | -0.41647 | 15.2376
76 | -0.036495 | -0.0091738 | 0.036535 | 0.0091994 | 4.0833e-05 | 2.5687e-05 | 0.055465 | 0.055465 | 0.055465 | 0.97925 | -0.39807 | 0.98045 | -0.37466 | 15.2376
77 | 0.036463 | 0.0091536 | -0.036429 | -0.0091322 | 3.4015e-05 | 2.14e-05 | 0.055465 | 0.055465 | 0.055465 | 0.97832 | -0.41647 | 0.97732 | -0.43605 | 15.2377
78 | -0.040731 | -0.010251 | 0.040739 | 0.010256 | 8.3075e-06 | 5.2437e-06 | 0.061832 | 0.061832 | 0.061832 | 0.98045 | -0.37466 | 0.98067 | -0.3704 | 16.9867
79 | 0.012016 | 0.0030123 | -0.012013 | -0.0030108 | 2.6952e-06 | 1.463e-06 | 0.018418 | 0.018418 | 0.018418 | 0.97081 | -0.56321 | 0.97057 | -0.56792 | 5.0599
80 | 0.028875 | 0.007244 | -0.02886 | -0.0072347 | 1.4914e-05 | 9.284e-06 | 0.043819 | 0.043819 | 0.043819 | 0.98059 | -0.37297 | 0.98004 | -0.38381 | 12.0382
81 | -0.028875 | -0.007244 | 0.028888 | 0.0072525 | 1.3643e-05 | 8.4923e-06 | 0.043819 | 0.043819 | 0.043819 | 0.98059 | -0.37297 | 0.9811 | -0.36307 | 12.0382
82 | 0.013648 | 0.0034224 | -0.013643 | -0.0034191 | 5.7781e-06 | 3.2461e-06 | 0.020723 | 0.020723 | 0.020723 | 0.98004 | -0.38381 | 0.97959 | -0.3927 | 5.6932
83 | -0.036635 | -0.0091939 | 0.036651 | 0.0092039 | 1.5892e-05 | 9.9975e-06 | 0.055568 | 0.055567 | 0.055568 | 0.9811 | -0.36307 | 0.98156 | -0.35398 | 15.2658
84 | 0.21002 | 0.053417 | -0.21 | -0.053406 | 1.6747e-05 | 1.0577e-05 | 0.31753 | 0.31753 | 0.31753 | 0.98507 | -0.2847 | 0.98498 | -0.28636 | 17.4466
85 | 0.20534 | 0.052238 | -0.20523 | -0.052169 | 0.00010835 | 6.8392e-05 | 0.31048 | 0.31048 | 0.31048 | 0.98498 | -0.28636 | 0.98441 | -0.29731 | 17.0596
86 | -0.20337 | -0.051607 | 0.20362 | 0.051766 | 0.00025264 | 0.00015944 | 0.30806 | 0.30806 | 0.30806 | 0.98308 | -0.32311 | 0.98441 | -0.29731 | 16.9262
87 | 0.0089466 | 0.0022426 | -0.0089455 | -0.002242 | 1.1778e-06 | 5.3668e-07 | 0.013542 | 0.013542 | 0.013542 | 0.98308 | -0.32311 | 0.98294 | -0.32587 | 3.7204
88 | 0.0089455 | 0.002242 | -0.008945 | -0.0022418 | 4.576e-07 | 2.0853e-07 | 0.013542 | 0.013542 | 0.013542 | 0.98294 | -0.32587 | 0.98288 | -0.32695 | 3.7204
89 | 0.0029293 | 0.00073391 | -0.0029291 | -0.0007341 | 1.7457e-07 | -1.8958e-07 | 0.0044297 | 0.0044298 | 0.0044298 | 0.98397 | -0.30616 | 0.9839 | -0.30741 | 1.217
90 | 0.058589 | 0.014791 | -0.058564 | -0.014775 | 2.5098e-05 | 1.5954e-05 | 0.088641 | 0.088641 | 0.088641 | 0.98397 | -0.30616 | 0.98351 | -0.31511 | 24.3519
91 | 0.011323 | 0.0028385 | -0.01132 | -0.002837 | 2.844e-06 | 1.5089e-06 | 0.017355 | 0.017355 | 0.017355 | 0.97081 | -0.56333 | 0.97054 | -0.5686 | 4.7679
92 | 0.05516 | 0.013922 | -0.055119 | -0.013896 | 4.0317e-05 | 2.5607e-05 | 0.08349 | 0.08349 | 0.08349 | 0.98351 | -0.31511 | 0.98272 | -0.33038 | 22.9368
93 | 0.032445 | 0.0081338 | -0.032439 | -0.0081299 | 6.2198e-06 | 3.8955e-06 | 0.0494 | 0.0494 | 0.0494 | 0.97732 | -0.43605 | 0.97711 | -0.44007 | 13.5713
94 | -0.045457 | -0.011439 | 0.045487 | 0.011458 | 2.9971e-05 | 1.8969e-05 | 0.068991 | 0.068991 | 0.068991 | 0.98067 | -0.3704 | 0.98138 | -0.35661 | 18.9536
95 | -0.036651 | -0.0092039 | 0.036679 | 0.0092218 | 2.8382e-05 | 1.7855e-05 | 0.055567 | 0.055567 | 0.055567 | 0.98156 | -0.35398 | 0.98239 | -0.33776 | 15.2658
96 | 0.052022 | 0.01312 | -0.051974 | -0.01309 | 4.7411e-05 | 3.0085e-05 | 0.0788 | 0.0788 | 0.0788 | 0.98272 | -0.33038 | 0.98174 | -0.34944 | 21.6483
97 | -0.066939 | -0.016815 | 0.066955 | 0.016825 | 1.6219e-05 | 1.0327e-05 | 0.1014 | 0.1014 | 0.1014 | 0.98239 | -0.33776 | 0.98265 | -0.33268 | 27.8584
98 | -0.070481 | -0.017709 | 0.070554 | 0.017756 | 7.335e-05 | 4.6726e-05 | 0.10674 | 0.10674 | 0.10674 | 0.98265 | -0.33268 | 0.98377 | -0.31091 | 29.3252
99 | -0.086645 | -0.021791 | 0.086715 | 0.021835 | 6.9283e-05 | 4.4204e-05 | 0.13108 | 0.13108 | 0.13108 | 0.98377 | -0.31091 | 0.98463 | -0.29418 | 36.012
100 | 0.016091 | 0.0040352 | -0.016088 | -0.0040333 | 3.1967e-06 | 1.8633e-06 | 0.02434 | 0.02434 | 0.02434 | 0.98377 | -0.31091 | 0.98356 | -0.31507 | 6.6868
101 | -0.09016 | -0.022699 | 0.090323 | 0.022803 | 0.00016314 | 0.00010411 | 0.13629 | 0.13629 | 0.13629 | 0.98463 | -0.29418 | 0.98658 | -0.2564 | 37.4424
102 | 0.016088 | 0.0040333 | -0.016086 | -0.004032 | 2.2277e-06 | 1.2985e-06 | 0.02434 | 0.02434 | 0.02434 | 0.98356 | -0.31507 | 0.98341 | -0.31798 | 6.6869
103 | 0.015056 | 0.0037736 | -0.015055 | -0.0037731 | 7.9984e-07 | 4.5944e-07 | 0.022747 | 0.022747 | 0.022747 | 0.98488 | -0.29162 | 0.98482 | -0.29274 | 6.2493
104 | -0.015056 | -0.0037736 | 0.01506 | 0.003776 | 4.1762e-06 | 2.3988e-06 | 0.022747 | 0.022747 | 0.022747 | 0.98488 | -0.29162 | 0.98517 | -0.2858 | 6.2493
105 | -0.021513 | -0.0053933 | 0.021526 | 0.0054013 | 1.3081e-05 | 7.9508e-06 | 0.032494 | 0.032494 | 0.032494 | 0.98517 | -0.2858 | 0.98583 | -0.27305 | 8.927
106 | -0.021526 | -0.0054013 | 0.021567 | 0.0054263 | 4.11e-05 | 2.4978e-05 | 0.032494 | 0.032494 | 0.032494 | 0.98583 | -0.27305 | 0.98788 | -0.23309 | 8.927
107 | -0.021567 | -0.0054263 | 0.021574 | 0.00543 | 6.1437e-06 | 3.7333e-06 | 0.032494 | 0.032494 | 0.032494 | 0.98788 | -0.23309 | 0.98819 | -0.22713 | 8.9269
108 | 0.00031855 | 7.9415e-05 | -0.00031855 | -7.9835e-05 | 2.8357e-09 | -4.2025e-07 | 0.00047927 | 0.00047942 | 0.00047942 | 0.98871 | -0.21714 | 0.9887 | -0.21733 | 0.13171
109 | -0.00031855 | -7.9415e-05 | 0.00031856 | 7.8162e-05 | 8.4431e-09 | -1.2528e-06 | 0.00047927 | 0.00047883 | 0.00047927 | 0.98871 | -0.21714 | 0.98873 | -0.21658 | 0.13167
110 | 0.023582 | 0.0059377 | -0.02357 | -0.0059304 | 1.1884e-05 | 7.2831e-06 | 0.0355 | 0.0355 | 0.0355 | 0.98873 | -0.21658 | 0.98819 | -0.22713 | 9.7528
111 | -0.023901 | -0.0060158 | 0.023942 | 0.0060412 | 4.1368e-05 | 2.538e-05 | 0.035979 | 0.035979 | 0.035979 | 0.98873 | -0.21658 | 0.9906 | -0.18043 | 9.8843
112 | -0.027468 | -0.006925 | 0.027477 | 0.0069307 | 9.2602e-06 | 5.7399e-06 | 0.041275 | 0.041275 | 0.041275 | 0.9906 | -0.18043 | 0.99097 | -0.17339 | 11.3394
113 | 0.13267 | 0.03357 | -0.1324 | -0.033399 | 0.00026786 | 0.0001712 | 0.19965 | 0.19965 | 0.19965 | 0.98935 | -0.2028 | 0.98717 | -0.24497 | 54.8483
114 | 0.12957 | 0.032689 | -0.12949 | -0.032644 | 7.0913e-05 | 4.5321e-05 | 0.19538 | 0.19538 | 0.19538 | 0.98717 | -0.24497 | 0.98658 | -0.2564 | 53.6756
115 | 0.039171 | 0.009841 | -0.039153 | -0.0098297 | 1.7953e-05 | 1.1315e-05 | 0.059089 | 0.059089 | 0.059089 | 0.98658 | -0.2564 | 0.98608 | -0.26601 | 16.2333
116 | 0.03675 | 0.0092274 | -0.036744 | -0.0092238 | 5.7632e-06 | 3.6248e-06 | 0.055463 | 0.055463 | 0.055463 | 0.98608 | -0.26601 | 0.98591 | -0.2693 | 15.237
117 | 0.033272 | 0.0083536 | -0.033263 | -0.008348 | 8.8894e-06 | 5.5694e-06 | 0.050222 | 0.050222 | 0.050222 | 0.98591 | -0.2693 | 0.98563 | -0.2749 | 13.7973
118 | 0.033263 | 0.008348 | -0.033253 | -0.0083414 | 1.05e-05 | 6.5787e-06 | 0.050222 | 0.050222 | 0.050222 | 0.98563 | -0.2749 | 0.98529 | -0.28152 | 13.7973
119 | -0.012607 | -0.0031598 | 0.012608 | 0.0031603 | 8.0178e-07 | 4.3861e-07 | 0.019077 | 0.019077 | 0.019077 | 0.98334 | -0.31932 | 0.98341 | -0.31798 | 5.241
120 | 0.0030275 | 0.00075863 | -0.0030274 | -0.00075874 | 1.1082e-07 | -1.0831e-07 | 0.0045773 | 0.0045773 | 0.0045773 | 0.9842 | -0.30281 | 0.98416 | -0.30358 | 1.2575
121 | -0.0030275 | -0.00075863 | 0.0030276 | 0.00075857 | 5.7914e-08 | -5.661e-08 | 0.0045773 | 0.0045772 | 0.0045773 | 0.9842 | -0.30281 | 0.98422 | -0.30241 | 1.2575
122 | -0.0094573 | -0.00237 | 0.0094581 | 0.0023704 | 7.6106e-07 | 3.6091e-07 | 0.014298 | 0.014298 | 0.014298 | 0.98422 | -0.30241 | 0.9843 | -0.30072 | 3.9281
123 | 0.02664 | 0.006684 | -0.026629 | -0.0066776 | 1.0311e-05 | 6.3827e-06 | 0.040235 | 0.040235 | 0.040235 | 0.98529 | -0.28152 | 0.98487 | -0.28964 | 11.0535
124 | 0.0052765 | 0.0013221 | -0.0052761 | -0.001322 | 4.4309e-07 | 4.756e-08 | 0.0079766 | 0.0079767 | 0.0079767 | 0.9843 | -0.30072 | 0.98421 | -0.30248 | 2.1914
125 | 0.048502 | 0.01222 | -0.048485 | -0.012209 | 1.6625e-05 | 1.0536e-05 | 0.073537 | 0.073537 | 0.073537 | 0.98174 | -0.34944 | 0.98138 | -0.35661 | 20.2024
126 | 0.0015981 | 0.00040023 | -0.001598 | -0.00040051 | 5.3823e-08 | -2.7801e-07 | 0.002416 | 0.0024161 | 0.0024161 | 0.98421 | -0.30248 | 0.98418 | -0.30319 | 0.66377

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.62162 | 0.15923

## res_load
| p_mw | q_mvar
0 | 0.0032063 | 0.00080357
1 | 0.0055588 | 0.0013932
2 | 0.0026459 | 0.00066313
3 | 0.0036506 | 0.00091494
4 | 0.0026202 | 0.00065668
5 | 0.0042252 | 0.0010589
6 | 0.00070204 | 0.00017595
7 | 0.0037428 | 0.00093802
8 | 0.0038802 | 0.00097247
9 | 0.003607 | 0.00090399
10 | 0.0048275 | 0.0012099
11 | 0.013861 | 0.0034739
12 | 0.013966 | 0.0035001
13 | 0.0017246 | 0.00043222
14 | 0.014228 | 0.0035658
15 | 0.0061926 | 0.001552
16 | 0.0080279 | 0.002012
17 | 0.0038537 | 0.00096582
18 | 0.0066292 | 0.0016614
19 | 0.0093899 | 0.0023533
20 | 0.0084382 | 0.0021148
21 | 0.006514 | 0.0016326
22 | 0.0076316 | 0.0019127
23 | 0.0028552 | 0.00071559
24 | 0.0073215 | 0.001835
25 | 0.0074871 | 0.0018764
26 | 0.0063904 | 0.0016016
27 | 0.0074484 | 0.0018668
28 | 0.0036695 | 0.00091966
29 | 0.0033116 | 0.00082996
30 | 0.0027287 | 0.00068388
31 | 0.004677 | 0.0011722
32 | 0.0052368 | 0.0013125
33 | 0.0030107 | 0.00075456
34 | 0.0049515 | 0.001241
35 | 0.002915 | 0.00073057
36 | 0.0026366 | 0.0006608
37 | 0.0033113 | 0.0008299
38 | 0.0016603 | 0.00041611
39 | 0.0070508 | 0.0017671
40 | 0.0023801 | 0.0005965
41 | 0.003521 | 0.00088245
42 | 0.0030249 | 0.00075812
43 | 0.0027831 | 0.0006975
44 | 0.0027051 | 0.00067797
45 | 0.0030098 | 0.00075432
46 | 0.0047402 | 0.001188
47 | 0.0061915 | 0.0015517
48 | 0.003618 | 0.00090675
49 | 0.0036985 | 0.00092694
50 | 0.0064278 | 0.001611
51 | 0.0033193 | 0.00083189
52 | 0.011321 | 0.0028373
53 | 0.011468 | 0.002874
54 | 0.0041951 | 0.0010514
55 | 0.012013 | 0.0030108
56 | 0.011591 | 0.002905
57 | 0.015211 | 0.0038124
58 | 0.0077463 | 0.0019414
59 | 0.0046622 | 0.0011685
60 | 0.010217 | 0.0025605
61 | 0.008945 | 0.0022418
62 | 0.08097 | 0.020293
63 | 0.0029291 | 0.0007341
64 | 0.0034045 | 0.00085326
65 | 0.0039838 | 0.00099844
66 | 0.0036245 | 0.00090839
67 | 0.0016074 | 0.00040285
68 | 0.0047185 | 0.0011826
69 | 0.013643 | 0.0034191
70 | 0.032439 | 0.0081299
71 | 0.01132 | 0.002837
72 | 0.0030975 | 0.00077631
73 | 0.0035258 | 0.00088366
74 | 0.0034454 | 0.00086349
75 | 0.015055 | 0.0037731
76 | 0.0064533 | 0.0016174
77 | 0.00031855 | 7.9835e-05
78 | 0.0019966 | 0.00050039
79 | 0.0035262 | 0.00088374
80 | 0.0029268 | 0.00073353
81 | 0.0028318 | 0.00070973
82 | 0.0024033 | 0.00060231
83 | 0.0034722 | 0.00087021
84 | 0.0041711 | 0.0010454
85 | 0.0034782 | 0.00087173
86 | 0.0030274 | 0.00075874
87 | 0.0064298 | 0.0016115
88 | 0.0066132 | 0.0016574
89 | 0.0042511 | 0.0010654
90 | 0.0034724 | 0.00087028
91 | 0.0029979 | 0.00075135
92 | 0.003678 | 0.00092179
93 | 0.001598 | 0.00040051
94 | 0.0038936 | 0.00097582

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1